## PLANT CHECK
BULL CREEK PLANT CHECK
SHEET KEY
DATE/TIME |  | 2019-08-12 09:03 |  |  |  |  | OPERATOR |  | CW/DH |  |  | FILL IN BEFORE GOING ON PLANT CK.
FILL IN AFTER GOING ON PLANT CK.
Raw Water Pumps |  |  | 2,3,5 |  |  | Raw UV | 0.384 | mg/l |  |  |  | FOR MIDNIGHT PLANT OK
Caison Level |  | 8.6 | SCADA Raw flow |  | 26.9 | Raw TOC | 10.1053 | mg/l |  |  |  | THIS IS WHAT YOU TRANSFER TO DAILY
Control Valve% Open Raw |  |  | 47 | Plant 1 | 76 | Plant 2 | 99 | Plant 3 | 41 |  |  | NO NEED TO TYPE IN THESE BLANKS FOR ROUNDS ONLY
MGD
Total Raw Flow |  |  | 26.9 |  | MGD | Fin North1 Flow |  | 3590 | 5.1696 | Master Meter Readings
Plant 1 Raw Flow |  |  | 10.3 |  | MGD | Fin 1 Pumps |  | 7 |  | South 1 |  | 23189612
Plant 2 Raw Flow |  |  | 10.3 |  | MGD | Fin Coastal1 Flow |  | 3782 | 5.4461 | South 2 |  | 41058995
Plant 3 Raw Flow |  |  | 6.3 |  | MGD | Fin 1 Pumps |  | 1 |  | Conway |  | 8782604
Total Filter Flow |  |  | 25.5 |  | MGD | Fin Perry 2 Flow |  | 6080 | 8.7552 | Perry |  | 30571784
Plant 1 Filter Flow |  |  | 8.5 |  | MGD | Fin 2 Pumps |  | 1,2 |  | Raw PLT 1 |  | 28096432
Plant 2 Filter Flow |  |  | 8.5 |  | MGD | Fin Conway 2 Flow |  | 3074 | 4.4266 | Raw PLT 2 |  | 28042889
Plant 3 Filter Flow |  |  | 8.5 |  | MGD | Fin 2 Pumps |  | 1,2 |  | Raw PLT 3 |  | 4331704
[12 empty] | Flow | Totalizer
Chemical |  |  | DOSE |  | Calculated |  | Measured |  |  | Decant Weir flow |  | 1263 | 1414683
|  |  | ppm |  | Feed ml/min |  | Feed ml/min |  |  | Sludge Bl.Dwn meter |  | 0.438 | 8776.9217
Alum | DESIRED DOSE |  | 75 |  | 3159.525 |  | 2750 |  |  | Thickener Torque 1 |  | 20 | Sludge Judge | 2 | feet
[5 empty] | 3159.525 |  | 2800 |  |  | Thickener Torque 2 |  |  | Sludge Judge
[5 empty] | 1975.05 |  | 2750 |  |  | BACKWASH WATER USED
[5 empty] | 8251.575 |  | 8300 |  | 75.4401 |  |  | Tank Levels
[12 empty] | BULK |  | 24h Chem. Used | FINISH 24HR
Polymer | Plant 1 | basin 1 | 0.2 |  | 361.0845 |  | 360 |  | 0.19939 | Alum |  | 9022 | 6466 | 2791 | 3945
NUMBER OF BASIN | 2 | basin 2 | 0.2 |  | 361.0845 |  | 330 |  | 0.18277 | Caustic 1 |  | 4818 |  | 166 | 397
Polymer | Plant 2 | basin 3 | 0.18 |  | 324.976 |  | 380 |  | 0.21046 | Caustic 3 |  | 3817 |  | 75 | 382
NUMBER OF BASIN | 2 | basin 4 | 0.18 |  | 324.976 |  | 370 |  | 0.20493 | CL2 Pre/Post |  | 10'/422
Polymer | Plant 3 | basin 5 | 0.18 |  | 198.7718 |  | 425 |  | 0.38484 | CL2 Post |  | 23'
NUMBER OF BASIN | 2 | basin 6 | 0.18 |  | 198.7718 |  | 100 |  | 0.090551 | Phosphate |  | 1904 |  | 34 | 450
Polymer |  | Thickener | 0.8 |  |  |  | 500 |  | 0.95112 | Fluoride
Fliter Aid |  | plt1 | 0.06 |  | 966.6818 |  | 960 |  | 0.059585 | CAL~FLO |  | 12.25 |  |  | 10.5
Fliter Aid |  | plt2 | 0.06 |  | 966.6818 |  | 960 |  | 0.059585 | Zinc |  | 3213 |  | 4 | 54
Fliter Aid |  | plt3 | 0.06 |  | 966.6818 |  | 950 |  | 0.058965 | Polymer PLT 1 |  |  |  | 3 | 25
[11 empty] | Polymer PLT 3 |  |  | 2.5 | 29
Chlorine |  | Pre 1 | 1.7 |  | 324.6276 |  | 300 |  | 1.571 | Ammonia |  | 9.39
Chlorine |  | Pre 2 | 1.6 |  | 305.5318 |  | 340 |  | 1.7805 | Hylime LBS/Day
Chlorine |  | Pre 3 | 1.7 |  | 324.6276 |  | 330 |  | 1.7281 | PAC LBS/Day |  | 675
BI-SULFITE
Caustic |  | Post 1 | 7.5 |  | 436.9704 |  | 480 |  | 8.2385 | FILTER AIDE |  | 15 |  | 28
Caustic |  | Post 2 | 7.5 |  | 218.4852 |  | 190 |  | 6.5222 |  |  |  | ALUM TOWER |  | 7.5
Caustic |  | Pre 1 | 0 |  | 0 |  |  |  | 0
Caustic |  | Pre 2 | 0 |  | 0 |  |  |  | 0
Caustic |  | Pre 3 | 0 |  | 0 |  |  |  | 0
Chemical |  |  |  |  | Calculated |  |  |  | Calculated
|  |  | Plant 1&2 | Plt 3 | Fin 1 ml/min |  |  |  | Fin 2 ml/min
Chlorine |  | Post | 4.3 | 3.2 | 1496.2491 | 4.3101 | 1500 |  | 521.7307 | 3.1907 | 520
Phosphate |  |  | 1.1 |  | 81.345 | 1.2306 | 91 |  | 40.6725 | 1.0818 | 40
Zinc |  |  | 0.1 |  | 11.7658 | 0.10199 | 12 |  | 5.8829 | 0.10199 | 6
Ammonia | All Cl2 / | 5.185 | 0.81939 |  | 305.357 | 0.81843 | 305 |  | 106.4757 | 0.56351 | 105
Fluoride |  |  | 0.5 |  | 98.1267 | 0.49935 | 98 |  | 49.0633 | 0.39745 | 39
Hylime Pounds per Day |  |  | 0 | Pump Speed |  | 0 | PPM | 0 |  |  | PLT 1 | PLT 2 | PLT 3 | RAW |  |  | FIN 1 NH3 | [6 empty] | FIN 2 NH3
PAC Pounds per Day |  |  | 675 | Pump Speed |  | 60 | PPM | 3.0087 | Cal~flow Pump % |  |  |  |  | 69 |  |  | (((((D14+D15)*8.34*((D46)/E57)/(E58/100)))/7.74)*3785/1440) | [6 empty] | ((((D16*8.34*(E46/E57)/(E58/100)))/7.74)*3785/1440)
[10 empty] | PPM | #N/A | #N/A | #N/A | 4242.6302
Free Chlorine on Filters |  |  | PLT 1 | 0.3 |  | 0.27 | PLT 3 | 0.4
Chlorine Strenght % weight/volume |  |  |  |  | Post | 2 | Pre | 0.1 |  | min CT | TARGET CT |  | Stream Current
Post Chlorine Dose / Ammonia Dose |  |  |  | 4.9 |  | Decant Ph | 5.68 |  | CT PLT 1 | 0.32 | 0.42 | PLT 1
Aquos Ammonia %Strength |  |  |  | 19.5 |  | Decant cl2 | 0.02 |  | CT PLT 2 | 0.32 | 0.42 | PLT 2
CL2 SPG | 1.17 |  | NH3 SPG | 0.928 |  | Decant pump | 17 |  | CT PLT 3 | 0.22 | 0.32 | PLT 3
| RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [8 empty] | SETTLED | [8 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
|  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW |  |  | DOSE |  |  |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  |  |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST
TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL |  | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLY THICKENER | DECANT | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC
0:00
43689.3771 | 2,3,5 | 47 | 10.3 | 10.3 | 6.3 | 26.9 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.6157 | 1,2 | 13.1818 | 23.7974 | 1.8187 | 43689.3771 | 75.4401 | 4242.6302 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.7805 | 1.7281 | 0.19939 | 0.18277 | 0.21046 | 0.20493 | 0.38484 | 0.090551 | 0.95112 | 2 | 0.059585 | 0.059585 | 0.058965 | 1.2306 | 0.49935 | 0.10199 | 4.3101 | 0.81843 | 8.2385 | 1.0818 | 0.39745 | 0.10199 | 3.1907 | 0.56351 | 6.5222
[18 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 300 | 340 | 330 | 360 | 330 | 380 | 370 | 425 | 100 | 500 |  | 960 | 960 | 950 | 91 | 98 | 12 | 1500 | 305 | 480 | 40 | 39 | 6 | 520 | 105 | 190
BULK TANK Chemical Inventory
[33 empty] | Alum | 9022 |  | 6466 |  | 0
[33 empty] | Caustic | 4818 |  | 3817
[33 empty] | Hypochlorite | 10'/422 |  | 23'
[33 empty] | Phosphate | 1904
[33 empty] | Fluoride | 0
[33 empty] | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92
[33 empty] | Zinc | 3213
[33 empty] | Polymer | 0 |  | DRUMS
[33 empty] | NH3 | 9.39
[33 empty] | Lime | 0
[33 empty] | Cabon | 675
[33 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[33 empty] | Alum | 2791 | Phosphate | 34
[33 empty] | Caustic 1 | 166 | Fluoride | 0
[33 empty] | Caustic 2 | 75 | Zinc | 4
[33 empty] | Hypochlorite 1 | 0 | Polymer 1 | 3
[33 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2.5
[34 empty] | FINISHED SOUTH 1 |  | END: | 23189612
[34 empty] | FINISHED SOUTH 2 |  | END: | 41058995
[34 empty] | FINISHED CONWAY |  | END: | 8782604
[34 empty] | FINISHED PERRY |  | END: | 30571784
[34 empty] | RAW PLANT 1 |  | END: | 28096432
[34 empty] | RAW PLANT 2 |  | END: | 28042889
[34 empty] | RAW PLANT 3 |  | END: | 4331704
[34 empty] | DECANT |  | END: | 1414683
[34 empty] | BLOW DOWN |  | END: | 8776.9217
Note on M3: Ctrl+s Will save the sheet
Note on M4: Ctrl+m Will remove all ml/min
Note on M5: Ctrl+o Will remove all Master Meter
Note on D12: PLANT 3 FLOW IS MAX FOR CT CAL. IN LESS BASIN IS DOWN
Note on D20: RAW FLOW X mg/Lx4.18=ml/min Ex. 29.9x61.6x4.18=Total PPM
Note on O25: TOTAL GAL. CHEMICAL USED 24HR FROM TRANSFER SHEETS
Note on P25: CHEMICAL FINISH 24HR LEVEL FROM LEVEL INDICATOR
Note on D26: ((7500*PPM*1440)/(1000*1000*454))/(FLOW*8.34)*#OF BASIN
Note on M34: TANK LEVEL FROM THE DAY BEFORE FROM DAY BEFORE SHEET
Note on N34: TRUCK IN
Note on O34: TRUCK OUT
Note on P34: LEVEL
Note on M35: IN THE CHEM BUILDING
Note on N35: OUTSIDE
Note on M36: NUMBER ONLY
Note on O36: NUMBERS ONLY
Note on M39: FROM SCADA TOTAL LBS YESTERDAY
Note on M40: FROM SCADA TOTAL LBS YESTERDAY
Note on D50: DOSE - AVG FILTER RES PLT 1 & PLT 2 X 8.34 X FIN FLOW PLT 1 PLT 2 /%SOL/(8.34 X SPF) X 3785 / 1440 = ML/MIN
Note on D51: Fin Flow X PPM X 4.35= ML/MIN
Note on D52: PPM X 2.63 / .38 X FLOW= ML/MIM
Note on D53: ML/MIN X 1440 / 3785 / FLOW / 8.34 = PPM
Note on F53: FOLW X 8.34 X ((CL2 mg/l / CL2/NH3) / (NH3% / 100) / 7.74) X 3785 / 1440 = ML/MIN
Note on D54: ML/MIN/2.63*1.9/8.34/FLOW=PPM
Note on AI81: from day before
Note on AK81: Truck out
Note on AL81: 12:00

## LIME CAL (hidden)
PUMP % | MIL/MIN | FOR CALCULATION FACTOR
5 | 307.4366 | #N/A | #N/A | #N/A | 65
6 | 368.924
7 | 430.4114
8 | 491.8988
9 | 553.3862
10 | 614.8736
11 | 676.361
12 | 737.8484
13 | 799.3358
14 | 860.8232
15 | 922.3106
16 | 983.798
17 | 1045.2854
18 | 1106.7728
19 | 1168.2602
20 | 1229.7476
21 | 1291.235
22 | 1352.7224
23 | 1414.2098
24 | 1475.6972
25 | 1537.1846
26 | 1598.672
27 | 1660.1594
28 | 1721.6468
29 | 1783.1342
30 | 1844.6216
31 | 1906.109
32 | 1967.5964
33 | 2029.0838
34 | 2090.5712
35 | 2152.0586
36 | 2213.546
37 | 2275.0334
38 | 2336.5208
39 | 2398.0082
40 | 2459.4956
41 | 2520.983
42 | 2582.4704
43 | 2643.9578
44 | 2705.4452
45 | 2766.9326
46 | 2828.42
47 | 2889.9074
48 | 2951.3948
49 | 3012.8822
50 | 3074.3696
51 | 3135.857
52 | 3197.3444
53 | 3258.8318
54 | 3320.3192
55 | 3381.8066
56 | 3443.294
57 | 3504.7814
58 | 3566.2688
59 | 3627.7562
60 | 3689.2436
61 | 3750.731
62 | 3812.2184
63 | 3873.7058
64 | 3935.1932
65 | 3996.6806
66 | 4058.168
67 | 4119.6554
68 | 4181.1428
69 | 4242.6302
70 | 4304.1176
71 | 4365.605
72 | 4427.0924
73 | 4488.5798
74 | 4550.0672
75 | 4611.5546
76 | 4673.042
77 | 4734.5294
78 | 4796.0168
79 | 4857.5042
80 | 4918.9916
81 | 4980.479
82 | 5041.9664
83 | 5103.4538
84 | 5164.9412
85 | 5226.4286
86 | 5287.916
87 | 5349.4034
88 | 5410.8908
89 | 5472.3782
90 | 5533.8656
91 | 5595.353
92 | 5656.8404
93 | 5718.3278
94 | 5779.8152
95 | 5841.3026
96 | 5902.79
97 | 5964.2774
98 | 6025.7648
99 | 6087.2522
100 | 6148.7396
101 | 6210.227
102 | 6271.7144
103 | 6333.2018
104 | 6394.6892
105 | 6456.1766
106 | 6517.664
107 | 6579.1514
108 | 6640.6388
109 | 6702.1262
110 | 6763.6136
111 | 6825.101
112 | 6886.5884
113 | 6948.0758
114 | 7009.5632
115 | 7071.0506
116 | 7132.538
117 | 7194.0254
118 | 7255.5128
119 | 7317.0002
120 | 7378.4876
121 | 7439.975
122 | 7501.4624
123 | 7562.9498
124 | 7624.4372
125 | 7685.9246
126 | 7747.412
127 | 7808.8994
128 | 7870.3868
129 | 7931.8742
130 | 7993.3616
131 | 8054.849
132 | 8116.3364
133 | 8177.8238
134 | 8239.3112
135 | 8300.7986
136 | 8362.286
137 | 8423.7734
138 | 8485.2608
139 | 8546.7482
140 | 8608.2356
141 | 8669.723
142 | 8731.2104
143 | 8792.6978
144 | 8854.1852
145 | 8915.6726
146 | 8977.16
147 | 9038.6474
148 | 9100.1348
149 | 9161.6222
150 | 9223.1096
151 | 9284.597
152 | 9346.0844
153 | 9407.5718
154 | 9469.0592
155 | 9530.5466
156 | 9592.034
157 | 9653.5214
158 | 9715.0088
159 | 9776.4962
160 | 9837.9836
161 | 9899.471
162 | 9960.9584
163 | 10022.4458
164 | 10083.9332
165 | 10145.4206
166 | 10206.908
167 | 10268.3954
168 | 10329.8828
169 | 10391.3702
170 | 10452.8576
171 | 10514.345
172 | 10575.8324
173 | 10637.3198
174 | 10698.8072
175 | 10760.2946
176 | 10821.782
177 | 10883.2694
178 | 10944.7568
179 | 11006.2442
180 | 11067.7316
181 | 11129.219
182 | 11190.7064
183 | 11252.1938
184 | 11313.6812
185 | 11375.1686
186 | 11436.656
187 | 11498.1434
188 | 11559.6308
189 | 11621.1182
190 | 11682.6056
191 | 11744.093
192 | 11805.5804
193 | 11867.0678
194 | 11928.5552
195 | 11990.0426
196 | 12051.53
197 | 12113.0174
198 | 12174.5048
199 | 12235.9922
200 | 12297.4796
201 | 12358.967
202 | 12420.4544
203 | 12481.9418
204 | 12543.4292
205 | 12604.9166
206 | 12666.404
207 | 12727.8914
208 | 12789.3788

## TIMER LOG
DATE | 2019-08-12 09:03 |  | TIME | 43689.3771 | OPERATOR | CW/DH
PUMP AND MOTOR RUN TIME LOG
LOCATION | RUN TIMES |  |  | PRESSURE/AMPS |  | Comments
EQUIPMENT NAME |  |  |  |  | RUNNING
South Pump #1 |  | Hr |  | AMPS |  | PSI
South Pump #2 |  | Hr |  | AMPS
South Pump #3 |  | Hr |  | AMPS
South Pump #4 |  | Hr |  | AMPS
North Pump #5 |  | Hr |  | AMPS |  | PSI
North Pump #6 |  | Hr |  | AMPS
North Pump #7 |  | Hr |  | AMPS
North Pump #8 |  | Hr |  | AMPS
Finish Vac Pump #1 |  | Hr |  | in
Finish Vac Pump #2 |  | Hr |  | in
Service Water Pump #1 |  | Hr |  | PSI
Service Water Pump #2 |  | Hr |  | PSI
Service Water Pump #3 |  | Hr |  | PSI
Hydro Tank Compressor |  | Hr |  | PSI
Sludge Spray Pump #1 |  | Hr
Sludge Spray Pump #2 |  | Hr
Sludge Spray Pump #3 |  | Hr
Sludge Bl. Dwn Pump #1 |  | Hr
Sludge Bl. Dwn Pump #2 |  | Hr
Spill Lagoon Pump #1 |  | Hr
Spill Lagoon Pump #2 |  | Hr
Boge Compressor Lime Pack |  | Hr |  | Temp
Lime Pack Compressor #1 |  | Hr
Plant #3 Filter Blower #1 |  | Hr
Plant #3 Filter Blower #2 |  | Hr
Plant #3 Compressor #1 |  | Hr
Plant #3 Compressor #2 |  | Hr
Boge Compressor Plant #3 |  |  |  | Temp

## CHEM 1
CHEMICAL TRANSFER SHEET PLANT 3 | [7 empty] | CHEMICAL TRANSFER SHEET PLANT 1 and 2
DATE | 2019-08-12 09:03 | TIME | 43689.3771 | OPERATORS |  | CW/DH |  | DATE | 2019-08-12 09:03 | TIME | 43689.3771 |  | OPERATORS |  | CW/DH
ALUM START 24HR. LEVEL |  |  |  | GAL. |  |  |  |  | PAC TOTAL |  | LB/DAY |  | LIME TOTAL |  |  | GAL/DAY
START |  | GAL. FINISH |  | GAL. |  |  |  |  | AMMONIA |  | GAL/DAY |  | CHLORINE |  |  | GAUDAY
START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER START 24HR. LEVEL |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | TOTAL GAL. POLYMER USED 24HR.
START |  | GAL. FINISH |  | GAL.
| FINISH 24HR. LEVEL |  |  | GAL.
|  |  |  | TOTAL GAL. ALUM USED 24HR. |  |  | GAL. | CAUSTIC START 24HR. LEVEL |  |  |  | GAL.
[8 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
POLYMER START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL.
POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | [8 empty] | TOTAL GAL. CAUSTIC USED 24HR.
TOTAL GAL. POLYMER USED 24HR.
[8 empty] | PHOSPHATE START 24HR. LEVEL |  |  |  | GAL.
CAUSTIC START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. |  | START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | PHOSPHATE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. PHOSPHATE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | ZINC CHLORIDE START 24HR. LEVEL |  |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL. |  |  |  | ZINC CHLORIDE FINISH 24HR. LEVEL |  |  |  |  | GAL. | TOTAL GAL. ZINC USED 24HR.
|  |  |  | TOTAL GAL. CAUSTIC USED 24HR. |  |  | GAL.
[8 empty] | FILTER AIDE START 24HR. LEVEL |  |  |  | GAL.
PRE HYPOCHLORITE START 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER AIDE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. FILTER AIDE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
PRE HYPOCHLORITE FINISH 24HR. LEVEL |  |  |  |  | GAL. | FINISH
|  |  | TOTAL GAL. HYPOCHLORITE USED 24HR. |  |  |  | GAL
FILTER AIDE START 24HR. LEVEL
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER CAUSTIC START 24HR. LEVEL | [5 empty] | GAL.
FILTER AIDE FINISH 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH
[8 empty] | FILTER CAUSTIC FINISH 24HR. LEVEL | [6 empty] | GAL.
LIME START |  |  | FT FINISH |  | FT TOTAL | [6 empty] | TOTAL FILT. CAUSTIC USED 24HR. |  |  |  |  | GAL.

## 1
DATE: | 2018-02-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-01 | [23 empty] | DATE: | 2018-02-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43132.0164 | 1,3,6 | 32 | 5.5 | 9.8 | 9.8 | 25.1 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 9.5069 | 1,2 | 15.0264 | 24.5333 | 1.0066 | 43132.0164 | 39.938 | #N/A | 0 | 620 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0272 | 1.5694 | 1.4267 | 0.14521 | 0.093349 | 0.16008 | 0.16008 | 0.13389 | 0.11642 | 1.4267 | 1 | 0.060874 | 0.060874 | 0.060874 | 1.1052 | 0.49975 | 0.10188 | 4.3099 | 0.78953 | 9.352 | 1.12 | 0.38869 | 0.09262 | 3.0733 | 0.5556 | 6.5464 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6 | 0.353 | 4 | 0.59 | 11.1 | 5.9 | 0.42149 |  | 6.05 | 0.396 | 4 | 0.67 | 10.5 | 10.4 | 0.73321 | 6.08 | 0.503 | 4 | 0.67 | 11.9 | 10.7 | 0.71444 | [13 empty] | 7.3 | 0.056 | 1 | 4.1 | 10.4 |  |  |  | 7.9 | 0.053 | 1 | 3.9 | 10.6 |  |  |  | 3.6 | 3.6 | 3.1 | [18 empty] | 4100 | [6 empty] | 0 | 0 | 0 | 180 | 275 | 250 | 280 | 180 | 275 | 275 | 230 | 200 | 750 |  | 900 | 900 | 900 | 75 | 90 | 11 | 1320 | 270 | 500 | 38 | 35 | 5 | 440 | 95 | 175 |  | 1:00 | 0.59 | 5.9 | 43.1186 | 25.44 | 6 | 11.1 | 13 | 1.9569 | 10 | 6 | 0.30149 | 1:00 | 0.67 | 10.4 | 24.4615 | 16.3892 | 6.05 | 10.5 | 15 | 1.0926 | 10 | 6.5 | 0.61321 | 1:00 | 0.67 | 10.7 | 25.2336 | 16.9065 | 6.08 | 11.9 | 15 | 1.1271 | 10 | 6.5 | 0.59444
2:00 | [72 empty] | 43132.0516 | 3,1,6 | 34 | 6.5 | 10.3 | 10.3 | 27.1 | 8.6 | 8.6 | 8.6 | 25.8 | 7,1 | 9.0518 | 1,2 | 15.7421 | 24.7939 | 0 | 43132.0516 | 39.6972 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0352 | 1.5528 | 1.5528 | 0.24574 | 0.15798 | 0.15231 | 0.15231 | 0.12739 | 0.11077 | 1.4267 | 0 | 0.055212 | 0.055212 | 0.055212 | 1.0024 | 0.45326 | 0.092404 | 3.9509 | 0.71609 | 9.4151 | 1.0158 | 0.45326 | 0.084004 | 2.8339 | 0.50391 | 6.5142 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.92 | 24 | 19 | 8.29 | 48 | 87 | 11.1 | 0.197 |  | 6.06 | 10 | 0.054 | 6.09 | 10 |  | 6.04 | 10 | [8 empty] | 0.036 | [14 empty] | 0.027 | 1 | 0.39 |  | 0.037 | 0.023 | 1 | 0.46 |  | 0.029 | 1 | 0.59 | [38 empty] | 4400 | [6 empty] | 0 | 0 | 0 | 200 | 300 | 300 | 280 | 180 | 275 | 275 | 230 | 200 | 750 |  | 900 | 900 | 900 | 75 | 90 | 11 | 1320 | 270 | 555 | 38 | 45 | 5 | 440 | 95 | 192 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43132.3355 | 3,1,6 | 40 | 6 | 10.5 | 10.6 | 27.1 | 8.6 | 8.6 | 8.6 | 25.8 | 7,1 | 9.0518 | 1,2 | 15.7421 | 24.7939 | 1.1922 | 43132.3355 | 40.3468 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0.98342 | 1.3457 | 1.501 | 0.21868 | 0.16163 | 0.13039 | 0.15484 | 0.15069 | 0.15069 | 0 | 1.5 | 0.061346 | 0.061346 | 0.060119 | 1.0158 | 0.49858 | 0.1008 | 4.057 | 0.71609 | 9.4151 | 1.0158 | 0.4029 | 0.1008 | 2.94 | 0.66304 | 6.5142 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.31 | 0.054 | 1 | 4 | 10.3 |  |  |  | 7.92 | 0.056 | 1 | 3.9 | 10.7 |  |  |  | 3.6 | 3.6 | 3.2 | [18 empty] | 4472 | [6 empty] | 0 | 0 | 0 | 190 | 260 | 290 | 230 | 170 | 240 | 285 | 280 | 280 | 0 |  | 1000 | 1000 | 980 | 76 | 99 | 12 | 1360 | 270 | 555 | 38 | 40 | 6 | 460 | 125 | 192 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43132.8299 | 3,1,6 | 38 | 6 | 10.5 | 10.5 | 27 | 8.6 | 8.6 | 8.6 | 25.8 | 7,1 | 8.9035 | 1,2 | 18.6667 | 27.5702 | 0.93168 | 43132.8299 | 40.4962 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0.98342 | 1.294 | 1.4492 | 0.19016 | 0.16163 | 0.11953 | 0.10866 | 0.13583 | 0.076062 | 1.2745 | 1 | 0.061346 | 0.061346 | 0.061346 | 1.096 | 0.49858 | 0.1008 | 4.168 | 0.71609 | 9.4999 | 1.096 | 0.4029 | 0.1008 | 3.3243 | 0.68957 | 6.5142 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.99 | 26 | 19 | 12.1 | 39 | 105 | 10.4 | 0.207 |  | 6 | 10 | 0.047 | 6.02 | 10 |  | 6 | 10 | [8 empty] | 0.04 | [14 empty] | 0.05 | 1 | 0.64 |  | 0.039 | 0.034 | 1 | 0.62 |  | 0.034 | 1 | 0.54 | [38 empty] | 4472 | [6 empty] | 0 | 0 | 0 | 190 | 250 | 280 | 200 | 170 | 220 | 200 | 250 | 140 | 670 |  | 1000 | 1000 | 1000 | 82 | 99 | 12 | 1400 | 270 | 560 | 41 | 40 | 6 | 540 | 130 | 192 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.054 | [9 empty] | 5.94 | 0.433 | 4 | 0.56 | 10.5 | 6 | 0.4266 |  | 5.99 | 0.465 | 4 | 0.68 | 10.2 | 10.4 | 0.65145 | 5.97 | 0.563 | 4 | 0.65 | 11.8 | 10.5 | 0.62556 |  |  |  | 0.011 | [9 empty] | 7.38 | 0.051 | 1 | 4.1 | 10.3 | 27 | 29 | 0.019 | 7.49 | 0.053 | 1 | 4.1 | 10.6 | 29 | 32 | 0.016 | 3.6 | 3.9 | 3.4 | [55 empty] | 9:00 | 0.56 | 6 | 42.4 | 23.744 | 5.94 | 10.5 | 13 | 1.8265 | 10 | 6 | 0.3066 | 9:00 | 0.68 | 10.4 | 24.4615 | 16.6338 | 5.99 | 10.2 | 13 | 1.2795 | 10 | 6 | 0.53145 | 9:00 | 0.65 | 10.5 | 25.7143 | 16.7143 | 5.97 | 11.8 | 13 | 1.2857 | 10 | 6 | 0.50556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.99 | 25 | 19 | 10.5 | 41 | 103 | 10.6 | 0.199 |  | 5.98 | 10 | 0.042 | 6 | 11 |  | 5.97 | 10 | [8 empty] | 0.039 | [14 empty] | 0.023 | 1 | 0.56 |  | 0.037 | 0.026 | 1 | 0.43 |  | 0.034 | 1 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.431 | 4 | 0.61 | 11.5 | 6 | 0.4266 |  | 6.06 | 0.446 | 4 | 0.65 | 10.9 | 10.4 | 0.73321 | 6.06 | 0.492 | 4 | 0.71 | 11.8 | 10.5 | 0.70333 | [13 empty] | 7.28 | 0.062 | 1 | 3.9 | 10.3 |  |  |  | 7.38 | 0.063 | 1 | 4 | 11.4 |  |  |  | 3.7 | 3.8 | 3.4 | [55 empty] | 13:00 | 0.61 | 6 | 42.4 | 25.864 | 6 | 11.5 | 13 | 1.9895 | 10 | 6 | 0.3066 | 13:00 | 0.65 | 10.4 | 24.4615 | 15.9 | 6.06 | 10.9 | 15 | 1.06 | 10 | 6.5 | 0.61321 | 13:00 | 0.71 | 10.5 | 25.7143 | 18.2571 | 6.06 | 11.8 | 15 | 1.2171 | 10 | 6.5 | 0.58333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.88 | 24 | 18 | 9.07 | 44 | 106 | 11.1 | 0.226 |  | 5.91 | 10 | 0.048 | 5.89 | 10 |  | 6 | 11 | [8 empty] | 0.044 | [14 empty] | 0.021 | 1 | 0.51 |  | 0.041 | 0.016 | 1 | 0.4 |  | 0.035 | 1 | 0.46 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.31 | 0.054 | 1 | 3.8 | 10.1 |  |  |  | 7.34 | 0.057 | 1 | 3.9 | 11 |  |  |  | 3.8 | 3.8 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.94 | 24 | 18 | 9.13 | 42 | 114 | 11.3 | 0.235 |  | 5.92 | 10 | 0.045 | 5.86 | 10 |  | 6 | 10 | [8 empty] | 0.036 | [14 empty] | 0.023 | 1 | 0.5 |  | 0.036 | 0.019 | 1 | 0.46 |  | 0.035 | 1 | 0.43 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.061 | [9 empty] | 6 | 0.409 | 4 | 0.63 | 11 | 6 | 0.4266 |  | 6 | 0.436 | 4 | 0.66 | 106 | 10.5 | 0.28509 | 6.01 | 0.493 | 4 | 0.69 | 12 | 10.5 | 0.70333 |  |  |  | 0.02 | [9 empty] | 7.26 | 0.056 | 1 | 4 | 10.1 | 28 | 30 | 0.018 | 7.52 | 0.059 | 1 | 4.2 | 11 | 28 | 30 | 0.018 | 3.6 | 3.6 | 3.2 | [55 empty] | 21:00 | 0.63 | 6 | 42.4 | 26.712 | 6 | 11 | 13 | 2.0548 | 10 | 6 | 0.3066 | 21:00 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6 | 106 | 4 | 3.9977 | 25 | 6 | 0.16509 | 21:00 | 0.69 | 10.5 | 25.7143 | 17.7429 | 6.01 | 12 | 15 | 1.1829 | 10 | 6.5 | 0.58333
22:00 | [72 empty] | DOSE |  | TOTAL | 24 | 41.1 | 41.2 | 106.3 | 33.6 | 33.6 | 33.6 | 100.8 | 0 | 36.5141 | 0 | 65.1773 | 101.6914 | 3.1305 | TOTAL | 160.4783 | #N/A | 0 | 1820 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.0292 | 5.7618 | 5.9297 | 0.79979 | 0.57459 | 0.56231 | 0.57589 | 0.54779 | 0.45395 | 4.1279 | 3.5 | 0.23878 | 0.23878 | 0.23755 | 4.2194 | 1.9502 | 0.3959 | 16.4858 | 2.9378 | 37.682 | 4.2475 | 1.6477 | 0.37823 | 12.1716 | 2.4121 | 26.089 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.98 | 24 | 20 | 9.54 | 40 | 148 | 11.2 | 0.19 |  | 5.96 | 10 | 0.063 | 5.98 | 10 |  | 6 | 10 | [8 empty] | 0.041 | [14 empty] | 0.023 | 1 | 0.49 |  | 0.041 | 0.029 | 1 | 0.43 |  | 0.036 | 1 | 0.49 | [22 empty] | AVERAGE | 6 | 10.275 | 10.3 | 26.575 | 8.4 | 8.4 | 8.4 | 25.2 |  | 9.1285 |  | 16.2943 | 25.4228 | 0.78262 | AVERAGE | 40.1196 | #N/A |  | 455 | #N/A | #N/A | #N/A |  |  |  | 1.0073 | 1.4405 | 1.4824 | 0.19995 | 0.14365 | 0.14058 | 0.14397 | 0.13695 | 0.11349 | 1.032 | 0.875 | 0.059695 | 0.059695 | 0.059388 | 1.0548 | 0.48754 | 0.098974 | 4.1215 | 0.73445 | 9.4205 | 1.0619 | 0.41194 | 0.094558 | 3.0429 | 0.60303 | 6.5222 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 41.7 | 147 | 113 | 58.63 | 254 | 663 | 65.7 | 1.254 | 0.115 | 35.83 | 60 | 0.299 | 35.84 | 61 | 0 | 36.01 | 61 | 0 | 23.94 | 1.626 | 16 | 2.39 | 44.1 | 23.9 | 1.7013 | 0.236 | 24.1 | 1.743 | 16 | 2.66 | 137.6 | 41.7 | 2.403 | 24.12 | 2.051 | 16 | 2.72 | 47.5 | 42.2 | 2.7467 | 0.167 | 6 | 3.09 | 0.031 | 0.231 | 0.147 | 6 | 2.8 | 0 | 0.203 | 6 | 3.01 | 0 | 43.84 | 0.333 | 6 | 23.9 | 61.5 | 55 | 59 | 0.037 | 45.55 | 0.341 | 6 | 24 | 65.3 | 57 | 62 | 0.034 | 21.9 | 22.3 | 19.6 |  |  | MINIMUM | 5.5 | 9.8 | 9.8 | 25.1 | 7.8 | 7.8 | 7.8 | 23.4 |  | 8.9035 |  | 15.0264 | 24.5333 | 0 | MINIMUM | 39.6972 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 0.98342 | 1.294 | 1.4267 | 0.14521 | 0.093349 | 0.11953 | 0.10866 | 0.12739 | 0.076062 | 0 | 0 | 0.055212 | 0.055212 | 0.055212 | 1.0024 | 0.45326 | 0.092404 | 3.9509 | 0.71609 | 9.352 | 1.0158 | 0.38869 | 0.084004 | 2.8339 | 0.50391 | 6.5142 |  | MIN | 0.56 | 6 | 42.4 | 23.744 | 5.94 | 10.5 | 13 | 1.8265 |  |  |  | MIN | 0.65 | 10.4 | 24.4615 | 15.9 | 6.06 | 10.9 | 15 | 1.06 |  |  |  | MIN | 0.67 | 10.7 | 25.2336 | 16.9065 | 6.08 | 11.9 | 15 | 1.1271 |  |  |  | 1.06
AVERAGE | 6.95 | 24.5 | 18.8333 | 9.7717 | 42.3333 | 110.5 | 10.95 | 0.209 | 0.0575 | 5.9717 | 10 | 0.049833 | 5.9733 | 10.1667 |  | 6.0017 | 10.1667 |  | 5.985 | 0.4065 | 4 | 0.5975 | 11.025 | 5.975 | 0.42533 | 0.039333 | 6.025 | 0.43575 | 4 | 0.665 | 34.4 | 10.425 | 0.60074 | 6.03 | 0.51275 | 4 | 0.68 | 11.875 | 10.55 | 0.68667 | 0.027833 | 1 | 0.515 | 0.0155 | 0.0385 | 0.0245 | 1 | 0.46667 |  | 0.033833 | 1 | 0.50167 |  | 7.3067 | 0.0555 | 1 | 3.9833 | 10.25 | 27.5 | 29.5 | 0.0185 | 7.5917 | 0.056833 | 1 | 4 | 10.8833 | 28.5 | 31 | 0.017 | 3.65 | 3.7167 | 3.2667 |  |  | MAXIMUM | 6.5 | 10.5 | 10.6 | 27.1 | 8.6 | 8.6 | 8.6 | 25.8 |  | 9.5069 |  | 18.6667 | 27.5702 | 1.1922 | MAXIMUM | 40.4962 | #N/A |  | 620 | #N/A | #N/A | #N/A |  |  |  | 1.0352 | 1.5694 | 1.5528 | 0.24574 | 0.16163 | 0.16008 | 0.16008 | 0.15069 | 0.15069 | 1.4267 | 1.5 | 0.059695 | 0.059695 | 0.059388 | 1.1052 | 0.49975 | 0.10188 | 4.3099 | 0.78953 | 9.4999 | 1.12 | 0.45326 | 0.1008 | 3.3243 | 0.68957 | 6.5464
MINIMUM | 6.88 | 24 | 18 | 8.29 | 39 | 87 | 10.4 | 0.19 | 0.054 | 5.91 | 10 | 0.042 | 5.86 | 10 |  | 5.97 | 10 |  | 5.94 | 0.353 | 4 | 0.56 | 10.5 | 5.9 | 0.42149 | 0.036 | 5.99 | 0.396 | 4 | 0.65 | 10.2 | 10.4 | 0.28509 | 5.97 | 0.492 | 4 | 0.65 | 11.8 | 10.5 | 0.62556 | 0.021 | 1 | 0.39 | 0.011 | 0.036 | 0.016 | 1 | 0.4 |  | 0.029 | 1 | 0.43 |  | 7.26 | 0.051 | 1 | 3.8 | 10.1 | 27 | 29 | 0.018 | 7.34 | 0.053 | 1 | 3.9 | 10.6 | 28 | 30 | 0.016 | 3.6 | 3.6 | 3.1 | [15 empty] | Ml/Min |  | TOTAL | 17444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 1085 | 1120 | 990 | 700 | 1010 | 1035 | 990 | 820 | 2170 | 0 | 3800 | 3800 | 3780 | 308 | 378 | 46 | 5400 | 1080 | 2170 | 155 | 160 | 22 | 1880 | 445 | 751
MAXIMUM | 6.99 | 26 | 20 | 12.1 | 48 | 148 | 11.3 | 0.235 | 0.061 | 6.06 | 10 | 0.063 | 6.09 | 11 |  | 6.04 | 11 |  | 6 | 0.433 | 4 | 0.63 | 11.5 | 6 | 0.4266 | 0.044 | 6.06 | 0.465 | 4 | 0.68 | 106 | 10.5 | 0.73321 | 6.08 | 0.563 | 4 | 0.71 | 12 | 10.7 | 0.71444 | 0.05 | 1 | 0.64 | 0.02 | 0.041 | 0.034 | 1 | 0.62 |  | 0.036 | 1 | 0.59 |  | 7.38 | 0.062 | 1 | 4.1 | 10.4 | 28 | 30 | 0.019 | 7.92 | 0.063 | 1 | 4.2 | 11.4 | 29 | 32 | 0.018 | 3.8 | 3.9 | 3.4 | [17 empty] | AVERAGE | 4361 | [9 empty] | 190 | 271.25 | 280 | 247.5 | 175 | 252.5 | 258.75 | 247.5 | 205 | 542.5 |  | 950 | 950 | 945 | 77 | 94.5 | 11.5 | 1350 | 270 | 542.5 | 38.75 | 40 | 5.5 | 470 | 111.25 | 187.75
# 0F DAYS IN THE MONTH |  | 28 |  | TOTAL AVG COAG PH: |  |  |  | 5.9822 |  | TOTAL AVG COAG ALK: |  |  |  | 10.1111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.563 |  |  |  |  | TOTAL AVG SETTLED PH: | [6 empty] | 6.0133 | TOTAL MIN SETTLED DISEN.: | [7 empty] | 0.56 | TOTAL FILTER MAX NTU | [6 empty] | 0.05 | [20 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 4100 | [9 empty] | 180 | 250 | 250 | 200 | 170 | 220 | 200 | 230 | 140 | 0 |  | 900 | 900 | 900 | 75 | 90 | 11 | 1320 | 270 | 500 | 38 | 35 | 5 | 440 | 95 | 175
[90 empty] | MAXIMUM | 4472 | [9 empty] | 200 | 300 | 300 | 280 | 180 | 275 | 285 | 280 | 280 | 750 |  | 1000 | 1000 | 1000 | 82 | 99 | 12 | 1400 | 270 | 560 | 41 | 45 | 6 | 540 | 130 | 192
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.928 |  | TOTAL MGD: |  | 4.743 |  |  | FINISHED SOUTH 1 |  | START: | 23057091 |  | END: | 23061834 |  |  | Alum | 6403 |  | 6745 |  | 0 | [45 empty] | 0.65 | 10.4 | 24.4615 | 15.9 | 6.06 | 10.9 | 15 | 1.06
[73 empty] | FINISHED 2 | 14.638 |  | TOTAL MGD: |  | 5.185 |  |  | FINISHED SOUTH 2 |  | START: | 40902392 |  | END: | 40907577 |  |  | Caustic | 5677 |  | 5883
[73 empty] | TOTAL RAW | 25.755 |  | TOTAL MGD: |  | 4.703 |  |  | FINISHED CONWAY |  | START: | 8664748 |  | END: | 8669451 |  |  | Hypochlorite | 12 |  | 27.5
[76 empty] | TOTAL MGD: |  | 9.935 |  |  | FINISHED PERRY |  | START: | 30296689 |  | END: | 30306624 |  |  | Phosphate | 100
[76 empty] | TOTAL MGD: |  | 5.587 |  |  | RAW PLANT 1 |  | START: | 27863923 |  | END: | 27869510 |  |  | Fluoride | 2500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.665 |  |  | RAW PLANT 2 |  | START: | 27782116 |  | END: | 27791781 |  |  | Cal~Flo | 11.49 | 0 | 0 | 11.49 | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.503 |  |  | RAW PLANT 3 |  | START: | 4089966 |  | END: | 4100469 |  |  | Zinc | 472
[76 empty] | TOTAL MGD: |  | 1.263 |  |  | DECANT |  | START: | 1374800 |  | END: | 1376063 |  |  | Polymer | 9 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.60328 |  |  | BLOW DOWN |  | START: | 8755.9957 |  | END: | 8756.599 |  |  | NH3 | 7.31
[90 empty] | Lime | 0 | [28 empty] | 1.0202
[82 empty] | BACKWASH WATER USED : |  |  |  |  | 0 |  |  | Cabon | 650
[90 empty] | BI-SULFITE | 1050 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 1681 | Phosphate | 72
[90 empty] | Caustic 1 | 212 | Fluoride | 0
[90 empty] | Caustic 2 | 80 | Zinc | 7.5
[90 empty] | Hypochlorite 1 | 151 | Polymer 1 | 1.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23061834
[91 empty] | FINISHED SOUTH 2 |  | END: | 40907577
[91 empty] | FINISHED CONWAY |  | END: | 8669451
[91 empty] | FINISHED PERRY |  | END: | 30306624
[91 empty] | RAW PLANT 1 |  | END: | 27869510
[91 empty] | RAW PLANT 2 |  | END: | 27791781
[91 empty] | RAW PLANT 3 |  | END: | 4100469
[91 empty] | DECANT |  | END: | 1376063
[91 empty] | BLOW DOWN |  | END: | 8756.599
Note on AX36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 2
DATE: | 2018-02-02 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CBW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-02 | [23 empty] | DATE: | 2018-02-02
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-02 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43133.0262 | 3,1,6 | 38 | 6 | 10.5 | 10.5 | 27 | 8.6 | 8.6 | 8.6 | 25.8 | 7,1 | 8.9035 | 1,2 | 18.6667 | 27.5702 | 0.93168 | 43133.0262 | 40.4962 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0.98342 | 1.294 | 1.4492 | 0.19016 | 0.16163 | 0.11953 | 0.10866 | 0.13583 | 0.076062 | 1.2745 | 1 | 0.061346 | 0.061346 | 0.061346 | 1.096 | 0.49858 | 0.1008 | 4.168 | 0.71609 | 9.4999 | 1.096 | 0.4029 | 0.1008 | 3.3243 | 0.68957 | 6.5142 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.05 | 0.409 | 4 | 0.63 | 11.3 | 6 | 0.47377 |  | 6.07 | 0.429 | 4 | 0.7 | 10.8 | 10.5 | 0.7391 | 6.06 | 0.463 | 4 | 0.68 | 12.6 | 10.5 | 0.70333 | [13 empty] | 7.36 | 0.053 | 1 | 4 | 10.1 |  |  |  | 7.42 | 0.053 | 1 | 4 | 10.8 |  |  |  | 3.8 | 3.6 | 3.4 | [18 empty] | 4472 | [6 empty] | 0 | 0 | 0 | 190 | 250 | 280 | 200 | 170 | 220 | 200 | 250 | 140 | 670 |  | 1000 | 1000 | 1000 | 82 | 99 | 12 | 1400 | 270 | 560 | 41 | 40 | 6 | 540 | 130 | 192 |  | 1:00 | 0.63 | 6 | 42.4 | 26.712 | 6.05 | 11.3 | 15 | 1.7808 | 10 | 6.5 | 0.35377 | 1:00 | 0.7 | 10.5 | 24.2286 | 16.96 | 6.07 | 10.8 | 15 | 1.1307 | 10 | 6.5 | 0.6191 | 1:00 | 0.68 | 10.5 | 25.7143 | 17.4857 | 6.06 | 12.6 | 15 | 1.1657 | 10 | 6.5 | 0.58333
2:00 | [72 empty] | 43133.3289 | 3,1,6 | 38 | 5.6 | 9.7 | 9.9 | 25.2 | 7.9 | 7.9 | 7.9 | 23.7 | 7,1 | 8.9035 | 1,2 | 18.6667 | 27.5702 | 1.4272 | 43133.3289 | 40.3617 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0142 | 1.3241 | 1.5213 | 0.13752 | 0.14262 | 0.13527 | 0.13527 | 0.13253 | 0.069148 | 0.30436 | 2 | 0.060104 | 0.060104 | 0.058768 | 1.1349 | 0.4989 | 0.091447 | 4.2661 | 0.7651 | 9.5106 | 1.1058 | 0.39474 | 0.10974 | 3.2317 | 0.69292 | 7.0914 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.93 | 24 | 20 | 10.3 | 44 | 123 | 11.1 | 0.22 |  | 6.09 | 10 | 0.066 | 6 | 10 |  | 6 | 10 | [8 empty] | 0.042 | [14 empty] | 0.029 | 1 | 0.43 |  | 0.042 | 0.029 | 1 | 0.46 |  | 0.039 | 1 | 0.53 | [38 empty] | 4160 | [6 empty] | 0 | 0 | 0 | 180 | 235 | 270 | 135 | 140 | 230 | 230 | 230 | 120 | 160 |  | 900 | 900 | 880 | 78 | 91 | 10 | 1320 | 265 | 515 | 38 | 36 | 6 | 480 | 120 | 192 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43133.7807 | 3,1,6 | 32 | 5.6 | 9.7 | 9.9 | 25.2 | 7.9 | 7.9 | 7.9 | 23.7 | 7,1 | 9.5141 | 1,2 | 13.307 | 22.8211 | 1.4011 | 43133.7807 | 40.3617 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.1269 | 1.465 | 1.4086 | 0.14262 | 0.14262 | 0.11762 | 0.13527 | 0.13253 | 0.11525 | 1.2745 | 1 | 0.060104 | 0.060104 | 0.060104 | 1.0912 | 0.47697 | 0.10059 | 4.2011 | 0.77954 | 9.4183 | 1.1058 | 0.39474 | 0.091447 | 3.0352 | 0.54856 | 7.0914 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.35 | 0.054 | 1 | 4 | 10.1 |  |  |  | 7.5 | 0.056 | 1 | 4.3 | 11 |  |  |  | 3.7 | 3.8 | 3.4 | [18 empty] | 4160 | [6 empty] | 0 | 0 | 0 | 200 | 260 | 250 | 140 | 140 | 200 | 230 | 230 | 200 | 670 |  | 900 | 900 | 900 | 75 | 87 | 11 | 1320 | 270 | 510 | 38 | 36 | 5 | 420 | 95 | 192 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.87 | 25 | 20 | 32.3 | 33 | 252 | 11.1 | 0.228 |  | 5.96 | 10 | 0.037 | 5.86 | 10 |  | 5.9 | 10 | [8 empty] | 0.032 | [14 empty] | 0.028 | 1 | 0.36 |  | 0.035 | 0.037 | 1 | 0.4 |  | 0.042 | 1 | 0.4 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.012 | [9 empty] | 6.03 | 0.349 | 4 | 0.5 | 10.9 | 5.5 | 0.44429 |  | 5.97 | 0.473 | 4 | 0.67 | 10.4 | 9.3 | 0.59524 | 5.97 | 0.504 | 4 | 0.73 | 12.1 | 9.5 | 0.57741 |  |  |  | 0.015 | [9 empty] | 7.35 | 0.06 | 1 | 4.1 | 10.1 | 26 | 21 | 0.014 | 8.53 | 0.066 | 1 | 4.7 | 11 | 25 | 20 | 0.009 | 3.7 | 4 | 3.5 | [55 empty] | 9:00 | 0.5 | 5.5 | 46.2545 | 23.1273 | 6.03 | 10.9 | 15 | 1.5418 | 10 | 6.5 | 0.32429 | 9:00 | 0.67 | 9.3 | 27.3548 | 18.3277 | 5.97 | 10.4 | 13 | 1.4098 | 10 | 6 | 0.47524 | 9:00 | 0.73 | 9.5 | 28.4211 | 20.7474 | 5.97 | 12.1 | 13 | 1.596 | 10 | 6 | 0.45741
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.87 | 25 | 20 | 33.2 | 36 | 253 | 10.9 | 0.194 |  | 6.02 | 11 | 0.041 | 5.87 | 10 |  | 5.87 | 10 | [8 empty] | 0.031 | [14 empty] | 0.023 | 1 | 0.39 |  | 0.032 | 0.013 | 1 | 0.42 |  | 0.039 | 1 | 0.68 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.9 | 0.362 | 4 | 0.63 | 11.3 | 5.5 | 0.40105 |  | 5.95 | 0.426 | 4 | 0.63 | 10.7 | 9.3 | 0.59524 | 5.96 | 0.454 | 4 | 0.85 | 12.2 | 9.5 | 0.57741 | [13 empty] | 7.23 | 0.063 | 1 | 3.9 | 10.1 |  |  |  | 7.74 | 0.052 | 1 | 3.8 | 11.4 |  |  |  | 3.7 | 4 | 4 | [55 empty] | 13:00 | 0.63 | 5.5 | 46.2545 | 29.1404 | 5.9 | 11.3 | 13 | 2.2416 | 10 | 6 | 0.28105 | 13:00 | 0.63 | 9.3 | 27.3548 | 17.2335 | 5.95 | 10.7 | 13 | 1.3257 | 10 | 6 | 0.47524 | 13:00 | 0.85 | 9.5 | 28.4211 | 24.1579 | 5.96 | 12.2 | 13 | 1.8583 | 10 | 6 | 0.45741
14:00 | [126 empty] | 285 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.9 | 25 | 19 | 27 | 40 | 219 | 11.1 | 0.207 |  | 5.75 | 9 | 0.036 | 5.76 | 9 |  | 5.76 | 9 | [8 empty] | 0.033 | [14 empty] | 0.022 | 1 | 0.37 |  | 0.035 | 0.016 | 1 | 0.41 |  | 0.039 | 1 | 0.61 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.22 | 0.061 | 1 | 3.8 | 10.1 |  |  |  | 7.85 | 0.056 | 1 | 4 | 11.4 |  |  |  | 3.8 | 3.9 | 4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.93 | 23 | 19 | 34 | 47 | 276 | 11.1 | 0.225 |  | 6.02 | 9 | 0.025 | 5.8 | 9 |  | 5.8 | 9 | [8 empty] | 0.026 | [14 empty] | 0.024 | 1 | 0.39 |  | 0.017 | 0.016 | 1 | 0.43 |  | 0.038 | 1 | 0.63 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.154 | [9 empty] | 5.9 | 0.286 | 4 | 0.66 | 10.9 | 5.5 | 0.40105 |  | 5.92 | 0.306 | 4 | 0.63 | 10.5 | 9.3 | 0.59524 | 5.95 | 0.469 | 4 | 0.83 | 12.2 | 9.5 | 0.57741 |  |  |  | 0.012 | [9 empty] | 7.43 | 0.061 | 1 | 3.5 | 10.2 | 26 | 21 | 0.005 | 7.9 | 0.056 | 1 | 3.7 | 10.8 | 26 | 21 | 0.002 | 3.8 | 4 | 4.4 | [55 empty] | 21:00 | 0.66 | 5.5 | 46.2545 | 30.528 | 5.9 | 10.9 | 13 | 2.3483 | 10 | 6 | 0.28105 | 21:00 | 0.63 | 9.3 | 27.3548 | 17.2335 | 5.92 | 10.5 | 13 | 1.3257 | 10 | 6 | 0.47524 | 21:00 | 0.83 | 9.5 | 28.4211 | 23.5895 | 5.95 | 12.2 | 13 | 1.8146 | 10 | 6 | 0.45741
22:00 | [72 empty] | DOSE |  | TOTAL | 17.2 | 29.9 | 30.3 | 77.4 | 24.4 | 24.4 | 24.4 | 73.2 | 0 | 27.3211 | 0 | 50.6405 | 77.9616 | 3.76 | TOTAL | 121.2196 | #N/A | 0 | 1200 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 3.1245 | 4.083 | 4.3792 | 0.4703 | 0.44687 | 0.37241 | 0.37919 | 0.40089 | 0.26046 | 2.8534 | 4 | 0.18155 | 0.18155 | 0.18022 | 3.3221 | 1.4745 | 0.29284 | 12.6352 | 2.2607 | 28.4288 | 3.3075 | 1.1924 | 0.30199 | 9.5913 | 1.9311 | 20.697 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.82 | 23 | 19 | 42.3 | 45 | 322 | 10.6 | 0.227 |  | 6.03 | 8 | 0.058 | 5.93 | 8 |  | 5.88 | 8 | [8 empty] | 0.05 | [14 empty] | 0.023 | 1 | 0.4 |  | 0.051 | 0.019 | 1 | 0.46 |  | 0.039 | 1 | 0.63 | [22 empty] | AVERAGE | 5.7333 | 9.9667 | 10.1 | 25.8 | 8.1333 | 8.1333 | 8.1333 | 24.4 |  | 9.107 |  | 16.8802 | 25.9872 | 1.2533 | AVERAGE | 40.4065 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.0415 | 1.361 | 1.4597 | 0.15677 | 0.14896 | 0.12414 | 0.1264 | 0.13363 | 0.086819 | 0.95112 | 1.3333 | 0.060518 | 0.060518 | 0.060073 | 1.1074 | 0.49149 | 0.097615 | 4.2117 | 0.75358 | 9.4763 | 1.1025 | 0.39746 | 0.10066 | 3.1971 | 0.64368 | 6.899 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 41.32 | 145 | 117 | 179.1 | 245 | 1445 | 65.9 | 1.301 | 0.166 | 35.87 | 57 | 0.263 | 35.22 | 56 | 0 | 35.21 | 56 | 0 | 23.88 | 1.406 | 16 | 2.42 | 44.4 | 22.5 | 1.7202 | 0.214 | 23.91 | 1.634 | 16 | 2.63 | 42.4 | 38.4 | 2.5248 | 23.94 | 1.89 | 16 | 3.09 | 49.1 | 39 | 2.4356 | 0.149 | 6 | 2.34 | 0.027 | 0.212 | 0.13 | 6 | 2.58 | 0 | 0.236 | 6 | 3.48 | 0 | 43.94 | 0.352 | 6 | 23.3 | 60.7 | 52 | 42 | 0.019 | 46.94 | 0.339 | 6 | 24.5 | 66.4 | 51 | 41 | 0.011 | 22.5 | 23.3 | 22.7 |  |  | MINIMUM | 5.6 | 9.7 | 9.9 | 25.2 | 7.9 | 7.9 | 7.9 | 23.7 |  | 8.9035 |  | 13.307 | 22.8211 | 0.93168 | MINIMUM | 40.3617 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 0.98342 | 1.294 | 1.4086 | 0.13752 | 0.14262 | 0.11762 | 0.10866 | 0.13253 | 0.069148 | 0.30436 | 1 | 0.060104 | 0.060104 | 0.058768 | 1.0912 | 0.47697 | 0.091447 | 4.168 | 0.71609 | 9.4183 | 1.096 | 0.39474 | 0.091447 | 3.0352 | 0.54856 | 6.5142 |  | MIN | 0.5 | 5.5 | 46.2545 | 23.1273 | 6.03 | 10.9 | 15 | 1.5418 |  |  |  | MIN | 0.7 | 10.5 | 24.2286 | 16.96 | 6.07 | 10.8 | 15 | 1.1307 |  |  |  | MIN | 0.68 | 10.5 | 25.7143 | 17.4857 | 6.06 | 12.6 | 15 | 1.1657 |  |  |  | 1.1307
AVERAGE | 6.8867 | 24.1667 | 19.5 | 29.85 | 40.8333 | 240.8333 | 10.9833 | 0.21683 | 0.083 | 5.9783 | 9.5 | 0.043833 | 5.87 | 9.3333 |  | 5.8683 | 9.3333 |  | 5.97 | 0.3515 | 4 | 0.605 | 11.1 | 5.625 | 0.43004 | 0.035667 | 5.9775 | 0.4085 | 4 | 0.6575 | 10.6 | 9.6 | 0.6312 | 5.985 | 0.4725 | 4 | 0.7725 | 12.275 | 9.75 | 0.60889 | 0.024833 | 1 | 0.39 | 0.0135 | 0.035333 | 0.021667 | 1 | 0.43 |  | 0.039333 | 1 | 0.58 |  | 7.3233 | 0.058667 | 1 | 3.8833 | 10.1167 | 26 | 21 | 0.0095 | 7.8233 | 0.0565 | 1 | 4.0833 | 11.0667 | 25.5 | 20.5 | 0.0055 | 3.75 | 3.8833 | 3.7833 |  |  | MAXIMUM | 6 | 10.5 | 10.5 | 27 | 8.6 | 8.6 | 8.6 | 25.8 |  | 9.5141 |  | 18.6667 | 27.5702 | 1.4272 | MAXIMUM | 40.4962 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.1269 | 1.465 | 1.5213 | 0.19016 | 0.16163 | 0.13527 | 0.13527 | 0.13583 | 0.11525 | 1.2745 | 2 | 0.061346 | 0.061346 | 0.061346 | 1.1349 | 0.4989 | 0.1008 | 4.2661 | 0.77954 | 9.5106 | 1.1058 | 0.4029 | 0.10974 | 3.3243 | 0.69292 | 7.0914
MINIMUM | 6.82 | 23 | 19 | 10.3 | 33 | 123 | 10.6 | 0.194 | 0.012 | 5.75 | 8 | 0.025 | 5.76 | 8 |  | 5.76 | 8 |  | 5.9 | 0.286 | 4 | 0.5 | 10.9 | 5.5 | 0.40105 | 0.026 | 5.92 | 0.306 | 4 | 0.63 | 10.4 | 9.3 | 0.59524 | 5.95 | 0.454 | 4 | 0.68 | 12.1 | 9.5 | 0.57741 | 0.022 | 1 | 0.36 | 0.012 | 0.017 | 0.013 | 1 | 0.4 |  | 0.038 | 1 | 0.4 |  | 7.22 | 0.053 | 1 | 3.5 | 10.1 | 26 | 21 | 0.005 | 7.42 | 0.052 | 1 | 3.7 | 10.8 | 25 | 20 | 0.002 | 3.7 | 3.6 | 3.4 | [15 empty] | MIL/MIN |  | TOTAL | 12792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 745 | 800 | 475 | 450 | 650 | 660 | 710 | 460 | 1500 | 0 | 2800 | 2800 | 2780 | 235 | 277 | 33 | 4040 | 805 | 1585 | 117 | 112 | 17 | 1440 | 345 | 576
MAXIMUM | 6.93 | 25 | 20 | 42.3 | 47 | 322 | 11.1 | 0.228 | 0.154 | 6.09 | 11 | 0.066 | 6 | 10 |  | 6 | 10 |  | 6.05 | 0.409 | 4 | 0.66 | 11.3 | 6 | 0.47377 | 0.05 | 6.07 | 0.473 | 4 | 0.7 | 10.8 | 10.5 | 0.7391 | 6.06 | 0.504 | 4 | 0.85 | 12.6 | 10.5 | 0.70333 | 0.029 | 1 | 0.43 | 0.015 | 0.051 | 0.037 | 1 | 0.46 |  | 0.042 | 1 | 0.68 |  | 7.43 | 0.063 | 1 | 4.1 | 10.2 | 26 | 21 | 0.014 | 8.53 | 0.066 | 1 | 4.7 | 11.4 | 26 | 21 | 0.009 | 3.8 | 4 | 4.4 | [17 empty] | AVERAGE | 4264 | [9 empty] | 190 | 248.3333 | 266.6667 | 158.3333 | 150 | 216.6667 | 220 | 236.6667 | 153.3333 | 500 |  | 933.3333 | 933.3333 | 926.6667 | 78.3333 | 92.3333 | 11 | 1346.6667 | 268.3333 | 528.3333 | 39 | 37.3333 | 5.6667 | 480 | 115 | 192
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9056 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.504 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.5 | [5 empty] | 5.9775 |  |  |  |  | 0.042 |  |  |  |  | 0.5 | [6 empty] | 0.042 | [16 empty] | Pump Station MIN |  | 3.4 | [17 empty] | MINIMUM | 4160 | [9 empty] | 180 | 235 | 250 | 135 | 140 | 200 | 200 | 230 | 120 | 160 |  | 900 | 900 | 880 | 75 | 87 | 10 | 1320 | 265 | 510 | 38 | 36 | 5 | 420 | 95 | 192
[90 empty] | MAXIMUM | 4472 | [9 empty] | 200 | 260 | 280 | 200 | 170 | 230 | 230 | 250 | 200 | 670 |  | 1000 | 1000 | 1000 | 82 | 99 | 12 | 1400 | 270 | 560 | 41 | 40 | 6 | 540 | 130 | 192
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.306 |  | TOTAL MGD: |  | 4.105 |  |  | FINISHED SOUTH 1 |  | START: | 23061834 |  | END: | 23065939 |  |  | Alum | 6006 |  | 6385 |  | 0 | [45 empty] | 0.7 | 10.5 | 24.2286 | 16.96 | 6.07 | 10.8 | 15 | 1.1307
[73 empty] | FINISHED 2 | 13.016 |  | TOTAL MGD: |  | 5.201 |  |  | FINISHED SOUTH 2 |  | START: | 40907577 |  | END: | 40912778 |  |  | Caustic | 5528 |  | 5883
[73 empty] | TOTAL RAW | 26.148 |  | TOTAL MGD: |  | 4.243 |  |  | FINISHED CONWAY |  | START: | 8669451 |  | END: | 8673694 |  |  | Hypochlorite | 13 |  | 34
[76 empty] | TOTAL MGD: |  | 8.773 |  |  | FINISHED PERRY |  | START: | 30306624 |  | END: | 30315397 |  |  | Phosphate | 3082
[76 empty] | TOTAL MGD: |  | 6.031 |  |  | RAW PLANT 1 |  | START: | 27869510 |  | END: | 27875541 |  |  | Fluoride | 2450 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.38 |  |  | RAW PLANT 2 |  | START: | 27791781 |  | END: | 27802161 |  |  | Cal~Flo | 11.93 | 0 | 0 | 11.93 | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.737 |  |  | RAW PLANT 3 |  | START: | 4100469 |  | END: | 4110206 |  |  | Zinc | 3648
[76 empty] | TOTAL MGD: |  | 1.376 |  |  | DECANT |  | START: | 1376063 |  | END: | 1377439 |  |  | Polymer | 9 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.54751 |  |  | BLOW DOWN |  | START: | 8756.599 |  | END: | 8757.1465 |  |  | NH3 | 6.71
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 1030 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 1616 | Phosphate | 43
[90 empty] | Caustic 1 | 204 | Fluoride | 0
[90 empty] | Caustic 2 | 81 | Zinc | 7
[90 empty] | Hypochlorite 1 | 143 | Polymer 1 | 1
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1
[91 empty] | FINISHED SOUTH 1 |  | END: | 23065939
[91 empty] | FINISHED SOUTH 2 |  | END: | 40912778
[91 empty] | FINISHED CONWAY |  | END: | 8673694
[91 empty] | FINISHED PERRY |  | END: | 30315397
[91 empty] | RAW PLANT 1 |  | END: | 27875541
[91 empty] | RAW PLANT 2 |  | END: | 27802161
[91 empty] | RAW PLANT 3 |  | END: | 4110206
[91 empty] | DECANT |  | END: | 1377439
[91 empty] | BLOW DOWN |  | END: | 8757.1465
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 3
DATE: | 2018-02-03 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-03 | [23 empty] | DATE: | 2018-02-03
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-03 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43134.0241 | 3,1,6 | 32 | 5.6 | 9.7 | 9.9 | 25.2 | 7.9 | 7.9 | 7.9 | 23.7 | 7,1 | 9.5141 | 1,2 | 13.307 | 22.8211 | 1.4011 | 43134.0241 | 40.3617 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.1269 | 1.465 | 1.4086 | 0.14262 | 0.14262 | 0.11762 | 0.13527 | 0.13253 | 0.11525 | 1.2745 | 1 | 0.060104 | 0.060104 | 0.060104 | 1.0912 | 0.47697 | 0.10059 | 4.2011 | 0.77954 | 9.4183 | 1.1058 | 0.39474 | 0.091447 | 3.0352 | 0.54856 | 7.0914 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.98 | 0.332 | 4 | 0.66 | 10.8 | 5.5 | 0.40105 |  | 5.97 | 0.359 | 4 | 0.76 | 10.3 | 9.3 | 0.59524 | 5.98 | 0.439 | 4 | 0.8 | 12.1 | 9.5 | 0.57741 | [13 empty] | 7.29 | 0.059 | 1 | 4 | 9.9 |  |  |  | 7.44 | 0.056 | 1 | 4.1 | 10.5 |  |  |  | 3.7 | 4 | 2.9 | [18 empty] | 4160 | [6 empty] | 0 | 0 | 0 | 200 | 260 | 250 | 140 | 140 | 200 | 230 | 230 | 200 | 670 |  | 900 | 900 | 900 | 75 | 87 | 11 | 1320 | 270 | 510 | 38 | 36 | 5 | 420 | 95 | 192 |  | 1:00 | 0.66 | 5.5 | 46.2545 | 30.528 | 5.98 | 10.8 | 13 | 2.3483 | 10 | 6 | 0.28105 | 1:00 | 0.76 | 9.3 | 27.3548 | 20.7897 | 5.97 | 10.3 | 13 | 1.5992 | 10 | 6 | 0.47524 | 1:00 | 0.8 | 9.5 | 28.4211 | 22.7368 | 5.98 | 12.1 | 13 | 1.749 | 10 | 6 | 0.45741
2:00 | [72 empty] | 43134.3613 | 3,1,6 | 32 | 5.5 | 9.6 | 9.6 | 24.7 | 7.7 | 7.7 | 7.7 | 23.1 | 7,1 | 9.5141 | 1,2 | 13.307 | 22.8211 | 1.0633 | 43134.3613 | 40.3868 | #N/A | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0984 | 1.3296 | 1.6186 | 0.13484 | 0.13484 | 0.13667 | 0.13667 | 0.13073 | 0.083193 | 0.45654 | 1 | 0.060295 | 0.060295 | 0.060295 | 1.1196 | 0.50061 | 0.1032 | 4.2408 | 0.77016 | 9.4924 | 1.1345 | 0.38249 | 0.11259 | 3.2167 | 0.53319 | 7.2756 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.85 | 23 | 19 | 34.4 | 50 | 270 | 10.7 | 0.249 |  | 6 | 8 | 0.047 | 5.93 | 8 |  | 5.9 | 8 | [8 empty] | 0.036 | [14 empty] | 0.029 | 1 | 0.43 |  | 0.036 | 0.019 | 1 | 0.46 |  | 0.039 | 1 | 0.6 | [38 empty] | 4080 | [6 empty] | 0 | 0 | 0 | 190 | 230 | 280 | 130 | 130 | 230 | 230 | 220 | 140 | 240 |  | 880 | 880 | 880 | 75 | 89 | 11 | 1300 | 260 | 501 | 38 | 34 | 6 | 440 | 90 | 192 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.24 | 0.056 | 1 | 4 | 9.8 |  |  |  | 7.55 | 0.053 | 1 | 4.1 | 10.1 |  |  |  | 3.7 | 4 | 3.4 | [55 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43134.8179 | 3,5,6 | 37 | 6 | 10.3 | 10.3 | 26.6 | 8.4 | 8.4 | 8.4 | 25.2 | 7,1 | 8.8618 | 1,2 | 16.7875 | 25.6493 | 1.4904 | 43134.8179 | 41.1052 | 1229.7476 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0598 | 1.3248 | 1.5367 | 0.14262 | 0.13311 | 0.13846 | 0.13846 | 0.12739 | 0.11077 | 1.2745 | 1 | 0.056526 | 0.056526 | 0.056526 | 1.0947 | 0.50014 | 0.1032 | 4.2787 | 0.80102 | 9.5003 | 1.0947 | 0.39186 | 0.1032 | 3.1253 | 0.57022 | 7.2598 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.92 | 23 | 22 | 38.7 | 46 | 274 | 10.2 | 0.236 |  | 5.75 | 10 | 0.047 | 5.74 | 10 |  | 5.71 | 10 | [8 empty] | 0.038 | [14 empty] | 0.024 | 1 | 0.59 |  | 0.033 | 0.02 | 1 | 0.35 |  | 0.042 | 1 | 0.61 | [38 empty] | 4472 | [6 empty] | 0 | 0 | 0 | 200 | 250 | 290 | 150 | 140 | 250 | 250 | 230 | 200 | 670 |  | 900 | 900 | 900 | 80 | 97 | 12 | 1480 | 295 | 547 | 40 | 38 | 6 | 500 | 105 | 209 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.179 | [9 empty] | 5.79 | 0.313 | 4 | 0.62 | 10.4 | 5.5 | 0.40105 |  | 5.88 | 0.447 | 4 | 0.7 | 9.9 | 9.6 | 0.76151 | 5.89 | 0.471 | 4 | 0.7 | 12 | 9.6 | 0.58222 |  |  |  | 0.012 | [9 empty] | 7.15 | 0.051 | 1 | 4 | 9.6 | 21 | 20 | 0.018 | 7.44 | 0.052 | 1 | 3.5 | 10.4 | 23 | 19 | 0.011 | 3.7 | 3.9 | 3.3 | [55 empty] | 9:00 | 0.62 | 5.5 | 46.2545 | 28.6778 | 5.79 | 10.4 | 13 | 2.206 | 10 | 6 | 0.28105 | 9:00 | 0.7 | 9.6 | 26.5 | 18.55 | 5.88 | 9.9 | 17 | 1.0912 | 5 | 6 | 0.64151 | 9:00 | 0.7 | 9.6 | 28.125 | 19.6875 | 5.89 | 12 | 13 | 1.5144 | 10 | 6 | 0.46222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.46 | 24 | 22 | 41.5 | 41 | 304 | 10.2 | 0.208 |  | 5.78 | 10 | 0.038 | 5.83 | 9 |  | 5.84 | 10 | [8 empty] | 0.036 | [14 empty] | 0.02 | 1 | 0.27 |  | 0.033 | 0.05 | 1 | 0.26 |  | 0.043 | 1 | 0.39 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.82 | 0.309 | 4 | 0.48 | 10.5 | 5.5 | 0.40105 |  | 5.91 | 0.418 | 4 | 0.7 | 9.7 | 9.5 | 0.75483 | 5.97 | 0.394 | 4 | 0.65 | 11.8 | 9.8 | 0.59185 | [13 empty] | 7.6 | 0.049 | 1 | 3.9 | 9.5 |  |  |  | 7.58 | 0.05 | 1 | 3.8 | 10.6 |  |  |  | 3.7 | 3.8 | 3.3 | [55 empty] | 13:00 | 0.48 | 5.5 | 46.2545 | 22.2022 | 5.82 | 10.5 | 13 | 1.7079 | 10 | 6 | 0.28105 | 13:00 | 0.7 | 9.5 | 26.7789 | 18.7453 | 5.91 | 9.7 | 17 | 1.1027 | 5 | 6 | 0.63483 | 13:00 | 0.65 | 9.8 | 27.551 | 17.9082 | 5.97 | 11.8 | 13 | 1.3776 | 10 | 6 | 0.47185
14:00 | [126 empty] | 285 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.9 | 23 | 21 | 29.1 | 40 | 230 | 10.3 | 0.241 |  | 5.76 | 9 | 0.046 | 5.76 | 8 |  | 5.76 | 8 | [8 empty] | 0.038 | [14 empty] | 0.024 | 1 | 0.25 |  | 0.035 | 0.02 | 1 | 0.27 |  | 0.042 | 1 | 0.41 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.31 | 0.067 | 1 | 3.8 | 9.6 |  |  |  | 7.87 | 0.049 | 1 | 4 | 10.5 |  |  |  | 3.7 | 3.7 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.89 | 23 | 21 | 28.7 | 50 | 228 | 10.2 | 0.257 |  | 6.3 | 9 | 0.061 | 6.38 | 9 |  | 6.38 | 9 | [8 empty] | 0.037 | [14 empty] | 0.024 | 1 | 0.3 |  | 0.039 | 0.028 | 1 | 0.36 |  | 0.04 | 1 | 0.43 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.131 | [9 empty] | 6 | 0.369 | 4 | 0.53 | 10.3 | 5.8 | 0.41638 |  | 6.06 | 0.43 | 4 | 0.89 | 9.5 | 10 | 0.90616 | 5.98 | 0.429 | 4 | 0.69 | 11.5 | 10 | 0.60148 |  |  |  | 0.022 | [9 empty] | 7.4 | 0.066 | 1 | 4 | 9.6 | 22 | 20 | 0.023 | 7.81 | 0.056 | 1 | 4.2 | 10.3 | 22 | 20 | 0.021 | 3.7 | 3.7 | 3.3 | [55 empty] | 21:00 | 0.53 | 5.8 | 43.8621 | 23.2469 | 6 | 10.3 | 13 | 1.7882 | 10 | 6 | 0.29638 | 21:00 | 0.89 | 10 | 25.44 | 22.6416 | 6.06 | 9.5 | 20 | 1.1321 | 5 | 6.5 | 0.78616 | 21:00 | 0.69 | 10 | 27 | 18.63 | 5.98 | 11.5 | 13 | 1.4331 | 10 | 6 | 0.48148
22:00 | [72 empty] | DOSE |  | TOTAL | 17.1 | 29.6 | 29.8 | 76.5 | 24 | 24 | 24 | 72 | 0 | 27.8899 | 0 | 43.4016 | 71.2915 | 3.9549 | TOTAL | 121.8538 | #N/A | 0 | 1200 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 3.2851 | 4.1193 | 4.564 | 0.42007 | 0.41056 | 0.39276 | 0.4104 | 0.39065 | 0.30921 | 3.0055 | 3 | 0.17692 | 0.17692 | 0.17692 | 3.3055 | 1.4777 | 0.307 | 12.7206 | 2.3507 | 28.4109 | 3.335 | 1.1691 | 0.30724 | 9.3773 | 1.652 | 21.6268 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.94 | 23 | 22 | 34.4 | 41 | 258 | 10.3 | 0.219 |  | 6.22 | 9 | 0.069 | 6.2 | 9 |  | 6.2 | 9 | [8 empty] | 0.047 | [14 empty] | 0.03 | 1 | 0.39 |  | 0.049 | 0.038 | 1 | 0.39 |  | 0.042 | 1 | 0.43 | [22 empty] | AVERAGE | 5.7 | 9.8667 | 9.9333 | 25.5 | 8 | 8 | 8 | 24 |  | 9.2966 |  | 14.4672 | 23.7638 | 1.3183 | AVERAGE | 40.6179 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.095 | 1.3731 | 1.5213 | 0.14002 | 0.13685 | 0.13092 | 0.1368 | 0.13022 | 0.10307 | 1.0018 | 1 | 0.058975 | 0.058975 | 0.058975 | 1.1018 | 0.49258 | 0.10233 | 4.2402 | 0.78357 | 9.4703 | 1.1117 | 0.3897 | 0.10241 | 3.1258 | 0.55066 | 7.2089 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.96 | 139 | 127 | 206.8 | 268 | 1564 | 61.9 | 1.41 | 0.31 | 35.81 | 55 | 0.308 | 35.84 | 53 | 0 | 35.79 | 54 | 0 | 23.59 | 1.323 | 16 | 2.29 | 42 | 22.3 | 1.6195 | 0.232 | 23.82 | 1.654 | 16 | 3.05 | 39.4 | 38.4 | 3.0177 | 23.82 | 1.733 | 16 | 2.84 | 47.4 | 38.9 | 2.353 | 0.151 | 6 | 2.23 | 0.034 | 0.225 | 0.175 | 6 | 2.09 | 0 | 0.248 | 6 | 2.87 | 0 | 43.99 | 0.348 | 6 | 23.7 | 58 | 43 | 40 | 0.041 | 45.69 | 0.316 | 6 | 23.7 | 62.4 | 45 | 39 | 0.032 | 22.2 | 23.1 | 19.5 |  |  | MINIMUM | 5.5 | 9.6 | 9.6 | 24.7 | 7.7 | 7.7 | 7.7 | 23.1 |  | 8.8618 |  | 13.307 | 22.8211 | 1.0633 | MINIMUM | 40.3617 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.0598 | 1.3248 | 1.4086 | 0.13484 | 0.13311 | 0.11762 | 0.13527 | 0.12739 | 0.083193 | 0.45654 | 1 | 0.056526 | 0.056526 | 0.056526 | 1.0912 | 0.47697 | 0.10059 | 4.2011 | 0.77016 | 9.4183 | 1.0947 | 0.38249 | 0.091447 | 3.0352 | 0.53319 | 7.0914 |  | MIN | 0.48 | 5.5 | 46.2545 | 22.2022 | 5.82 | 10.5 | 13 | 1.7079 |  |  |  | MIN | 0.7 | 9.6 | 26.5 | 18.55 | 5.88 | 9.9 | 17 | 1.0912 |  |  |  | MIN | 0.65 | 9.8 | 27.551 | 17.9082 | 5.97 | 11.8 | 13 | 1.3776 |  |  |  | 1.0912
AVERAGE | 6.8267 | 23.1667 | 21.1667 | 34.4667 | 44.6667 | 260.6667 | 10.3167 | 0.235 | 0.155 | 5.9683 | 9.1667 | 0.051333 | 5.9733 | 8.8333 |  | 5.965 | 9 |  | 5.8975 | 0.33075 | 4 | 0.5725 | 10.5 | 5.575 | 0.40489 | 0.038667 | 5.955 | 0.4135 | 4 | 0.7625 | 9.85 | 9.6 | 0.75443 | 5.955 | 0.43325 | 4 | 0.71 | 11.85 | 9.725 | 0.58824 | 0.025167 | 1 | 0.37167 | 0.017 | 0.0375 | 0.029167 | 1 | 0.34833 |  | 0.041333 | 1 | 0.47833 |  | 7.3317 | 0.058 | 1 | 3.95 | 9.6667 | 21.5 | 20 | 0.0205 | 7.615 | 0.052667 | 1 | 3.95 | 10.4 | 22.5 | 19.5 | 0.016 | 3.7 | 3.85 | 3.25 |  |  | MAXIMUM | 6 | 10.3 | 10.3 | 26.6 | 8.4 | 8.4 | 8.4 | 25.2 |  | 9.5141 |  | 16.7875 | 25.6493 | 1.4904 | MAXIMUM | 41.1052 | #N/A |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.1269 | 1.465 | 1.6186 | 0.14262 | 0.14262 | 0.13846 | 0.13846 | 0.13253 | 0.11525 | 1.2745 | 1 | 0.060295 | 0.060295 | 0.060295 | 1.1196 | 0.50061 | 0.1032 | 4.2787 | 0.80102 | 9.5003 | 1.1345 | 0.39474 | 0.11259 | 3.2167 | 0.57022 | 7.2756
MINIMUM | 6.46 | 23 | 19 | 28.7 | 40 | 228 | 10.2 | 0.208 | 0.131 | 5.75 | 8 | 0.038 | 5.74 | 8 |  | 5.71 | 8 |  | 5.79 | 0.309 | 4 | 0.48 | 10.3 | 5.5 | 0.40105 | 0.036 | 5.88 | 0.359 | 4 | 0.7 | 9.5 | 9.3 | 0.59524 | 5.89 | 0.394 | 4 | 0.65 | 11.5 | 9.5 | 0.57741 | 0.02 | 1 | 0.25 | 0.012 | 0.033 | 0.019 | 1 | 0.26 |  | 0.039 | 1 | 0.39 |  | 7.15 | 0.049 | 1 | 3.8 | 9.5 | 21 | 20 | 0.018 | 7.44 | 0.049 | 1 | 3.5 | 10.1 | 22 | 19 | 0.011 | 3.7 | 3.7 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 12712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 740 | 820 | 420 | 410 | 680 | 710 | 680 | 540 | 1580 | 0 | 2680 | 2680 | 2680 | 230 | 273 | 34 | 4100 | 825 | 1558 | 116 | 108 | 17 | 1360 | 290 | 593
MAXIMUM | 6.94 | 24 | 22 | 41.5 | 50 | 304 | 10.7 | 0.257 | 0.179 | 6.3 | 10 | 0.069 | 6.38 | 10 |  | 6.38 | 10 |  | 6 | 0.369 | 4 | 0.66 | 10.8 | 5.8 | 0.41638 | 0.047 | 6.06 | 0.447 | 4 | 0.89 | 10.3 | 10 | 0.90616 | 5.98 | 0.471 | 4 | 0.8 | 12.1 | 10 | 0.60148 | 0.03 | 1 | 0.59 | 0.022 | 0.049 | 0.05 | 1 | 0.46 |  | 0.043 | 1 | 0.61 |  | 7.6 | 0.067 | 1 | 4 | 9.9 | 22 | 20 | 0.023 | 7.87 | 0.056 | 1 | 4.2 | 10.6 | 23 | 20 | 0.021 | 3.7 | 4 | 3.4 | [17 empty] | AVERAGE | 4237.3333 | [9 empty] | 196.6667 | 246.6667 | 273.3333 | 140 | 136.6667 | 226.6667 | 236.6667 | 226.6667 | 180 | 526.6667 |  | 893.3333 | 893.3333 | 893.3333 | 76.6667 | 91 | 11.3333 | 1366.6667 | 275 | 519.3333 | 38.6667 | 36 | 5.6667 | 453.3333 | 96.6667 | 197.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9689 |  | TOTAL AVG COAG ALK: |  |  |  | 9 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.471 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.48 | [5 empty] | 5.9358 |  |  |  |  | 0.05 |  |  |  |  | 0.48 | [6 empty] | 0.05 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 4080 | [9 empty] | 190 | 230 | 250 | 130 | 130 | 200 | 230 | 220 | 140 | 240 |  | 880 | 880 | 880 | 75 | 87 | 11 | 1300 | 260 | 501 | 38 | 34 | 5 | 420 | 90 | 192
[90 empty] | MAXIMUM | 4472 | [9 empty] | 200 | 260 | 290 | 150 | 140 | 250 | 250 | 230 | 200 | 670 |  | 900 | 900 | 900 | 80 | 97 | 12 | 1480 | 295 | 547 | 40 | 38 | 6 | 500 | 105 | 209
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.358 |  | TOTAL MGD: |  | 4.527 |  |  | FINISHED SOUTH 1 |  | START: | 23065939 |  | END: | 23070466 |  |  | Alum | 5522 |  | 5964 |  | 0 | [45 empty] | 0.7 | 9.6 | 26.5 | 18.55 | 5.88 | 9.9 | 17 | 1.0912
[73 empty] | FINISHED 2 | 14.14 |  | TOTAL MGD: |  | 5.831 |  |  | FINISHED SOUTH 2 |  | START: | 40912778 |  | END: | 40918609 |  |  | Caustic | 5294 |  | 5790
[73 empty] | TOTAL RAW | 28.135 |  | TOTAL MGD: |  | 4.245 |  |  | FINISHED CONWAY |  | START: | 8673694 |  | END: | 8677939 |  |  | Hypochlorite | 12 |  | 33
[76 empty] | TOTAL MGD: |  | 9.895 |  |  | FINISHED PERRY |  | START: | 30315397 |  | END: | 30325292 |  |  | Phosphate | 3067
[76 empty] | TOTAL MGD: |  | 5.755 |  |  | RAW PLANT 1 |  | START: | 27875541 |  | END: | 27881296 |  |  | Fluoride | 2450 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.908 |  |  | RAW PLANT 2 |  | START: | 27802161 |  | END: | 27812069 |  |  | Cal~Flo | 11.93 | 0 | 0 | 11.83 | 84.2 | 25
[76 empty] | TOTAL MGD: |  | 12.472 |  |  | RAW PLANT 3 |  | START: | 4110206 |  | END: | 4122678 |  |  | Zinc | 3640
[76 empty] | TOTAL MGD: |  | 1.241 |  |  | DECANT |  | START: | 1377439 |  | END: | 1378680 |  |  | Polymer | 8 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.49872 |  |  | BLOW DOWN |  | START: | 8757.1465 |  | END: | 8757.6452 |  |  | NH3 | 654
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 1200 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 1632 | Phosphate | 51
[90 empty] | Caustic 1 | 205 | Fluoride | 0
[90 empty] | Caustic 2 | 80 | Zinc | 7
[90 empty] | Hypochlorite 1 | 133 | Polymer 1 | 1.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1
[91 empty] | FINISHED SOUTH 1 |  | END: | 23070466
[91 empty] | FINISHED SOUTH 2 |  | END: | 40918609
[91 empty] | FINISHED CONWAY |  | END: | 8677939
[91 empty] | FINISHED PERRY |  | END: | 30325292
[91 empty] | RAW PLANT 1 |  | END: | 27881296
[91 empty] | RAW PLANT 2 |  | END: | 27812069
[91 empty] | RAW PLANT 3 |  | END: | 4122678
[91 empty] | DECANT |  | END: | 1378680
[91 empty] | BLOW DOWN |  | END: | 8757.6452
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.comBCOperator:
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 4
DATE: | 2018-02-04 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-04 | [23 empty] | DATE: | 2018-02-04
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-04 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43135.0366 | 3,5,6 | 37 | 6 | 10.3 | 10.3 | 26.6 | 8.4 | 8.4 | 8.4 | 25.2 | 7,1 | 8.8618 | 1,2 | 16.7875 | 25.6493 | 1.4904 | 43135.0366 | 41.1052 | 1229.7476 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0598 | 1.3248 | 1.5367 | 0.13311 | 0.13311 | 0.11077 | 0.11077 | 0.11077 | 0.099694 | 1.2745 | 1 | 0.056526 | 0.056526 | 0.056526 | 1.0947 | 0.50014 | 0.1032 | 4.2787 | 0.80102 | 9.0834 | 1.0947 | 0.39186 | 0.1032 | 3.1253 | 0.57022 | 6.5998 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.18 | 0.363 | 4 | 0.59 | 10.5 | 5.9 | 0.46788 |  | 6.2 | 0.359 | 4 | 0.89 | 9.7 | 10.2 | 0.92189 | 6.17 | 0.376 | 4 | 0.7 | 11.8 | 10.6 | 0.70889 | [13 empty] | 7.81 | 0.059 | 1 | 4.3 | 9.4 |  |  |  | 8 | 0.056 | 1 | 4.1 | 10.1 |  |  |  | 3.7 | 3.8 | 3.3 | [18 empty] | 4472 | [6 empty] | 0 | 0 | 0 | 200 | 250 | 290 | 140 | 140 | 200 | 200 | 200 | 180 | 670 |  | 900 | 900 | 900 | 80 | 97 | 12 | 1480 | 295 | 523 | 40 | 38 | 6 | 500 | 105 | 190 |  | 1:00 | 0.59 | 5.9 | 43.1186 | 25.44 | 6.18 | 10.5 | 15 | 1.696 | 10 | 6.5 | 0.34788 | 1:00 | 0.89 | 10.2 | 24.9412 | 22.1976 | 6.2 | 9.7 | 20 | 1.1099 | 5 | 6.5 | 0.80189 | 1:00 | 0.7 | 10.6 | 25.4717 | 17.8302 | 6.17 | 11.8 | 15 | 1.1887 | 10 | 6.5 | 0.58889
2:00 | [72 empty] | 43135.1445 | 3,5,6 | 42 | 8 | 10.5 | 10.5 | 29 | 9.2 | 9.2 | 9.2 | 27.6 | 7,1 | 10.8418 | 1,2 | 16.9402 | 27.7819 | 1.4904 | 43135.1445 | 40.4688 | 1229.7476 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0.96766 | 1.2096 | 1.4031 | 0.10696 | 0.10696 | 0.10866 | 0.10866 | 0.10866 | 0.097795 | 1.2745 | 1 | 0.057345 | 0.057345 | 0.057345 | 1.0995 | 0.49902 | 0.09423 | 4.0284 | 0.80326 | 9.1182 | 1.0995 | 0.40487 | 0.09423 | 3.038 | 0.54543 | 6.5968 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.87 | 24 | 21 | 29.6 | 40 | 240 | 10 | 0.249 |  | 6.06 | 10 | 0.069 | 6 | 10 |  | 6 | 10 | [8 empty] | 0.045 | [14 empty] | 0.03 | 1 | 0.39 |  | 0.046 | 0.035 | 1 | 0.38 |  | 0.039 | 1 | 0.4 | [38 empty] | 4800 | [6 empty] | 0 | 0 | 0 | 200 | 250 | 290 | 150 | 150 | 200 | 200 | 200 | 180 | 670 |  | 1000 | 1000 | 1000 | 88 | 106 | 12 | 1520 | 324 | 575 | 44 | 43 | 6 | 530 | 110 | 208 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43135.3733 | 3,5,6 | 42 | 8 | 10.5 | 10.5 | 29 | 9.2 | 9.2 | 9.2 | 27.6 | 7,1 | 10.8418 | 1,2 | 16.9402 | 27.7819 | 0 | 43135.3733 | 45.3587 | 922.3106 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0644 | 1.3547 | 1.5483 | 0.12479 | 0.12836 | 0.13039 | 0.13039 | 0.13039 | 0.097795 | 0.38045 | 0 | 0.060213 | 0.060213 | 0.060213 | 1.0995 | 0 | 0.09423 | 4.1771 | 0.80574 | 9.1023 | 1.0995 | 0.40487 | 0.09423 | 3.1867 | 0.57022 | 6.5968 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.4 | 0.056 | 1 | 4.2 | 9.2 |  |  |  | 7.8 | 0.054 | 1 | 4 | 10.2 |  |  |  | 3.7 | 3.9 | 3.4 | [18 empty] | 5380 | [6 empty] | 0 | 0 | 0 | 220 | 280 | 320 | 175 | 180 | 240 | 240 | 240 | 180 | 200 |  | 1050 | 1050 | 1050 | 88 | 0 | 12 | 1580 | 325 | 574 | 44 | 43 | 6 | 560 | 115 | 208 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43135.6455 | 3,5,6 | 42 | 6.2 | 10.7 | 10.7 | 27.6 | 8.7 | 8.7 | 8.7 | 26.1 | 7,1 | 10.8418 | 1,2 | 16.9402 | 27.7819 | 0 | 43135.6455 | 45.3563 | 1352.7224 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0233 | 1.3303 | 1.5093 | 0.13802 | 0.13802 | 0.12796 | 0.13062 | 0.12796 | 0.095967 | 0.38045 | 0 | 0.060641 | 0.060641 | 0.060035 | 1.1098 | 0.49783 | 0.099646 | 4.245 | 0.79962 | 9.1056 | 1.1098 | 0.39827 | 0.099646 | 3.1366 | 0.57677 | 6.607 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.64 | 22 | 22 | 28 | 45 | 225 | 9.7 | 0.288 |  | 5.68 | 10 | 0.051 | 5.71 | 11 |  | 5.72 | 10 | [8 empty] | 0.037 | [14 empty] | 0.026 | 1 | 0.35 |  | 0.036 | 0.038 | 1 | 0.41 |  | 0.045 | 1 | 0.36 | [38 empty] | 5120 | [6 empty] | 0 | 0 | 0 | 200 | 260 | 295 | 150 | 150 | 240 | 245 | 240 | 180 | 200 |  | 1000 | 1000 | 990 | 84 | 100 | 12 | 1520 | 305 | 543 | 42 | 40 | 6 | 520 | 110 | 197 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43135.8209 | 3,5,6 | 42 | 6.2 | 10.7 | 10.7 | 27.6 | 8.7 | 8.7 | 8.7 | 26.1 | 7,1 | 11.317 | 1,2 | 15.4742 | 26.7912 | 0.87552 | 43135.8209 | 45.3563 | 1229.7476 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.2791 | 1.5349 | 1.5349 | 0.15182 | 0.13802 | 0.12796 | 0.12796 | 0.11996 | 0.13329 | 1.4457 | 1 | 0.060641 | 0.060641 | 0.060641 | 1.0966 | 0.49783 | 0.099646 | 4.1925 | 0.81272 | 9.1894 | 1.1098 | 0.49783 | 0.099646 | 3.1366 | 0.57677 | 6.607 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.123 | [9 empty] | 5.9 | 0.491 | 4 | 0.64 | 9.9 | 8 | 0.65459 |  | 5.94 | 0.531 | 4 | 0.8 | 9.3 | 10.5 | 0.82165 | 5.95 | 0.405 | 4 | 0.65 | 11.1 | 10.5 | 0.62556 |  |  |  | 0.026 | [9 empty] | 7.61 | 0.061 | 1 | 4.2 | 9.1 | 23 | 22 | 0.028 | 7.78 | 0.051 | 1 | 4.2 | 10.1 | 21 | 24 | 0.031 | 3.7 | 3.8 | 3.5 | [18 empty] | 5120 | [6 empty] | 0 | 0 | 0 | 250 | 300 | 300 | 165 | 150 | 240 | 240 | 225 | 250 | 760 |  | 1000 | 1000 | 1000 | 83 | 100 | 12 | 1500 | 310 | 548 | 42 | 50 | 6 | 520 | 110 | 197 |  | 9:00 | 0.64 | 8 | 31.8 | 20.352 | 5.9 | 9.9 | 17 | 1.1972 | 5 | 6 | 0.53459 | 9:00 | 0.8 | 10.5 | 24.2286 | 19.3829 | 5.94 | 9.3 | 17 | 1.1402 | 5 | 6 | 0.70165 | 9:00 | 0.65 | 10.5 | 25.7143 | 16.7143 | 5.95 | 11.1 | 13 | 1.2857 | 10 | 6 | 0.50556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.84 | 22 | 22 | 30.1 | 46 | 247 | 9.8 | 0.262 |  | 5.75 | 10 | 0.055 | 5.76 | 9 |  | 5.8 | 9 | [8 empty] | 0.031 | [14 empty] | 0.026 | 1 | 0.42 |  | 0.035 | 0.033 | 1 | 0.48 |  | 0.044 | 1 | 0.48 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.93 | 0.402 | 4 | 0.59 | 10.3 | 8 | 0.52881 |  | 5.89 | 0.582 | 4 | 0.75 | 9.8 | 10.5 | 0.82165 | 5.92 | 0.51 | 4 | 0.65 | 11.2 | 10.5 | 0.62556 | [13 empty] | 7.57 | 0.061 | 1 | 4.4 | 9.3 |  |  |  | 7.55 | 0.067 | 1 | 3.7 | 10.6 |  |  |  | 3.8 | 3.8 | 3.5 | [55 empty] | 13:00 | 0.59 | 8 | 31.8 | 18.762 | 5.93 | 10.3 | 13 | 1.4432 | 10 | 6 | 0.40881 | 13:00 | 0.75 | 10.5 | 24.2286 | 18.1714 | 5.89 | 9.8 | 17 | 1.0689 | 5 | 6 | 0.70165 | 13:00 | 0.65 | 10.5 | 25.7143 | 16.7143 | 5.92 | 11.2 | 13 | 1.2857 | 10 | 6 | 0.50556
14:00 | [126 empty] | 290 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.78 | 21 | 22 | 25 | 55 | 215 | 9.8 | 0.284 |  | 5.7 | 9 | 0.06 | 5.69 | 9 |  | 5.7 | 9 | [8 empty] | 0.034 | [14 empty] | 0.026 | 1 | 0.4 |  | 0.042 | 0.018 | 1 | 0.29 |  | 0.044 | 1 | 0.44 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.42 | 0.063 | 1 | 4.4 | 9.4 |  |  |  | 7.44 | 0.058 | 1 | 4.1 | 10.7 |  |  |  | 3.8 | 3.9 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.86 | 22 | 22 | 22.5 | 58 | 198 | 10 | 0.32 |  | 5.7 | 9 | 0.079 | 5.7 | 9 |  | 5.7 | 9 | [8 empty] | 0.06 | [14 empty] | 0.029 | 1 | 0.44 |  | 0.065 | 0.022 | 1 | 0.33 |  | 0.042 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.101 | [9 empty] | 5.96 | 0.403 | 4 | 0.6 | 10.8 | 8 | 0.52881 |  | 5.93 | 0.469 | 4 | 0.82 | 9.8 | 10.5 | 0.82165 | 5.96 | 0.593 | 4 | 0.66 | 11.1 | 10.5 | 0.62556 |  |  |  | 0.022 | [9 empty] | 7.38 | 0.063 | 1 | 4.4 | 9.5 | 22 | 23 | 0.019 | 7.57 | 0.066 | 1 | 4.2 | 10.6 | 22 | 23 | 0.03 | 3.8 | 3.9 | 3.5 | [55 empty] | 21:00 | 0.6 | 8 | 31.8 | 19.08 | 5.96 | 10.8 | 13 | 1.4677 | 10 | 6 | 0.40881 | 21:00 | 0.82 | 10.5 | 24.2286 | 19.8674 | 5.93 | 9.8 | 17 | 1.1687 | 5 | 6 | 0.70165 | 21:00 | 0.66 | 10.5 | 25.7143 | 16.9714 | 5.96 | 11.1 | 13 | 1.3055 | 10 | 6 | 0.50556
22:00 | [72 empty] | DOSE |  | TOTAL | 34.4 | 52.7 | 52.7 | 139.8 | 44.2 | 44.2 | 44.2 | 132.6 | 0 | 52.704 | 0 | 83.0822 | 135.7862 | 3.8563 | TOTAL | 217.6453 | 5964.2758 | 0 | 2000 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 5.3943 | 6.7543 | 7.5324 | 0.6547 | 0.64446 | 0.60574 | 0.6084 | 0.59774 | 0.52454 | 4.7556 | 3 | 0.29537 | 0.29537 | 0.29476 | 5.5 | 1.9948 | 0.49096 | 20.9217 | 4.0224 | 45.599 | 5.5132 | 2.0977 | 0.49096 | 15.6231 | 2.8394 | 33.0075 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.86 | 22 | 22 | 24.3 | 57 | 223 | 10.3 | 0.299 |  | 6.05 | 9 | 0.063 | 6.01 | 9 |  | 5.97 | 9 | [8 empty] | 0.056 | [14 empty] | 0.028 | 1 | 0.43 |  | 0.053 | 0.025 | 1 | 0.36 |  | 0.045 | 1 | 0.43 | [22 empty] | AVERAGE | 6.88 | 10.54 | 10.54 | 27.96 | 8.84 | 8.84 | 8.84 | 26.52 |  | 10.5408 |  | 16.6164 | 27.1572 | 0.77126 | AVERAGE | 43.5291 | 1192.8552 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.0789 | 1.3509 | 1.5065 | 0.13094 | 0.12889 | 0.12115 | 0.12168 | 0.11955 | 0.10491 | 0.95112 | 0.6 | 0.059073 | 0.059073 | 0.058952 | 1.1 | 0.39897 | 0.098192 | 4.1843 | 0.80447 | 9.1198 | 1.1026 | 0.41954 | 0.098192 | 3.1246 | 0.56788 | 6.6015 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.85 | 133 | 131 | 159.5 | 301 | 1348 | 59.6 | 1.702 | 0.224 | 34.94 | 57 | 0.377 | 34.87 | 57 | 0 | 34.89 | 56 | 0 | 23.97 | 1.659 | 16 | 2.42 | 41.5 | 29.9 | 2.1801 | 0.263 | 23.96 | 1.941 | 16 | 3.26 | 38.6 | 41.7 | 3.3868 | 24 | 1.884 | 16 | 2.66 | 45.2 | 42.1 | 2.5856 | 0.165 | 6 | 2.43 | 0.048 | 0.277 | 0.171 | 6 | 2.25 | 0 | 0.259 | 6 | 2.57 | 0 | 45.19 | 0.363 | 6 | 25.9 | 55.9 | 45 | 45 | 0.047 | 46.14 | 0.352 | 6 | 24.3 | 62.3 | 43 | 47 | 0.061 | 22.5 | 23.1 | 20.6 |  |  | MINIMUM | 6 | 10.3 | 10.3 | 26.6 | 8.4 | 8.4 | 8.4 | 25.2 |  | 8.8618 |  | 15.4742 | 25.6493 | 0 | MINIMUM | 40.4688 | 922.3106 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 0.96766 | 1.2096 | 1.4031 | 0.10696 | 0.10696 | 0.10866 | 0.10866 | 0.10866 | 0.095967 | 0.38045 | 0 | 0.056526 | 0.056526 | 0.056526 | 1.0947 | 0 | 0.09423 | 4.0284 | 0.79962 | 9.0834 | 1.0947 | 0.39186 | 0.09423 | 3.038 | 0.54543 | 6.5968 |  | MIN | 0.64 | 8 | 31.8 | 20.352 | 5.9 | 9.9 | 17 | 1.1972 |  |  |  | MIN | 0.75 | 10.5 | 24.2286 | 18.1714 | 5.89 | 9.8 | 17 | 1.0689 |  |  |  | MIN | 0.7 | 10.6 | 25.4717 | 17.8302 | 6.17 | 11.8 | 15 | 1.1887 |  |  |  | 1.0689
AVERAGE | 6.8083 | 22.1667 | 21.8333 | 26.5833 | 50.1667 | 224.6667 | 9.9333 | 0.28367 | 0.112 | 5.8233 | 9.5 | 0.062833 | 5.8117 | 9.5 |  | 5.815 | 9.3333 |  | 5.9925 | 0.41475 | 4 | 0.605 | 10.375 | 7.475 | 0.54502 | 0.043833 | 5.99 | 0.48525 | 4 | 0.815 | 9.65 | 10.425 | 0.84671 | 6 | 0.471 | 4 | 0.665 | 11.3 | 10.525 | 0.64639 | 0.0275 | 1 | 0.405 | 0.024 | 0.046167 | 0.0285 | 1 | 0.375 |  | 0.043167 | 1 | 0.42833 |  | 7.5317 | 0.0605 | 1 | 4.3167 | 9.3167 | 22.5 | 22.5 | 0.0235 | 7.69 | 0.058667 | 1 | 4.05 | 10.3833 | 21.5 | 23.5 | 0.0305 | 3.75 | 3.85 | 3.4333 |  |  | MAXIMUM | 8 | 10.7 | 10.7 | 29 | 9.2 | 9.2 | 9.2 | 27.6 |  | 11.317 |  | 16.9402 | 27.7819 | 1.4904 | MAXIMUM | 45.3587 | 1352.7224 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.2791 | 1.5349 | 1.5483 | 0.15182 | 0.13802 | 0.13039 | 0.13062 | 0.13039 | 0.13329 | 1.4457 | 1 | 0.060641 | 0.060641 | 0.060641 | 1.1098 | 0.50014 | 0.1032 | 4.2787 | 0.81272 | 9.1894 | 1.1098 | 0.49783 | 0.1032 | 3.1867 | 0.57677 | 6.607
MINIMUM | 6.64 | 21 | 21 | 22.5 | 40 | 198 | 9.7 | 0.249 | 0.101 | 5.68 | 9 | 0.051 | 5.69 | 9 |  | 5.7 | 9 |  | 5.9 | 0.363 | 4 | 0.59 | 9.9 | 5.9 | 0.46788 | 0.031 | 5.89 | 0.359 | 4 | 0.75 | 9.3 | 10.2 | 0.82165 | 5.92 | 0.376 | 4 | 0.65 | 11.1 | 10.5 | 0.62556 | 0.026 | 1 | 0.35 | 0.022 | 0.035 | 0.018 | 1 | 0.29 |  | 0.039 | 1 | 0.36 |  | 7.38 | 0.056 | 1 | 4.2 | 9.1 | 22 | 22 | 0.019 | 7.44 | 0.051 | 1 | 3.7 | 10.1 | 21 | 23 | 0.03 | 3.7 | 3.8 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 24892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 1340 | 1495 | 780 | 770 | 1120 | 1125 | 1105 | 970 | 2500 | 0 | 4950 | 4950 | 4940 | 423 | 403 | 60 | 7600 | 1559 | 2763 | 212 | 214 | 30 | 2630 | 550 | 1000
MAXIMUM | 6.87 | 24 | 22 | 30.1 | 58 | 247 | 10.3 | 0.32 | 0.123 | 6.06 | 10 | 0.079 | 6.01 | 11 |  | 6 | 10 |  | 6.18 | 0.491 | 4 | 0.64 | 10.8 | 8 | 0.65459 | 0.06 | 6.2 | 0.582 | 4 | 0.89 | 9.8 | 10.5 | 0.92189 | 6.17 | 0.593 | 4 | 0.7 | 11.8 | 10.6 | 0.70889 | 0.03 | 1 | 0.44 | 0.026 | 0.065 | 0.038 | 1 | 0.48 |  | 0.045 | 1 | 0.48 |  | 7.81 | 0.063 | 1 | 4.4 | 9.5 | 23 | 23 | 0.028 | 8 | 0.067 | 1 | 4.2 | 10.7 | 22 | 24 | 0.031 | 3.8 | 3.9 | 3.5 | [17 empty] | AVERAGE | 4978.4 | [9 empty] | 214 | 268 | 299 | 156 | 154 | 224 | 225 | 221 | 194 | 500 |  | 990 | 990 | 988 | 84.6 | 80.6 | 12 | 1520 | 311.8 | 552.6 | 42.4 | 42.8 | 6 | 526 | 110 | 200
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.8167 |  | TOTAL AVG COAG ALK: |  |  |  | 9.4444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.593 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.59 | [5 empty] | 5.9942 |  |  |  |  | 0.045 |  |  |  |  | 0.59 | [6 empty] | 0.045 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 4472 | [9 empty] | 200 | 250 | 290 | 140 | 140 | 200 | 200 | 200 | 180 | 200 |  | 900 | 900 | 900 | 80 | 0 | 12 | 1480 | 295 | 523 | 40 | 38 | 6 | 500 | 105 | 190
[90 empty] | MAXIMUM | 5380 | [9 empty] | 250 | 300 | 320 | 175 | 180 | 240 | 245 | 240 | 250 | 760 |  | 1050 | 1050 | 1050 | 88 | 106 | 12 | 1580 | 325 | 575 | 44 | 50 | 6 | 560 | 115 | 208
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.23 |  | TOTAL MGD: |  | 5.355 |  |  | FINISHED SOUTH 1 |  | START: | 23070466 |  | END: | 23075821 |  |  | Alum | 5052 |  | 5543 |  | 0 | [45 empty] | 0.75 | 10.5 | 24.2286 | 18.1714 | 5.89 | 9.8 | 17 | 1.0689
[73 empty] | FINISHED 2 | 14.577 |  | TOTAL MGD: |  | 5.875 |  |  | FINISHED SOUTH 2 |  | START: | 40918609 |  | END: | 40924484 |  |  | Caustic | 5118 |  | 5693
[73 empty] | TOTAL RAW | 27.554 |  | TOTAL MGD: |  | 4.279 |  |  | FINISHED CONWAY |  | START: | 8677939 |  | END: | 8682218 |  |  | Hypochlorite | 11 |  | 31.5
[76 empty] | TOTAL MGD: |  | 10.298 |  |  | FINISHED PERRY |  | START: | 30325292 |  | END: | 30335590 |  |  | Phosphate | 2974
[76 empty] | TOTAL MGD: |  | 6.148 |  |  | RAW PLANT 1 |  | START: | 27881296 |  | END: | 27887444 |  |  | Fluoride | 2400 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.589 |  |  | RAW PLANT 2 |  | START: | 27812069 |  | END: | 27822658 |  |  | Cal~Flo | 11.83 | 0 | 0 | 11.4 | 362.06 | 25
[76 empty] | TOTAL MGD: |  | 10.817 |  |  | RAW PLANT 3 |  | START: | 4122678 |  | END: | 4133495 |  |  | Zinc | 3.1
[76 empty] | TOTAL MGD: |  | 1.051 |  |  | DECANT |  | START: | 1378680 |  | END: | 1379731 |  |  | Polymer | 8 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.52325 |  |  | BLOW DOWN |  | START: | 8757.6452 |  | END: | 8758.1684 |  |  | NH3 | 6.33
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 1100 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 1877 | Phosphate | 27
[90 empty] | Caustic 1 | 209 | Fluoride | 0
[90 empty] | Caustic 2 | 81 | Zinc | 7.5
[90 empty] | Hypochlorite 1 | 156 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23075821
[91 empty] | FINISHED SOUTH 2 |  | END: | 40924484
[91 empty] | FINISHED CONWAY |  | END: | 8682218
[91 empty] | FINISHED PERRY |  | END: | 30335590
[91 empty] | RAW PLANT 1 |  | END: | 27887444
[91 empty] | RAW PLANT 2 |  | END: | 27822658
[91 empty] | RAW PLANT 3 |  | END: | 4133495
[91 empty] | DECANT |  | END: | 1379731
[91 empty] | BLOW DOWN |  | END: | 8758.1684
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 5
DATE: | 2018-02-05 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-05 | [23 empty] | DATE: | 2018-02-05
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-05 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43136.02 | 3,5,6 | 42 | 6.2 | 10.7 | 10.7 | 27.6 | 8.7 | 8.7 | 8.7 | 26.1 | 7,1 | 11.317 | 1,2 | 15.4742 | 26.7912 | 0.87552 | 43136.02 | 45.3563 | 1229.7476 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.2791 | 1.5349 | 1.5349 | 0.14722 | 0.14722 | 0.13329 | 0.13329 | 0.11996 | 0.13329 | 1.4457 | 1 | 0.060641 | 0.060641 | 0.060641 | 1.0966 | 0.49783 | 0.099646 | 4.1925 | 0.81272 | 9.1894 | 1.1098 | 0.49783 | 0.099646 | 3.1366 | 0.57677 | 6.607 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.91 | 0.396 | 5 | 0.53 | 10.3 | 6 | 0.4266 |  | 5.92 | 0.399 | 4 | 0.8 | 9.7 | 10.3 | 0.80829 | 5.94 | 0.579 | 5 | 0.6 | 11.6 | 10.4 | 0.62074 | [13 empty] | 7.69 | 0.07 | 1 | 4.2 | 9.9 |  |  |  | 7.86 | 0.073 | 1 | 4.2 | 10.6 |  |  |  | 3.9 | 3.8 | 4.2 | [18 empty] | 5120 | [6 empty] | 0 | 0 | 0 | 250 | 300 | 300 | 160 | 160 | 250 | 250 | 225 | 250 | 760 |  | 1000 | 1000 | 1000 | 83 | 100 | 12 | 1500 | 310 | 548 | 42 | 50 | 6 | 520 | 110 | 197 |  | 1:00 | 0.53 | 6 | 42.4 | 22.472 | 5.91 | 10.3 | 13 | 1.7286 | 10 | 6 | 0.3066 | 1:00 | 0.8 | 10.3 | 24.699 | 19.7592 | 5.92 | 9.7 | 17 | 1.1623 | 5 | 6 | 0.68829 | 1:00 | 0.6 | 10.4 | 25.9615 | 15.5769 | 5.94 | 11.6 | 13 | 1.1982 | 10 | 6 | 0.50074
2:00 | [72 empty] | 43136.3527 | 3,5,6 | 33 | 5.6 | 10 | 10 | 25.6 | 8 | 8 | 8 | 24 | 7,1 | 11.317 | 1,2 | 15.4742 | 26.7912 | 0 | 43136.3527 | 50.4279 | 1352.7224 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.1128 | 1.4467 | 1.6136 | 0.1528 | 0.1528 | 0.13691 | 0.13691 | 0.13121 | 0.10268 | 0 | 0 | 0.060671 | 0.060671 | 0.060012 | 1.1207 | 0.49808 | 0.099335 | 4.28 | 0.7983 | 9.1182 | 1.092 | 0.3898 | 0.10837 | 3.2041 | 0.57022 | 6.6016 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.9 | 22 | 21 | 25.9 | 63 | 218 | 10.5 | 0.321 |  | 5.9 | 9 | 0.058 | 5.83 | 9 |  | 5.83 | 9 | [8 empty] | 0.046 | [14 empty] | 0.031 | 1 | 0.39 |  | 0.046 | 0.036 | 1 | 0.59 |  | 0.045 | 1 | 0.36 | [38 empty] | 5280 | [6 empty] | 0 | 0 | 0 | 200 | 260 | 290 | 150 | 150 | 240 | 240 | 230 | 180 | 760 |  | 920 | 920 | 910 | 78 | 92 | 11 | 1410 | 280 | 500 | 38 | 36 | 6 | 490 | 100 | 181 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43136.795 | 3,5,6 | 33 | 5.6 | 10 | 10 | 25.6 | 8 | 8 | 8 | 24 | 7,1 | 10.9958 | 1,2 | 13.1774 | 24.1733 | 1.5466 | 43136.795 | 65.9001 | 3258.8318 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.3354 | 1.5579 | 1.6692 | 0 | 0.1528 | 0.14832 | 0.14832 | 0.14832 | 0.13691 | 1.2745 | 2 | 0.060671 | 0.060671 | 0.060671 | 1.1063 | 0.49808 | 0.10837 | 4.18 | 0.82682 | 9.2458 | 1.092 | 0.3898 | 0.10837 | 3.1351 | 0.62724 | 5.8721 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.63 | 0.069 | 1 | 4.2 | 9.8 |  |  |  | 7.89 | 0.07 | 1 | 4.2 | 10.5 |  |  |  | 3.9 | 3.8 | 4 | [18 empty] | 6900 | [6 empty] | 0 | 0 | 0 | 240 | 280 | 300 | 0 | 300 | 260 | 260 | 260 | 240 | 670 |  | 920 | 920 | 920 | 77 | 92 | 12 | 1410 | 290 | 507 | 38 | 36 | 6 | 520 | 110 | 161 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.82 | 23 | 21 | 24.2 | 64 | 214 | 10.4 | 0.333 |  | 5.71 | 8 | 0.061 | 5.7 | 8 |  | 5.71 | 8 | [8 empty] | 0.054 | [14 empty] | 0.041 | 1 | 0.42 |  | 0.05 | 0.043 | 1 | 0.55 |  | 0.043 | 1 | 0.39 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.98 | [9 empty] | 5.83 | 0.582 | 5 | 0.37 | 10.3 | 5.6 | 0.40616 |  | 5.87 | 0.58 | 4 | 0.54 | 10 | 10 | 0.63101 | 5.9 | 0.596 | 5 | 0.5 | 11.6 | 9.8 | 0.59185 |  |  |  | 0.29 | [9 empty] | 7.84 | 0.063 | 1 | 4.5 | 10.5 | 25 | 36 | 0.19 | 8.06 | 0.065 | 1 | 4.4 | 10.6 | 26 | 39 | 0.19 | 4 | 3.9 | 2.9 | [55 empty] | 9:00 | 0.37 | 5.6 | 45.4286 | 16.8086 | 5.83 | 10.3 | 13 | 1.293 | 10 | 6 | 0.28616 | 9:00 | 0.54 | 10 | 25.44 | 13.7376 | 5.87 | 10 | 13 | 1.0567 | 10 | 6 | 0.51101 | 9:00 | 0.5 | 9.8 | 27.551 | 13.7755 | 5.9 | 11.6 | 13 | 1.0597 | 10 | 6 | 0.47185
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.71 | 22 | 22 | 23 | 63 | 209 | 10.4 | 0.345 |  | 5.76 | 8 | 0.068 | 5.75 | 8 |  | 5.74 | 7 | [8 empty] | 0.056 | [14 empty] | 0.039 | 1 | 0.4 |  | 0.054 | 0.04 | 1 | 0.52 |  | 0.044 | 1 | 0.36 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.8 | 0.899 | 7 | 0.4 | 10.2 | 5 | 0.3755 |  | 5.85 | 0.67 | 5 | 0.53 | 10.3 | 10 | 0.63101 | 5.9 | 0.657 | 5 | 0.52 | 12 | 10 | 0.60148 | [13 empty] | 7.61 | 0.061 | 1 | 3.9 | 9.8 |  |  |  | 8.01 | 0.069 | 1 | 3.9 | 11.2 |  |  |  | 4.5 | 3.9 | 3 | [55 empty] | 13:00 | 0.4 | 5 | 50.88 | 20.352 | 5.8 | 10.2 | 13 | 1.5655 | 10 | 6 | 0.2555 | 13:00 | 0.53 | 10 | 25.44 | 13.4832 | 5.85 | 10.3 | 13 | 1.0372 | 10 | 6 | 0.51101 | 13:00 | 0.52 | 10 | 27 | 14.04 | 5.9 | 12 | 13 | 1.08 | 10 | 6 | 0.48148
14:00 | [126 empty] | 272 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.72 | 23 | 21 | 19.7 | 61 | 200 | 10.7 | 0.351 |  | 5.91 | 10 | 0.071 | 5.89 | 10 |  | 5.9 | 10 | [8 empty] | 0.054 | [14 empty] | 0.059 | 1 | 0.18 |  | 0.056 | 0.026 | 1 | 0.14 |  | 0.046 | 1 | 0.17 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.55 | 0.057 | 1 | 4.2 | 10 |  |  |  | 7.91 | 0.06 | 1 | 4.1 | 11.1 |  |  |  | 4.5 | 3.9 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.81 | 23 | 21 | 18 | 65 | 179 | 11.4 | 0.347 |  | 5.8 | 9 | 0.056 | 5.8 | 9 |  | 5.8 | 9 | [8 empty] | 0.051 | [14 empty] | 0.046 | 1 | 0.2 |  | 0.043 | 0.018 | 1 | 0.23 |  | 0.042 | 1 | 0.23 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.071 | [9 empty] | 5.81 | 0.642 | 5 | 0.8 | 9.9 | 5 | 0.45412 |  | 5.83 | 0.557 | 5 | 0.59 | 10.1 | 9.9 | 0.6259 | 5.83 | 0.669 | 5 | 0.63 | 11.3 | 10.6 | 0.63037 |  |  |  | 0.025 | [9 empty] | 7.73 | 0.063 | 1 | 4.3 | 9.9 | 26 | 38 | 0.023 | 7.76 | 0.063 | 1 | 4.6 | 10.7 | 26 | 38 | 0.025 | 4.4 | 4 | 3 | [55 empty] | 21:00 | 0.8 | 5 | 50.88 | 40.704 | 5.81 | 9.9 | 17 | 2.3944 | 5 | 6 | 0.33412 | 21:00 | 0.59 | 9.9 | 25.697 | 15.1612 | 5.83 | 10.1 | 13 | 1.1662 | 10 | 6 | 0.5059 | 21:00 | 0.63 | 10.6 | 25.4717 | 16.0472 | 5.83 | 11.3 | 13 | 1.2344 | 10 | 6 | 0.51037
22:00 | [72 empty] | DOSE |  | TOTAL | 17.4 | 30.7 | 30.7 | 78.8 | 24.7 | 24.7 | 24.7 | 74.1 | 0 | 33.6298 | 0 | 44.1259 | 77.7557 | 2.4221 | TOTAL | 161.6842 | 5841.3018 | 0 | 1200 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 3.7273 | 4.5395 | 4.8177 | 0.30002 | 0.45283 | 0.41852 | 0.41852 | 0.39949 | 0.37288 | 2.7202 | 3 | 0.18198 | 0.18198 | 0.18132 | 3.3236 | 1.494 | 0.30735 | 12.6526 | 2.4378 | 27.5535 | 3.2937 | 1.2774 | 0.31638 | 9.4758 | 1.7742 | 19.0807 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.76 | 23 | 21 | 22 | 63 | 200 | 11.3 | 0.313 |  | 5.95 | 9 | 0.059 | 5.94 | 9 |  | 5.88 | 9 | [8 empty] | 0.052 | [14 empty] | 0.044 | 1 | 0.23 |  | 0.052 | 0.023 | 1 | 0.29 |  | 0.049 | 1 | 0.36 | [22 empty] | AVERAGE | 5.8 | 10.2333 | 10.2333 | 26.2667 | 8.2333 | 8.2333 | 8.2333 | 24.7 |  | 11.2099 |  | 14.7086 | 25.9186 | 0.80736 | AVERAGE | 53.8947 | 1947.1006 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.2424 | 1.5132 | 1.6059 | 0.10001 | 0.15094 | 0.13951 | 0.13951 | 0.13316 | 0.12429 | 0.90674 | 1 | 0.060661 | 0.060661 | 0.060442 | 1.1079 | 0.498 | 0.10245 | 4.2175 | 0.81261 | 9.1845 | 1.0979 | 0.42581 | 0.10546 | 3.1586 | 0.59141 | 6.3602 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.72 | 136 | 127 | 132.8 | 379 | 1220 | 64.7 | 2.01 | 1.051 | 35.03 | 53 | 0.373 | 34.91 | 53 | 0 | 34.86 | 52 | 0 | 23.35 | 2.519 | 22 | 2.1 | 40.7 | 21.6 | 1.6624 | 0.313 | 23.47 | 2.206 | 18 | 2.46 | 40.1 | 40.2 | 2.6962 | 23.57 | 2.501 | 20 | 2.25 | 46.5 | 40.8 | 2.4444 | 0.26 | 6 | 1.82 | 0.315 | 0.301 | 0.186 | 6 | 2.32 | 0 | 0.269 | 6 | 1.87 | 0 | 46.05 | 0.383 | 6 | 25.3 | 59.9 | 51 | 74 | 0.213 | 47.49 | 0.4 | 6 | 25.4 | 64.7 | 52 | 77 | 0.215 | 25.2 | 23.3 | 20.2 |  |  | MINIMUM | 5.6 | 10 | 10 | 25.6 | 8 | 8 | 8 | 24 |  | 10.9958 |  | 13.1774 | 24.1733 | 0 | MINIMUM | 45.3563 | 1229.7476 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.1128 | 1.4467 | 1.5349 | 0 | 0.14722 | 0.13329 | 0.13329 | 0.11996 | 0.10268 | 0 | 0 | 0.060641 | 0.060641 | 0.060012 | 1.0966 | 0.49783 | 0.099335 | 4.18 | 0.7983 | 9.1182 | 1.092 | 0.3898 | 0.099646 | 3.1351 | 0.57022 | 5.8721 |  | MIN | 0.37 | 5.6 | 45.4286 | 16.8086 | 5.83 | 10.3 | 13 | 1.293 |  |  |  | MIN | 0.53 | 10 | 25.44 | 13.4832 | 5.85 | 10.3 | 13 | 1.0372 |  |  |  | MIN | 0.5 | 9.8 | 27.551 | 13.7755 | 5.9 | 11.6 | 13 | 1.0597 |  |  |  | 1.0372
AVERAGE | 6.7867 | 22.6667 | 21.1667 | 22.1333 | 63.1667 | 203.3333 | 10.7833 | 0.335 | 0.5255 | 5.8383 | 8.8333 | 0.062167 | 5.8183 | 8.8333 |  | 5.81 | 8.6667 |  | 5.8375 | 0.62975 | 5.5 | 0.525 | 10.175 | 5.4 | 0.4156 | 0.052167 | 5.8675 | 0.5515 | 4.5 | 0.615 | 10.025 | 10.05 | 0.67405 | 5.8925 | 0.62525 | 5 | 0.5625 | 11.625 | 10.2 | 0.61111 | 0.043333 | 1 | 0.30333 | 0.1575 | 0.050167 | 0.031 | 1 | 0.38667 |  | 0.044833 | 1 | 0.31167 |  | 7.675 | 0.063833 | 1 | 4.2167 | 9.9833 | 25.5 | 37 | 0.1065 | 7.915 | 0.066667 | 1 | 4.2333 | 10.7833 | 26 | 38.5 | 0.1075 | 4.2 | 3.8833 | 3.3667 |  |  | MAXIMUM | 6.2 | 10.7 | 10.7 | 27.6 | 8.7 | 8.7 | 8.7 | 26.1 |  | 11.317 |  | 15.4742 | 26.7912 | 1.5466 | MAXIMUM | 65.9001 | 3258.8318 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.3354 | 1.5579 | 1.6692 | 0.1528 | 0.1528 | 0.14832 | 0.14832 | 0.14832 | 0.13691 | 1.4457 | 2 | 0.060671 | 0.060671 | 0.060671 | 1.1207 | 0.49808 | 0.10837 | 4.28 | 0.82682 | 9.2458 | 1.1098 | 0.49783 | 0.10837 | 3.2041 | 0.62724 | 6.607
MINIMUM | 6.71 | 22 | 21 | 18 | 61 | 179 | 10.4 | 0.313 | 0.071 | 5.71 | 8 | 0.056 | 5.7 | 8 |  | 5.71 | 7 |  | 5.8 | 0.396 | 5 | 0.37 | 9.9 | 5 | 0.3755 | 0.046 | 5.83 | 0.399 | 4 | 0.53 | 9.7 | 9.9 | 0.6259 | 5.83 | 0.579 | 5 | 0.5 | 11.3 | 9.8 | 0.59185 | 0.031 | 1 | 0.18 | 0.025 | 0.043 | 0.018 | 1 | 0.14 |  | 0.042 | 1 | 0.17 |  | 7.55 | 0.057 | 1 | 3.9 | 9.8 | 25 | 36 | 0.023 | 7.76 | 0.06 | 1 | 3.9 | 10.5 | 26 | 38 | 0.025 | 3.9 | 3.8 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 17300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 840 | 890 | 310 | 610 | 750 | 750 | 715 | 670 | 2190 | 0 | 2840 | 2840 | 2830 | 238 | 284 | 35 | 4320 | 880 | 1555 | 118 | 122 | 18 | 1530 | 320 | 539
MAXIMUM | 6.9 | 23 | 22 | 25.9 | 65 | 218 | 11.4 | 0.351 | 0.98 | 5.95 | 10 | 0.071 | 5.94 | 10 |  | 5.9 | 10 |  | 5.91 | 0.899 | 7 | 0.8 | 10.3 | 6 | 0.45412 | 0.056 | 5.92 | 0.67 | 5 | 0.8 | 10.3 | 10.3 | 0.80829 | 5.94 | 0.669 | 5 | 0.63 | 12 | 10.6 | 0.63037 | 0.059 | 1 | 0.42 | 0.29 | 0.056 | 0.043 | 1 | 0.59 |  | 0.049 | 1 | 0.39 |  | 7.84 | 0.07 | 1 | 4.5 | 10.5 | 26 | 38 | 0.19 | 8.06 | 0.073 | 1 | 4.6 | 11.2 | 26 | 39 | 0.19 | 4.5 | 4 | 4.2 | [17 empty] | AVERAGE | 5766.6667 | [9 empty] | 230 | 280 | 296.6667 | 103.3333 | 203.3333 | 250 | 250 | 238.3333 | 223.3333 | 730 |  | 946.6667 | 946.6667 | 943.3333 | 79.3333 | 94.6667 | 11.6667 | 1440 | 293.3333 | 518.3333 | 39.3333 | 40.6667 | 6 | 510 | 106.6667 | 179.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.8222 |  | TOTAL AVG COAG ALK: |  |  |  | 8.7778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.899 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.37 | [5 empty] | 5.8658 |  |  |  |  | 0.059 |  |  |  |  | 0.37 | [6 empty] | 0.059 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 5120 | [9 empty] | 200 | 260 | 290 | 0 | 150 | 240 | 240 | 225 | 180 | 670 |  | 920 | 920 | 910 | 77 | 92 | 11 | 1410 | 280 | 500 | 38 | 36 | 6 | 490 | 100 | 161
[90 empty] | MAXIMUM | 6900 | [9 empty] | 250 | 300 | 300 | 160 | 300 | 260 | 260 | 260 | 250 | 760 |  | 1000 | 1000 | 1000 | 83 | 100 | 12 | 1500 | 310 | 548 | 42 | 50 | 6 | 520 | 110 | 197
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.061 |  | TOTAL MGD: |  | 4.335 |  |  | FINISHED SOUTH 1 |  | START: | 23075821 |  | END: | 23080156 |  |  | Alum | 6867 |  | 5085 |  | 0 | [45 empty] | 0.53 | 10 | 25.44 | 13.4832 | 5.85 | 10.3 | 13 | 1.0372
[73 empty] | FINISHED 2 | 13.183 |  | TOTAL MGD: |  | 5.726 |  |  | FINISHED SOUTH 2 |  | START: | 40924484 |  | END: | 40930210 |  |  | Caustic | 4913 |  | 5591
[73 empty] | TOTAL RAW | 25.357 |  | TOTAL MGD: |  | 4.149 |  |  | FINISHED CONWAY |  | START: | 8682218 |  | END: | 8686367 |  |  | Hypochlorite | 9 |  | 30
[76 empty] | TOTAL MGD: |  | 9.034 |  |  | FINISHED PERRY |  | START: | 30335590 |  | END: | 30344624 |  |  | Phosphate | 2974
[76 empty] | TOTAL MGD: |  | 5.311 |  |  | RAW PLANT 1 |  | START: | 27887444 |  | END: | 27892755 |  |  | Fluoride | 2400 |  |  |  |  | %
[76 empty] | TOTAL MGD: |  | 9.965 |  |  | RAW PLANT 2 |  | START: | 27822658 |  | END: | 27832623 |  |  | Cal~Flo | 11.4 | 0 | 0 | 10.14 | 1060.92 | 25
[76 empty] | TOTAL MGD: |  | 10.081 |  |  | RAW PLANT 3 |  | START: | 4133495 |  | END: | 4143576 |  |  | Zinc | 3140
[76 empty] | TOTAL MGD: |  | 1.306 |  |  | DECANT |  | START: | 1379731 |  | END: | 1381037 |  |  | Polymer | 8 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.97678 |  |  | BLOW DOWN |  | START: | 8758.1684 |  | END: | 8759.1452 |  |  | NH3 | 6.15
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 1100 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2096 | Phosphate | 43
[90 empty] | Caustic 1 | 199 | Fluoride | 0
[90 empty] | Caustic 2 | 73 | Zinc | 7.5
[90 empty] | Hypochlorite 1 | 149 | Polymer 1 | 0.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23080156
[91 empty] | FINISHED SOUTH 2 |  | END: | 40930210
[91 empty] | FINISHED CONWAY |  | END: | 8686367
[91 empty] | FINISHED PERRY |  | END: | 30344624
[91 empty] | RAW PLANT 1 |  | END: | 27892755
[91 empty] | RAW PLANT 2 |  | END: | 27832623
[91 empty] | RAW PLANT 3 |  | END: | 4143576
[91 empty] | DECANT |  | END: | 1381037
[91 empty] | BLOW DOWN |  | END: | 8759.1452
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 6
DATE: | 2018-02-06 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-06 | [23 empty] | DATE: | 2018-02-06
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-06 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43137.0409 | 3,5,6 | 33 | 5.6 | 10 | 10 | 25.6 | 8 | 8 | 8 | 24 | 7,1 | 10.9958 | 1,2 | 13.1774 | 24.1733 | 1.5466 | 43137.0409 | 65.9001 | 3258.8318 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.3354 | 1.5579 | 1.6692 | 0 | 0.1528 | 0.14832 | 0.14832 | 0.14832 | 0.13691 | 1.2745 | 2 | 0.060671 | 0.060671 | 0.060671 | 1.1063 | 0.49808 | 0.10837 | 4.18 | 0.82682 | 9.2458 | 1.092 | 0.3898 | 0.10837 | 3.1351 | 0.62724 | 5.8721 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.589 | 7 | 0.65 | 9.9 | 5 | 0.45412 |  | 5.96 | 0.553 | 6 | 0.56 | 10.1 | 10 | 0.63101 | 5.96 | 0.558 | 7 | 0.6 | 11.5 | 10 | 0.60148 | [13 empty] | 7.55 | 0.062 | 2 | 4.3 | 10.1 |  |  |  | 7.63 | 0.064 | 2 | 4.4 | 10.6 |  |  |  | 4.4 | 4 | 3.6 | [18 empty] | 6900 | [6 empty] | 0 | 0 | 0 | 240 | 280 | 300 | 0 | 300 | 260 | 260 | 260 | 240 | 670 |  | 920 | 920 | 920 | 77 | 92 | 12 | 1410 | 290 | 507 | 38 | 36 | 6 | 520 | 110 | 161 |  | 1:00 | 0.65 | 5 | 50.88 | 33.072 | 5.96 | 9.9 | 17 | 1.9454 | 5 | 6 | 0.33412 | 1:00 | 0.56 | 10 | 25.44 | 14.2464 | 5.96 | 10.1 | 13 | 1.0959 | 10 | 6 | 0.51101 | 1:00 | 0.6 | 10 | 27 | 16.2 | 5.96 | 11.5 | 13 | 1.2462 | 10 | 6 | 0.48148
2:00 | [72 empty] | 43137.3243 | 1,2,3 | 33 | 4.7 | 10 | 10 | 24.7 | 7.7 | 7.7 | 7.8 | 23.2 | 7,1 | 10.9958 | 1,2 | 13.1774 | 24.1733 | 0.19747 | 43137.3243 | 70.6176 | 3566.2688 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.0406 | 1.6186 | 1.5979 | 0 | 0.18206 | 0.15973 | 0.17114 | 0.14832 | 0.15403 | 0.53263 | 3.5 | 0.061665 | 0.061665 | 0.059522 | 1.1046 | 0.50061 | 0.093823 | 4.2774 | 0.82941 | 9.1513 | 1.12 | 0.38869 | 0.09262 | 3.2112 | 0.61408 | 5.4241 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.89 | 23 | 22 | 20.1 | 69 | 193 | 10.5 | 0.354 |  | 5.94 | 9 | 0.079 | 5.96 | 9 |  | 5.91 | 9 | [8 empty] | 0.051 | [14 empty] | 0.034 | 1 | 0.32 |  | 0.051 | 0.04 | 1 | 0.36 |  | 0.04 | 1 | 0.4 | [38 empty] | 7134 | [6 empty] | 0 | 0 | 0 | 180 | 280 | 280 | 0 | 300 | 280 | 300 | 260 | 270 | 280 |  | 900 | 900 | 880 | 74 | 89 | 10 | 1390 | 280 | 483 | 38 | 35 | 5 | 520 | 105 | 145 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43137.8059 | 1,2,3 | 33 | 4.7 | 10 | 10 | 24.7 | 7.7 | 7.7 | 7.8 | 23.2 | 7,1 | 11.1197 | 1,2 | 10.957 | 22.0766 | 0.93744 | 43137.8059 | 70.578 | 4365.605 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4452 | 2.0233 | 2.0544 | 0.23062 | 0.33985 | 0.14832 | 0.15973 | 0.15403 | 0.16544 | 1.5218 | 4 | 0.061665 | 0.061665 | 0.060874 | 1.1046 | 0.50061 | 0.1032 | 4.1547 | 0.8146 | 8.905 | 1.0905 | 0.38869 | 0.09262 | 3.0642 | 0.64332 | 5.4241 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.5 | 0.061 | 2 | 4.2 | 10 |  |  |  | 7.86 | 0.063 | 2 | 4.3 | 10.6 |  |  |  | 4.4 | 4 | 3.6 | [18 empty] | 7130 | [6 empty] | 0 | 0 | 0 | 250 | 350 | 360 | 190 | 280 | 260 | 280 | 270 | 290 | 800 |  | 900 | 900 | 900 | 74 | 89 | 11 | 1330 | 275 | 470 | 37 | 35 | 5 | 500 | 110 | 145 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43137.9123 | 1,2,3 | 41 | 5 | 11 | 11 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.1045 | 1,2 | 13.2192 | 23.3237 | 0.93744 | 43137.9123 | 70.633 | 4550.0672 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.3092 | 1.8329 | 1.6234 | 0.2396 | 0.34228 | 0.15558 | 0.15558 | 0.14002 | 0.1504 | 1.5218 | 4 | 0.062068 | 0.062068 | 0.062068 | 1.0953 | 0.49935 | 0.10199 | 4.1461 | 0.81843 | 8.9079 | 1.1089 | 0.39745 | 0.10199 | 2.9844 | 0.64401 | 5.3894 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.69 | 21 | 20 | 18.2 | 61 | 178 | 10.7 | 0.362 |  | 5.65 | 8 | 0.052 | 5.59 | 7 |  | 5.6 | 8 | [8 empty] | 0.048 | [14 empty] | 0.024 | 1 | 0.24 |  | 0.047 | 0.048 | 1 | 0.17 |  | 0.039 | 1 | 0.18 | [38 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 250 | 350 | 310 | 210 | 300 | 300 | 300 | 270 | 290 | 800 |  | 1000 | 1000 | 1000 | 81 | 98 | 12 | 1465 | 305 | 519 | 41 | 39 | 6 | 530 | 120 | 157 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.088 | [9 empty] | 5.82 | 0.527 | 5 | 0.7 | 10 | 4.7 | 0.36017 |  | 5.83 | 0.476 | 5 | 0.55 | 10.2 | 10 | 0.63101 | 5.84 | 0.5 | 5 | 0.6 | 11.3 | 10 | 0.60148 |  |  |  | 0.03 | [9 empty] | 7.52 | 0.056 | 1 | 4.1 | 11 | 26 | 46 | 0.025 | 7.9 | 0.054 | 1 | 4.5 | 12 | 26 | 45 | 0.028 | 4.3 | 4 | 3.7 | [55 empty] | 9:00 | 0.7 | 4.7 | 54.1277 | 37.8894 | 5.82 | 10 | 13 | 2.9146 | 10 | 6 | 0.24017 | 9:00 | 0.55 | 10 | 25.44 | 13.992 | 5.83 | 10.2 | 13 | 1.0763 | 10 | 6 | 0.51101 | 9:00 | 0.6 | 10 | 27 | 16.2 | 5.84 | 11.3 | 13 | 1.2462 | 10 | 6 | 0.48148
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.85 | 21 | 20 | 21 | 58 | 205 | 11 | 0.344 |  | 5.74 | 9 | 0.059 | 5.88 | 9 |  | 5.88 | 9 | [8 empty] | 0.052 | [14 empty] | 0.026 | 1 | 0.33 |  | 0.054 | 0.021 | 1 | 0.21 |  | 0.037 | 1 | 0.24 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.87 | 0.548 | 5 | 0.66 | 10.5 | 4.7 | 0.36017 |  | 5.91 | 0.485 | 5 | 0.55 | 10.9 | 10 | 0.63101 | 5.92 | 0.506 | 5 | 0.6 | 11.6 | 10 | 0.60148 | [13 empty] | 7.8 | 0.062 | 1 | 4.5 | 10.3 |  |  |  | 7.68 | 0.051 | 1 | 4.3 | 11.7 |  |  |  | 4.2 | 4 | 3.7 | [55 empty] | 13:00 | 0.66 | 4.7 | 54.1277 | 35.7243 | 5.87 | 10.5 | 13 | 2.748 | 10 | 6 | 0.24017 | 13:00 | 0.55 | 10 | 25.44 | 13.992 | 5.91 | 10.9 | 13 | 1.0763 | 10 | 6 | 0.51101 | 13:00 | 0.6 | 10 | 27 | 16.2 | 5.92 | 11.6 | 13 | 1.2462 | 10 | 6 | 0.48148
14:00 | [126 empty] | 244 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.75 | 20 | 20 | 20.1 | 66 | 188 | 11 | 0.363 |  | 6.02 | 9 | 0.074 | 6.05 | 10 |  | 6.07 | 10 | [8 empty] | 0.055 | [14 empty] | 0.028 | 1 | 0.3 |  | 0.057 | 0.027 | 1 | 0.13 |  | 0.039 | 1 | 0.14 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.77 | 0.059 | 1 | 4.1 | 10.4 |  |  |  | 8.15 | 0.068 | 1 | 4 | 11.3 |  |  |  | 4.3 | 4 | 3.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.81 | 20 | 20 | 17.3 | 72 | 174 | 11.4 | 0.365 |  | 6.1 | 9 | 0.061 | 6.11 | 9 |  | 6.05 | 9 | [8 empty] | 0.065 | [14 empty] | 0.034 | 1 | 0.3 |  | 0.068 | 0.022 | 1 | 0.3 |  | 0.039 | 1 | 0.29 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.066 | [9 empty] | 6.1 | 0.554 | 6 | 0.66 | 10.4 | 4.8 | 0.40302 |  | 6.14 | 0.484 | 5 | 0.63 | 10.7 | 10 | 0.70962 | 6.1 | 0.539 | 6 | 0.66 | 11.9 | 10 | 0.67556 |  |  |  | 0.019 | [9 empty] | 8 | 0.059 | 1 | 4.3 | 10.3 | 26 | 48 | 0.026 | 7.89 | 0.066 | 1 | 4.2 | 11.5 | 26 | 48 | 0.026 | 4.3 | 4 | 3.5 | [55 empty] | 21:00 | 0.66 | 4.8 | 53 | 34.98 | 6.1 | 10.4 | 15 | 2.332 | 10 | 6.5 | 0.28302 | 21:00 | 0.63 | 10 | 25.44 | 16.0272 | 6.14 | 10.7 | 15 | 1.0685 | 10 | 6.5 | 0.58962 | 21:00 | 0.66 | 10 | 27 | 17.82 | 6.1 | 11.9 | 15 | 1.188 | 10 | 6.5 | 0.55556
22:00 | [72 empty] | DOSE |  | TOTAL | 20 | 41 | 41 | 102 | 31.9 | 31.9 | 32.1 | 95.9 | 0 | 43.2158 | 0 | 50.531 | 93.7469 | 3.6189 | TOTAL | 277.7286 | 15740.7728 | 0 | 1600 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 5.1303 | 7.0327 | 6.9449 | 0.47021 | 1.017 | 0.61196 | 0.63478 | 0.59069 | 0.60677 | 4.8507 | 13.5 | 0.24607 | 0.24607 | 0.24314 | 4.4109 | 1.9987 | 0.40738 | 16.7583 | 3.2892 | 36.2101 | 4.4112 | 1.5646 | 0.39559 | 12.3949 | 2.5287 | 22.1098 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.8 | 21 | 21 | 21.8 | 66 | 200 | 11.2 | 0.35 |  | 6.06 | 9 | 0.07 | 6 | 9 |  | 6 | 9 | [8 empty] | 0.06 | [14 empty] | 0.034 | 1 | 0.33 |  | 0.059 | 0.034 | 1 | 0.36 |  | 0.036 | 1 | 0.39 | [22 empty] | AVERAGE | 5 | 10.25 | 10.25 | 25.5 | 7.975 | 7.975 | 8.025 | 23.975 |  | 10.804 |  | 12.6328 | 23.4367 | 0.90473 | AVERAGE | 69.4322 | 3935.1932 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.2826 | 1.7582 | 1.7362 | 0.11755 | 0.25425 | 0.15299 | 0.15869 | 0.14767 | 0.15169 | 1.2127 | 3.375 | 0.061517 | 0.061517 | 0.060784 | 1.1027 | 0.49966 | 0.10185 | 4.1896 | 0.82231 | 9.0525 | 1.1028 | 0.39116 | 0.098899 | 3.0987 | 0.63216 | 5.5274 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.79 | 126 | 123 | 118.5 | 392 | 1138 | 65.8 | 2.138 | 0.154 | 35.51 | 53 | 0.395 | 35.59 | 53 | 0 | 35.51 | 54 | 0 | 23.75 | 2.218 | 23 | 2.67 | 40.8 | 19.2 | 1.5775 | 0.331 | 23.84 | 1.998 | 21 | 2.29 | 41.9 | 40 | 2.6026 | 23.82 | 2.103 | 23 | 2.46 | 46.3 | 40 | 2.48 | 0.18 | 6 | 1.82 | 0.049 | 0.336 | 0.192 | 6 | 1.53 | 0 | 0.23 | 6 | 1.64 | 0 | 46.14 | 0.359 | 8 | 25.5 | 62.1 | 52 | 94 | 0.051 | 47.11 | 0.366 | 8 | 25.7 | 67.7 | 52 | 93 | 0.054 | 25.9 | 24 | 21.7 |  |  | MINIMUM | 4.7 | 10 | 10 | 24.7 | 7.7 | 7.7 | 7.8 | 23.2 |  | 10.1045 |  | 10.957 | 22.0766 | 0.19747 | MINIMUM | 65.9001 | 3258.8318 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.0406 | 1.5579 | 1.5979 | 0 | 0.1528 | 0.14832 | 0.14832 | 0.14002 | 0.13691 | 0.53263 | 2 | 0.060671 | 0.060671 | 0.059522 | 1.0953 | 0.49808 | 0.093823 | 4.1461 | 0.8146 | 8.905 | 1.0905 | 0.38869 | 0.09262 | 2.9844 | 0.61408 | 5.3894 |  | MIN | 0.65 | 5 | 50.88 | 33.072 | 5.96 | 9.9 | 17 | 1.9454 |  |  |  | MIN | 0.63 | 10 | 25.44 | 16.0272 | 6.14 | 10.7 | 15 | 1.0685 |  |  |  | MIN | 0.66 | 10 | 27 | 17.82 | 6.1 | 11.9 | 15 | 1.188 |  |  |  | 1.0685
AVERAGE | 6.7983 | 21 | 20.5 | 19.75 | 65.3333 | 189.6667 | 10.9667 | 0.35633 | 0.077 | 5.9183 | 8.8333 | 0.065833 | 5.9317 | 8.8333 |  | 5.9183 | 9 |  | 5.9375 | 0.5545 | 5.75 | 0.6675 | 10.2 | 4.8 | 0.39437 | 0.055167 | 5.96 | 0.4995 | 5.25 | 0.5725 | 10.475 | 10 | 0.65066 | 5.955 | 0.52575 | 5.75 | 0.615 | 11.575 | 10 | 0.62 | 0.03 | 1 | 0.30333 | 0.0245 | 0.056 | 0.032 | 1 | 0.255 |  | 0.038333 | 1 | 0.27333 |  | 7.69 | 0.059833 | 1.3333 | 4.25 | 10.35 | 26 | 47 | 0.0255 | 7.8517 | 0.061 | 1.3333 | 4.2833 | 11.2833 | 26 | 46.5 | 0.027 | 4.3167 | 4 | 3.6167 |  |  | MAXIMUM | 5.6 | 11 | 11 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 11.1197 |  | 13.2192 | 24.1733 | 1.5466 | MAXIMUM | 70.633 | 4550.0672 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.4452 | 2.0233 | 2.0544 | 0.2396 | 0.34228 | 0.15973 | 0.17114 | 0.15403 | 0.16544 | 1.5218 | 4 | 0.062068 | 0.062068 | 0.062068 | 1.1063 | 0.50061 | 0.10837 | 4.2774 | 0.82941 | 9.2458 | 1.12 | 0.39745 | 0.10837 | 3.2112 | 0.64401 | 5.8721
MINIMUM | 6.69 | 20 | 20 | 17.3 | 58 | 174 | 10.5 | 0.344 | 0.066 | 5.65 | 8 | 0.052 | 5.59 | 7 |  | 5.6 | 8 |  | 5.82 | 0.527 | 5 | 0.65 | 9.9 | 4.7 | 0.36017 | 0.048 | 5.83 | 0.476 | 5 | 0.55 | 10.1 | 10 | 0.63101 | 5.84 | 0.5 | 5 | 0.6 | 11.3 | 10 | 0.60148 | 0.024 | 1 | 0.24 | 0.019 | 0.047 | 0.021 | 1 | 0.13 |  | 0.036 | 1 | 0.14 |  | 7.5 | 0.056 | 1 | 4.1 | 10 | 26 | 46 | 0.025 | 7.63 | 0.051 | 1 | 4 | 10.6 | 26 | 45 | 0.026 | 4.2 | 4 | 3.5 | [15 empty] | MIL/MIN |  | TOTAL | 28964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 1260 | 1250 | 400 | 1180 | 1100 | 1140 | 1060 | 1090 | 2550 | 0 | 3720 | 3720 | 3700 | 306 | 368 | 45 | 5595 | 1150 | 1979 | 154 | 145 | 22 | 2070 | 445 | 608
MAXIMUM | 6.89 | 23 | 22 | 21.8 | 72 | 205 | 11.4 | 0.365 | 0.088 | 6.1 | 9 | 0.079 | 6.11 | 10 |  | 6.07 | 10 |  | 6.1 | 0.589 | 7 | 0.7 | 10.5 | 5 | 0.45412 | 0.065 | 6.14 | 0.553 | 6 | 0.63 | 10.9 | 10 | 0.70962 | 6.1 | 0.558 | 7 | 0.66 | 11.9 | 10 | 0.67556 | 0.034 | 1 | 0.33 | 0.03 | 0.068 | 0.048 | 1 | 0.36 |  | 0.04 | 1 | 0.4 |  | 8 | 0.062 | 2 | 4.5 | 11 | 26 | 48 | 0.026 | 8.15 | 0.068 | 2 | 4.5 | 12 | 26 | 48 | 0.028 | 4.4 | 4 | 3.7 | [17 empty] | AVERAGE | 7241 | [9 empty] | 230 | 315 | 312.5 | 100 | 295 | 275 | 285 | 265 | 272.5 | 637.5 |  | 930 | 930 | 925 | 76.5 | 92 | 11.25 | 1398.75 | 287.5 | 494.75 | 38.5 | 36.25 | 5.5 | 517.5 | 111.25 | 152
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9228 |  | TOTAL AVG COAG ALK: |  |  |  | 8.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.589 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.55 | [5 empty] | 5.9508 |  |  |  |  | 0.048 |  |  |  |  | 0.55 | [6 empty] | 0.048 | [16 empty] | Pump Station MIN |  | 3.5 | [17 empty] | MINIMUM | 6900 | [9 empty] | 180 | 280 | 280 | 0 | 280 | 260 | 260 | 260 | 240 | 280 |  | 900 | 900 | 880 | 74 | 89 | 10 | 1330 | 275 | 470 | 37 | 35 | 5 | 500 | 105 | 145
[90 empty] | MAXIMUM | 7800 | [9 empty] | 250 | 350 | 360 | 210 | 300 | 300 | 300 | 270 | 290 | 800 |  | 1000 | 1000 | 1000 | 81 | 98 | 12 | 1465 | 305 | 519 | 41 | 39 | 6 | 530 | 120 | 161
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.875 |  | TOTAL MGD: |  | 4.328 |  |  | FINISHED SOUTH 1 |  | START: | 23080156 |  | END: | 23084484 |  |  | Alum | 5876 |  | 6580 |  | 0 | [45 empty] | 0.63 | 10 | 25.44 | 16.0272 | 6.14 | 10.7 | 15 | 1.0685
[73 empty] | FINISHED 2 | 13.733 |  | TOTAL MGD: |  | 5.547 |  |  | FINISHED SOUTH 2 |  | START: | 40930210 |  | END: | 40935757 |  |  | Caustic | 4656 |  | 5573
[73 empty] | TOTAL RAW | 25.517 |  | TOTAL MGD: |  | 4.065 |  |  | FINISHED CONWAY |  | START: | 8686367 |  | END: | 8690432 |  |  | Hypochlorite | 8 |  | 29
[76 empty] | TOTAL MGD: |  | 9.668 |  |  | FINISHED PERRY |  | START: | 30344624 |  | END: | 30354292 |  |  | Phosphate | 2862
[76 empty] | TOTAL MGD: |  | 4.742 |  |  | RAW PLANT 1 |  | START: | 27892755 |  | END: | 27897497 |  |  | Fluoride | 2150 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.582 |  |  | RAW PLANT 2 |  | START: | 27832623 |  | END: | 27842205 |  |  | Cal~Flo | 10.8 | 0 | 0 | 8.6 | 1852.4 | 25
[76 empty] | TOTAL MGD: |  | 11.193 |  |  | RAW PLANT 3 |  | START: | 4143576 |  | END: | 4154769 |  |  | Zinc | 3140
[76 empty] | TOTAL MGD: |  | 1.097 |  |  | DECANT |  | START: | 1381037 |  | END: | 1382134 |  |  | Polymer | 12 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.60438 |  |  | BLOW DOWN |  | START: | 8759.1452 |  | END: | 8759.7496 |  |  | NH3 | 5.97
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 1050 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2886 | Phosphate | 45
[90 empty] | Caustic 1 | 183 | Fluoride | 0
[90 empty] | Caustic 2 | 61 | Zinc | 6.5
[90 empty] | Hypochlorite 1 | 165 | Polymer 1 | 1.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23084484
[91 empty] | FINISHED SOUTH 2 |  | END: | 40935757
[91 empty] | FINISHED CONWAY |  | END: | 8690432
[91 empty] | FINISHED PERRY |  | END: | 30354292
[91 empty] | RAW PLANT 1 |  | END: | 27897497
[91 empty] | RAW PLANT 2 |  | END: | 27842205
[91 empty] | RAW PLANT 3 |  | END: | 4154769
[91 empty] | DECANT |  | END: | 1382134
[91 empty] | BLOW DOWN |  | END: | 8759.7496
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 7
DATE: | 2018-02-07 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-07 | [23 empty] | DATE: | 2018-02-07
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-07 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43138.0382 | 1,2,3 | 41 | 5 | 11 | 11 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.1045 | 1,2 | 13.2192 | 23.3237 | 0.93744 | 43138.0382 | 70.633 | 4550.0672 | 0 | 400 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.3092 | 1.8329 | 1.6234 | 0.2396 | 0.34228 | 0.15558 | 0.15558 | 0.14002 | 0.1504 | 1.5218 | 4 | 0.062068 | 0.062068 | 0.062068 | 1.0953 | 0.49935 | 0.10199 | 4.1461 | 0.81843 | 8.9079 | 1.1089 | 0.39745 | 0.10199 | 2.9844 | 0.64401 | 5.3894 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.2 | 0.586 | 6 | 0.56 | 10.4 | 5.3 | 0.4325 |  | 6.22 | 0.579 | 6 | 0.69 | 10.6 | 10.6 | 0.745 | 6.2 | 0.553 | 7 | 0.73 | 11.9 | 11.4 | 0.75333 | [13 empty] | 7.73 | 0.064 | 1 | 4 | 10.3 |  |  |  | 7.67 | 0.066 | 1 | 4.2 | 10.9 |  |  |  | 4.2 | 4 | 3.7 | [18 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 250 | 350 | 310 | 210 | 300 | 300 | 300 | 270 | 290 | 800 |  | 1000 | 1000 | 1000 | 81 | 98 | 12 | 1465 | 305 | 519 | 41 | 39 | 6 | 530 | 120 | 157 |  | 1:00 | 0.56 | 5.3 | 48 | 26.88 | 6.2 | 10.4 | 15 | 1.792 | 10 | 6.5 | 0.3125 | 1:00 | 0.69 | 10.6 | 24 | 16.56 | 6.22 | 10.6 | 15 | 1.104 | 10 | 6.5 | 0.625 | 1:00 | 0.73 | 11.4 | 23.6842 | 17.2895 | 6.2 | 11.9 | 15 | 1.1526 | 10 | 6.5 | 0.63333
2:00 | [72 empty] | 43138.3685 | 1,2,3 | 50 | 9.5 | 9.5 | 9.5 | 28.5 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.1218 | 1,2 | 16.9546 | 27.0763 | 0.93744 | 43138.3685 | 65.0281 | 3689.2436 | 0 | 715 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 1.5218 | 7.5 | 0.060206 | 0.060206 | 0.060206 | 1.1089 | 0.49935 | 0.10199 | 4.1941 | 0.78891 | 9.0109 | 1.1359 | 0.50955 | 0.10199 | 3.2344 | 0.57961 | 5.664 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.8 | 21 | 20 | 23.2 | 69 | 210 | 11 | 0.347 |  | 6.2 | 10 | 0.081 | 6.2 | 10 |  | 6.19 | 10 | [8 empty] | 0.068 | [14 empty] | 0.034 | 1 | 0.36 |  | 0.067 | 0.034 | 1 | 0.3 |  | 0.035 | 1 | 0.39 | [38 empty] | 7580 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 275 | 275 | 275 | 275 | 275 | 275 | 800 |  | 970 | 970 | 970 | 82 | 98 | 12 | 1440 | 294 | 525 | 42 | 50 | 6 | 530 | 108 | 165 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43138.5552 | 1,2,3 | 50 | 9.5 | 9.5 | 9.5 | 28.5 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 12.2904 | 1,2 | 15.5923 | 27.8827 | 0 | 43138.5552 | 65.0281 | 3689.2436 | 0 | 715 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 1.5218 | 1 | 0.060206 | 0.060206 | 0.060206 | 1.1089 | 0.49935 | 0.10199 | 4.1941 | 0.78891 | 7.7236 | 1.1359 | 0.40764 | 0.10199 | 3.2344 | 0.57961 | 3.9476 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.36 | 0.063 | 1 | 4 | 10.3 |  |  |  | 7.63 | 0.069 | 1 | 4.2 | 11 |  |  |  | 4.1 | 4 | 3.5 | [18 empty] | 7580 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 275 | 275 | 275 | 275 | 275 | 275 | 800 |  | 970 | 970 | 970 | 82 | 98 | 12 | 1440 | 294 | 450 | 42 | 40 | 6 | 530 | 108 | 115 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.73 | 22 | 20 | 20.1 | 62 | 186 | 11.8 | 0.333 |  | 5.99 | 10 | 0.068 | 6.02 | 10 |  | 6.01 | 10 | [8 empty] | 0.05 | [14 empty] | 0.028 | 1 | 0.25 |  | 0.051 | 0.022 | 1 | 0.26 |  | 0.038 | 1 | 0.22 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.077 | [9 empty] | 6.12 | 0.674 | 8 | 0.76 | 11 | 9.5 | 0.68014 |  | 6.12 | 0.679 | 8 | 0.59 | 11.2 | 9.5 | 0.68014 | 6.1 | 0.678 | 9 | 0.56 | 12.5 | 9.5 | 0.64778 |  |  |  | 0.025 | [9 empty] | 8.02 | 0.058 | 1 | 3.8 | 10.6 | 27 | 47 | 0.021 | 7.9 | 0.058 | 1 | 4 | 10.6 | 23 | 49 | 0.02 | 4 | 4 | 3.8 | [55 empty] | 9:00 | 0.76 | 9.5 | 26.7789 | 20.352 | 6.12 | 11 | 15 | 1.3568 | 10 | 6.5 | 0.56014 | 9:00 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.12 | 11.2 | 15 | 1.0533 | 10 | 6.5 | 0.56014 | 9:00 | 0.56 | 9.5 | 28.4211 | 15.9158 | 6.1 | 12.5 | 15 | 1.0611 | 10 | 6.5 | 0.52778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.75 | 23 | 19 | 23.5 | 63 | 208 | 11.6 | 0.33 |  | 5.97 | 10 | 0.07 | 5.97 | 11 |  | 5.94 | 11 | [8 empty] | 0.05 | [14 empty] | 0.042 | 1 | 0.15 |  | 0.051 | 0.033 | 1 | 0.09 |  | 0.05 | 1 | 0.14 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.04 | 0.488 | 5 | 0.54 | 11.8 | 8.3 | 0.60939 |  | 6.01 | 0.39 | 4 | 0.66 | 12.4 | 10 | 0.70962 | 6.07 | 0.559 | 6 | 0.6 | 13.7 | 10.2 | 0.68667 | [13 empty] | 7.97 | 0.052 | 1 | 3.9 | 10.9 |  |  |  | 7.86 | 0.05 | 1 | 3.5 | 10.9 |  |  |  | 3.9 | 3.9 | 4.2 | [55 empty] | 13:00 | 0.54 | 8.3 | 30.6506 | 16.5513 | 6.04 | 11.8 | 15 | 1.1034 | 10 | 6.5 | 0.48939 | 13:00 | 0.66 | 10 | 25.44 | 16.7904 | 6.01 | 12.4 | 15 | 1.1194 | 10 | 6.5 | 0.58962 | 13:00 | 0.6 | 10.2 | 26.4706 | 15.8824 | 6.07 | 13.7 | 15 | 1.0588 | 10 | 6.5 | 0.56667
14:00 | [126 empty] | 246 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.78 | 24 | 20 | 26.4 | 62 | 228 | 12.4 | 0.335 |  | 5.98 | 12 | 0.07 | 5.95 | 12 |  | 5.97 | 11 | [8 empty] | 0.054 | [14 empty] | 0.03 | 1 | 0.18 |  | 0.053 | 0.024 | 1 | 0.12 |  | 0.04 | 1 | 0.16 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.77 | 0.05 | 1 | 3.8 | 11.1 |  |  |  | 7.47 | 0.049 | 1 | 3.7 | 12.7 |  |  |  | 3.6 | 3.9 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.73 | 20 | 19 | 24.5 | 72 | 218 | 12.3 | 0.351 |  | 5.7 | 9 | 0.06 | 5.72 | 9 |  | 5.69 | 9 | [8 empty] | 0.051 | [14 empty] | 0.028 | 1 | 0.15 |  | 0.056 | 0.023 | 1 | 0.32 |  | 0.056 | 1 | 0.4 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.084 | [9 empty] | 6.01 | 0.466 | 5 | 0.61 | 12.2 | 9.5 | 0.68014 |  | 5.99 | 0.313 | 5 | 0.55 | 12.8 | 9.5 | 0.60546 | 5.99 | 0.722 | 5 | 0.6 | 14.6 | 9.5 | 0.57741 |  |  |  | 0.021 | [9 empty] | 7.52 | 0.061 | 1 | 3.9 | 11.6 | 22 | 32 | 0.022 | 7.24 | 0.063 | 1 | 3.9 | 12.4 | 20 | 32 | 0.026 | 3.6 | 3.7 | 3.4 | [55 empty] | 21:00 | 0.61 | 9.5 | 26.7789 | 16.3352 | 6.01 | 12.2 | 15 | 1.089 | 10 | 6.5 | 0.56014 | 21:00 | 0.55 | 9.5 | 26.7789 | 14.7284 | 5.99 | 12.8 | 13 | 1.133 | 10 | 6 | 0.48546 | 21:00 | 0.6 | 9.5 | 28.4211 | 17.0526 | 5.99 | 14.6 | 13 | 1.3117 | 10 | 6 | 0.45741
22:00 | [72 empty] | DOSE |  | TOTAL | 24 | 30 | 30 | 84 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 32.5166 | 0 | 45.7661 | 78.2827 | 1.8749 | TOTAL | 200.6892 | 11928.5544 | 0 | 1830 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.4513 | 4.9749 | 4.7655 | 0.56987 | 0.67255 | 0.48585 | 0.48585 | 0.4703 | 0.48067 | 4.5654 | 12.5 | 0.18248 | 0.18248 | 0.18248 | 3.313 | 1.4981 | 0.30597 | 12.5343 | 2.3963 | 25.6425 | 3.3807 | 1.3146 | 0.30597 | 9.4531 | 1.8032 | 15.001 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.71 | 24 | 20 | 28.2 | 67 | 243 | 12.2 | 0.347 |  | 5.96 | 10 | 0.062 | 5.93 | 10 |  | 5.92 | 10 | [8 empty] | 0.051 | [14 empty] | 0.032 | 1 | 0.29 |  | 0.055 | 0.023 | 1 | 0.33 |  | 0.06 | 1 | 0.42 | [22 empty] | AVERAGE | 8 | 10 | 10 | 28 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.8389 |  | 15.2554 | 26.0942 | 0.62496 | AVERAGE | 66.8964 | 3976.1848 |  | 610 | #N/A | #N/A | #N/A |  |  |  | 1.4838 | 1.6583 | 1.5885 | 0.18996 | 0.22418 | 0.16195 | 0.16195 | 0.15677 | 0.16022 | 1.5218 | 4.1667 | 0.060827 | 0.060827 | 0.060827 | 1.1043 | 0.49935 | 0.10199 | 4.1781 | 0.79875 | 8.5475 | 1.1269 | 0.43821 | 0.10199 | 3.151 | 0.60108 | 5.0003 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.5 | 134 | 118 | 145.9 | 395 | 1293 | 71.3 | 2.043 | 0.161 | 35.8 | 61 | 0.411 | 35.79 | 62 | 0 | 35.72 | 61 | 0 | 24.37 | 2.214 | 24 | 2.47 | 45.4 | 32.6 | 2.4022 | 0.324 | 24.34 | 1.961 | 23 | 2.49 | 47 | 39.6 | 2.7402 | 24.36 | 2.512 | 27 | 2.49 | 52.7 | 40.6 | 2.6652 | 0.194 | 6 | 1.38 | 0.046 | 0.333 | 0.159 | 6 | 1.42 | 0 | 0.279 | 6 | 1.73 | 0 | 46.37 | 0.348 | 6 | 23.4 | 64.8 | 49 | 79 | 0.043 | 45.77 | 0.355 | 6 | 23.5 | 68.5 | 43 | 81 | 0.046 | 23.4 | 23.5 | 22.4 |  |  | MINIMUM | 5 | 9.5 | 9.5 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.1045 |  | 13.2192 | 23.3237 | 0 | MINIMUM | 65.0281 | 3689.2436 |  | 400 | #N/A | #N/A | #N/A |  |  |  | 1.3092 | 1.571 | 1.571 | 0.16514 | 0.16514 | 0.15558 | 0.15558 | 0.14002 | 0.1504 | 1.5218 | 1 | 0.060206 | 0.060206 | 0.060206 | 1.0953 | 0.49935 | 0.10199 | 4.1461 | 0.78891 | 7.7236 | 1.1089 | 0.39745 | 0.10199 | 2.9844 | 0.57961 | 3.9476 |  | MIN | 0.61 | 9.5 | 26.7789 | 16.3352 | 6.01 | 12.2 | 15 | 1.089 |  |  |  | MIN | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.12 | 11.2 | 15 | 1.0533 |  |  |  | MIN | 0.6 | 10.2 | 26.4706 | 15.8824 | 6.07 | 13.7 | 15 | 1.0588 |  |  |  | 1.0533
AVERAGE | 6.75 | 22.3333 | 19.6667 | 24.3167 | 65.8333 | 215.5 | 11.8833 | 0.3405 | 0.0805 | 5.9667 | 10.1667 | 0.0685 | 5.965 | 10.3333 |  | 5.9533 | 10.1667 |  | 6.0925 | 0.5535 | 6 | 0.6175 | 11.35 | 8.15 | 0.60054 | 0.054 | 6.085 | 0.49025 | 5.75 | 0.6225 | 11.75 | 9.9 | 0.68506 | 6.09 | 0.628 | 6.75 | 0.6225 | 13.175 | 10.15 | 0.6663 | 0.032333 | 1 | 0.23 | 0.023 | 0.0555 | 0.0265 | 1 | 0.23667 |  | 0.0465 | 1 | 0.28833 |  | 7.7283 | 0.058 | 1 | 3.9 | 10.8 | 24.5 | 39.5 | 0.0215 | 7.6283 | 0.059167 | 1 | 3.9167 | 11.4167 | 21.5 | 40.5 | 0.023 | 3.9 | 3.9167 | 3.7333 |  |  | MAXIMUM | 9.5 | 11 | 11 | 28.5 | 8.5 | 8.5 | 8.5 | 25.5 |  | 12.2904 |  | 16.9546 | 27.8827 | 0.93744 | MAXIMUM | 70.633 | 4550.0672 |  | 715 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.8329 | 1.6234 | 0.2396 | 0.34228 | 0.16514 | 0.16514 | 0.16514 | 0.16514 | 1.5218 | 7.5 | 0.062068 | 0.062068 | 0.062068 | 1.1089 | 0.49935 | 0.10199 | 4.1941 | 0.81843 | 9.0109 | 1.1359 | 0.50955 | 0.10199 | 3.2344 | 0.64401 | 5.664
MINIMUM | 6.71 | 20 | 19 | 20.1 | 62 | 186 | 11 | 0.33 | 0.077 | 5.7 | 9 | 0.06 | 5.72 | 9 |  | 5.69 | 9 |  | 6.01 | 0.466 | 5 | 0.54 | 10.4 | 5.3 | 0.4325 | 0.05 | 5.99 | 0.313 | 4 | 0.55 | 10.6 | 9.5 | 0.60546 | 5.99 | 0.553 | 5 | 0.56 | 11.9 | 9.5 | 0.57741 | 0.028 | 1 | 0.15 | 0.021 | 0.051 | 0.022 | 1 | 0.09 |  | 0.035 | 1 | 0.14 |  | 7.36 | 0.05 | 1 | 3.8 | 10.3 | 22 | 32 | 0.021 | 7.24 | 0.049 | 1 | 3.5 | 10.6 | 20 | 32 | 0.02 | 3.6 | 3.7 | 3.4 | [15 empty] | MIL/MIN |  | TOTAL | 22960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 950 | 910 | 760 | 850 | 850 | 850 | 820 | 840 | 2400 | 0 | 2940 | 2940 | 2940 | 245 | 294 | 36 | 4345 | 893 | 1494 | 125 | 129 | 18 | 1590 | 336 | 437
MAXIMUM | 6.8 | 24 | 20 | 28.2 | 72 | 243 | 12.4 | 0.351 | 0.084 | 6.2 | 12 | 0.081 | 6.2 | 12 |  | 6.19 | 11 |  | 6.2 | 0.674 | 8 | 0.76 | 12.2 | 9.5 | 0.68014 | 0.068 | 6.22 | 0.679 | 8 | 0.69 | 12.8 | 10.6 | 0.745 | 6.2 | 0.722 | 9 | 0.73 | 14.6 | 11.4 | 0.75333 | 0.042 | 1 | 0.36 | 0.025 | 0.067 | 0.034 | 1 | 0.33 |  | 0.06 | 1 | 0.42 |  | 8.02 | 0.064 | 1 | 4 | 11.6 | 27 | 47 | 0.022 | 7.9 | 0.069 | 1 | 4.2 | 12.7 | 23 | 49 | 0.026 | 4.2 | 4 | 4.2 | [17 empty] | AVERAGE | 7653.3333 | [9 empty] | 283.3333 | 316.6667 | 303.3333 | 253.3333 | 283.3333 | 283.3333 | 283.3333 | 273.3333 | 280 | 800 |  | 980 | 980 | 980 | 81.6667 | 98 | 12 | 1448.3333 | 297.6667 | 498 | 41.6667 | 43 | 6 | 530 | 112 | 145.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9617 |  | TOTAL AVG COAG ALK: |  |  |  | 10.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.722 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.0892 |  |  |  |  | 0.06 |  |  |  |  | 0.54 | [6 empty] | 0.06 | [16 empty] | Pump Station MIN |  | 3.4 | [17 empty] | MINIMUM | 7580 | [9 empty] | 250 | 300 | 300 | 210 | 275 | 275 | 275 | 270 | 275 | 800 |  | 970 | 970 | 970 | 81 | 98 | 12 | 1440 | 294 | 450 | 41 | 39 | 6 | 530 | 108 | 115
[90 empty] | MAXIMUM | 7800 | [9 empty] | 300 | 350 | 310 | 275 | 300 | 300 | 300 | 275 | 290 | 800 |  | 1000 | 1000 | 1000 | 82 | 98 | 12 | 1465 | 305 | 525 | 42 | 50 | 6 | 530 | 120 | 165
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.019 |  | TOTAL MGD: |  | 5.726 |  |  | FINISHED SOUTH 1 |  | START: | 23084484 |  | END: | 23090210 |  |  | Alum | 7604 |  | 6048 |  | 0 | [45 empty] | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.12 | 11.2 | 15 | 1.0533
[73 empty] | FINISHED 2 | 18.518 |  | TOTAL MGD: |  | 6.293 |  |  | FINISHED SOUTH 2 |  | START: | 40935757 |  | END: | 40942050 |  |  | Caustic | 4531 |  | 5483
[73 empty] | TOTAL RAW | 27.954 |  | TOTAL MGD: |  | 5.424 |  |  | FINISHED CONWAY |  | START: | 8690432 |  | END: | 8695856 |  |  | Hypochlorite | 6'/416 |  | 38.5'
[76 empty] | TOTAL MGD: |  | 13.094 |  |  | FINISHED PERRY |  | START: | 30354292 |  | END: | 30367386 |  |  | Phosphate | 2896
[76 empty] | TOTAL MGD: |  | 7.522 |  |  | RAW PLANT 1 |  | START: | 27897497 |  | END: | 27905019 |  |  | Fluoride | 0 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.239 |  |  | RAW PLANT 2 |  | START: | 27842205 |  | END: | 27852444 |  |  | Cal~Flo | 8.6 | 7.51 | 16.71 | 15.79 | 1692.42 | 25
[76 empty] | TOTAL MGD: |  | 10.193 |  |  | RAW PLANT 3 |  | START: | 4154769 |  | END: | 4164962 |  |  | Zinc | 3201
[76 empty] | TOTAL MGD: |  | 1.3 |  |  | DECANT |  | START: | 1382134 |  | END: | 1383434 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.75889 |  |  | BLOW DOWN |  | START: | 8759.7496 |  | END: | 8760.5085 |  |  | NH3 | 13.29
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 715
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2602 | Phosphate | 46
[90 empty] | Caustic 1 | 186 | Fluoride | 0
[90 empty] | Caustic 2 | 60 | Zinc | 6
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1
[91 empty] | FINISHED SOUTH 1 |  | END: | 23090210
[91 empty] | FINISHED SOUTH 2 |  | END: | 40942050
[91 empty] | FINISHED CONWAY |  | END: | 8695856
[91 empty] | FINISHED PERRY |  | END: | 30367386
[91 empty] | RAW PLANT 1 |  | END: | 27905019
[91 empty] | RAW PLANT 2 |  | END: | 27852444
[91 empty] | RAW PLANT 3 |  | END: | 4164962
[91 empty] | DECANT |  | END: | 1383434
[91 empty] | BLOW DOWN |  | END: | 8760.5085
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 8
DATE: | 2018-02-08 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-08 | [23 empty] | DATE: | 2018-02-08
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-08 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43139.0157 | 1,2,3 | 50 | 9.5 | 9.5 | 9.5 | 28.5 | 9 | 9 | 9 | 27 | 7,1 | 8.7941 | 1,2 | 13.8499 | 22.644 | 1.8029 | 43139.0157 | 65.0281 | 3381.8066 | 0 | 715 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6816 | 1.7805 | 1.7805 | 0.19216 | 0.16814 | 0.20417 | 0.26422 | 0.16814 | 0.15613 | 1.4267 | 2 | 0.060378 | 0.059792 | 0.059792 | 1.0983 | 0.50049 | 0.096324 | 4.2049 | 0.82365 | 7.2945 | 1.0728 | 0.40424 | 0.096324 | 3.2012 | 0.60823 | 3.7283 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.417 | 4 | 0.62 | 12.1 | 9.5 | 0.60546 |  | 5.99 | 0.375 | 4 | 0.56 | 12.7 | 9.5 | 0.60546 | 5.99 | 0.434 | 5 | 0.56 | 13.3 | 9.5 | 0.57741 | [13 empty] | 7.27 | 0.065 | 2 | 4.2 | 11.6 |  |  |  | 7.05 | 0.055 | 2 | 3.7 | 12.2 |  |  |  | 3.7 | 3.8 | 3.1 | [18 empty] | 7580 | [6 empty] | 0 | 0 | 0 | 340 | 360 | 360 | 320 | 280 | 340 | 440 | 280 | 260 | 750 |  | 1030 | 1020 | 1020 | 86 | 104 | 12 | 1600 | 325 | 450 | 42 | 42 | 6 | 600 | 120 | 115 |  | 1:00 | 0.62 | 9.5 | 26.7789 | 16.6029 | 5.96 | 12.1 | 13 | 1.2771 | 10 | 6 | 0.48546 | 1:00 | 0.56 | 9.5 | 26.7789 | 14.9962 | 5.99 | 12.7 | 13 | 1.1536 | 10 | 6 | 0.48546 | 1:00 | 0.56 | 9.5 | 28.4211 | 15.9158 | 5.99 | 13.3 | 13 | 1.2243 | 10 | 6 | 0.45741
2:00 | [72 empty] | 43139.3898 | 1,2,3 | 48 | 9.5 | 9.5 | 9.5 | 28.5 | 9 | 9 | 9 | 27 | 7,1 | 9.5141 | 1,2 | 15.0408 | 24.5549 | 2.2594 | 43139.3898 | 60.0523 | 4058.168 | 0 | 715 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4838 | 1.4838 | 1.4838 | 0.18015 | 0.18015 | 0.18015 | 0.18015 | 0.16814 | 0.16814 | 1.4267 | 1.5 | 0.059792 | 0.059792 | 0.059792 | 1.0983 | 0.50049 | 0.096324 | 4.2054 | 0.76029 | 7.5377 | 1.09 | 0.39 | 0.11 | 3.24 | 0.57 | 5.5114 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.66 | 19 | 15 | 29.6 | 70 | 246 | 13.4 | 0.347 |  | 6 | 8 | 0.064 | 5.92 | 7 |  | 5.91 | 8 | [8 empty] | 0.055 | [14 empty] | 0.028 | 1 | 0.46 |  | 0.057 | 0.023 | 1 | 0.27 |  | 0.062 | 2 | 0.36 | [38 empty] | 7000 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 750 |  | 1020 | 1020 | 1020 | 86 | 104 | 12 | 1470 | 300 | 465 | 38 | 36 | 6 | 480 | 100 | 170 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43139.8509 | 1,2,3 | 48 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | 7,1 | 9.5141 | 1,2 | 15.0408 | 24.5549 | 0 | 43139.8509 | 60.0221 | 3443.294 | 0 | 640 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 2.1143 | 2.17 | 1.7805 | 0.22819 | 0.21476 | 0.1745 | 0.25503 | 0.20134 | 0.09396 | 1.4267 | 3.5 | 0.060671 | 0.060671 | 0.059353 | 1.1494 | 0.49808 | 0.099335 | 4.2149 | 0.75554 | 8.4799 | 1.092 | 0.3898 | 0.10837 | 3.237 | 0.57022 | 6.2004 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.29 | 0.052 | 1 | 4.1 | 12.2 |  |  |  | 7.22 | 0.051 | 1 | 4 | 11.9 |  |  |  | 3.9 | 3.7 | 3.2 | [18 empty] | 6260 | [6 empty] | 0 | 0 | 0 | 380 | 390 | 320 | 340 | 320 | 260 | 380 | 300 | 140 | 750 |  | 920 | 920 | 900 | 80 | 92 | 11 | 1310 | 265 | 465 | 38 | 36 | 6 | 480 | 100 | 170 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.72 | 18 | 20 | 26 | 69 | 223 | 12.6 | 0.317 |  | 6.02 | 11 | 0.051 | 5.91 | 10 |  | 5.9 | 11 | [8 empty] | 0.041 | [14 empty] | 0.027 | 1 | 0.5 |  | 0.051 | 0.022 | 1 | 0.46 |  | 0.054 | 2 | 0.5 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.099 | [9 empty] | 5.97 | 0.501 | 5 | 0.84 | 12.2 | 9.2 | 0.59013 |  | 5.98 | 0.317 | 4 | 0.82 | 12.2 | 9.2 | 0.59013 | 5.97 | 0.489 | 5 | 0.56 | 13.7 | 9.3 | 0.56778 |  |  |  | 0.024 | [9 empty] | 7.76 | 0.054 | 1 | 4.6 | 11.2 | 25 | 48 | 0.026 | 7.55 | 0.056 | 1 | 4 | 12.6 | 24 | 43 | 0.025 | 4.1 | 3.9 | 3.4 | [55 empty] | 9:00 | 0.84 | 9.2 | 27.6522 | 23.2278 | 5.97 | 12.2 | 13 | 1.7868 | 10 | 6 | 0.47013 | 9:00 | 0.82 | 9.2 | 27.6522 | 22.6748 | 5.98 | 12.2 | 13 | 1.7442 | 10 | 6 | 0.47013 | 9:00 | 0.56 | 9.3 | 29.0323 | 16.2581 | 5.97 | 13.7 | 13 | 1.2506 | 10 | 6 | 0.44778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.89 | 20 | 19 | 28.3 | 61 | 239 | 12.6 | 0.308 |  | 6.09 | 10 | 0.068 | 6.11 | 9 |  | 6.08 | 10 | [8 empty] | 0.049 | [14 empty] | 0.032 | 1 | 0.41 |  | 0.049 | 0.04 | 1 | 0.6 |  | 0.052 | 1 | 0.52 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.499 | 4 | 0.57 | 12.3 | 9.2 | 0.66245 |  | 6.08 | 0.35 | 4 | 0.58 | 12.2 | 9.2 | 0.66245 | 6.13 | 0.491 | 4 | 0.54 | 13.7 | 9.3 | 0.63667 | [13 empty] | 8.01 | 0.051 | 1 | 5 | 11.4 |  |  |  | 7.66 | 0.053 | 1 | 4.5 | 12.9 |  |  |  | 4.2 | 3.8 | 3.4 | [55 empty] | 13:00 | 0.57 | 9.2 | 27.6522 | 15.7617 | 6.03 | 12.3 | 15 | 1.0508 | 10 | 6.5 | 0.54245 | 13:00 | 0.58 | 9.2 | 27.6522 | 16.0383 | 6.08 | 12.2 | 15 | 1.0692 | 10 | 6.5 | 0.54245 | 13:00 | 0.54 | 9.3 | 29.0323 | 15.6774 | 6.13 | 13.7 | 15 | 1.0452 | 10 | 6.5 | 0.51667
14:00 | [126 empty] | 245 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.85 | 22 | 20 | 32.3 | 56 | 263 | 13 | 0.287 |  | 6.03 | 11 | 0.067 | 6.05 | 12 |  | 6.05 | 11 | [8 empty] | 0.053 | [14 empty] | 0.039 | 1 | 0.38 |  | 0.046 | 0.044 | 1 | 0.55 |  | 0.058 | 1 | 0.47 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 8.1 | 0.049 | 1 | 4.8 | 11.4 |  |  |  | 7.73 | 0.052 | 1 | 4.6 | 13.1 |  |  |  | 4.3 | 3.9 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.68 | 18 | 22 | 30 | 68 | 250 | 12.5 | 0.311 |  | 5.88 | 7.058 | 0.058 | 5.93 | 8 |  | 5.93 | 7 | [8 empty] | 0.05 | [14 empty] | 0.027 | 1 | 0.28 |  | 0.052 | 0.038 | 1 | 0.58 |  | 0.056 | 1 | 0.49 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.114 | [9 empty] | 6.06 | 0.571 | 3 | 0.58 | 12.4 | 8.5 | 0.62118 |  | 6.08 | 0.371 | 3 | 0.67 | 12.8 | 8.5 | 0.62118 | 6.08 | 0.568 | 3 | 0.76 | 14.6 | 8.5 | 0.59222 |  |  |  | 0.027 | [9 empty] | 7.75 | 0.084 | 1 | 3.6 | 11.5 | 25 | 40 | 0.029 | 7.98 | 0.068 | 1 | 4.4 | 12 | 21 | 42 | 0.033 | 4.3 | 4.1 | 3.6 | [55 empty] | 21:00 | 0.58 | 8.5 | 29.9294 | 17.3591 | 6.06 | 12.4 | 15 | 1.1573 | 10 | 6.5 | 0.50118 | 21:00 | 0.67 | 8.5 | 29.9294 | 20.0527 | 6.08 | 12.8 | 15 | 1.3368 | 10 | 6.5 | 0.50118 | 21:00 | 0.76 | 8.5 | 31.7647 | 24.1412 | 6.08 | 14.6 | 15 | 1.6094 | 10 | 6.5 | 0.47222
22:00 | [72 empty] | DOSE |  | TOTAL | 27.5 | 27.5 | 27.5 | 82.5 | 26 | 26 | 26 | 78 | 0 | 27.8222 | 0 | 43.9315 | 71.7538 | 4.0622 | TOTAL | 185.1025 | 10883.2686 | 0 | 2070 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 5.2797 | 5.4342 | 5.0448 | 0.60049 | 0.56305 | 0.55881 | 0.6994 | 0.53762 | 0.41823 | 4.2801 | 7 | 0.18084 | 0.18026 | 0.17894 | 3.3461 | 1.4991 | 0.29198 | 12.6252 | 2.3395 | 23.3121 | 3.2548 | 1.184 | 0.31469 | 9.6782 | 1.7484 | 15.4401 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.8 | 20 | 20 | 33.6 | 71 | 251 | 12.5 | 0.305 |  | 6 | 8 | 0.056 | 5.96 | 8 |  | 5.93 | 8 | [8 empty] | 0.05 | [14 empty] | 0.026 | 1 | 0.34 |  | 0.05 | 0.035 | 1 | 0.55 |  | 0.053 | 1 | 0.42 | [22 empty] | AVERAGE | 9.1667 | 9.1667 | 9.1667 | 27.5 | 8.6667 | 8.6667 | 8.6667 | 26 |  | 9.2741 |  | 14.6438 | 23.9179 | 1.3541 | AVERAGE | 61.7008 | 3627.7562 |  | 690 | #N/A | #N/A | #N/A |  |  |  | 1.7599 | 1.8114 | 1.6816 | 0.20016 | 0.18768 | 0.18627 | 0.23313 | 0.17921 | 0.13941 | 1.4267 | 2.3333 | 0.060281 | 0.060085 | 0.059646 | 1.1154 | 0.49968 | 0.097328 | 4.2084 | 0.77983 | 7.7707 | 1.0849 | 0.39468 | 0.1049 | 3.2261 | 0.58282 | 5.1467 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.6 | 117 | 116 | 179.8 | 395 | 1472 | 76.6 | 1.875 | 0.213 | 36.02 | 55.058 | 0.364 | 35.88 | 54 | 0 | 35.8 | 55 | 0 | 24.02 | 1.988 | 16 | 2.61 | 49 | 36.4 | 2.4792 | 0.298 | 24.13 | 1.413 | 15 | 2.63 | 49.9 | 36.4 | 2.4792 | 24.17 | 1.982 | 17 | 2.42 | 55.3 | 36.6 | 2.3741 | 0.179 | 6 | 2.37 | 0.051 | 0.305 | 0.202 | 6 | 3.01 | 0 | 0.335 | 8 | 2.76 | 0 | 46.18 | 0.355 | 7 | 26.3 | 69.3 | 50 | 88 | 0.055 | 45.19 | 0.335 | 7 | 25.2 | 74.7 | 45 | 85 | 0.058 | 24.5 | 23.2 | 20 |  |  | MINIMUM | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 |  | 8.7941 |  | 13.8499 | 22.644 | 0 | MINIMUM | 60.0221 | 3381.8066 |  | 640 | #N/A | #N/A | #N/A |  |  |  | 1.4838 | 1.4838 | 1.4838 | 0.18015 | 0.16814 | 0.1745 | 0.18015 | 0.16814 | 0.09396 | 1.4267 | 1.5 | 0.059792 | 0.059792 | 0.059353 | 1.0983 | 0.49808 | 0.096324 | 4.2049 | 0.75554 | 7.2945 | 1.0728 | 0.3898 | 0.096324 | 3.2012 | 0.57 | 3.7283 |  | MIN | 0.57 | 9.2 | 27.6522 | 15.7617 | 6.03 | 12.3 | 15 | 1.0508 |  |  |  | MIN | 0.58 | 9.2 | 27.6522 | 16.0383 | 6.08 | 12.2 | 15 | 1.0692 |  |  |  | MIN | 0.54 | 9.3 | 29.0323 | 15.6774 | 6.13 | 13.7 | 15 | 1.0452 |  |  |  | 1.0452
AVERAGE | 6.7667 | 19.5 | 19.3333 | 29.9667 | 65.8333 | 245.3333 | 12.7667 | 0.3125 | 0.1065 | 6.0033 | 9.1763 | 0.060667 | 5.98 | 9 |  | 5.9667 | 9.1667 |  | 6.005 | 0.497 | 4 | 0.6525 | 12.25 | 9.1 | 0.6198 | 0.049667 | 6.0325 | 0.35325 | 3.75 | 0.6575 | 12.475 | 9.1 | 0.6198 | 6.0425 | 0.4955 | 4.25 | 0.605 | 13.825 | 9.15 | 0.59352 | 0.029833 | 1 | 0.395 | 0.0255 | 0.050833 | 0.033667 | 1 | 0.50167 |  | 0.055833 | 1.3333 | 0.46 |  | 7.6967 | 0.059167 | 1.1667 | 4.3833 | 11.55 | 25 | 44 | 0.0275 | 7.5317 | 0.055833 | 1.1667 | 4.2 | 12.45 | 22.5 | 42.5 | 0.029 | 4.0833 | 3.8667 | 3.3333 |  |  | MAXIMUM | 9.5 | 9.5 | 9.5 | 28.5 | 9 | 9 | 9 | 27 |  | 9.5141 |  | 15.0408 | 24.5549 | 2.2594 | MAXIMUM | 65.0281 | 4058.168 |  | 715 | #N/A | #N/A | #N/A |  |  |  | 2.1143 | 2.17 | 1.7805 | 0.22819 | 0.21476 | 0.20417 | 0.26422 | 0.20134 | 0.16814 | 1.4267 | 3.5 | 0.060671 | 0.060671 | 0.059792 | 1.1494 | 0.50049 | 0.099335 | 4.2149 | 0.82365 | 8.4799 | 1.092 | 0.40424 | 0.11 | 3.24 | 0.60823 | 6.2004
MINIMUM | 6.66 | 18 | 15 | 26 | 56 | 223 | 12.5 | 0.287 | 0.099 | 5.88 | 7.058 | 0.051 | 5.91 | 7 |  | 5.9 | 7 |  | 5.96 | 0.417 | 3 | 0.57 | 12.1 | 8.5 | 0.59013 | 0.041 | 5.98 | 0.317 | 3 | 0.56 | 12.2 | 8.5 | 0.59013 | 5.97 | 0.434 | 3 | 0.54 | 13.3 | 8.5 | 0.56778 | 0.026 | 1 | 0.28 | 0.024 | 0.046 | 0.022 | 1 | 0.27 |  | 0.052 | 1 | 0.36 |  | 7.27 | 0.049 | 1 | 3.6 | 11.2 | 25 | 40 | 0.026 | 7.05 | 0.051 | 1 | 3.7 | 11.9 | 21 | 42 | 0.025 | 3.7 | 3.7 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 20840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 1050 | 980 | 960 | 900 | 900 | 1120 | 860 | 680 | 2250 | 0 | 2970 | 2960 | 2940 | 252 | 300 | 35 | 4380 | 890 | 1380 | 118 | 114 | 18 | 1560 | 320 | 455
MAXIMUM | 6.89 | 22 | 22 | 33.6 | 71 | 263 | 13.4 | 0.347 | 0.114 | 6.09 | 11 | 0.068 | 6.11 | 12 |  | 6.08 | 11 |  | 6.06 | 0.571 | 5 | 0.84 | 12.4 | 9.5 | 0.66245 | 0.055 | 6.08 | 0.375 | 4 | 0.82 | 12.8 | 9.5 | 0.66245 | 6.13 | 0.568 | 5 | 0.76 | 14.6 | 9.5 | 0.63667 | 0.039 | 1 | 0.5 | 0.027 | 0.057 | 0.044 | 1 | 0.6 |  | 0.062 | 2 | 0.52 |  | 8.1 | 0.084 | 2 | 5 | 12.2 | 25 | 48 | 0.029 | 7.98 | 0.068 | 2 | 4.6 | 13.1 | 24 | 43 | 0.033 | 4.3 | 4.1 | 3.6 | [17 empty] | AVERAGE | 6946.6667 | [9 empty] | 340 | 350 | 326.6667 | 320 | 300 | 300 | 373.3333 | 286.6667 | 226.6667 | 750 |  | 990 | 986.6667 | 980 | 84 | 100 | 11.6667 | 1460 | 296.6667 | 460 | 39.3333 | 38 | 6 | 520 | 106.6667 | 151.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9833 |  | TOTAL AVG COAG ALK: |  |  |  | 9.1143 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.571 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.0267 |  |  |  |  | 0.062 |  |  |  |  | 0.54 | [6 empty] | 0.062 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 6260 | [9 empty] | 300 | 300 | 300 | 300 | 280 | 260 | 300 | 280 | 140 | 750 |  | 920 | 920 | 900 | 80 | 92 | 11 | 1310 | 265 | 450 | 38 | 36 | 6 | 480 | 100 | 115
[90 empty] | MAXIMUM | 7580 | [9 empty] | 380 | 390 | 360 | 340 | 320 | 340 | 440 | 300 | 280 | 750 |  | 1030 | 1020 | 1020 | 86 | 104 | 12 | 1600 | 325 | 465 | 42 | 42 | 6 | 600 | 120 | 170
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.379 |  | TOTAL MGD: |  | 5.114 |  |  | FINISHED SOUTH 1 |  | START: | 23090210 |  | END: | 23095324 |  |  | Alum | 6815 |  | 7715 |  | 0 | [45 empty] | 0.54 | 9.3 | 29.0323 | 15.6774 | 6.13 | 13.7 | 15 | 1.0452
[73 empty] | FINISHED 2 | 15.218 |  | TOTAL MGD: |  | 5.265 |  |  | FINISHED SOUTH 2 |  | START: | 40942050 |  | END: | 40947315 |  |  | Caustic | 4360 |  | 5481
[73 empty] | TOTAL RAW | 27.561 |  | TOTAL MGD: |  | 4.564 |  |  | FINISHED CONWAY |  | START: | 8695856 |  | END: | 8700420 |  |  | Hypochlorite | 4.5'/396 |  | 37'
[76 empty] | TOTAL MGD: |  | 10.654 |  |  | FINISHED PERRY |  | START: | 30367386 |  | END: | 30378040 |  |  | Phosphate | 2880
[76 empty] | TOTAL MGD: |  | 9.127 |  |  | RAW PLANT 1 |  | START: | 27905019 |  | END: | 27914146 |  |  | Fluoride | 0 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.126 |  |  | RAW PLANT 2 |  | START: | 27852444 |  | END: | 27861570 |  |  | Cal~Flo | 15.79 | 0 | 0 | 14.2 | 1338.78 | 25
[76 empty] | TOTAL MGD: |  | 9.308 |  |  | RAW PLANT 3 |  | START: | 4164962 |  | END: | 4174270 |  |  | Zinc | 3185
[76 empty] | TOTAL MGD: |  | 2.063 |  |  | DECANT |  | START: | 1383434 |  | END: | 1385497 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.96053 |  |  | BLOW DOWN |  | START: | 8760.5085 |  | END: | 8761.469 |  |  | NH3 | 13.08
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 640
[90 empty] | BI-SULFITE | 1050 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2552 | Phosphate | 49
[90 empty] | Caustic 1 | 178 | Fluoride | 0
[90 empty] | Caustic 2 | 67 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23095324
[91 empty] | FINISHED SOUTH 2 |  | END: | 40947315
[91 empty] | FINISHED CONWAY |  | END: | 8700420
[91 empty] | FINISHED PERRY |  | END: | 30378040
[91 empty] | RAW PLANT 1 |  | END: | 27914146
[91 empty] | RAW PLANT 2 |  | END: | 27861570
[91 empty] | RAW PLANT 3 |  | END: | 4174270
[91 empty] | DECANT |  | END: | 1385497
[91 empty] | BLOW DOWN |  | END: | 8761.469
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 9
DATE: | 2018-02-09 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-09 | [23 empty] | DATE: | 2018-02-09
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-09 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43140.0093 | 1,2,3 | 48 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | 7,1 | 9.5141 | 1,2 | 15.0408 | 24.5549 | 2.2867 | 43140.0093 | 60.0221 | 3566 | 0 | 640 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 2.1143 | 2.17 | 1.7805 | 0.22819 | 0.21476 | 0.1745 | 0.25503 | 0.20134 | 0.09396 | 1.4267 | 3.5 | 0.060671 | 0.060671 | 0.059353 | 1.1494 | 0.49808 | 0.099335 | 4.2149 | 0.75554 | 8.4799 | 1.092 | 0.3898 | 0.10837 | 3.237 | 0.57022 | 6.2004 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.505 | 4 | 0.71 | 12 | 8.5 | 0.62118 |  | 6.04 | 0.461 | 4 | 0.79 | 12.4 | 8.5 | 0.62118 | 6.01 | 0.376 | 4 | 0.54 | 14.4 | 8.5 | 0.59222 | [13 empty] | 8.2 | 0.055 | 1 | 4 | 11.5 |  |  |  | 7.6 | 0.054 | 1 | 3.6 | 12.1 |  |  |  | 4.1 | 3.9 | 3.6 | [18 empty] | 6260 | [6 empty] | 0 | 0 | 0 | 380 | 390 | 320 | 340 | 320 | 260 | 380 | 300 | 140 | 750 |  | 920 | 920 | 900 | 80 | 92 | 11 | 1310 | 265 | 465 | 38 | 36 | 6 | 480 | 100 | 170 |  | 1:00 | 0.71 | 8.5 | 29.9294 | 21.2499 | 6.06 | 12 | 15 | 1.4167 | 10 | 6.5 | 0.50118 | 1:00 | 0.79 | 8.5 | 29.9294 | 23.6442 | 6.04 | 12.4 | 15 | 1.5763 | 10 | 6.5 | 0.50118 | 1:00 | 0.54 | 8.5 | 31.7647 | 17.1529 | 6.01 | 14.4 | 15 | 1.1435 | 10 | 6.5 | 0.47222
2:00 | [72 empty] | 43140.3336 | 1,2,3 | 48 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | 7,1 | 12.7066 | 1,2 | 16.4102 | 29.1168 | 0.78336 | 43140.3336 | 55.0362 | 2766.9326 | 0 | 640 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6692 | 1.6692 | 1.6692 | 0.18456 | 0.18456 | 0.18456 | 0.18456 | 0.15101 | 0.15101 | 1.4267 | 2 | 0.060012 | 0.060012 | 0.060012 | 1.1207 | 0.49808 | 0.10837 | 4.2099 | 0.76409 | 7.2945 | 1.1494 | 0.3898 | 0.10837 | 3.17 | 0.55881 | 5.2885 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.77 | 19 | 16 | 40.8 | 64 | 316 | 12.5 | 0.298 |  | 6.07 | 8 | 0.061 | 6.01 | 8 |  | 6.01 | 7 | [8 empty] | 0.051 | [14 empty] | 0.027 | 1 | 0.45 |  | 0.049 | 0.033 | 1 | 0.5 |  | 0.053 | 1 | 0.49 | [38 empty] | 5740 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 275 | 275 | 275 | 275 | 225 | 225 | 750 |  | 910 | 910 | 910 | 78 | 92 | 12 | 1310 | 268 | 400 | 40 | 36 | 6 | 470 | 98 | 145 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43140.4951 | 1,2,3 | 30 | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 11.2795 | 1,2 | 13.7362 | 25.0157 | 0 | 43140.4951 | 55.0122 | 2643.9578 | 0 | 640 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6321 | 1.6321 | 1.6321 | 0.16044 | 0.16044 | 0.16044 | 0.16044 | 0.14262 | 0.14262 | 1.4267 | 1 | 0.059792 | 0.059792 | 0.059792 | 1.1034 | 0.50819 | 0.096324 | 4.1852 | 0.76029 | 6.8082 | 1.1034 | 0.36959 | 0.11559 | 3.227 | 0.54741 | 5.2521 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.61 | 0.051 | 1 | 3.8 | 11.4 |  |  |  | 7.57 | 0.054 | 1 | 3.7 | 11.7 |  |  |  | 4.1 | 4 | 3.5 | [18 empty] | 5400 | [6 empty] | 0 | 0 | 0 | 275 | 275 | 275 | 225 | 225 | 225 | 225 | 200 | 200 | 750 |  | 850 | 850 | 850 | 72 | 88 | 10 | 1220 | 250 | 350 | 36 | 32 | 6 | 450 | 90 | 135 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43140.8363 | 1,2,3 | 32 | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 11.2795 | 1,2 | 13.7362 | 25.0157 | 0 | 43140.8363 | 55.216 | 2398 | 0 | 600 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6618 | 1.4244 | 1.6618 | 0.14262 | 0.17114 | 0.14262 | 0.22819 | 0.14262 | 0.15688 | 1.4267 | 2 | 0.059089 | 0.059089 | 0.060496 | 1.1034 | 0.49086 | 0.096324 | 4.1969 | 0.7907 | 6.8082 | 1.1034 | 0.35804 | 0.096324 | 3.187 | 0.57782 | 5.2521 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.72 | 21 | 18 | 38.6 | 53 | 305 | 13.5 | 0.289 |  | 5.96 | 10 | 0.054 | 5.97 | 10 |  | 5.99 | 10 | [8 empty] | 0.045 | [14 empty] | 0.028 | 1 | 0.42 |  | 0.044 | 0.031 | 1 | 0.45 |  | 0.049 | 1 | 0.45 | [38 empty] | 5420 | [6 empty] | 0 | 0 | 0 | 280 | 240 | 280 | 200 | 240 | 200 | 320 | 200 | 220 | 750 |  | 840 | 840 | 860 | 72 | 85 | 10 | 1260 | 260 | 350 | 36 | 31 | 5 | 450 | 95 | 135 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.133 | [9 empty] | 6 | 0.485 | 4 | 0.68 | 12.5 | 8.5 | 0.55436 |  | 6.02 | 0.35 | 4 | 0.72 | 13 | 8.5 | 0.62118 | 6.02 | 0.45 | 4 | 0.58 | 14.5 | 8.5 | 0.59222 |  |  |  | 0.018 | [9 empty] | 7.67 | 0.055 | 1 | 4 | 11.2 | 26 | 47 | 0.02 | 7.69 | 0.059 | 1 | 3.9 | 12.9 | 21 | 43 | 0.02 | 4 | 3.9 | 3.5 | [55 empty] | 9:00 | 0.68 | 8.5 | 29.9294 | 20.352 | 6 | 12.5 | 13 | 1.5655 | 10 | 6 | 0.43436 | 9:00 | 0.72 | 8.5 | 29.9294 | 21.5492 | 6.02 | 13 | 15 | 1.4366 | 10 | 6.5 | 0.50118 | 9:00 | 0.58 | 8.5 | 31.7647 | 18.4235 | 6.02 | 14.5 | 15 | 1.2282 | 10 | 6.5 | 0.47222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.73 | 20 | 17 | 38.2 | 60 | 296 | 12.5 | 0.302 |  | 5.94 | 10 | 0.062 | 5.91 | 11 |  | 5.95 | 11 | [8 empty] | 0.044 | [14 empty] | 0.024 | 1 | 0.32 |  | 0.041 | 0.031 | 1 | 0.41 |  | 0.045 | 1 | 0.44 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.98 | 0.398 | 4 | 0.64 | 12.1 | 7.8 | 0.51858 |  | 5.99 | 0.293 | 3 | 0.7 | 12.9 | 7.9 | 0.52369 | 6 | 0.416 | 4 | 0.78 | 14.3 | 8 | 0.50519 | [13 empty] | 7.55 | 0.05 | 1 | 4.7 | 11.4 |  |  |  | 7.5 | 0.052 | 1 | 4.8 | 13.1 |  |  |  | 4 | 3.7 | 3.5 | [55 empty] | 13:00 | 0.64 | 7.8 | 32.6154 | 20.8738 | 5.98 | 12.1 | 13 | 1.6057 | 10 | 6 | 0.39858 | 13:00 | 0.7 | 7.9 | 32.2025 | 22.5418 | 5.99 | 12.9 | 13 | 1.734 | 10 | 6 | 0.40369 | 13:00 | 0.78 | 8 | 33.75 | 26.325 | 6 | 14.3 | 13 | 2.025 | 10 | 6 | 0.38519
14:00 | [126 empty] | 198 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.86 | 22 | 17 | 40.7 | 46 | 275 | 12.8 | 0.243 |  | 5.92 | 10 | 0.051 | 5.95 | 10 |  | 5.92 | 10 | [8 empty] | 0.043 | [14 empty] | 0.028 | 1 | 0.3 |  | 0.041 | 0.032 | 1 | 0.38 |  | 0.04 | 1 | 0.42 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.53 | 0.048 | 1 | 4.7 | 11.3 |  |  |  | 7.48 | 0.05 | 1 | 4.4 | 12.7 |  |  |  | 4.1 | 3.7 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.84 | 20 | 18 | 36.8 | 57 | 276 | 12 | 0.27 |  | 5.96 | 10 | 0.049 | 5.94 | 10 |  | 5.95 | 10 | [8 empty] | 0.043 | [14 empty] | 0.023 | 1 | 0.36 |  | 0.043 | 0.022 | 1 | 0.4 |  | 0.044 | 1 | 0.44 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.111 | [9 empty] | 6.2 | 0.459 | 5 | 0.64 | 11.6 | 8 | 0.5917 |  | 6.14 | 0.278 | 5 | 0.57 | 11.6 | 8 | 0.5917 | 6.1 | 0.498 | 4 | 0.57 | 13.1 | 8 | 0.56444 |  |  |  | 0.014 | [9 empty] | 7.47 | 0.053 | 1 | 3.7 | 11.6 | 22 | 35 | 0.02 | 7.48 | 0.062 | 1 | 3.6 | 12 | 22 | 33 | 0.019 | 4 | 3.8 | 3.3 | [55 empty] | 21:00 | 0.64 | 8 | 31.8 | 20.352 | 6.2 | 11.6 | 15 | 1.3568 | 10 | 6.5 | 0.4717 | 21:00 | 0.57 | 8 | 31.8 | 18.126 | 6.14 | 11.6 | 15 | 1.2084 | 10 | 6.5 | 0.4717 | 21:00 | 0.57 | 8 | 33.75 | 19.2375 | 6.1 | 13.1 | 15 | 1.2825 | 10 | 6.5 | 0.44444
22:00 | [72 empty] | DOSE |  | TOTAL | 33 | 33 | 33 | 99 | 31 | 31 | 31 | 93 | 0 | 44.7797 | 0 | 58.9234 | 103.703 | 3.0701 | TOTAL | 225.2864 | 11374.8904 | 0 | 2520 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 7.0775 | 6.8957 | 6.7437 | 0.71581 | 0.73091 | 0.66212 | 0.82823 | 0.63758 | 0.54446 | 5.7067 | 8.5 | 0.23956 | 0.23956 | 0.23965 | 4.477 | 1.9952 | 0.40035 | 16.8069 | 3.0706 | 29.3909 | 4.4483 | 1.5072 | 0.42864 | 12.8212 | 2.2543 | 21.9931 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.78 | 22 | 20 | 29.3 | 52 | 224 | 11.8 | 0.267 |  | 5.93 | 10 | 0.051 | 5.92 | 10 |  | 5.9 | 10 | [8 empty] | 0.044 | [14 empty] | 0.022 | 1 | 0.3 |  | 0.043 | 0.02 | 1 | 0.34 |  | 0.039 | 1 | 0.4 | [22 empty] | AVERAGE | 8.25 | 8.25 | 8.25 | 24.75 | 7.75 | 7.75 | 7.75 | 23.25 |  | 11.1949 |  | 14.7308 | 25.9258 | 0.76752 | AVERAGE | 56.3216 | 2843.7226 |  | 630 | #N/A | #N/A | #N/A |  |  |  | 1.7694 | 1.7239 | 1.6859 | 0.17895 | 0.18273 | 0.16553 | 0.20706 | 0.1594 | 0.13612 | 1.4267 | 2.125 | 0.059891 | 0.059891 | 0.059913 | 1.1193 | 0.4988 | 0.10009 | 4.2017 | 0.76766 | 7.3477 | 1.1121 | 0.37681 | 0.10716 | 3.2053 | 0.56357 | 5.4983 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.7 | 124 | 106 | 224.4 | 332 | 1692 | 75.1 | 1.669 | 0.244 | 35.78 | 58 | 0.328 | 35.7 | 59 | 0 | 35.72 | 58 | 0 | 24.24 | 1.847 | 17 | 2.67 | 48.2 | 32.8 | 2.2858 | 0.27 | 24.19 | 1.382 | 16 | 2.78 | 49.9 | 32.9 | 2.3578 | 24.13 | 1.74 | 16 | 2.47 | 56.3 | 33 | 2.2541 | 0.152 | 6 | 2.15 | 0.032 | 0.261 | 0.169 | 6 | 2.48 | 0 | 0.27 | 6 | 2.64 | 0 | 46.03 | 0.312 | 6 | 24.9 | 68.4 | 48 | 82 | 0.04 | 45.32 | 0.331 | 6 | 24 | 74.5 | 43 | 76 | 0.039 | 24.3 | 23 | 20.8 |  |  | MINIMUM | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 |  | 9.5141 |  | 13.7362 | 24.5549 | 0 | MINIMUM | 55.0122 | 2398 |  | 600 | #N/A | #N/A | #N/A |  |  |  | 1.6321 | 1.4244 | 1.6321 | 0.14262 | 0.16044 | 0.14262 | 0.16044 | 0.14262 | 0.09396 | 1.4267 | 1 | 0.059089 | 0.059089 | 0.059353 | 1.1034 | 0.49086 | 0.096324 | 4.1852 | 0.75554 | 6.8082 | 1.092 | 0.35804 | 0.096324 | 3.17 | 0.54741 | 5.2521 |  | MIN | 0.64 | 8 | 31.8 | 20.352 | 6.2 | 11.6 | 15 | 1.3568 |  |  |  | MIN | 0.57 | 8 | 31.8 | 18.126 | 6.14 | 11.6 | 15 | 1.2084 |  |  |  | MIN | 0.54 | 8.5 | 31.7647 | 17.1529 | 6.01 | 14.4 | 15 | 1.1435 |  |  |  | 1.1435
AVERAGE | 6.7833 | 20.6667 | 17.6667 | 37.4 | 55.3333 | 282 | 12.5167 | 0.27817 | 0.122 | 5.9633 | 9.6667 | 0.054667 | 5.95 | 9.8333 |  | 5.9533 | 9.6667 |  | 6.06 | 0.46175 | 4.25 | 0.6675 | 12.05 | 8.2 | 0.57145 | 0.045 | 6.0475 | 0.3455 | 4 | 0.695 | 12.475 | 8.225 | 0.58944 | 6.0325 | 0.435 | 4 | 0.6175 | 14.075 | 8.25 | 0.56352 | 0.025333 | 1 | 0.35833 | 0.016 | 0.0435 | 0.028167 | 1 | 0.41333 |  | 0.045 | 1 | 0.44 |  | 7.6717 | 0.052 | 1 | 4.15 | 11.4 | 24 | 41 | 0.02 | 7.5533 | 0.055167 | 1 | 4 | 12.4167 | 21.5 | 38 | 0.0195 | 4.05 | 3.8333 | 3.4667 |  |  | MAXIMUM | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 |  | 12.7066 |  | 16.4102 | 29.1168 | 2.2867 | MAXIMUM | 60.0221 | 3566 |  | 640 | #N/A | #N/A | #N/A |  |  |  | 2.1143 | 2.17 | 1.7805 | 0.22819 | 0.21476 | 0.18456 | 0.25503 | 0.20134 | 0.15688 | 1.4267 | 3.5 | 0.060671 | 0.060671 | 0.060496 | 1.1494 | 0.50819 | 0.10837 | 4.2149 | 0.7907 | 8.4799 | 1.1494 | 0.3898 | 0.11559 | 3.237 | 0.57782 | 6.2004
MINIMUM | 6.72 | 19 | 16 | 29.3 | 46 | 224 | 11.8 | 0.243 | 0.111 | 5.92 | 8 | 0.049 | 5.91 | 8 |  | 5.9 | 7 |  | 5.98 | 0.398 | 4 | 0.64 | 11.6 | 7.8 | 0.51858 | 0.043 | 5.99 | 0.278 | 3 | 0.57 | 11.6 | 7.9 | 0.52369 | 6 | 0.376 | 4 | 0.54 | 13.1 | 8 | 0.50519 | 0.022 | 1 | 0.3 | 0.014 | 0.041 | 0.02 | 1 | 0.34 |  | 0.039 | 1 | 0.4 |  | 7.47 | 0.048 | 1 | 3.7 | 11.2 | 22 | 35 | 0.02 | 7.48 | 0.05 | 1 | 3.6 | 11.7 | 21 | 33 | 0.019 | 4 | 3.7 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 22820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1235 | 1205 | 1175 | 1040 | 1060 | 960 | 1200 | 925 | 785 | 3000 | 0 | 3520 | 3520 | 3520 | 302 | 357 | 43 | 5100 | 1043 | 1565 | 150 | 135 | 23 | 1850 | 383 | 585
MAXIMUM | 6.86 | 22 | 20 | 40.8 | 64 | 316 | 13.5 | 0.302 | 0.133 | 6.07 | 10 | 0.062 | 6.01 | 11 |  | 6.01 | 11 |  | 6.2 | 0.505 | 5 | 0.71 | 12.5 | 8.5 | 0.62118 | 0.051 | 6.14 | 0.461 | 5 | 0.79 | 13 | 8.5 | 0.62118 | 6.1 | 0.498 | 4 | 0.78 | 14.5 | 8.5 | 0.59222 | 0.028 | 1 | 0.45 | 0.018 | 0.049 | 0.033 | 1 | 0.5 |  | 0.053 | 1 | 0.49 |  | 8.2 | 0.055 | 1 | 4.7 | 11.6 | 26 | 47 | 0.02 | 7.69 | 0.062 | 1 | 4.8 | 13.1 | 22 | 43 | 0.02 | 4.1 | 4 | 3.6 | [17 empty] | AVERAGE | 5705 | [9 empty] | 308.75 | 301.25 | 293.75 | 260 | 265 | 240 | 300 | 231.25 | 196.25 | 750 |  | 880 | 880 | 880 | 75.5 | 89.25 | 10.75 | 1275 | 260.75 | 391.25 | 37.5 | 33.75 | 5.75 | 462.5 | 95.75 | 146.25
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9556 |  | TOTAL AVG COAG ALK: |  |  |  | 9.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.505 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.0467 |  |  |  |  | 0.053 |  |  |  |  | 0.54 | [6 empty] | 0.053 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 5400 | [9 empty] | 275 | 240 | 275 | 200 | 225 | 200 | 225 | 200 | 140 | 750 |  | 840 | 840 | 850 | 72 | 85 | 10 | 1220 | 250 | 350 | 36 | 31 | 5 | 450 | 90 | 135
[90 empty] | MAXIMUM | 6260 | [9 empty] | 380 | 390 | 320 | 340 | 320 | 275 | 380 | 300 | 225 | 750 |  | 920 | 920 | 910 | 80 | 92 | 12 | 1310 | 268 | 465 | 40 | 36 | 6 | 480 | 100 | 170
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.519 |  | TOTAL MGD: |  | 4.044 |  |  | FINISHED SOUTH 1 |  | START: | 23095324 |  | END: | 23099368 |  |  | Alum | 6196 |  | 7155 |  | 0 | [45 empty] | 0.54 | 8.5 | 31.7647 | 17.1529 | 6.01 | 14.4 | 15 | 1.1435
[73 empty] | FINISHED 2 | 13.35 |  | TOTAL MGD: |  | 5.475 |  |  | FINISHED SOUTH 2 |  | START: | 40947315 |  | END: | 40952790 |  |  | Caustic | 4255 |  | 5391
[73 empty] | TOTAL RAW | 24.431 |  | TOTAL MGD: |  | 3.92 |  |  | FINISHED CONWAY |  | START: | 8700420 |  | END: | 8704340 |  |  | Hypochlorite | 13'/379 |  | 26.5'
[76 empty] | TOTAL MGD: |  | 9.43 |  |  | FINISHED PERRY |  | START: | 30378040 |  | END: | 30387470 |  |  | Phosphate | 2800
[76 empty] | TOTAL MGD: |  | 8.071 |  |  | RAW PLANT 1 |  | START: | 27914146 |  | END: | 27922217 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.08 |  |  | RAW PLANT 2 |  | START: | 27861570 |  | END: | 27869650 |  |  | Cal~Flo | 14.2 | 0 | 0 | 12.94 | 1060.92 | 25
[76 empty] | TOTAL MGD: |  | 8.28 |  |  | RAW PLANT 3 |  | START: | 4174270 |  | END: | 4182550 |  |  | Zinc | 3178
[76 empty] | TOTAL MGD: |  | 1.258 |  |  | DECANT |  | START: | 1385497 |  | END: | 1386755 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.83823 |  |  | BLOW DOWN |  | START: | 8761.469 |  | END: | 8762.3072 |  |  | NH3 | 12.89
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 600
[90 empty] | BI-SULFITE | 1050 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2091 | Phosphate | 40
[90 empty] | Caustic 1 | 139 | Fluoride | 0
[90 empty] | Caustic 2 | 59 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1
[91 empty] | FINISHED SOUTH 1 |  | END: | 23099368
[91 empty] | FINISHED SOUTH 2 |  | END: | 40952790
[91 empty] | FINISHED CONWAY |  | END: | 8704340
[91 empty] | FINISHED PERRY |  | END: | 30387470
[91 empty] | RAW PLANT 1 |  | END: | 27922217
[91 empty] | RAW PLANT 2 |  | END: | 27869650
[91 empty] | RAW PLANT 3 |  | END: | 4182550
[91 empty] | DECANT |  | END: | 1386755
[91 empty] | BLOW DOWN |  | END: | 8762.3072
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 10
DATE: | 2018-02-10 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-10 | [23 empty] | DATE: | 2018-02-10
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-10 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43141.0016 | 1,2,3 | 32 | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 11.2795 | 1,2 | 13.7362 | 25.0157 | 1.2384 | 43141.0016 | 55.216 | 2398 | 0 | 600 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6618 | 1.4244 | 1.6618 | 0.14262 | 0.17114 | 0.14262 | 0.22819 | 0.14262 | 0.15688 | 1.4267 | 2 | 0.059089 | 0.059089 | 0.060496 | 1.1034 | 0.49086 | 0.096324 | 4.1969 | 0.7907 | 6.8082 | 1.1034 | 0.35804 | 0.096324 | 3.187 | 0.57782 | 5.2521 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.94 | 0.421 | 4 | 0.77 | 11.5 | 8 | 0.52881 |  | 6.06 | 0.33 | 3 | 0.7 | 11.4 | 8 | 0.5917 | 6.01 | 0.338 | 3 | 0.64 | 13.1 | 8 | 0.56444 | [13 empty] | 7.24 | 0.046 | 1 | 3.7 | 11.5 |  |  |  | 7.34 | 0.044 | 1 | 3.8 | 11.7 |  |  |  | 3.9 | 3.6 | 3.6 | [18 empty] | 5420 | [6 empty] | 0 | 0 | 0 | 280 | 240 | 280 | 200 | 240 | 200 | 320 | 200 | 220 | 750 |  | 840 | 840 | 860 | 72 | 85 | 10 | 1260 | 260 | 350 | 36 | 31 | 5 | 450 | 95 | 135 |  | 1:00 | 0.77 | 8 | 31.8 | 24.486 | 5.94 | 11.5 | 13 | 1.8835 | 10 | 6 | 0.40881 | 1:00 | 0.7 | 8 | 31.8 | 22.26 | 6.06 | 11.4 | 15 | 1.484 | 10 | 6.5 | 0.4717 | 1:00 | 0.64 | 8 | 33.75 | 21.6 | 6.01 | 13.1 | 15 | 1.44 | 10 | 6.5 | 0.44444
2:00 | [72 empty] | 43141.3509 | 1,2,3 | 36 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | 7,1 | 7.0142 | 1,2 | 14.1624 | 21.1766 | 1.2442 | 43141.3509 | 48.8998 | 2152.0586 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6692 | 1.6692 | 1.6692 | 0.15101 | 0.15101 | 0.15101 | 0.15101 | 0.14765 | 0.14765 | 1.4267 | 1 | 0.060012 | 0.060012 | 0.060012 | 1.1207 | 0.49808 | 0.10837 | 4.1884 | 0.76979 | 7.2034 | 1.092 | 0.49808 | 0.10837 | 3.217 | 0.55881 | 5.4709 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.79 | 20 | 15 | 29.4 | 48 | 238 | 12.5 | 0.252 |  | 6.05 | 8 | 0.05 | 5.97 | 8 |  | 5.93 | 7 | [8 empty] | 0.043 | [14 empty] | 0.022 | 1 | 0.44 |  | 0.043 | 0.023 | 1 | 0.41 |  | 0.041 | 1 | 0.48 | [38 empty] | 5100 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 225 | 225 | 225 | 225 | 220 | 220 | 750 |  | 910 | 910 | 910 | 78 | 92 | 12 | 1320 | 270 | 395 | 38 | 46 | 6 | 480 | 98 | 150 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43141.4796 | 1,2,3 | 36 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 7.0142 | 1,2 | 14.1624 | 21.1766 | 0 | 43141.4796 | 46.1831 | 2152.0586 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.15846 | 0.15846 | 0.15846 | 0.15846 | 0.14262 | 0.14262 | 1.4267 | 0 | 0.060206 | 0.060206 | 0.060206 | 1.1089 | 0.49935 | 0.10199 | 4.1817 | 0.76476 | 7.7236 | 1.0818 | 0.40764 | 0.10199 | 3.5927 | 0.54741 | 6.0073 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.13 | 0.044 | 1 | 3.7 | 11.7 |  |  |  | 7.21 | 0.046 | 1 | 3.7 | 11.6 |  |  |  | 3.9 | 3.6 | 4 | [18 empty] | 5100 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 225 | 225 | 750 |  | 970 | 970 | 970 | 82 | 98 | 12 | 1400 | 285 | 450 | 40 | 40 | 6 | 580 | 102 | 175 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43141.8235 | 1,2,3 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 7.0142 | 1,2 | 14.1624 | 21.1766 | 0 | 43141.8235 | 46.5453 | 1845 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4663 | 1.3616 | 1.4663 | 0.19016 | 0.19016 | 0.19016 | 0.1648 | 0.12677 | 0.13945 | 1.4267 | 3 | 0.058344 | 0.058344 | 0.059585 | 1.0818 | 0.49935 | 0.10199 | 4.2104 | 0.77818 | 7.7236 | 1.0818 | 0.39745 | 0.084992 | 3.1834 | 0.53668 | 6.0073 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.78 | 22 | 17 | 26.5 | 45 | 219 | 12.5 | 0.252 |  | 5.97 | 10 | 0.051 | 5.95 | 10 |  | 5.92 | 10 | [8 empty] | 0.041 | [14 empty] | 0.022 | 1 | 0.46 |  | 0.039 | 0.026 | 1 | 0.48 |  | 0.04 | 1 | 0.52 | [38 empty] | 5140 | [6 empty] | 0 | 0 | 0 | 280 | 260 | 280 | 300 | 300 | 300 | 260 | 200 | 220 | 750 |  | 940 | 940 | 960 | 80 | 98 | 12 | 1420 | 290 | 450 | 40 | 39 | 5 | 500 | 100 | 175 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.109 | [9 empty] | 5.99 | 0.44 | 4 | 0.68 | 12 | 8.5 | 0.55436 |  | 6.03 | 0.253 | 3 | 0.69 | 12 | 8.5 | 0.62118 | 6.04 | 0.446 | 3 | 0.78 | 13 | 8.5 | 0.59222 |  |  |  | 0.025 | [9 empty] | 7.39 | 0.046 | 1 | 3.8 | 11.3 | 20 | 30 | 0.03 | 7.34 | 0.05 | 1 | 3.4 | 12.3 | 20 | 29 | 0.021 | 3.8 | 3.7 | 4 | [55 empty] | 9:00 | 0.68 | 8.5 | 29.9294 | 20.352 | 5.99 | 12 | 13 | 1.5655 | 10 | 6 | 0.43436 | 9:00 | 0.69 | 8.5 | 29.9294 | 20.6513 | 6.03 | 12 | 15 | 1.3768 | 10 | 6.5 | 0.50118 | 9:00 | 0.78 | 8.5 | 31.7647 | 24.7765 | 6.04 | 13 | 15 | 1.6518 | 10 | 6.5 | 0.47222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.73 | 21 | 16 | 27 | 58 | 256 | 12.6 | 0.277 |  | 5.88 | 11 | 0.052 | 5.87 | 11 |  | 5.86 | 10 | [8 empty] | 0.034 | [14 empty] | 0.07 | 1 | 0.48 |  | 0.033 | 0.026 | 1 | 0.41 |  | 0.042 | 1 | 0.54 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.05 | 0.462 | 4 | 0.74 | 12.1 | 9 | 0.65066 |  | 6 | 0.351 | 4 | 0.78 | 12.7 | 9 | 0.57991 | 6.01 | 0.465 | 4 | 0.79 | 13.8 | 9.2 | 0.63111 | [13 empty] | 7.56 | 0.045 | 1 | 3.7 | 11.3 |  |  |  | 7.32 | 0.048 | 1 | 3.4 | 12.8 |  |  |  | 3.9 | 3.7 | 2.9 | [55 empty] | 13:00 | 0.74 | 9 | 28.2667 | 20.9173 | 6.05 | 12.1 | 15 | 1.3945 | 10 | 6.5 | 0.53066 | 13:00 | 0.78 | 9 | 28.2667 | 22.048 | 6 | 12.7 | 13 | 1.696 | 10 | 6 | 0.45991 | 13:00 | 0.79 | 9.2 | 29.3478 | 23.1848 | 6.01 | 13.8 | 15 | 1.5457 | 10 | 6.5 | 0.51111
14:00 | [126 empty] | 224 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.76 | 22 | 16 | 31.6 | 48 | 238 | 12.6 | 0.246 |  | 5.98 | 11 | 0.047 | 5.96 | 11 |  | 5.95 | 11 | [8 empty] | 0.034 | [14 empty] | 0.046 | 1 | 0.42 |  | 0.034 | 0.028 | 1 | 0.38 |  | 0.043 | 1 | 0.5 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.93 | 0.047 | 1 | 3.6 | 11.4 |  |  |  | 7.77 | 0.046 | 1 | 3.3 | 13.1 |  |  |  | 3.9 | 3.6 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.75 | 20 | 21 | 35 | 52 | 270 | 12.5 | 0.289 |  | 5.77 | 8 | 0.051 | 5.74 | 8 |  | 5.74 | 8 | [8 empty] | 0.042 | [14 empty] | 0.057 | 1 | 0.27 |  | 0.051 | 0.031 | 1 | 0.2 |  | 0.045 | 1 | 0.35 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.117 | [9 empty] | 6.07 | 0.737 | 6 | 0.59 | 12.1 | 9 | 0.65066 |  | 6.03 | 0.371 | 5 | 0.57 | 12.7 | 9 | 0.65066 | 6.06 | 0.515 | 4 | 0.59 | 13.8 | 9 | 0.62 |  |  |  | 0.027 | [9 empty] | 7.49 | 0.089 | 2 | 3 | 12 | 24 | 36 | 0.033 | 7.58 | 0.066 | 1 | 3.2 | 12.3 | 25 | 36 | 0.029 | 3.8 | 3.7 | 3.1 | [55 empty] | 21:00 | 0.59 | 9 | 28.2667 | 16.6773 | 6.07 | 12.1 | 15 | 1.1118 | 10 | 6.5 | 0.53066 | 21:00 | 0.57 | 9 | 28.2667 | 16.112 | 6.03 | 12.7 | 15 | 1.0741 | 10 | 6.5 | 0.53066 | 21:00 | 0.59 | 9 | 30 | 17.7 | 6.06 | 13.8 | 15 | 1.18 | 10 | 6.5 | 0.5
22:00 | [72 empty] | DOSE |  | TOTAL | 34.5 | 34.5 | 34.5 | 103.5 | 32.5 | 32.5 | 32.5 | 97.5 | 0 | 32.3222 | 0 | 56.2234 | 88.5456 | 2.4826 | TOTAL | 196.8442 | 8547.1172 | 0 | 2600 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 6.3683 | 6.0262 | 6.3683 | 0.64224 | 0.67077 | 0.64224 | 0.70246 | 0.55966 | 0.58659 | 5.7067 | 6 | 0.23765 | 0.23765 | 0.2403 | 4.4148 | 1.9877 | 0.40867 | 16.7774 | 3.1034 | 29.4589 | 4.359 | 1.6612 | 0.39167 | 13.1802 | 2.2207 | 22.7375 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.68 | 20 | 20 | 33.7 | 62 | 277 | 12.6 | 0.32 |  | 5.9 | 8 | 0.058 | 5.87 | 8 |  | 5.85 | 8 | [8 empty] | 0.04 | [14 empty] | 0.054 | 1 | 0.29 |  | 0.05 | 0.033 | 1 | 0.29 |  | 0.05 | 1 | 0.36 | [22 empty] | AVERAGE | 8.625 | 8.625 | 8.625 | 25.875 | 8.125 | 8.125 | 8.125 | 24.375 |  | 8.0806 |  | 14.0558 | 22.1364 | 0.62064 | AVERAGE | 49.211 | 2136.7793 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.5921 | 1.5066 | 1.5921 | 0.16056 | 0.16769 | 0.16056 | 0.17561 | 0.13991 | 0.14665 | 1.4267 | 1.5 | 0.059413 | 0.059413 | 0.060075 | 1.1037 | 0.49691 | 0.10217 | 4.1944 | 0.77586 | 7.3647 | 1.0898 | 0.4153 | 0.097918 | 3.295 | 0.55518 | 5.6844 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.49 | 125 | 105 | 183.2 | 313 | 1498 | 75.3 | 1.636 | 0.226 | 35.55 | 56 | 0.309 | 35.36 | 56 | 0 | 35.25 | 54 | 0 | 24.05 | 2.06 | 18 | 2.78 | 47.7 | 34.5 | 2.3845 | 0.234 | 24.12 | 1.305 | 15 | 2.74 | 48.8 | 34.5 | 2.4434 | 24.12 | 1.764 | 14 | 2.8 | 53.7 | 34.7 | 2.4078 | 0.271 | 6 | 2.36 | 0.052 | 0.25 | 0.167 | 6 | 2.17 | 0 | 0.261 | 6 | 2.75 | 0 | 44.74 | 0.317 | 7 | 21.5 | 69.2 | 44 | 66 | 0.063 | 44.56 | 0.3 | 6 | 20.8 | 73.8 | 45 | 65 | 0.05 | 23.2 | 21.9 | 20.6 |  |  | MINIMUM | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 |  | 7.0142 |  | 13.7362 | 21.1766 | 0 | MINIMUM | 46.1831 | 1845 |  | 600 | #N/A | #N/A | #N/A |  |  |  | 1.4663 | 1.3616 | 1.4663 | 0.14262 | 0.15101 | 0.14262 | 0.15101 | 0.12677 | 0.13945 | 1.4267 | 0 | 0.058344 | 0.058344 | 0.059585 | 1.0818 | 0.49086 | 0.096324 | 4.1817 | 0.76476 | 6.8082 | 1.0818 | 0.35804 | 0.084992 | 3.1834 | 0.53668 | 5.2521 |  | MIN | 0.59 | 9 | 28.2667 | 16.6773 | 6.07 | 12.1 | 15 | 1.1118 |  |  |  | MIN | 0.57 | 9 | 28.2667 | 16.112 | 6.03 | 12.7 | 15 | 1.0741 |  |  |  | MIN | 0.59 | 9 | 30 | 17.7 | 6.06 | 13.8 | 15 | 1.18 |  |  |  | 1.0741
AVERAGE | 6.7483 | 20.8333 | 17.5 | 30.5333 | 52.1667 | 249.6667 | 12.55 | 0.27267 | 0.113 | 5.925 | 9.3333 | 0.0515 | 5.8933 | 9.3333 |  | 5.875 | 9 |  | 6.0125 | 0.515 | 4.5 | 0.695 | 11.925 | 8.625 | 0.59612 | 0.039 | 6.03 | 0.32625 | 3.75 | 0.685 | 12.2 | 8.625 | 0.61086 | 6.03 | 0.441 | 3.5 | 0.7 | 13.425 | 8.675 | 0.60194 | 0.045167 | 1 | 0.39333 | 0.026 | 0.041667 | 0.027833 | 1 | 0.36167 |  | 0.0435 | 1 | 0.45833 |  | 7.4567 | 0.052833 | 1.1667 | 3.5833 | 11.5333 | 22 | 33 | 0.0315 | 7.4267 | 0.05 | 1 | 3.4667 | 12.3 | 22.5 | 32.5 | 0.025 | 3.8667 | 3.65 | 3.4333 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 11.2795 |  | 14.1624 | 25.0157 | 1.2442 | MAXIMUM | 55.216 | 2398 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.6692 | 1.6692 | 1.6692 | 0.19016 | 0.19016 | 0.19016 | 0.22819 | 0.14765 | 0.15688 | 1.4267 | 3 | 0.060206 | 0.060206 | 0.060496 | 1.1207 | 0.49935 | 0.10837 | 4.2104 | 0.7907 | 7.7236 | 1.1034 | 0.49808 | 0.10837 | 3.5927 | 0.57782 | 6.0073
MINIMUM | 6.68 | 20 | 15 | 26.5 | 45 | 219 | 12.5 | 0.246 | 0.109 | 5.77 | 8 | 0.047 | 5.74 | 8 |  | 5.74 | 7 |  | 5.94 | 0.421 | 4 | 0.59 | 11.5 | 8 | 0.52881 | 0.034 | 6 | 0.253 | 3 | 0.57 | 11.4 | 8 | 0.57991 | 6.01 | 0.338 | 3 | 0.59 | 13 | 8 | 0.56444 | 0.022 | 1 | 0.27 | 0.025 | 0.033 | 0.023 | 1 | 0.2 |  | 0.04 | 1 | 0.35 |  | 7.13 | 0.044 | 1 | 3 | 11.3 | 20 | 30 | 0.03 | 7.21 | 0.044 | 1 | 3.2 | 11.6 | 20 | 29 | 0.021 | 3.8 | 3.6 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 20760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 1100 | 1160 | 975 | 1015 | 975 | 1055 | 845 | 885 | 3000 | 0 | 3660 | 3660 | 3700 | 312 | 373 | 46 | 5400 | 1105 | 1645 | 154 | 156 | 22 | 2010 | 395 | 635
MAXIMUM | 6.79 | 22 | 21 | 35 | 62 | 277 | 12.6 | 0.32 | 0.117 | 6.05 | 11 | 0.058 | 5.97 | 11 |  | 5.95 | 11 |  | 6.07 | 0.737 | 6 | 0.77 | 12.1 | 9 | 0.65066 | 0.043 | 6.06 | 0.371 | 5 | 0.78 | 12.7 | 9 | 0.65066 | 6.06 | 0.515 | 4 | 0.79 | 13.8 | 9.2 | 0.63111 | 0.07 | 1 | 0.48 | 0.027 | 0.051 | 0.033 | 1 | 0.48 |  | 0.05 | 1 | 0.54 |  | 7.93 | 0.089 | 2 | 3.8 | 12 | 24 | 36 | 0.033 | 7.77 | 0.066 | 1 | 3.8 | 13.1 | 25 | 36 | 0.029 | 3.9 | 3.7 | 4 | [17 empty] | AVERAGE | 5190 | [9 empty] | 290 | 275 | 290 | 243.75 | 253.75 | 243.75 | 263.75 | 211.25 | 221.25 | 750 |  | 915 | 915 | 925 | 78 | 93.25 | 11.5 | 1350 | 276.25 | 411.25 | 38.5 | 39 | 5.5 | 502.5 | 98.75 | 158.75
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.8978 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.737 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.57 | [5 empty] | 6.0242 |  |  |  |  | 0.07 |  |  |  |  | 0.57 | [6 empty] | 0.07 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 5100 | [9 empty] | 280 | 240 | 280 | 200 | 225 | 200 | 225 | 200 | 220 | 750 |  | 840 | 840 | 860 | 72 | 85 | 10 | 1260 | 260 | 350 | 36 | 31 | 5 | 450 | 95 | 135
[90 empty] | MAXIMUM | 5420 | [9 empty] | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 225 | 225 | 750 |  | 970 | 970 | 970 | 82 | 98 | 12 | 1420 | 290 | 450 | 40 | 46 | 6 | 580 | 102 | 175
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.714 |  | TOTAL MGD: |  | 4.672 |  |  | FINISHED SOUTH 1 |  | START: | 23099368 |  | END: | 23104040 |  |  | Alum | 5645 |  | 6660 |  | 0 | [45 empty] | 0.57 | 9 | 28.2667 | 16.112 | 6.03 | 12.7 | 15 | 1.0741
[73 empty] | FINISHED 2 | 14.522 |  | TOTAL MGD: |  | 5.042 |  |  | FINISHED SOUTH 2 |  | START: | 40952790 |  | END: | 40957832 |  |  | Caustic | 4118 |  | 5272
[73 empty] | TOTAL RAW | 26.106 |  | TOTAL MGD: |  | 4.014 |  |  | FINISHED CONWAY |  | START: | 8704340 |  | END: | 8708354 |  |  | Hypochlorite | 12'/354 |  | 24.5'
[76 empty] | TOTAL MGD: |  | 10.508 |  |  | FINISHED PERRY |  | START: | 30387470 |  | END: | 30397978 |  |  | Phosphate | 2825
[76 empty] | TOTAL MGD: |  | 8.651 |  |  | RAW PLANT 1 |  | START: | 27922217 |  | END: | 27930868 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.655 |  |  | RAW PLANT 2 |  | START: | 27869650 |  | END: | 27878305 |  |  | Cal~Flo | 12.94 | 0 | 0 | 12.03 | 766.22 | 25
[76 empty] | TOTAL MGD: |  | 8.8 |  |  | RAW PLANT 3 |  | START: | 4182550 |  | END: | 4191350 |  |  | Zinc | 3199
[76 empty] | TOTAL MGD: |  | 1.447 |  |  | DECANT |  | START: | 1386755 |  | END: | 1388202 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.92958 |  |  | BLOW DOWN |  | START: | 8762.3072 |  | END: | 8763.2368 |  |  | NH3 | 12.71
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 675
[90 empty] | BI-SULFITE | 1050 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 1918 | Phosphate | 55
[90 empty] | Caustic 1 | 154 | Fluoride | 0
[90 empty] | Caustic 2 | 70 | Zinc | 6
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23104040
[91 empty] | FINISHED SOUTH 2 |  | END: | 40957832
[91 empty] | FINISHED CONWAY |  | END: | 8708354
[91 empty] | FINISHED PERRY |  | END: | 30397978
[91 empty] | RAW PLANT 1 |  | END: | 27930868
[91 empty] | RAW PLANT 2 |  | END: | 27878305
[91 empty] | RAW PLANT 3 |  | END: | 4191350
[91 empty] | DECANT |  | END: | 1388202
[91 empty] | BLOW DOWN |  | END: | 8763.2368
1 | 1,5,6 |  |  | 28 | 8.8 | 8 |  | 9.6 |  | 26.4 | 8.3 | 7.5 | 9.1 | 24.9 | 7 | 19.4256 | 0 | 0.02772 | 19.4533 | 1 | 0 | 1900 | 650 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | [5 empty] | 0 | 0 |  | 0 | 0.3 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.4 | #DIV/0! | 0
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 11
DATE: | 2018-02-11 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-11 | [23 empty] | DATE: | 2018-02-11
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-11 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43142.0019 | 1,2,3 | 40 | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 | 7,1 | 7.0142 | 1,2 | 14.1624 | 21.1766 | 1.5264 | 43142.0019 | 55 | 2214 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4163 | 1.3151 | 1.4163 | 0.18402 | 0.18402 | 0.18402 | 0.15949 | 0.12268 | 0.13495 | 1.4267 | 3 | 0.056355 | 0.056355 | 0.057554 | 1.0449 | 0.48233 | 0.098514 | 4.0805 | 0.75165 | 7.4603 | 1.0449 | 0.3839 | 0.082095 | 3.0919 | 0.51838 | 5.8025 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.99 | 0.661 | 5 | 0.53 | 12.3 | 9 | 0.57991 |  | 5.96 | 0.642 | 5 | 0.48 | 12.4 | 9 | 0.57991 | 5.98 | 0.429 | 4 | 0.47 | 13.9 | 9 | 0.55333 | [13 empty] | 7.55 | 0.061 | 1 | 3.8 | 12.2 |  |  |  | 7.44 | 0.057 | 1 | 3.5 | 12.5 |  |  |  | 3.5 | 3.5 | 3 | [18 empty] | 6210 | [6 empty] | 0 | 0 | 0 | 280 | 260 | 280 | 300 | 300 | 300 | 260 | 200 | 220 | 750 |  | 940 | 940 | 960 | 80 | 98 | 12 | 1420 | 290 | 450 | 40 | 39 | 5 | 500 | 100 | 175 |  | 1:00 | 0.53 | 9 | 28.2667 | 14.9813 | 5.99 | 12.3 | 13 | 1.1524 | 10 | 6 | 0.45991 | 1:00 | 0.48 | 9 | 28.2667 | 13.568 | 5.96 | 12.4 | 13 | 1.0437 | 10 | 6 | 0.45991 | 1:00 | 0.47 | 9 | 30 | 14.1 | 5.98 | 13.9 | 13 | 1.0846 | 10 | 6 | 0.43333
2:00 | [72 empty] | 43142.3422 | 1,2,3 | 40 | 8.7 | 8.6 | 8.7 | 26 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.6926 | 1,2 | 13.1832 | 22.8758 | 1.2758 | 43142.3422 | 54.9182 | 2828.42 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.16393 | 0.16393 | 0.16583 | 0.16583 | 0.13114 | 0.14426 | 1.4267 | 2 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.1304 | 0.79428 | 7.7236 | 1.0818 | 0.48916 | 0.10199 | 3.2117 | 0.60108 | 6.0073 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.84 | 18 | 16 | 39 | 67 | 314 | 12.7 | 0.324 |  | 6.06 | 7 | 0.058 | 5.97 | 7 |  | 5.9 | 7 | [8 empty] | 0.052 | [14 empty] | 0.05 | 1 | 0.34 |  | 0.046 | 0.031 | 1 | 0.3 |  | 0.052 | 1 | 0.26 | [38 empty] | 5840 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 200 | 220 | 750 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1420 | 296 | 450 | 40 | 48 | 6 | 550 | 112 | 175 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43142.8842 | 1,2,3 | 36 | 8.7 | 8.7 | 8.7 | 26.1 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.8619 | 1,2 | 15.1762 | 26.0381 | 0 | 43142.8842 | 55.4572 | 2582.4704 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4663 | 1.4663 | 1.4663 | 0.19671 | 0.20983 | 0.1836 | 0.17048 | 0.14426 | 0.13114 | 1.4267 | 3 | 0.059585 | 0.059585 | 0.058344 | 1.0818 | 0.49935 | 0.10199 | 4.2082 | 0.81843 | 6.8655 | 1.0818 | 0.39745 | 0.10199 | 3.178 | 0.59034 | 6.0073 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.64 | 0.063 | 1 | 4.2 | 12.9 |  |  |  | 7.43 | 0.063 | 1 | 3.5 | 12.7 |  |  |  | 3.5 | 3.4 | 3.1 | [18 empty] | 5920 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 280 | 300 | 320 | 280 | 260 | 220 | 200 | 750 |  | 960 | 960 | 940 | 80 | 98 | 12 | 1490 | 305 | 400 | 40 | 39 | 6 | 540 | 110 | 175 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.7 | 20 | 16 | 38.9 | 58 | 308 | 13 | 0.308 |  | 5.99 | 8 | 0.066 | 5.95 | 8 |  | 5.9 | 8 | [8 empty] | 0.05 | [14 empty] | 0.05 | 1 | 0.33 |  | 0.048 | 0.032 | 1 | 0.38 |  | 0.052 | 1 | 0.5 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.143 | [9 empty] | 5.93 | 0.654 | 6 | 0.51 | 13 | 8.7 | 0.56458 |  | 5.96 | 0.498 | 5 | 0.54 | 13 | 8.7 | 0.56458 | 5.96 | 0.559 | 5 | 0.65 | 14 | 8.7 | 0.53889 |  |  |  | 0.028 | [9 empty] | 8.55 | 0.065 | 1 | 5 | 12.1 | 21 | 28 | 0.032 | 7.58 | 0.069 | 1 | 3 | 13.1 | 20 | 32 | 0.039 | 3.7 | 3.4 | 3 | [55 empty] | 9:00 | 0.51 | 8.7 | 29.2414 | 14.9131 | 5.93 | 13 | 13 | 1.1472 | 10 | 6 | 0.44458 | 9:00 | 0.54 | 8.7 | 29.2414 | 15.7903 | 5.96 | 13 | 13 | 1.2146 | 10 | 6 | 0.44458 | 9:00 | 0.65 | 8.7 | 31.0345 | 20.1724 | 5.96 | 14 | 13 | 1.5517 | 10 | 6 | 0.41889
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.62 | 19 | 17 | 40.9 | 63 | 319 | 13.1 | 0.31 |  | 5.92 | 8 | 0.061 | 5.91 | 7 |  | 5.9 | 8 | [8 empty] | 0.047 | [14 empty] | 0.043 | 1 | 0.21 |  | 0.044 | 0.033 | 1 | 0.2 |  | 0.049 | 1 | 0.3 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.81 | 0.532 | 5 | 0.47 | 13.1 | 8.6 | 0.55947 |  | 5.77 | 0.41 | 5 | 0.56 | 13.7 | 8.7 | 0.56458 | 5.85 | 0.556 | 5 | 0.49 | 14.7 | 8.8 | 0.5437 | [13 empty] | 8.09 | 0.067 | 1 | 4.3 | 12.4 |  |  |  | 7.59 | 0.071 | 1 | 3.5 | 13.6 |  |  |  | 4 | 3.2 | 3 | [55 empty] | 13:00 | 0.47 | 8.6 | 29.5814 | 13.9033 | 5.81 | 13.1 | 13 | 1.0695 | 10 | 6 | 0.43947 | 13:00 | 0.56 | 8.7 | 29.2414 | 16.3752 | 5.77 | 13.7 | 13 | 1.2596 | 10 | 6 | 0.44458 | 13:00 | 0.49 | 8.8 | 30.6818 | 15.0341 | 5.85 | 14.7 | 13 | 1.1565 | 10 | 6 | 0.4237
14:00 | [126 empty] | 293 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.64 | 20 | 18 | 36.6 | 58 | 340 | 13.4 | 0.292 |  | 5.96 | 10 | 0.058 | 5.95 | 10 |  | 5.9 | 10 | [8 empty] | 0.046 | [14 empty] | 0.032 | 1 | 0.22 |  | 0.045 | 0.028 | 1 | 0.2 |  | 0.04 | 1 | 0.28 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 8.05 | 0.064 | 1 | 4 | 12.3 |  |  |  | 7.61 | 0.068 | 1 | 3.4 | 13.4 |  |  |  | 4.2 | 3.2 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.63 | 20 | 19 | 44.9 | 64 | 291 | 13.5 | 0.32 |  | 5.99 | 8 | 0.062 | 5.97 | 8 |  | 5.92 | 8 | [8 empty] | 0.044 | [14 empty] | 0.04 | 1 | 0.12 |  | 0.048 | 0.039 | 1 | 0.17 |  | 0.046 | 1 | 0.2 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.161 | [9 empty] | 5.81 | 0.535 | 5 | 0.48 | 13 | 8.6 | 0.55947 |  | 5.85 | 0.464 | 5 | 0.49 | 13.3 | 8.6 | 0.55947 | 5.94 | 0.567 | 4 | 0.55 | 14.9 | 8.6 | 0.53407 |  |  |  | 0.03 | [9 empty] | 7.83 | 0.074 | 1 | 4.5 | 13 | 23 | 30 | 0.03 | 7.58 | 0.059 | 1 | 4.1 | 13.5 | 20 | 28 | 0.036 | 4.3 | 3.2 | 3 | [55 empty] | 21:00 | 0.48 | 8.6 | 29.5814 | 14.1991 | 5.81 | 13 | 13 | 1.0922 | 10 | 6 | 0.43947 | 21:00 | 0.49 | 8.6 | 29.5814 | 14.4949 | 5.85 | 13.3 | 13 | 1.115 | 10 | 6 | 0.43947 | 21:00 | 0.55 | 8.6 | 31.3953 | 17.2674 | 5.94 | 14.9 | 13 | 1.3283 | 10 | 6 | 0.41407
22:00 | [72 empty] | DOSE |  | TOTAL | 26.7 | 26.6 | 26.7 | 80 | 25.8 | 25.8 | 25.8 | 77.4 | 0 | 27.5688 | 0 | 42.5218 | 70.0906 | 2.8022 | TOTAL | 165.3754 | 7624.8904 | 0 | 2025 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.4536 | 4.3525 | 4.4536 | 0.54466 | 0.55778 | 0.53346 | 0.4958 | 0.39808 | 0.41035 | 4.2801 | 8 | 0.17615 | 0.17615 | 0.1761 | 3.2086 | 1.481 | 0.30249 | 12.4191 | 2.3644 | 22.0494 | 3.2086 | 1.2705 | 0.28608 | 9.4817 | 1.7098 | 17.817 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.67 | 20 | 17 | 42 | 60 | 323 | 13.4 | 0.311 |  | 5.86 | 9 | 0.066 | 5.84 | 9 |  | 5.8 | 9 | [8 empty] | 0.047 | [14 empty] | 0.04 | 1 | 0.16 |  | 0.05 | 0.034 | 1 | 0.21 |  | 0.048 | 1 | 0.21 | [22 empty] | AVERAGE | 8.9 | 8.8667 | 8.9 | 26.6667 | 8.6 | 8.6 | 8.6 | 25.8 |  | 9.1896 |  | 14.1739 | 23.3635 | 0.93408 | AVERAGE | 55.1251 | 2541.6301 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.4845 | 1.4508 | 1.4845 | 0.18155 | 0.18593 | 0.17782 | 0.16527 | 0.13269 | 0.13678 | 1.4267 | 2.6667 | 0.058715 | 0.058715 | 0.058701 | 1.0695 | 0.49368 | 0.10083 | 4.1397 | 0.78812 | 7.3498 | 1.0695 | 0.4235 | 0.095359 | 3.1606 | 0.56993 | 5.939 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.1 | 117 | 103 | 242.3 | 370 | 1895 | 79.1 | 1.865 | 0.304 | 35.78 | 50 | 0.371 | 35.59 | 49 | 0 | 35.32 | 50 | 0 | 23.54 | 2.382 | 21 | 1.99 | 51.4 | 34.9 | 2.2634 | 0.286 | 23.54 | 2.014 | 20 | 2.07 | 52.4 | 35 | 2.2685 | 23.73 | 2.111 | 18 | 2.16 | 57.5 | 35.1 | 2.17 | 0.255 | 6 | 1.38 | 0.058 | 0.281 | 0.197 | 6 | 1.46 | 0 | 0.287 | 6 | 1.75 | 0 | 47.71 | 0.394 | 6 | 25.8 | 74.9 | 44 | 58 | 0.062 | 45.23 | 0.387 | 6 | 21 | 78.8 | 40 | 60 | 0.075 | 23.2 | 19.9 | 18.2 |  |  | MINIMUM | 8.7 | 8.6 | 8.7 | 26 | 8.5 | 8.5 | 8.5 | 25.5 |  | 7.0142 |  | 13.1832 | 21.1766 | 0 | MINIMUM | 54.9182 | 2214 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.4163 | 1.3151 | 1.4163 | 0.16393 | 0.16393 | 0.16583 | 0.15949 | 0.12268 | 0.13114 | 1.4267 | 2 | 0.056355 | 0.056355 | 0.057554 | 1.0449 | 0.48233 | 0.098514 | 4.0805 | 0.75165 | 6.8655 | 1.0449 | 0.3839 | 0.082095 | 3.0919 | 0.51838 | 5.8025 |  | MIN | 0.47 | 8.6 | 29.5814 | 13.9033 | 5.81 | 13.1 | 13 | 1.0695 |  |  |  | MIN | 0.48 | 9 | 28.2667 | 13.568 | 5.96 | 12.4 | 13 | 1.0437 |  |  |  | MIN | 0.47 | 9 | 30 | 14.1 | 5.98 | 13.9 | 13 | 1.0846 |  |  |  | 1.0437
AVERAGE | 6.6833 | 19.5 | 17.1667 | 40.3833 | 61.6667 | 315.8333 | 13.1833 | 0.31083 | 0.152 | 5.9633 | 8.3333 | 0.061833 | 5.9317 | 8.1667 |  | 5.8867 | 8.3333 |  | 5.885 | 0.5955 | 5.25 | 0.4975 | 12.85 | 8.725 | 0.56585 | 0.047667 | 5.885 | 0.5035 | 5 | 0.5175 | 13.1 | 8.75 | 0.56713 | 5.9325 | 0.52775 | 4.5 | 0.54 | 14.375 | 8.775 | 0.5425 | 0.0425 | 1 | 0.23 | 0.029 | 0.046833 | 0.032833 | 1 | 0.24333 |  | 0.047833 | 1 | 0.29167 |  | 7.9517 | 0.065667 | 1 | 4.3 | 12.4833 | 22 | 29 | 0.031 | 7.5383 | 0.0645 | 1 | 3.5 | 13.1333 | 20 | 30 | 0.0375 | 3.8667 | 3.3167 | 3.0333 |  |  | MAXIMUM | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 |  | 10.8619 |  | 15.1762 | 26.0381 | 1.5264 | MAXIMUM | 55.4572 | 2828.42 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.571 | 1.571 | 0.19671 | 0.20983 | 0.18402 | 0.17048 | 0.14426 | 0.14426 | 1.4267 | 3 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.2082 | 0.81843 | 7.7236 | 1.0818 | 0.48916 | 0.10199 | 3.2117 | 0.60108 | 6.0073
MINIMUM | 6.62 | 18 | 16 | 36.6 | 58 | 291 | 12.7 | 0.292 | 0.143 | 5.86 | 7 | 0.058 | 5.84 | 7 |  | 5.8 | 7 |  | 5.81 | 0.532 | 5 | 0.47 | 12.3 | 8.6 | 0.55947 | 0.044 | 5.77 | 0.41 | 5 | 0.48 | 12.4 | 8.6 | 0.55947 | 5.85 | 0.429 | 4 | 0.47 | 13.9 | 8.6 | 0.53407 | 0.032 | 1 | 0.12 | 0.028 | 0.044 | 0.028 | 1 | 0.17 |  | 0.04 | 1 | 0.2 |  | 7.55 | 0.061 | 1 | 3.8 | 12.1 | 21 | 28 | 0.03 | 7.43 | 0.057 | 1 | 3 | 12.5 | 20 | 28 | 0.036 | 3.5 | 3.2 | 3 | [15 empty] | MIL/MIN |  | TOTAL | 17970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 840 | 860 | 850 | 870 | 830 | 770 | 620 | 640 | 2250 | 0 | 2870 | 2870 | 2870 | 240 | 294 | 36 | 4330 | 891 | 1300 | 120 | 126 | 17 | 1590 | 322 | 525
MAXIMUM | 6.84 | 20 | 19 | 44.9 | 67 | 340 | 13.5 | 0.324 | 0.161 | 6.06 | 10 | 0.066 | 5.97 | 10 |  | 5.92 | 10 |  | 5.99 | 0.661 | 6 | 0.53 | 13.1 | 9 | 0.57991 | 0.052 | 5.96 | 0.642 | 5 | 0.56 | 13.7 | 9 | 0.57991 | 5.98 | 0.567 | 5 | 0.65 | 14.9 | 9 | 0.55333 | 0.05 | 1 | 0.34 | 0.03 | 0.05 | 0.039 | 1 | 0.38 |  | 0.052 | 1 | 0.5 |  | 8.55 | 0.074 | 1 | 5 | 13 | 23 | 30 | 0.032 | 7.61 | 0.071 | 1 | 4.1 | 13.6 | 20 | 32 | 0.039 | 4.3 | 3.5 | 3.1 | [17 empty] | AVERAGE | 5990 | [9 empty] | 286.6667 | 280 | 286.6667 | 283.3333 | 290 | 276.6667 | 256.6667 | 206.6667 | 213.3333 | 750 |  | 956.6667 | 956.6667 | 956.6667 | 80 | 98 | 12 | 1443.3333 | 297 | 433.3333 | 40 | 42 | 5.6667 | 530 | 107.3333 | 175
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9272 |  | TOTAL AVG COAG ALK: |  |  |  | 8.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.661 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 5.9008 |  |  |  |  | 0.052 |  |  |  |  | 0.47 | [6 empty] | 0.052 | [16 empty] | Pump Station MIN |  | 3 | [17 empty] | MINIMUM | 5840 | [9 empty] | 280 | 260 | 280 | 250 | 250 | 250 | 250 | 200 | 200 | 750 |  | 940 | 940 | 940 | 80 | 98 | 12 | 1420 | 290 | 400 | 40 | 39 | 5 | 500 | 100 | 175
[90 empty] | MAXIMUM | 6210 | [9 empty] | 300 | 300 | 300 | 300 | 320 | 300 | 260 | 220 | 220 | 750 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1490 | 305 | 450 | 40 | 48 | 6 | 550 | 112 | 175
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.121 |  | TOTAL MGD: |  | 4.153 |  |  | FINISHED SOUTH 1 |  | START: | 23104040 |  | END: | 23108193 |  |  | Alum | 5061 |  | 6140 |  | 0 | [45 empty] | 0.48 | 9 | 28.2667 | 13.568 | 5.96 | 12.4 | 13 | 1.0437
[73 empty] | FINISHED 2 | 14.84 |  | TOTAL MGD: |  | 5.968 |  |  | FINISHED SOUTH 2 |  | START: | 40957832 |  | END: | 40963800 |  |  | Caustic | 3874 |  | 5277
[73 empty] | TOTAL RAW | 26.755 |  | TOTAL MGD: |  | 4.291 |  |  | FINISHED CONWAY |  | START: | 8708354 |  | END: | 8712645 |  |  | Hypochlorite | 10'/442 |  | 23'
[76 empty] | TOTAL MGD: |  | 10.549 |  |  | FINISHED PERRY |  | START: | 30397978 |  | END: | 30408527 |  |  | Phosphate | 2696
[76 empty] | TOTAL MGD: |  | 8.845 |  |  | RAW PLANT 1 |  | START: | 27930868 |  | END: | 27939713 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.84 |  |  | RAW PLANT 2 |  | START: | 27878305 |  | END: | 27887145 |  |  | Cal~Flo | 12.03 | 0 | 0 | 11.08 | 799.9 | 25
[76 empty] | TOTAL MGD: |  | 9.07 |  |  | RAW PLANT 3 |  | START: | 4191350 |  | END: | 4200420 |  |  | Zinc | 3207
[76 empty] | TOTAL MGD: |  | 1.528 |  |  | DECANT |  | START: | 1388202 |  | END: | 1389730 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 1.0625 |  |  | BLOW DOWN |  | START: | 8763.2368 |  | END: | 8764.2993 |  |  | NH3 | 12.5
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 1050 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2210 | Phosphate | 45
[90 empty] | Caustic 1 | 218 | Fluoride | 0
[90 empty] | Caustic 2 | 75 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23108193
[91 empty] | FINISHED SOUTH 2 |  | END: | 40963800
[91 empty] | FINISHED CONWAY |  | END: | 8712645
[91 empty] | FINISHED PERRY |  | END: | 30408527
[91 empty] | RAW PLANT 1 |  | END: | 27939713
[91 empty] | RAW PLANT 2 |  | END: | 27887145
[91 empty] | RAW PLANT 3 |  | END: | 4200420
[91 empty] | DECANT |  | END: | 1389730
[91 empty] | BLOW DOWN |  | END: | 8764.2993
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 12
DATE: | 2018-02-12 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-12 | [23 empty] | DATE: | 2018-02-12
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-12 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43143.0067 | 1,2,3 | 36 | 8.7 | 8.7 | 8.7 | 26.1 | 8.2 | 8.2 | 8.2 | 24.6 | 7,1 | 10.8619 | 1,2 | 15.1762 | 26.0381 | 1.525 | 43143.0067 | 55.4572 | 2582.4704 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5199 | 1.5199 | 1.5199 | 0.19671 | 0.20983 | 0.1836 | 0.17048 | 0.14426 | 0.13114 | 1.4267 | 3 | 0.061765 | 0.061765 | 0.060478 | 1.1214 | 0.51762 | 0.10572 | 4.3545 | 0.84837 | 7.1166 | 1.1214 | 0.41199 | 0.10572 | 3.2841 | 0.61194 | 6.2271 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.565 | 5 | 0.72 | 13.3 | 8.6 | 0.55947 |  | 5.97 | 0.645 | 6 | 0.52 | 13.4 | 8.6 | 0.55947 | 5.97 | 0.419 | 5 | 0.61 | 14.9 | 8.6 | 0.53407 | [13 empty] | 7.85 | 0.067 | 2 | 4.4 | 13 |  |  |  | 7.56 | 0.056 | 2 | 4 | 13.3 |  |  |  | 4.3 | 3.4 | 3.1 | [18 empty] | 5920 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 280 | 300 | 320 | 280 | 260 | 220 | 200 | 750 |  | 960 | 960 | 940 | 80 | 98 | 12 | 1490 | 305 | 400 | 40 | 39 | 6 | 540 | 110 | 175 |  | 1:00 | 0.72 | 8.6 | 29.5814 | 21.2986 | 5.96 | 13.3 | 13 | 1.6384 | 10 | 6 | 0.43947 | 1:00 | 0.52 | 8.6 | 29.5814 | 15.3823 | 5.97 | 13.4 | 13 | 1.1833 | 10 | 6 | 0.43947 | 1:00 | 0.61 | 8.6 | 31.3953 | 19.1512 | 5.97 | 14.9 | 13 | 1.4732 | 10 | 6 | 0.41407
2:00 | [72 empty] | 43143.3625 | 1,2,3 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.1008 | 1,2 | 13.3229 | 22.4237 | 1.1592 | 43143.3625 | 54.8764 | 2828.42 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.15846 | 0.15846 | 0.15846 | 0.15846 | 0.13945 | 0.13945 | 1.4267 | 2.5 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.1972 | 0.64186 | 6.8655 | 1.0818 | 0.50955 | 0.10199 | 3.1907 | 0.56888 | 6.0073 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.78 | 16 | 15 | 44.2 | 66 | 342 | 14.1 | 0.311 |  | 6.02 | 7 | 0.062 | 5.95 | 7 |  | 5.91 | 8 | [8 empty] | 0.054 | [14 empty] | 0.038 | 1 | 0.39 |  | 0.051 | 0.038 | 2 | 0.33 |  | 0.051 | 2 | 0.4 | [38 empty] | 6060 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 220 | 220 | 750 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1430 | 300 | 400 | 40 | 50 | 6 | 520 | 106 | 175 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43143.5985 | 1,2,3 | 30 | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 9.1008 | 1,2 | 13.3229 | 22.4237 | 0 | 43143.5985 | 49.9185 | 2336.5208 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6321 | 1.6321 | 1.6321 | 0.16044 | 0.16044 | 0.16044 | 0.16044 | 0.14262 | 0.14262 | 1.4267 | 0 | 0.059792 | 0.059792 | 0.059792 | 1.1034 | 0.50819 | 0.096324 | 4.1919 | 0.78462 | 8.7535 | 1.1034 | 0.38114 | 0.096324 | 3.1979 | 0.57174 | 5.8356 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.32 | 0.065 | 1 | 4.4 | 13.6 |  |  |  | 7.31 | 0.056 | 1 | 4 | 13.1 |  |  |  | 4.3 | 3.3 | 3.2 | [18 empty] | 4900 | [6 empty] | 0 | 0 | 0 | 275 | 275 | 275 | 225 | 225 | 225 | 225 | 200 | 200 | 750 |  | 850 | 850 | 850 | 72 | 88 | 10 | 1260 | 258 | 450 | 36 | 33 | 5 | 460 | 94 | 150 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.68 | 18 | 16 | 44 | 52 | 332 | 14 | 0.27 |  | 5.96 | 9 | 0.057 | 5.9 | 10 |  | 5.92 | 9 | [8 empty] | 0.048 | [14 empty] | 0.039 | 1 | 0.38 |  | 0.045 | 0.032 | 1 | 0.37 |  | 0.049 | 1 | 0.45 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.176 | [9 empty] | 6 | 0.549 | 5 | 0.75 | 13.5 | 9 | 0.57991 |  | 6.02 | 0.493 | 5 | 0.61 | 14 | 9 | 0.65066 | 6 | 0.581 | 5 | 0.69 | 15 | 9 | 0.38667 |  |  |  | 0.023 | [9 empty] | 7.46 | 0.064 | 1 | 4.7 | 12.9 | 23 | 45 | 0.026 | 7.33 | 0.067 | 1 | 3.7 | 14.1 | 24 | 41 | 0.025 | 4.3 | 3.4 | 4 | [55 empty] | 9:00 | 0.75 | 9 | 28.2667 | 21.2 | 6 | 13.5 | 13 | 1.6308 | 10 | 6 | 0.45991 | 9:00 | 0.61 | 9 | 28.2667 | 17.2427 | 6.02 | 14 | 15 | 1.1495 | 10 | 6.5 | 0.53066 | 9:00 | 0.69 | 9 | 30 | 20.7 | 6 | 15 | 8 | 2.5875 | 15 | 6 | 0.26667
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.7 | 19 | 16 | 39 | 61 | 295 | 13.8 | 0.267 |  | 6.06 | 9 | 0.072 | 6 | 9 |  | 5.98 | 8 | [8 empty] | 0.041 | [14 empty] | 0.043 | 1 | 0.37 |  | 0.044 | 0.033 | 1 | 0.36 |  | 0.048 | 1 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.05 | 0.48 | 4 | 0.63 | 13.5 | 8.9 | 0.64476 |  | 6.09 | 0.503 | 5 | 0.7 | 14.1 | 8.9 | 0.64476 | 6.05 | 0.46 | 4 | 0.89 | 15.3 | 9.1 | 0.45704 | [13 empty] | 7.58 | 0.058 | 1 | 5 | 12.9 |  |  |  | 7.53 | 0.061 | 1 | 4.5 | 14.1 |  |  |  | 4.4 | 3.6 | 4.3 | [55 empty] | 13:00 | 0.63 | 8.9 | 28.5843 | 18.0081 | 6.05 | 13.5 | 15 | 1.2005 | 10 | 6.5 | 0.52476 | 13:00 | 0.7 | 8.9 | 28.5843 | 20.009 | 6.09 | 14.1 | 15 | 1.3339 | 10 | 6.5 | 0.52476 | 13:00 | 0.89 | 9.1 | 29.6703 | 26.4066 | 6.05 | 15.3 | 10 | 2.6407 | 15 | 6.5 | 0.33704
14:00 | [126 empty] | 229 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.72 | 20 | 16 | 39.4 | 54 | 298 | 14 | 0.251 |  | 6 | 10 | 0.047 | 6.01 | 10 |  | 5.99 | 10 | [8 empty] | 0.04 | [14 empty] | 0.035 | 1 | 0.35 |  | 0.035 | 0.025 | 1 | 0.36 |  | 0.04 | 1 | 0.45 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.92 | 0.055 | 1 | 5 | 12.9 |  |  |  | 7.74 | 0.058 | 1 | 4.8 | 14.2 |  |  |  | 4.3 | 3.7 | 3.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.76 | 23 | 18 | 37.6 | 55 | 285 | 13.8 | 0.259 |  | 5.99 | 9 | 0.046 | 6.03 | 9 |  | 5.96 | 9 | [8 empty] | 0.04 | [14 empty] | 0.048 | 1 | 0.23 |  | 0.045 | 0.024 | 1 | 0.26 |  | 0.089 | 1 | 0.41 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.168 | [9 empty] | 6.09 | 0.664 | 4 | 0.55 | 13.9 | 8 | 0.5917 |  | 6.07 | 0.337 | 3 | 0.55 | 13.5 | 8 | 0.5917 | 6.08 | 0.559 | 3 | 0.56 | 15.1 | 8 | 0.4163 |  |  |  | 0.03 | [9 empty] | 7.7 | 0.06 | 1 | 3.8 | 13.5 | 20 | 30 | 0.03 | 7.53 | 0.064 | 1 | 3.5 | 13.7 | 22 | 33 | 0.029 | 4.3 | 3.6 | 3.7 | [55 empty] | 21:00 | 0.55 | 8 | 31.8 | 17.49 | 6.09 | 13.9 | 15 | 1.166 | 10 | 6.5 | 0.4717 | 21:00 | 0.55 | 8 | 31.8 | 17.49 | 6.07 | 13.5 | 15 | 1.166 | 10 | 6.5 | 0.4717 | 21:00 | 0.56 | 8 | 33.75 | 18.9 | 6.08 | 15.1 | 10 | 1.89 | 15 | 6.5 | 0.2963
22:00 | [72 empty] | DOSE |  | TOTAL | 25.7 | 25.7 | 25.7 | 77.1 | 24.2 | 24.2 | 24.2 | 72.6 | 0 | 29.0635 | 0 | 41.8219 | 70.8854 | 2.6842 | TOTAL | 160.2521 | 7747.4112 | 0 | 1950 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.7231 | 4.7231 | 4.7231 | 0.51562 | 0.52874 | 0.50251 | 0.48939 | 0.42632 | 0.41321 | 4.2801 | 5.5 | 0.18176 | 0.18176 | 0.18048 | 3.3067 | 1.5252 | 0.30404 | 12.7436 | 2.2749 | 22.7355 | 3.3067 | 1.3027 | 0.30404 | 9.6727 | 1.7526 | 18.07 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.71 | 22 | 18 | 32.6 | 52 | 253 | 13.8 | 0.283 |  | 5.92 | 9 | 0.05 | 5.9 | 9 |  | 5.88 | 9 | [8 empty] | 0.04 | [14 empty] | 0.033 | 1 | 0.24 |  | 0.044 | 0.023 | 1 | 0.35 |  | 0.073 | 1 | 0.44 | [22 empty] | AVERAGE | 8.5667 | 8.5667 | 8.5667 | 25.7 | 8.0667 | 8.0667 | 8.0667 | 24.2 |  | 9.6878 |  | 13.9406 | 23.6285 | 0.89472 | AVERAGE | 53.4174 | 2582.4704 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.5744 | 1.5744 | 1.5744 | 0.17187 | 0.17625 | 0.1675 | 0.16313 | 0.14211 | 0.13774 | 1.4267 | 1.8333 | 0.060588 | 0.060588 | 0.060159 | 1.1022 | 0.50839 | 0.10135 | 4.2479 | 0.75829 | 7.5785 | 1.1022 | 0.43422 | 0.10135 | 3.2242 | 0.58418 | 6.0233 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.35 | 118 | 99 | 236.8 | 340 | 1805 | 83.5 | 1.641 | 0.344 | 35.95 | 53 | 0.334 | 0 | 54 | 0 | 35.64 | 53 | 0 | 24.1 | 2.258 | 18 | 2.65 | 54.2 | 34.5 | 2.3758 | 0.263 | 24.15 | 1.978 | 19 | 2.38 | 55 | 34.5 | 2.4466 | 24.1 | 2.019 | 17 | 2.75 | 60.3 | 34.7 | 1.7941 | 0.236 | 6 | 1.96 | 0.053 | 0.264 | 0.175 | 7 | 2.03 | 0 | 0.35 | 7 | 2.65 | 0 | 45.83 | 0.369 | 7 | 27.3 | 78.8 | 43 | 75 | 0.056 | 45 | 0.362 | 7 | 24.5 | 82.5 | 46 | 74 | 0.054 | 25.9 | 21 | 22 |  |  | MINIMUM | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 |  | 9.1008 |  | 13.3229 | 22.4237 | 0 | MINIMUM | 49.9185 | 2336.5208 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.5199 | 1.5199 | 1.5199 | 0.15846 | 0.15846 | 0.15846 | 0.15846 | 0.13945 | 0.13114 | 1.4267 | 0 | 0.059792 | 0.059792 | 0.059792 | 1.0818 | 0.49935 | 0.096324 | 4.1919 | 0.64186 | 6.8655 | 1.0818 | 0.38114 | 0.096324 | 3.1907 | 0.56888 | 5.8356 |  | MIN | 0.55 | 8 | 31.8 | 17.49 | 6.09 | 13.9 | 15 | 1.166 |  |  |  | MIN | 0.61 | 9 | 28.2667 | 17.2427 | 6.02 | 14 | 15 | 1.1495 |  |  |  | MIN | 0.61 | 8.6 | 31.3953 | 19.1512 | 5.97 | 14.9 | 13 | 1.4732 |  |  |  | 1.1495
AVERAGE | 6.725 | 19.6667 | 16.5 | 39.4667 | 56.6667 | 300.8333 | 13.9167 | 0.2735 | 0.172 | 5.9917 | 8.8333 | 0.055667 |  | 9 |  | 5.94 | 8.8333 |  | 6.025 | 0.5645 | 4.5 | 0.6625 | 13.55 | 8.625 | 0.59396 | 0.043833 | 6.0375 | 0.4945 | 4.75 | 0.595 | 13.75 | 8.625 | 0.61165 | 6.025 | 0.50475 | 4.25 | 0.6875 | 15.075 | 8.675 | 0.44852 | 0.039333 | 1 | 0.32667 | 0.0265 | 0.044 | 0.029167 | 1.1667 | 0.33833 |  | 0.058333 | 1.1667 | 0.44167 |  | 7.6383 | 0.0615 | 1.1667 | 4.55 | 13.1333 | 21.5 | 37.5 | 0.028 | 7.5 | 0.060333 | 1.1667 | 4.0833 | 13.75 | 23 | 37 | 0.027 | 4.3167 | 3.5 | 3.6667 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.8619 |  | 15.1762 | 26.0381 | 1.525 | MAXIMUM | 55.4572 | 2828.42 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.6321 | 1.6321 | 1.6321 | 0.19671 | 0.20983 | 0.1836 | 0.17048 | 0.14426 | 0.14262 | 1.4267 | 3 | 0.061765 | 0.061765 | 0.060478 | 1.1214 | 0.51762 | 0.10572 | 4.3545 | 0.84837 | 8.7535 | 1.1214 | 0.50955 | 0.10572 | 3.2841 | 0.61194 | 6.2271
MINIMUM | 6.68 | 16 | 15 | 32.6 | 52 | 253 | 13.8 | 0.251 | 0.168 | 5.92 | 7 | 0.046 |  | 7 |  | 5.88 | 8 |  | 5.96 | 0.48 | 4 | 0.55 | 13.3 | 8 | 0.55947 | 0.04 | 5.97 | 0.337 | 3 | 0.52 | 13.4 | 8 | 0.55947 | 5.97 | 0.419 | 3 | 0.56 | 14.9 | 8 | 0.38667 | 0.033 | 1 | 0.23 | 0.023 | 0.035 | 0.023 | 1 | 0.26 |  | 0.04 | 1 | 0.4 |  | 7.32 | 0.055 | 1 | 3.8 | 12.9 | 20 | 30 | 0.026 | 7.31 | 0.056 | 1 | 3.5 | 13.1 | 22 | 33 | 0.025 | 4.3 | 3.3 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 16880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855 | 855 | 855 | 775 | 795 | 755 | 735 | 640 | 620 | 2250 | 0 | 2780 | 2780 | 2760 | 232 | 284 | 34 | 4180 | 863 | 1250 | 116 | 122 | 17 | 1520 | 310 | 500
MAXIMUM | 6.78 | 23 | 18 | 44.2 | 66 | 342 | 14.1 | 0.311 | 0.176 | 6.06 | 10 | 0.072 |  | 10 |  | 5.99 | 10 |  | 6.09 | 0.664 | 5 | 0.75 | 13.9 | 9 | 0.64476 | 0.054 | 6.09 | 0.645 | 6 | 0.7 | 14.1 | 9 | 0.65066 | 6.08 | 0.581 | 5 | 0.89 | 15.3 | 9.1 | 0.53407 | 0.048 | 1 | 0.39 | 0.03 | 0.051 | 0.038 | 2 | 0.37 |  | 0.089 | 2 | 0.5 |  | 7.92 | 0.067 | 2 | 5 | 13.6 | 23 | 45 | 0.03 | 7.74 | 0.067 | 2 | 4.8 | 14.2 | 24 | 41 | 0.029 | 4.4 | 3.7 | 4.3 | [17 empty] | AVERAGE | 5626.6667 | [9 empty] | 285 | 285 | 285 | 258.3333 | 265 | 251.6667 | 245 | 213.3333 | 206.6667 | 750 |  | 926.6667 | 926.6667 | 920 | 77.3333 | 94.6667 | 11.3333 | 1393.3333 | 287.6667 | 416.6667 | 38.6667 | 40.6667 | 5.6667 | 506.6667 | 103.3333 | 166.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9658 |  | TOTAL AVG COAG ALK: |  |  |  | 8.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.664 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.52 | [5 empty] | 6.0292 |  |  |  |  | 0.089 |  |  |  |  | 0.52 | [6 empty] | 0.089 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 4900 | [9 empty] | 275 | 275 | 275 | 225 | 225 | 225 | 225 | 200 | 200 | 750 |  | 850 | 850 | 850 | 72 | 88 | 10 | 1260 | 258 | 400 | 36 | 33 | 5 | 460 | 94 | 150
[90 empty] | MAXIMUM | 6060 | [9 empty] | 300 | 300 | 300 | 300 | 320 | 280 | 260 | 220 | 220 | 750 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1490 | 305 | 450 | 40 | 50 | 6 | 540 | 110 | 175
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.416 |  | TOTAL MGD: |  | 3.995 |  |  | FINISHED SOUTH 1 |  | START: | 23108193 |  | END: | 23112188 |  |  | Alum | 6805 |  | 5620 |  | 0 | [45 empty] | 0.61 | 9 | 28.2667 | 17.2427 | 6.02 | 14 | 15 | 1.1495
[73 empty] | FINISHED 2 | 14.404 |  | TOTAL MGD: |  | 5.421 |  |  | FINISHED SOUTH 2 |  | START: | 40963800 |  | END: | 40969221 |  |  | Caustic | 3793 |  | 5181
[73 empty] | TOTAL RAW | 26.213 |  | TOTAL MGD: |  | 3.953 |  |  | FINISHED CONWAY |  | START: | 8712645 |  | END: | 8716598 |  |  | Hypochlorite | 14'/397 |  | 5.5'
[76 empty] | TOTAL MGD: |  | 10.451 |  |  | FINISHED PERRY |  | START: | 30408527 |  | END: | 30418978 |  |  | Phosphate | 2697
[76 empty] | TOTAL MGD: |  | 8.684 |  |  | RAW PLANT 1 |  | START: | 27939713 |  | END: | 27948397 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.663 |  |  | RAW PLANT 2 |  | START: | 27887145 |  | END: | 27895808 |  |  | Cal~Flo | 11.08 | 10.15 | 17.91 | 17.58 | 1060.92 | 25
[76 empty] | TOTAL MGD: |  | 8.866 |  |  | RAW PLANT 3 |  | START: | 4200420 |  | END: | 4209286 |  |  | Zinc | 3212
[76 empty] | TOTAL MGD: |  | 1.319 |  |  | DECANT |  | START: | 1389730 |  | END: | 1391049 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.94134 |  |  | BLOW DOWN |  | START: | 8764.2993 |  | END: | 8765.2407 |  |  | NH3 | 12.32
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 575
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2178 | Phosphate | 44
[90 empty] | Caustic 1 | 155 | Fluoride | 0
[90 empty] | Caustic 2 | 74 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 1
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23112188
[91 empty] | FINISHED SOUTH 2 |  | END: | 40969221
[91 empty] | FINISHED CONWAY |  | END: | 8716598
[91 empty] | FINISHED PERRY |  | END: | 30418978
[91 empty] | RAW PLANT 1 |  | END: | 27948397
[91 empty] | RAW PLANT 2 |  | END: | 27895808
[91 empty] | RAW PLANT 3 |  | END: | 4209286
[91 empty] | DECANT |  | END: | 1391049
[91 empty] | BLOW DOWN |  | END: | 8765.2407
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 13
DATE: | 2018-02-13 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 5 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 20 | [23 empty] | 6:00 - 18:00 |  | 5 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 5 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 20 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 20
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-13 | [23 empty] | DATE: | 2018-02-13
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-13 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43144.0087 | 2,3,5 | 32 | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 10.7194 | 1,2 | 16.645 | 27.3643 | 2.1456 | 43144.0087 | 60.3097 | 2213.546 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5431 | 1.4244 | 1.6618 | 0.15688 | 0.14262 | 0.17114 | 0.17114 | 0.14262 | 0.11409 | 1.4267 | 2 | 0.060496 | 0.060496 | 0.059089 | 1.1034 | 0.49664 | 0.096324 | 4.1869 | 0.7907 | 7.7808 | 1.1034 | 0.38114 | 0.096324 | 3.187 | 0.57782 | 5.8356 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.495 | 4 | 0.58 | 13.7 | 8 | 0.52881 |  | 6 | 0.349 | 4 | 0.55 | 13.6 | 8 | 0.52881 | 6.05 | 0.363 | 4 | 0.5 | 15.3 | 8 | 0.4163 | [13 empty] | 7.96 | 0.056 | 2 | 3.8 | 13.2 |  |  |  | 7.65 | 0.063 | 2 | 3.6 | 13.4 |  |  |  | 4.1 | 3.8 | 2.7 | [18 empty] | 5920 | [6 empty] | 0 | 0 | 0 | 260 | 240 | 280 | 220 | 200 | 240 | 240 | 200 | 160 | 750 |  | 860 | 860 | 840 | 72 | 86 | 10 | 1260 | 260 | 400 | 36 | 33 | 5 | 450 | 95 | 150 |  | 1:00 | 0.58 | 8 | 31.8 | 18.444 | 5.96 | 13.7 | 13 | 1.4188 | 10 | 6 | 0.40881 | 1:00 | 0.55 | 8 | 31.8 | 17.49 | 6 | 13.6 | 13 | 1.3454 | 10 | 6 | 0.40881 | 1:00 | 0.5 | 8 | 33.75 | 16.875 | 6.05 | 15.3 | 10 | 1.6875 | 15 | 6.5 | 0.2963
2:00 | [72 empty] | 43144.3422 | 2,3,5 | 32 | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 10.7194 | 1,2 | 16.645 | 27.3643 | 1.571 | 43144.3422 | 60.1059 | 2643.9578 | 0 | 625 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6618 | 1.6618 | 1.6618 | 0.17827 | 0.15688 | 0.16044 | 0.16044 | 0.14262 | 0.14262 | 1.4267 | 1.5 | 0.059792 | 0.059792 | 0.059792 | 1.1034 | 0.49664 | 0.096324 | 4.2015 | 0.77245 | 7.2945 | 1.1034 | 0.38114 | 0.11559 | 3.187 | 0.55957 | 5.8356 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.78 | 19 | 15 | 33 | 58 | 249 | 14.1 | 0.266 |  | 5.98 | 6 | 0.053 | 5.92 | 6 |  | 5.88 | 7 | [8 empty] | 0.043 | [14 empty] | 0.029 | 2 | 0.44 |  | 0.044 | 0.022 | 2 | 0.36 |  | 0.062 | 2 | 0.45 | [38 empty] | 5900 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 280 | 250 | 220 | 225 | 225 | 200 | 200 | 750 |  | 850 | 850 | 850 | 72 | 86 | 10 | 1250 | 254 | 375 | 36 | 33 | 6 | 450 | 92 | 150 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43144.8556 | 2,3,5 | 35 | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 | 7,1 | 10.7194 | 1,2 | 16.645 | 27.3643 | 0 | 43144.8556 | 59.9875 | 2520.983 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4288 | 1.3189 | 1.5387 | 0.1592 | 0.1592 | 0.17247 | 0.17247 | 0.14593 | 0.092867 | 1.4267 | 2 | 0.059922 | 0.059271 | 0.059922 | 0.11352 | 0.50263 | 0.10703 | 4.2009 | 0.78845 | 6.7542 | 1.1352 | 0.39568 | 0.10703 | 3.2285 | 0.59134 | 5.4034 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.33 | 0.058 | 2 | 3.5 | 13.4 |  |  |  | 7.46 | 0.061 | 1 | 3.6 | 13.1 |  |  |  | 3.8 | 4.1 | 3.4 | [18 empty] | 6330 | [6 empty] | 0 | 0 | 0 | 260 | 240 | 280 | 240 | 240 | 260 | 260 | 220 | 140 | 750 |  | 920 | 910 | 920 | 8 | 94 | 12 | 1380 | 280 | 375 | 40 | 37 | 6 | 520 | 105 | 150 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.78 | 20 | 14 | 32.1 | 52 | 254 | 14.4 | 0.256 |  | 5.94 | 8 | 0.051 | 5.9 | 8 |  | 5.89 | 8 | [8 empty] | 0.041 | [14 empty] | 0.028 | 2 | 0.41 |  | 0.04 | 0.02 | 2 | 0.33 |  | 0.059 | 2 | 0.44 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.125 | [9 empty] | 5.95 | 0.352 | 4 | 0.61 | 14 | 8 | 0.52881 |  | 5.99 | 0.337 | 4 | 0.56 | 14 | 8 | 0.52881 | 5.99 | 0.479 | 5 | 0.54 | 15.2 | 8 | 0.35704 |  |  |  | 0.031 | [9 empty] | 7.28 | 0.054 | 2 | 3.6 | 13.4 | 24 | 38 | 0.038 | 7.61 | 0.065 | 2 | 4 | 13.9 | 22 | 36 | 0.033 | 3.9 | 3.6 | 3.4 | [55 empty] | 9:00 | 0.61 | 8 | 31.8 | 19.398 | 5.95 | 14 | 13 | 1.4922 | 10 | 6 | 0.40881 | 9:00 | 0.56 | 8 | 31.8 | 17.808 | 5.99 | 14 | 13 | 1.3698 | 10 | 6 | 0.40881 | 9:00 | 0.54 | 8 | 33.75 | 18.225 | 5.99 | 15.2 | 8 | 2.2781 | 15 | 6 | 0.23704
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.69 | 19 | 14 | 29.3 | 48 | 230 | 14.2 | 0.259 |  | 5.93 | 8 | 0.047 | 5.94 | 9 |  | 5.93 | 8 | [8 empty] | 0.037 | [14 empty] | 0.027 | 1 | 0.28 |  | 0.038 | 0.03 | 1 | 0.42 |  | 0.057 | 1 | 0.17 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.97 | 0.42 | 4 | 0.54 | 14.6 | 8.4 | 0.54925 |  | 5.95 | 0.332 | 3 | 0.51 | 14.7 | 8.4 | 0.54925 | 5.99 | 0.454 | 4 | 0.56 | 15.1 | 8.6 | 0.37481 | [13 empty] | 7.54 | 0.05 | 1 | 4.1 | 13.4 |  |  |  | 7.4 | 0.058 | 1 | 4.3 | 13.8 |  |  |  | 3.7 | 3.6 | 3.3 | [55 empty] | 13:00 | 0.54 | 8.4 | 30.2857 | 16.3543 | 5.97 | 14.6 | 13 | 1.258 | 10 | 6 | 0.42925 | 13:00 | 0.51 | 8.4 | 30.2857 | 15.4457 | 5.95 | 14.7 | 13 | 1.1881 | 10 | 6 | 0.42925 | 13:00 | 0.56 | 8.6 | 31.3953 | 17.5814 | 5.99 | 15.1 | 8 | 2.1977 | 15 | 6 | 0.25481
14:00 | [126 empty] | 209 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.73 | 20 | 14 | 28.2 | 42 | 238 | 14.4 | 0.246 |  | 5.97 | 8 | 0.051 | 5.98 | 8 |  | 5.92 | 8 | [8 empty] | 0.041 | [14 empty] | 0.029 | 1 | 0.25 |  | 0.04 | 0.031 | 1 | 0.38 |  | 0.054 | 1 | 0.2 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.8 | 0.049 | 1 | 4.4 | 13.4 |  |  |  | 7.42 | 0.056 | 1 | 4.4 | 13.8 |  |  |  | 3.6 | 3.6 | 3.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.73 | 20 | 16 | 31.3 | 49 | 249 | 13.4 | 0.256 |  | 5.91 | 6 | 0.047 | 5.96 | 6 |  | 5.9 | 7 | [8 empty] | 0.038 | [14 empty] | 0.027 | 1 | 0.29 |  | 0.044 | 0.029 | 1 | 0.41 |  | 0.054 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.14 | [9 empty] | 6.02 | 0.413 | 4 | 0.56 | 13.2 | 8.6 | 0.62708 |  | 6.04 | 0.332 | 4 | 0.59 | 12.9 | 8.6 | 0.62708 | 6.02 | 0.477 | 4 | 0.53 | 14.5 | 8.6 | 0.59778 |  |  |  | 0.037 | [9 empty] | 7.45 | 0.063 | 2 | 3.5 | 13.1 | 21 | 34 | 0.031 | 7.24 | 0.053 | 1 | 3.4 | 15.3 | 20 | 31 | 0.039 | 3.5 | 3.7 | 3.1 | [55 empty] | 21:00 | 0.56 | 8.6 | 29.5814 | 16.5656 | 6.02 | 13.2 | 15 | 1.1044 | 10 | 6.5 | 0.50708 | 21:00 | 0.59 | 8.6 | 29.5814 | 17.453 | 6.04 | 12.9 | 15 | 1.1635 | 10 | 6.5 | 0.50708 | 21:00 | 0.53 | 8.6 | 31.3953 | 16.6395 | 6.02 | 14.5 | 15 | 1.1093 | 10 | 6.5 | 0.47778
22:00 | [72 empty] | DOSE |  | TOTAL | 24.6 | 24.6 | 24.6 | 73.8 | 23.1 | 23.1 | 23.1 | 69.3 | 0 | 32.1581 | 0 | 49.9349 | 82.093 | 3.7166 | TOTAL | 180.4031 | 7378.4868 | 0 | 1925 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.6337 | 4.4051 | 4.8623 | 0.49435 | 0.4587 | 0.50405 | 0.50405 | 0.43117 | 0.34958 | 4.2801 | 5.5 | 0.18021 | 0.17956 | 0.1788 | 2.3204 | 1.4959 | 0.29968 | 12.5892 | 2.3516 | 21.8296 | 3.3421 | 1.158 | 0.31894 | 9.6026 | 1.7287 | 17.0746 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.69 | 19 | 17 | 27.3 | 51 | 225 | 13.4 | 0.279 |  | 5.92 | 8 | 0.05 | 5.91 | 8 |  | 5.91 | 8 | [8 empty] | 0.04 | [14 empty] | 0.024 | 1 | 0.24 |  | 0.045 | 0.023 | 1 | 0.3 |  | 0.043 | 1 | 0.41 | [22 empty] | AVERAGE | 8.2 | 8.2 | 8.2 | 24.6 | 7.7 | 7.7 | 7.7 | 23.1 |  | 10.7194 |  | 16.645 | 27.3643 | 1.2389 | AVERAGE | 60.1344 | 2459.4956 |  | 641.6667 | #N/A | #N/A | #N/A |  |  |  | 1.5446 | 1.4684 | 1.6208 | 0.16478 | 0.1529 | 0.16802 | 0.16802 | 0.14372 | 0.11653 | 1.4267 | 1.8333 | 0.06007 | 0.059853 | 0.059601 | 0.77347 | 0.49863 | 0.099892 | 4.1964 | 0.78387 | 7.2765 | 1.114 | 0.38599 | 0.10631 | 3.2009 | 0.57624 | 5.6915 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.4 | 117 | 90 | 181.2 | 300 | 1445 | 83.9 | 1.562 | 0.265 | 35.65 | 44 | 0.299 | 35.61 | 45 | 0 | 35.43 | 46 | 0 | 23.9 | 1.68 | 16 | 2.29 | 55.5 | 33 | 2.2339 | 0.24 | 23.98 | 1.35 | 15 | 2.21 | 55.2 | 33 | 2.2339 | 24.05 | 1.773 | 17 | 2.13 | 60.1 | 33.2 | 1.7459 | 0 | 8 | 1.91 | 0.068 | 0.251 | 0.155 | 8 | 2.2 | 0 | 0.329 | 8 | 2.13 | 0 | 45.36 | 0.33 | 10 | 22.9 | 79.9 | 45 | 72 | 0.069 | 44.78 | 0.356 | 8 | 23.3 | 83.3 | 42 | 67 | 0.072 | 22.6 | 22.4 | 19.1 |  |  | MINIMUM | 8 | 8 | 8 | 24 | 7.5 | 7.5 | 7.5 | 22.5 |  | 10.7194 |  | 16.645 | 27.3643 | 0 | MINIMUM | 59.9875 | 2213.546 |  | 625 | #N/A | #N/A | #N/A |  |  |  | 1.4288 | 1.3189 | 1.5387 | 0.15688 | 0.14262 | 0.16044 | 0.16044 | 0.14262 | 0.092867 | 1.4267 | 1.5 | 0.059792 | 0.059271 | 0.059089 | 0.11352 | 0.49664 | 0.096324 | 4.1869 | 0.77245 | 6.7542 | 1.1034 | 0.38114 | 0.096324 | 3.187 | 0.55957 | 5.4034 |  | MIN | 0.56 | 8.6 | 29.5814 | 16.5656 | 6.02 | 13.2 | 15 | 1.1044 |  |  |  | MIN | 0.59 | 8.6 | 29.5814 | 17.453 | 6.04 | 12.9 | 15 | 1.1635 |  |  |  | MIN | 0.53 | 8.6 | 31.3953 | 16.6395 | 6.02 | 14.5 | 15 | 1.1093 |  |  |  | 1.1044
AVERAGE | 6.7333 | 19.5 | 15 | 30.2 | 50 | 240.8333 | 13.9833 | 0.26033 | 0.1325 | 5.9417 | 7.3333 | 0.049833 | 5.935 | 7.5 |  | 5.905 | 7.6667 |  | 5.975 | 0.42 | 4 | 0.5725 | 13.875 | 8.25 | 0.55848 | 0.04 | 5.995 | 0.3375 | 3.75 | 0.5525 | 13.8 | 8.25 | 0.55848 | 6.0125 | 0.44325 | 4.25 | 0.5325 | 15.025 | 8.3 | 0.43648 |  | 1.3333 | 0.31833 | 0.034 | 0.041833 | 0.025833 | 1.3333 | 0.36667 |  | 0.054833 | 1.3333 | 0.355 |  | 7.56 | 0.055 | 1.6667 | 3.8167 | 13.3167 | 22.5 | 36 | 0.0345 | 7.4633 | 0.059333 | 1.3333 | 3.8833 | 13.8833 | 21 | 33.5 | 0.036 | 3.7667 | 3.7333 | 3.1833 |  |  | MAXIMUM | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 |  | 10.7194 |  | 16.645 | 27.3643 | 2.1456 | MAXIMUM | 60.3097 | 2643.9578 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.6618 | 1.6618 | 1.6618 | 0.17827 | 0.1592 | 0.17247 | 0.17247 | 0.14593 | 0.14262 | 1.4267 | 2 | 0.060496 | 0.060496 | 0.059922 | 1.1034 | 0.50263 | 0.10703 | 4.2015 | 0.7907 | 7.7808 | 1.1352 | 0.39568 | 0.11559 | 3.2285 | 0.59134 | 5.8356
MINIMUM | 6.69 | 19 | 14 | 27.3 | 42 | 225 | 13.4 | 0.246 | 0.125 | 5.91 | 6 | 0.047 | 5.9 | 6 |  | 5.88 | 7 |  | 5.95 | 0.352 | 4 | 0.54 | 13.2 | 8 | 0.52881 | 0.037 | 5.95 | 0.332 | 3 | 0.51 | 12.9 | 8 | 0.52881 | 5.99 | 0.363 | 4 | 0.5 | 14.5 | 8 | 0.35704 |  | 1 | 0.24 | 0.031 | 0.038 | 0.02 | 1 | 0.3 |  | 0.043 | 1 | 0.17 |  | 7.28 | 0.049 | 1 | 3.5 | 13.1 | 21 | 34 | 0.031 | 7.24 | 0.053 | 1 | 3.4 | 13.1 | 20 | 31 | 0.033 | 3.5 | 3.6 | 2.7 | [15 empty] | MIL/MIN |  | TOTAL | 18150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 760 | 840 | 710 | 660 | 725 | 725 | 620 | 500 | 2250 | 0 | 2630 | 2620 | 2610 | 152 | 266 | 32 | 3890 | 794 | 1150 | 112 | 103 | 17 | 1420 | 292 | 450
MAXIMUM | 6.78 | 20 | 17 | 33 | 58 | 254 | 14.4 | 0.279 | 0.14 | 5.98 | 8 | 0.053 | 5.98 | 9 |  | 5.93 | 8 |  | 6.02 | 0.495 | 4 | 0.61 | 14.6 | 8.6 | 0.62708 | 0.043 | 6.04 | 0.349 | 4 | 0.59 | 14.7 | 8.6 | 0.62708 | 6.05 | 0.479 | 5 | 0.56 | 15.3 | 8.6 | 0.59778 |  | 2 | 0.44 | 0.037 | 0.045 | 0.031 | 2 | 0.42 |  | 0.062 | 2 | 0.46 |  | 7.96 | 0.063 | 2 | 4.4 | 13.4 | 24 | 38 | 0.038 | 7.65 | 0.065 | 2 | 4.4 | 15.3 | 22 | 36 | 0.039 | 4.1 | 4.1 | 3.4 | [17 empty] | AVERAGE | 6050 | [9 empty] | 266.6667 | 253.3333 | 280 | 236.6667 | 220 | 241.6667 | 241.6667 | 206.6667 | 166.6667 | 750 |  | 876.6667 | 873.3333 | 870 | 50.6667 | 88.6667 | 10.6667 | 1296.6667 | 264.6667 | 383.3333 | 37.3333 | 34.3333 | 5.6667 | 473.3333 | 97.3333 | 150
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9272 |  | TOTAL AVG COAG ALK: |  |  |  | 7.5 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.495 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.5 | [5 empty] | 5.9942 |  |  |  |  | 0.062 |  |  |  |  | 0.5 | [23 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 5900 | [9 empty] | 260 | 240 | 280 | 220 | 200 | 225 | 225 | 200 | 140 | 750 |  | 850 | 850 | 840 | 8 | 86 | 10 | 1250 | 254 | 375 | 36 | 33 | 5 | 450 | 92 | 150
[90 empty] | MAXIMUM | 6330 | [9 empty] | 280 | 280 | 280 | 250 | 240 | 260 | 260 | 220 | 200 | 750 |  | 920 | 910 | 920 | 72 | 94 | 12 | 1380 | 280 | 400 | 40 | 37 | 6 | 520 | 105 | 150
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 8.403 |  | TOTAL MGD: |  | 3.029 |  |  | FINISHED SOUTH 1 |  | START: | 23112188 |  | END: | 23115217 |  |  | Alum | 6196 |  | 7430 |  | 0 | [45 empty] | 0.56 | 8.6 | 29.5814 | 16.5656 | 6.02 | 13.2 | 15 | 1.1044
[73 empty] | FINISHED 2 | 15.165 |  | TOTAL MGD: |  | 5.374 |  |  | FINISHED SOUTH 2 |  | START: | 40969221 |  | END: | 40974595 |  |  | Caustic | 3654 |  | 5075
[73 empty] | TOTAL RAW | 25.197 |  | TOTAL MGD: |  | 3.979 |  |  | FINISHED CONWAY |  | START: | 8716598 |  | END: | 8720577 |  |  | Hypochlorite | 13' |  | 16.5'
[76 empty] | TOTAL MGD: |  | 11.186 |  |  | FINISHED PERRY |  | START: | 30418978 |  | END: | 30430164 |  |  | Phosphate | 2704
[76 empty] | TOTAL MGD: |  | 8.363 |  |  | RAW PLANT 1 |  | START: | 27948397 |  | END: | 27956760 |  |  | Fluoride | 1600 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.343 |  |  | RAW PLANT 2 |  | START: | 27895808 |  | END: | 27904151 |  |  | Cal~Flo | 17.58 | 0 | 0 | 16.4 | 993.56 | 25
[76 empty] | TOTAL MGD: |  | 8.491 |  |  | RAW PLANT 3 |  | START: | 4209286 |  | END: | 4217777 |  |  | Zinc | 3220
[76 empty] | TOTAL MGD: |  | 1.61 |  |  | DECANT |  | START: | 1391049 |  | END: | 1392659 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.7636 |  |  | BLOW DOWN |  | START: | 8765.2407 |  | END: | 8766.0043 |  |  | NH3 | 12.14
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2192 | Phosphate | 0
[90 empty] | Caustic 1 | 142 | Fluoride | 0
[90 empty] | Caustic 2 | 67 | Zinc | 5
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23115217
[91 empty] | FINISHED SOUTH 2 |  | END: | 40974595
[91 empty] | FINISHED CONWAY |  | END: | 8720577
[91 empty] | FINISHED PERRY |  | END: | 30430164
[91 empty] | RAW PLANT 1 |  | END: | 27956760
[91 empty] | RAW PLANT 2 |  | END: | 27904151
[91 empty] | RAW PLANT 3 |  | END: | 4217777
[91 empty] | DECANT |  | END: | 1392659
[91 empty] | BLOW DOWN |  | END: | 8766.0043
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 14
DATE: | 2018-02-14 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-14 | [23 empty] | DATE: | 2018-02-14
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-14 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43145.0002 | 2,3,5 | 35 | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 | 7,1 | 10.7194 | 1,2 | 16.645 | 27.3643 | 1.1779 | 43145.0002 | 59.9875 | 2520.983 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4288 | 1.3189 | 1.5387 | 0.1592 | 0.1592 | 0.17247 | 0.17247 | 0.14593 | 0.092867 | 1.4267 | 2 | 0.059922 | 0.059271 | 0.059922 | 0.11352 | 0.50263 | 0.10703 | 4.2009 | 0.78845 | 6.7542 | 1.1352 | 0.39568 | 0.10703 | 3.2285 | 0.59134 | 5.4034 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.92 | 0.598 | 4 | 0.51 | 12.9 | 9 | 0.57991 |  | 5.98 | 0.599 | 3 | 0.55 | 12.8 | 9 | 0.57991 | 5.97 | 0.358 | 3 | 0.47 | 14.3 | 9 | 0.55333 | [13 empty] | 7.2 | 0.051 | 1 | 3.6 | 12.9 |  |  |  | 7.2 | 0.047 | 1 | 3.2 | 12.8 |  |  |  | 3.3 | 3.4 | 3.3 | [18 empty] | 6330 | [6 empty] | 0 | 0 | 0 | 260 | 240 | 280 | 240 | 240 | 260 | 260 | 220 | 140 | 750 |  | 920 | 910 | 920 | 8 | 94 | 12 | 1380 | 280 | 375 | 40 | 37 | 6 | 520 | 105 | 150 |  | 1:00 | 0.51 | 9 | 28.2667 | 14.416 | 5.92 | 12.9 | 13 | 1.1089 | 10 | 6 | 0.45991 | 1:00 | 0.55 | 9 | 28.2667 | 15.5467 | 5.98 | 12.8 | 13 | 1.1959 | 10 | 6 | 0.45991 | 1:00 | 0.47 | 9 | 30 | 14.1 | 5.97 | 14.3 | 13 | 1.0846 | 10 | 6 | 0.43333
2:00 | [72 empty] | 43145.3433 | 2,3,5 | 34 | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 | 0,1 | 5.1883 | 1,2 | 18.7934 | 23.9818 | 0.99936 | 43145.3433 | 59.9875 | 2889.9074 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4838 | 1.2639 | 1.5112 | 0.16583 | 0.1592 | 0.13267 | 0.16583 | 0.12603 | 0.0995 | 1.4267 | 1 | 0.061876 | 0.061876 | 0.059922 | 1.1069 | 0.50263 | 0.10703 | 4.2115 | 0.77155 | 7.2045 | 1.1352 | 0.39568 | 0.10703 | 2.8835 | 0.56318 | 7.2045 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.68 | 16 | 18 | 28.1 | 56 | 221 | 13.7 | 0.269 |  | 5.99 | 7 | 0.049 | 5.95 | 6 |  | 5.88 | 7 | [8 empty] | 0.042 | [14 empty] | 0.027 | 1 | 0.4 |  | 0.038 | 0.021 | 1 | 0.42 |  | 0.047 | 1 | 0.49 | [38 empty] | 6330 | [6 empty] | 0 | 0 | 0 | 270 | 230 | 275 | 250 | 240 | 200 | 250 | 190 | 150 | 750 |  | 950 | 950 | 920 | 78 | 94 | 12 | 1350 | 274 | 400 | 40 | 37 | 6 | 425 | 100 | 200 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43145.8423 | 2,3,5 | 34 | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 | 0,1 | 5.1883 | 1,2 | 18.7934 | 23.9818 | 1.6032 | 43145.8423 | 59.8927 | 3197.3444 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5112 | 1.3738 | 1.3738 | 0.16583 | 0.15257 | 0.14925 | 0.15257 | 0.1194 | 0.0995 | 1.0653 | 1.5 | 0.061876 | 0.061876 | 0.059922 | 1.1352 | 0.50263 | 0.10703 | 4.3522 | 0.77437 | 7.2045 | 1.0785 | 0.39568 | 0.10703 | 3.3059 | 0.53502 | 7.2045 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.29 | 0.05 | 1 | 3.4 | 13.1 |  |  |  | 7.26 | 0.048 | 1 | 3.2 | 12.8 |  |  |  | 3.3 | 3.3 | 3.1 | [18 empty] | 6320 | [6 empty] | 0 | 0 | 0 | 275 | 250 | 250 | 250 | 230 | 225 | 230 | 180 | 150 | 560 |  | 950 | 950 | 920 | 80 | 94 | 12 | 1400 | 275 | 400 | 38 | 37 | 6 | 500 | 95 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.67 | 22 | 20 | 29.2 | 55 | 227 | 12.9 | 0.282 |  | 6.01 | 9 | 0.048 | 5.96 | 9 |  | 5.9 | 9 | [8 empty] | 0.049 | [14 empty] | 0.023 | 1 | 0.4 |  | 0.045 | 0.021 | 1 | 0.4 |  | 0.047 | 1 | 0.43 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.11 | [9 empty] | 5.98 | 0.482 | 4 | 0.82 | 12.5 | 8.6 | 0.55947 |  | 6.06 | 0.49 | 4 | 0.59 | 12.5 | 8.6 | 0.62708 | 6 | 0.409 | 4 | 0.56 | 14 | 8.6 | 0.53407 |  |  |  | 0.029 | [9 empty] | 7.6 | 0.056 | 2 | 3.7 | 12.9 | 23 | 40 | 0.032 | 7.65 | 0.053 | 2 | 3.8 | 12.8 | 22 | 42 | 0.027 | 3.2 | 3.2 | 3 | [55 empty] | 9:00 | 0.82 | 8.6 | 29.5814 | 24.2567 | 5.98 | 12.5 | 13 | 1.8659 | 10 | 6 | 0.43947 | 9:00 | 0.59 | 8.6 | 29.5814 | 17.453 | 6.06 | 12.5 | 15 | 1.1635 | 10 | 6.5 | 0.50708 | 9:00 | 0.56 | 8.6 | 31.3953 | 17.5814 | 6 | 14 | 13 | 1.3524 | 10 | 6 | 0.41407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.68 | 22 | 19 | 26.8 | 58 | 220 | 13 | 0.285 |  | 6 | 9 | 0.051 | 5.89 | 9 |  | 5.93 | 9 | [8 empty] | 0.048 | [14 empty] | 0.026 | 1 | 0.49 |  | 0.044 | 0.023 | 1 | 0.4 |  | 0.049 | 1 | 0.46 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.446 | 4 | 0.7 | 12.6 | 8.6 | 0.55947 |  | 6.06 | 0.439 | 5 | 0.58 | 12.6 | 8.6 | 0.62708 | 6.03 | 0.426 | 5 | 0.55 | 14.1 | 8.6 | 0.59778 | [13 empty] | 7.4 | 0.059 | 1 | 3.6 | 12.4 |  |  |  | 7.45 | 0.063 | 1 | 3.6 | 13.2 |  |  |  | 3.1 | 3.2 | 3 | [55 empty] | 13:00 | 0.7 | 8.6 | 29.5814 | 20.707 | 6 | 12.6 | 13 | 1.5928 | 10 | 6 | 0.43947 | 13:00 | 0.58 | 8.6 | 29.5814 | 17.1572 | 6.06 | 12.6 | 15 | 1.1438 | 10 | 6.5 | 0.50708 | 13:00 | 0.55 | 8.6 | 31.3953 | 17.2674 | 6.03 | 14.1 | 15 | 1.1512 | 10 | 6.5 | 0.47778
14:00 | [126 empty] | 243 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.68 | 22 | 19 | 27.3 | 56 | 215 | 13.2 | 0.276 |  | 6 | 9 | 0.065 | 6.06 | 9 |  | 6 | 9 | [8 empty] | 0.035 | [14 empty] | 0.025 | 1 | 0.39 |  | 0.035 | 0.024 | 1 | 0.39 |  | 0.05 | 1 | 0.43 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.83 | 0.056 | 1 | 4.4 | 13.1 |  |  |  | 7.91 | 0.06 | 1 | 4.2 | 13 |  |  |  | 2.9 | 3.3 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.25 | 22 | 18 | 26.6 | 48 | 207 | 13.4 | 0.285 |  | 5.77 | 11 | 0.056 | 5.89 | 10 |  | 5.8 | 11 | [8 empty] | ..047 | [14 empty] | 0.031 | 1 | 0.37 |  | 0.044 | 0.02 | 1 | 0.35 |  | 0.049 | 1 | 0.39 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.119 | [9 empty] | 5.86 | 0.292 | 4 | 0.75 | 13.4 | 8.6 | 0.55947 |  | 5.82 | 0.431 | 5 | 0.84 | 13 | 8.6 | 0.55947 | 5.81 | 0.359 | 4 | 0.63 | 14.5 | 8.6 | 0.53407 |  |  |  | 0.032 | [9 empty] | 7.42 | 0.059 | 1 | 3.9 | 12.9 | 22 | 39 | 0.036 | 7.19 | 0.062 | 1 | 3.8 | 13.1 | 22 | 38 | 0.034 | 2.9 | 3.3 | 2.9 | [55 empty] | 21:00 | 0.75 | 8.6 | 29.5814 | 22.186 | 5.86 | 13.4 | 13 | 1.7066 | 10 | 6 | 0.43947 | 21:00 | 0.84 | 8.6 | 29.5814 | 24.8484 | 5.82 | 13 | 13 | 1.9114 | 10 | 6 | 0.43947 | 21:00 | 0.63 | 8.6 | 31.3953 | 19.7791 | 5.81 | 14.5 | 13 | 1.5215 | 10 | 6 | 0.41407
22:00 | [72 empty] | DOSE |  | TOTAL | 25.8 | 25.8 | 25.8 | 77.4 | 24.3 | 24.3 | 24.3 | 72.9 | 0 | 21.096 | 0 | 54.2318 | 75.3278 | 3.7804 | TOTAL | 179.8677 | 8608.2348 | 0 | 1950 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.4238 | 3.9567 | 4.4238 | 0.49087 | 0.47097 | 0.45438 | 0.49087 | 0.39137 | 0.29187 | 3.9186 | 4.5 | 0.18368 | 0.18302 | 0.17977 | 2.3556 | 1.5079 | 0.32108 | 12.7646 | 2.3344 | 21.1632 | 3.3489 | 1.1871 | 0.32108 | 9.4179 | 1.6895 | 19.8123 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.7 | 23 | 19 | 25.5 | 54 | 203 | 13.4 | 0.292 |  | 6.12 | 11 | 0.067 | 6.12 | 11 |  | 6.07 | 11 | [8 empty] | 0.047 | [14 empty] | 0.055 | 1 | 0.35 |  | 0.037 | 0.02 | 1 | 0.39 |  | 0.05 | 1 | 0.46 | [22 empty] | AVERAGE | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 |  | 7.032 |  | 18.0773 | 25.1093 | 1.2601 | AVERAGE | 59.9559 | 2869.4116 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.4746 | 1.3189 | 1.4746 | 0.16362 | 0.15699 | 0.15146 | 0.16362 | 0.13046 | 0.097289 | 1.3062 | 1.5 | 0.061225 | 0.061008 | 0.059922 | 0.7852 | 0.50263 | 0.10703 | 4.2549 | 0.77812 | 7.0544 | 1.1163 | 0.39568 | 0.10703 | 3.1393 | 0.56318 | 6.6041 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.66 | 127 | 113 | 163.5 | 327 | 1293 | 79.6 | 1.689 | 0.229 | 35.89 | 56 | 0.336 | 35.87 | 54 | 0 | 35.58 | 56 | 0 | 23.76 | 1.818 | 16 | 2.78 | 51.4 | 34.8 | 2.2583 | 0.221 | 23.92 | 1.959 | 17 | 2.56 | 50.9 | 34.8 | 2.3935 | 23.81 | 1.552 | 16 | 2.21 | 56.9 | 34.8 | 2.2193 | 0.187 | 6 | 2.4 | 0.061 | 0.243 | 0.129 | 6 | 2.35 | 0 | 0.292 | 6 | 2.66 | 0 | 44.74 | 0.331 | 7 | 22.6 | 77.3 | 45 | 79 | 0.068 | 44.66 | 0.333 | 7 | 21.8 | 77.7 | 44 | 80 | 0.061 | 18.7 | 19.7 | 18.1 |  |  | MINIMUM | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 |  | 5.1883 |  | 16.645 | 23.9818 | 0.99936 | MINIMUM | 59.8927 | 2520.983 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.4288 | 1.2639 | 1.3738 | 0.1592 | 0.15257 | 0.13267 | 0.15257 | 0.1194 | 0.092867 | 1.0653 | 1 | 0.059922 | 0.059271 | 0.059922 | 0.11352 | 0.50263 | 0.10703 | 4.2009 | 0.77155 | 6.7542 | 1.0785 | 0.39568 | 0.10703 | 2.8835 | 0.53502 | 5.4034 |  | MIN | 0.51 | 9 | 28.2667 | 14.416 | 5.92 | 12.9 | 13 | 1.1089 |  |  |  | MIN | 0.58 | 8.6 | 29.5814 | 17.1572 | 6.06 | 12.6 | 15 | 1.1438 |  |  |  | MIN | 0.47 | 9 | 30 | 14.1 | 5.97 | 14.3 | 13 | 1.0846 |  |  |  | 1.0846
AVERAGE | 6.61 | 21.1667 | 18.8333 | 27.25 | 54.5 | 215.5 | 13.2667 | 0.2815 | 0.1145 | 5.9817 | 9.3333 | 0.056 | 5.9783 | 9 |  | 5.93 | 9.3333 |  | 5.94 | 0.4545 | 4 | 0.695 | 12.85 | 8.7 | 0.56458 | 0.0442 | 5.98 | 0.48975 | 4.25 | 0.64 | 12.725 | 8.7 | 0.59838 | 5.9525 | 0.388 | 4 | 0.5525 | 14.225 | 8.7 | 0.55481 | 0.031167 | 1 | 0.4 | 0.0305 | 0.0405 | 0.0215 | 1 | 0.39167 |  | 0.048667 | 1 | 0.44333 |  | 7.4567 | 0.055167 | 1.1667 | 3.7667 | 12.8833 | 22.5 | 39.5 | 0.034 | 7.4433 | 0.0555 | 1.1667 | 3.6333 | 12.95 | 22 | 40 | 0.0305 | 3.1167 | 3.2833 | 3.0167 |  |  | MAXIMUM | 8.6 | 8.6 | 8.6 | 25.8 | 8.1 | 8.1 | 8.1 | 24.3 |  | 10.7194 |  | 18.7934 | 27.3643 | 1.6032 | MAXIMUM | 59.9875 | 3197.3444 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.5112 | 1.3738 | 1.5387 | 0.16583 | 0.1592 | 0.17247 | 0.17247 | 0.14593 | 0.0995 | 1.4267 | 2 | 0.061876 | 0.061876 | 0.059922 | 1.1352 | 0.50263 | 0.10703 | 4.3522 | 0.78845 | 7.2045 | 1.1352 | 0.39568 | 0.10703 | 3.3059 | 0.59134 | 7.2045
MINIMUM | 6.25 | 16 | 18 | 25.5 | 48 | 203 | 12.9 | 0.269 | 0.11 | 5.77 | 7 | 0.048 | 5.89 | 6 |  | 5.8 | 7 |  | 5.86 | 0.292 | 4 | 0.51 | 12.5 | 8.6 | 0.55947 | 0.035 | 5.82 | 0.431 | 3 | 0.55 | 12.5 | 8.6 | 0.55947 | 5.81 | 0.358 | 3 | 0.47 | 14 | 8.6 | 0.53407 | 0.023 | 1 | 0.35 | 0.029 | 0.035 | 0.02 | 1 | 0.35 |  | 0.047 | 1 | 0.39 |  | 7.2 | 0.05 | 1 | 3.4 | 12.4 | 22 | 39 | 0.032 | 7.19 | 0.047 | 1 | 3.2 | 12.8 | 22 | 38 | 0.027 | 2.9 | 3.2 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 18980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 720 | 805 | 740 | 710 | 685 | 740 | 590 | 440 | 2060 | 0 | 2820 | 2810 | 2760 | 166 | 282 | 36 | 4130 | 829 | 1175 | 118 | 111 | 18 | 1445 | 300 | 550
MAXIMUM | 6.7 | 23 | 20 | 29.2 | 58 | 227 | 13.7 | 0.292 | 0.119 | 6.12 | 11 | 0.067 | 6.12 | 11 |  | 6.07 | 11 |  | 6 | 0.598 | 4 | 0.82 | 13.4 | 9 | 0.57991 | 0.049 | 6.06 | 0.599 | 5 | 0.84 | 13 | 9 | 0.62708 | 6.03 | 0.426 | 5 | 0.63 | 14.5 | 9 | 0.59778 | 0.055 | 1 | 0.49 | 0.032 | 0.045 | 0.024 | 1 | 0.42 |  | 0.05 | 1 | 0.49 |  | 7.83 | 0.059 | 2 | 4.4 | 13.1 | 23 | 40 | 0.036 | 7.91 | 0.063 | 2 | 4.2 | 13.2 | 22 | 42 | 0.034 | 3.3 | 3.4 | 3.3 | [17 empty] | AVERAGE | 6326.6667 | [9 empty] | 268.3333 | 240 | 268.3333 | 246.6667 | 236.6667 | 228.3333 | 246.6667 | 196.6667 | 146.6667 | 686.6667 |  | 940 | 936.6667 | 920 | 55.3333 | 94 | 12 | 1376.6667 | 276.3333 | 391.6667 | 39.3333 | 37 | 6 | 481.6667 | 100 | 183.3333
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9633 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.599 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 5.9575 |  |  |  |  | 0.055 |  |  |  |  | 0.47 | [6 empty] | 0.055 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 6320 | [9 empty] | 260 | 230 | 250 | 240 | 230 | 200 | 230 | 180 | 140 | 560 |  | 920 | 910 | 920 | 8 | 94 | 12 | 1350 | 274 | 375 | 38 | 37 | 6 | 425 | 95 | 150
[90 empty] | MAXIMUM | 6330 | [9 empty] | 275 | 250 | 280 | 250 | 240 | 260 | 260 | 220 | 150 | 750 |  | 950 | 950 | 920 | 80 | 94 | 12 | 1400 | 280 | 400 | 40 | 37 | 6 | 520 | 105 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.525 |  | TOTAL MGD: |  | 3.74 |  |  | FINISHED SOUTH 1 |  | START: | 23115217 |  | END: | 23118957 |  |  | Alum | 7560 |  | 9198 |  | 0 | [45 empty] | 0.47 | 9 | 30 | 14.1 | 5.97 | 14.3 | 13 | 1.0846
[73 empty] | FINISHED 2 | 14.557 |  | TOTAL MGD: |  | 5.785 |  |  | FINISHED SOUTH 2 |  | START: | 40974595 |  | END: | 40980380 |  |  | Caustic | 7064 |  | 5063
[73 empty] | TOTAL RAW | 26.105 |  | TOTAL MGD: |  | 3.662 |  |  | FINISHED CONWAY |  | START: | 8720577 |  | END: | 8724239 |  |  | Hypochlorite | 11.75 |  | 27
[76 empty] | TOTAL MGD: |  | 10.895 |  |  | FINISHED PERRY |  | START: | 30430164 |  | END: | 30441059 |  |  | Phosphate | 2526
[76 empty] | TOTAL MGD: |  | 8.676 |  |  | RAW PLANT 1 |  | START: | 27956760 |  | END: | 27965436 |  |  | Fluoride | 1600 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.662 |  |  | RAW PLANT 2 |  | START: | 27904151 |  | END: | 27912813 |  |  | Cal~Flo | 16.4 | 0 | 0 | 14.63 | 1490.34 | 25
[76 empty] | TOTAL MGD: |  | 8.767 |  |  | RAW PLANT 3 |  | START: | 4217777 |  | END: | 4226544 |  |  | Zinc | 3200
[76 empty] | TOTAL MGD: |  | 1.488 |  |  | DECANT |  | START: | 1392659 |  | END: | 1394147 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.63359 |  |  | BLOW DOWN |  | START: | 8766.0043 |  | END: | 8766.6379 |  |  | NH3 | 11.88
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 375
[90 empty] | BI-SULFITE | 900 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2365 | Phosphate | 45
[90 empty] | Caustic 1 | 156 | Fluoride | 0
[90 empty] | Caustic 2 | 87 | Zinc | 6
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23118957
[91 empty] | FINISHED SOUTH 2 |  | END: | 40980380
[91 empty] | FINISHED CONWAY |  | END: | 8724239
[91 empty] | FINISHED PERRY |  | END: | 30441059
[91 empty] | RAW PLANT 1 |  | END: | 27965436
[91 empty] | RAW PLANT 2 |  | END: | 27912813
[91 empty] | RAW PLANT 3 |  | END: | 4226544
[91 empty] | DECANT |  | END: | 1394147
[91 empty] | BLOW DOWN |  | END: | 8766.6379
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 15
DATE: | 2018-02-15 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [33 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-15 | [23 empty] | DATE: | 2018-02-15
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-15 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43146.0417 | 2,3,5 | 39 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | ,1 | 5.1883 | 1,2 | 18.7502 | 23.9386 | 0.81216 | 43146.0417 | 60.6719 | 3320.3192 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4925 | 1.3616 | 1.4663 | 0.1648 | 0.15846 | 0.1648 | 0.1648 | 0.13311 | 0.11409 | 1.4267 | 1 | 0.060827 | 0.060827 | 0.060827 | 1.0818 | 0.49935 | 0.10199 | 4.3701 | 0.76476 | 7.2431 | 1.1359 | 0.39745 | 0.10199 | 3.308 | 0.56351 | 8.4788 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.13 | 0.387 | 4 | 0.62 | 13.4 | 9 | 0.65066 |  | 6.18 | 0.444 | 5 | 0.68 | 13.1 | 9 | 0.65066 | 6.16 | 0.432 | 5 | 0.59 | 14.5 | 9 | 0.62 | [13 empty] | 7.85 | 0.06 | 1 | 3.4 | 13.1 |  |  |  | 8.01 | 0.069 | 1 | 3.5 | 13 |  |  |  | 3.2 | 3.6 | 4.1 | [18 empty] | 6700 | [6 empty] | 0 | 0 | 0 | 285 | 260 | 280 | 260 | 250 | 260 | 260 | 210 | 180 | 750 |  | 980 | 980 | 980 | 80 | 98 | 12 | 1500 | 285 | 422 | 42 | 39 | 6 | 540 | 105 | 247 |  | 1:00 | 0.62 | 9 | 28.2667 | 17.5253 | 6.13 | 13.4 | 15 | 1.1684 | 10 | 6.5 | 0.53066 | 1:00 | 0.68 | 9 | 28.2667 | 19.2213 | 6.18 | 13.1 | 15 | 1.2814 | 10 | 6.5 | 0.53066 | 1:00 | 0.59 | 9 | 30 | 17.7 | 6.16 | 14.5 | 15 | 1.18 | 10 | 6.5 | 0.5
2:00 | [72 empty] | 43146.344 | 2,3,5 | 39 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 8.2469 | 1,2 | 16.6896 | 24.9365 | 0.81216 | 43146.344 | 60.6719 | 3320.3192 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6234 | 1.571 | 1.571 | 0.1648 | 0.15846 | 0.15846 | 0.15846 | 0.12677 | 0.12994 | 1.4267 | 1 | 0.058965 | 0.058965 | 0.058965 | 1.0953 | 0.49935 | 0.10199 | 4.5042 | 0.80501 | 6.7968 | 1.0818 | 0.39745 | 0.10199 | 3.2007 | 0.56351 | 7.7923 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.72 | 22 | 18 | 26.5 | 51 | 212 | 13.3 | 0.26 |  | 6.03 | 10 | 0.054 | 6.04 | 10 |  | 6.05 | 11 | [8 empty] | 0.042 | [14 empty] | 0.046 | 1 | 0.35 |  | 0.035 | 0.021 | 1 | 0.34 |  | 0.049 | 1 | 0.41 | [38 empty] | 6700 | [6 empty] | 0 | 0 | 0 | 310 | 300 | 300 | 260 | 250 | 250 | 250 | 200 | 205 | 750 |  | 950 | 950 | 950 | 81 | 98 | 12 | 1550 | 300 | 396 | 40 | 39 | 6 | 520 | 105 | 227 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43146.8603 | 2,3,5 | 39 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | ,1 | 5.1883 | 1,2 | 18.7502 | 23.9386 | 1.5474 | 43146.8603 | 60.4908 | 3750.731 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.2045 | 1.571 | 1.5187 | 0.1648 | 0.1648 | 0.14579 | 0.15846 | 0.11409 | 0.08874 | 0.43752 | 3 | 0.060827 | 0.060827 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.0749 | 0.71109 | 6.7968 | 1.0818 | 0.39745 | 0.10199 | 3.308 | 0.50984 | 7.7923 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.65 | 0.056 | 1 | 3.3 | 13.1 |  |  |  | 7.81 | 0.067 | 1 | 3.4 | 12.9 |  |  |  | 3.1 | 3.6 | 3.5 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 230 | 300 | 290 | 260 | 260 | 230 | 250 | 180 | 140 | 230 |  | 980 | 980 | 970 | 80 | 98 | 12 | 1390 | 265 | 396 | 40 | 39 | 6 | 540 | 95 | 227 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.69 | 22 | 18 | 26.6 | 60 | 222 | 13.4 | 0.296 |  | 5.89 | 10 | 0.056 | 5.89 | 10 |  | 5.93 | 10 | [8 empty] | 0.047 | [14 empty] | 0.04 | 1 | 0.36 |  | 0.046 | 0.021 | 1 | 0.36 |  | 0.045 | 1 | 0.39 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.103 | [9 empty] | 6.07 | 0.337 | 5 | 0.6 | 13.2 | 9 | 0.65066 |  | 6.15 | 0.479 | 5 | 0.63 | 13 | 9 | 0.65066 | 6.14 | 0.415 | 4 | 0.59 | 14.5 | 9 | 0.62 |  |  |  | 0.007 | [9 empty] | 7.69 | 0.057 | 2 | 4.6 | 13.2 | 25 | 45 | 0.019 | 7.81 | 0.074 | 2 | 3.9 | 12.9 | 25 | 42 | 0.011 | 2.9 | 3.2 | 2.8 | [55 empty] | 9:00 | 0.6 | 9 | 28.2667 | 16.96 | 6.07 | 13.2 | 15 | 1.1307 | 10 | 6.5 | 0.53066 | 9:00 | 0.63 | 9 | 28.2667 | 17.808 | 6.15 | 13 | 15 | 1.1872 | 10 | 6.5 | 0.53066 | 9:00 | 0.59 | 9 | 30 | 17.7 | 6.14 | 14.5 | 15 | 1.18 | 10 | 6.5 | 0.5
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.64 | 22 | 19 | 26.8 | 55 | 220 | 13.7 | 0.288 |  | 6 | 10 | 0.059 | 5.96 | 10 |  | 5.9 | 10 | [8 empty] | 0.044 | [14 empty] | 0.039 | 1 | 0.33 |  | 0.045 | 0.03 | 1 | 0.33 |  | 0.044 | 1 | 0.36 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.298 | 5 | 0.6 | 13.4 | 9 | 0.65066 |  | 6.09 | 0.31 | 5 | 0.71 | 13.2 | 9 | 0.65066 | 6.1 | 0.373 | 5 | 0.73 | 14.6 | 9 | 0.62 | [13 empty] | 7.96 | 0.059 | 1 | 5 | 13.9 |  |  |  | 7.85 | 0.073 | 1 | 4.1 | 14 |  |  |  | 3.5 | 3.2 | 2.5 | [55 empty] | 13:00 | 0.6 | 9 | 28.2667 | 16.96 | 6.1 | 13.4 | 15 | 1.1307 | 10 | 6.5 | 0.53066 | 13:00 | 0.71 | 9 | 28.2667 | 20.0693 | 6.09 | 13.2 | 15 | 1.338 | 10 | 6.5 | 0.53066 | 13:00 | 0.73 | 9 | 30 | 21.9 | 6.1 | 14.6 | 15 | 1.46 | 10 | 6.5 | 0.5
14:00 | [126 empty] | 241 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.73 | 22 | 20 | 27 | 63 | 218 | 13.9 | 0.286 |  | 6.02 | 10 | 0.04 | 5.96 | 10 |  | 5.9 | 10 | [8 empty] | 0.033 | [14 empty] | 0.035 | 1 | 0.4 |  | 0.033 | 0.034 | 1 | 0.4 |  | 0.044 | 1 | 0.39 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.4 | 0.061 | 1 | 5 | 13.5 |  |  |  | 7.39 | 0.069 | 1 | 4 | 13 |  |  |  | 3.9 | 3.2 | 2.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.72 | 21 | 19 | 28.7 | 57 | 225 | 14.2 | 0.293 |  | 5.95 | 10 | 0.053 | 6.01 | 10 |  | 6.07 | 11 | [8 empty] | 0.047 | [14 empty] | 0.049 | 1 | 0.53 |  | 0.049 | 0.024 | 1 | 0.55 |  | 0.045 | 1 | 0.45 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.111 | [9 empty] | 6.11 | 0.336 | 4 | 0.76 | 14.3 | 9 | 0.65066 |  | 6.09 | 0.342 | 5 | 0.78 | 14 | 9 | 0.65066 | 6.1 | 0.361 | 4 | 0.59 | 15.5 | 9 | 0.45333 |  |  |  | 0.013 | [9 empty] | 7.45 | 0.069 | 1 | 4.8 | 13.5 | 23 | 41 | 0.021 | 7.53 | 0.059 | 1 | 4.1 | 13.7 | 23 | 42 | 0.016 | 4.2 | 3.4 | 2.9 | [55 empty] | 21:00 | 0.76 | 9 | 28.2667 | 21.4827 | 6.11 | 14.3 | 15 | 1.4322 | 10 | 6.5 | 0.53066 | 21:00 | 0.78 | 9 | 28.2667 | 22.048 | 6.09 | 14 | 15 | 1.4699 | 10 | 6.5 | 0.53066 | 21:00 | 0.59 | 9 | 30 | 17.7 | 6.1 | 15.5 | 10 | 1.77 | 15 | 6.5 | 0.33333
22:00 | [72 empty] | DOSE |  | TOTAL | 27 | 27 | 27 | 81 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 18.6235 | 0 | 54.1901 | 72.8136 | 3.1717 | TOTAL | 181.8346 | 10391.3694 | 0 | 1950 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.3203 | 4.5036 | 4.556 | 0.49441 | 0.48173 | 0.46905 | 0.48173 | 0.37397 | 0.33277 | 3.2909 | 5 | 0.18062 | 0.18062 | 0.18 | 3.259 | 1.4981 | 0.30597 | 12.9492 | 2.2809 | 20.8367 | 3.2995 | 1.1923 | 0.30597 | 9.8168 | 1.6369 | 24.0634 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.72 | 22 | 20 | 26.8 | 60 | 214 | 14.4 | 0.3 |  | 5.94 | 11 | 0.054 | 6.03 | 11 |  | 6.07 | 12 | [8 empty] | 0.045 | [14 empty] | 0.037 | 1 | 0.51 |  | 0.045 | 0.021 | 1 | 0.55 |  | 0.047 | 1 | 0.44 | [22 empty] | AVERAGE | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 6.2078 |  | 18.0634 | 24.2712 | 1.0572 | AVERAGE | 60.6115 | 3463.7898 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.4401 | 1.5012 | 1.5187 | 0.1648 | 0.16058 | 0.15635 | 0.16058 | 0.12466 | 0.11092 | 1.097 | 1.6667 | 0.060206 | 0.060206 | 0.059999 | 1.0863 | 0.49935 | 0.10199 | 4.3164 | 0.76029 | 6.9456 | 1.0998 | 0.39745 | 0.10199 | 3.2723 | 0.54562 | 8.0211 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.22 | 131 | 114 | 162.4 | 346 | 1311 | 82.9 | 1.723 | 0.214 | 35.83 | 61 | 0.316 | 35.89 | 61 | 0 | 35.92 | 64 | 0 | 24.41 | 1.358 | 18 | 2.58 | 54.3 | 36 | 2.6026 | 0.258 | 24.51 | 1.575 | 20 | 2.8 | 53.3 | 36 | 2.6026 | 24.5 | 1.581 | 18 | 2.5 | 59.1 | 36 | 2.3133 | 0.246 | 6 | 2.48 | 0.02 | 0.253 | 0.151 | 6 | 2.53 | 0 | 0.274 | 6 | 2.44 | 0 | 46 | 0.362 | 7 | 26.1 | 80.3 | 48 | 86 | 0.04 | 46.4 | 0.411 | 7 | 23 | 79.5 | 48 | 84 | 0.027 | 20.8 | 20.2 | 18.3 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 5.1883 |  | 16.6896 | 23.9386 | 0.81216 | MINIMUM | 60.4908 | 3320.3192 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.2045 | 1.3616 | 1.4663 | 0.1648 | 0.15846 | 0.14579 | 0.15846 | 0.11409 | 0.08874 | 0.43752 | 1 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.0749 | 0.71109 | 6.7968 | 1.0818 | 0.39745 | 0.10199 | 3.2007 | 0.50984 | 7.7923 |  | MIN | 0.6 | 9 | 28.2667 | 16.96 | 6.07 | 13.2 | 15 | 1.1307 |  |  |  | MIN | 0.63 | 9 | 28.2667 | 17.808 | 6.15 | 13 | 15 | 1.1872 |  |  |  | MIN | 0.59 | 9 | 30 | 17.7 | 6.16 | 14.5 | 15 | 1.18 |  |  |  | 1.1307
AVERAGE | 6.7033 | 21.8333 | 19 | 27.0667 | 57.6667 | 218.5 | 13.8167 | 0.28717 | 0.107 | 5.9717 | 10.1667 | 0.052667 | 5.9817 | 10.1667 |  | 5.9867 | 10.6667 |  | 6.1025 | 0.3395 | 4.5 | 0.645 | 13.575 | 9 | 0.65066 | 0.043 | 6.1275 | 0.39375 | 5 | 0.7 | 13.325 | 9 | 0.65066 | 6.125 | 0.39525 | 4.5 | 0.625 | 14.775 | 9 | 0.57833 | 0.041 | 1 | 0.41333 | 0.01 | 0.042167 | 0.025167 | 1 | 0.42167 |  | 0.045667 | 1 | 0.40667 |  | 7.6667 | 0.060333 | 1.1667 | 4.35 | 13.3833 | 24 | 43 | 0.02 | 7.7333 | 0.0685 | 1.1667 | 3.8333 | 13.25 | 24 | 42 | 0.0135 | 3.4667 | 3.3667 | 3.05 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 8.2469 |  | 18.7502 | 24.9365 | 1.5474 | MAXIMUM | 60.6719 | 3750.731 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.6234 | 1.571 | 1.571 | 0.1648 | 0.1648 | 0.1648 | 0.1648 | 0.13311 | 0.12994 | 1.4267 | 3 | 0.060827 | 0.060827 | 0.060827 | 1.0953 | 0.49935 | 0.10199 | 4.5042 | 0.80501 | 7.2431 | 1.1359 | 0.39745 | 0.10199 | 3.308 | 0.56351 | 8.4788
MINIMUM | 6.64 | 21 | 18 | 26.5 | 51 | 212 | 13.3 | 0.26 | 0.103 | 5.89 | 10 | 0.04 | 5.89 | 10 |  | 5.9 | 10 |  | 6.07 | 0.298 | 4 | 0.6 | 13.2 | 9 | 0.65066 | 0.033 | 6.09 | 0.31 | 5 | 0.63 | 13 | 9 | 0.65066 | 6.1 | 0.361 | 4 | 0.59 | 14.5 | 9 | 0.45333 | 0.035 | 1 | 0.33 | 0.007 | 0.033 | 0.021 | 1 | 0.33 |  | 0.044 | 1 | 0.36 |  | 7.4 | 0.056 | 1 | 3.3 | 13.1 | 23 | 41 | 0.019 | 7.39 | 0.059 | 1 | 3.4 | 12.9 | 23 | 42 | 0.011 | 2.9 | 3.2 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 20080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825 | 860 | 870 | 780 | 760 | 740 | 760 | 590 | 525 | 1730 | 0 | 2910 | 2910 | 2900 | 241 | 294 | 36 | 4440 | 850 | 1214 | 122 | 117 | 18 | 1600 | 305 | 701
MAXIMUM | 6.73 | 22 | 20 | 28.7 | 63 | 225 | 14.4 | 0.3 | 0.111 | 6.03 | 11 | 0.059 | 6.04 | 11 |  | 6.07 | 12 |  | 6.13 | 0.387 | 5 | 0.76 | 14.3 | 9 | 0.65066 | 0.047 | 6.18 | 0.479 | 5 | 0.78 | 14 | 9 | 0.65066 | 6.16 | 0.432 | 5 | 0.73 | 15.5 | 9 | 0.62 | 0.049 | 1 | 0.53 | 0.013 | 0.049 | 0.034 | 1 | 0.55 |  | 0.049 | 1 | 0.45 |  | 7.96 | 0.069 | 2 | 5 | 13.9 | 25 | 45 | 0.021 | 8.01 | 0.074 | 2 | 4.1 | 14 | 25 | 42 | 0.016 | 4.2 | 3.6 | 4.1 | [17 empty] | AVERAGE | 6693.3333 | [9 empty] | 275 | 286.6667 | 290 | 260 | 253.3333 | 246.6667 | 253.3333 | 196.6667 | 175 | 576.6667 |  | 970 | 970 | 966.6667 | 80.3333 | 98 | 12 | 1480 | 283.3333 | 404.6667 | 40.6667 | 39 | 6 | 533.3333 | 101.6667 | 233.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.98 |  | TOTAL AVG COAG ALK: |  |  |  | 10.3333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.479 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.59 | [5 empty] | 6.1183 |  |  |  |  | 0.049 |  |  |  |  | 0.59 | [6 empty] | 0.049 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 6680 | [9 empty] | 230 | 260 | 280 | 260 | 250 | 230 | 250 | 180 | 140 | 230 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1390 | 265 | 396 | 40 | 39 | 6 | 520 | 95 | 227
[90 empty] | MAXIMUM | 6700 | [9 empty] | 310 | 300 | 300 | 260 | 260 | 260 | 260 | 210 | 205 | 750 |  | 980 | 980 | 980 | 81 | 98 | 12 | 1550 | 300 | 422 | 42 | 39 | 6 | 540 | 105 | 247
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.307 |  | TOTAL MGD: |  | 4.807 |  |  | FINISHED SOUTH 1 |  | START: | 23118957 |  | END: | 23123764 |  |  | Alum | 9447 |  | 8420 |  | 0 | [45 empty] | 0.6 | 9 | 28.2667 | 16.96 | 6.07 | 13.2 | 15 | 1.1307
[73 empty] | FINISHED 2 | 14.535 |  | TOTAL MGD: |  | 5.5 |  |  | FINISHED SOUTH 2 |  | START: | 40980380 |  | END: | 40985880 |  |  | Caustic | 6921 |  | 4959
[73 empty] | TOTAL RAW | 26.558 |  | TOTAL MGD: |  | 4.02 |  |  | FINISHED CONWAY |  | START: | 8724239 |  | END: | 8728259 |  |  | Hypochlorite | 10 |  | 26
[76 empty] | TOTAL MGD: |  | 10.515 |  |  | FINISHED PERRY |  | START: | 30441059 |  | END: | 30451574 |  |  | Phosphate | 2516
[76 empty] | TOTAL MGD: |  | 8.736 |  |  | RAW PLANT 1 |  | START: | 27965436 |  | END: | 27974172 |  |  | Fluoride | 1600 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.717 |  |  | RAW PLANT 2 |  | START: | 27912813 |  | END: | 27921530 |  |  | Cal~Flo | 14.63 | 0 | 0 | 13.08 | 1305.1 | 25
[76 empty] | TOTAL MGD: |  | 9.105 |  |  | RAW PLANT 3 |  | START: | 4226544 |  | END: | 4235649 |  |  | Zinc | 3191
[76 empty] | TOTAL MGD: |  | 1.058 |  |  | DECANT |  | START: | 1394147 |  | END: | 1395205 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.53924 |  |  | BLOW DOWN |  | START: | 8766.6379 |  | END: | 8767.1771 |  |  | NH3 | 11.7
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 375
[90 empty] | BI-SULFITE | 850 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2506 | Phosphate | 45
[90 empty] | Caustic 1 | 146 | Fluoride | 0
[90 empty] | Caustic 2 | 95 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23123764
[91 empty] | FINISHED SOUTH 2 |  | END: | 40985880
[91 empty] | FINISHED CONWAY |  | END: | 8728259
[91 empty] | FINISHED PERRY |  | END: | 30451574
[91 empty] | RAW PLANT 1 |  | END: | 27974172
[91 empty] | RAW PLANT 2 |  | END: | 27921530
[91 empty] | RAW PLANT 3 |  | END: | 4235649
[91 empty] | DECANT |  | END: | 1395205
[91 empty] | BLOW DOWN |  | END: | 8767.1771
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 16
DATE: | 2018-02-16 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-16 | [23 empty] | DATE: | 2018-02-16
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-16 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43147.0169 | 2,3,5 | 39 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | ,1 | 5.1883 | 1,2 | 18.7502 | 23.9386 | 1.0135 | 43147.0169 | 60.4908 | 3750.731 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.2045 | 1.571 | 1.5187 | 0.1648 | 0.1648 | 0.14579 | 0.15846 | 0.11409 | 0.095078 | 0.43752 | 0 | 0.060827 | 0.060827 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 3.9139 | 0.64401 | 6.7968 | 1.0818 | 0.39745 | 0.10199 | 3.308 | 0.50984 | 7.7923 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.05 | 0.436 | 4 | 0.67 | 14.5 | 9 | 0.65066 |  | 6.11 | 0.505 | 5 | 0.81 | 14.2 | 9 | 0.65066 | 6.15 | 0.431 | 4 | 0.71 | 15.6 | 9 | 0.45333 | [13 empty] | 7.24 | 0.057 | 1 | 4.2 | 13.7 |  |  |  | 7.54 | 0.059 | 1 | 3.5 | 13.9 |  |  |  | 4.3 | 3.4 | 3 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 230 | 300 | 290 | 260 | 260 | 230 | 250 | 180 | 150 | 230 |  | 980 | 980 | 970 | 80 | 98 | 12 | 1330 | 240 | 396 | 40 | 39 | 6 | 540 | 95 | 227 |  | 1:00 | 0.67 | 9 | 28.2667 | 18.9387 | 6.05 | 14.5 | 15 | 1.2626 | 10 | 6.5 | 0.53066 | 1:00 | 0.81 | 9 | 28.2667 | 22.896 | 6.11 | 14.2 | 15 | 1.5264 | 10 | 6.5 | 0.53066 | 1:00 | 0.71 | 9 | 30 | 21.3 | 6.15 | 15.6 | 10 | 2.13 | 15 | 6.5 | 0.33333
2:00 | [72 empty] | 43147.3572 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 8.4427 | 1,2 | 12.5222 | 20.965 | 0.73728 | 43147.3572 | 60.5814 | 3812.2184 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.7281 | 1.8329 | 1.571 | 0.1648 | 0.15846 | 0.1648 | 0.15212 | 0.12677 | 0.12677 | 1.4267 | 1 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.1217 | 0.67084 | 7.0028 | 1.0818 | 0.39745 | 0.10199 | 3.2107 | 0.53668 | 7.7923 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.72 | 22 | 20 | 25.9 | 58 | 218 | 14.3 | 0.296 |  | 6.01 | 11 | 0.046 | 6.05 | 11 |  | 6.08 | 12 | [8 empty] | 0.04 | [14 empty] | 0.038 | 1 | 0.47 |  | 0.042 | 0.022 | 1 | 0.54 |  | 0.047 | 1 | 0.42 | [38 empty] | 6690 | [6 empty] | 0 | 0 | 0 | 330 | 350 | 300 | 260 | 250 | 260 | 240 | 200 | 200 | 750 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1400 | 250 | 408 | 40 | 39 | 6 | 520 | 100 | 227 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43147.8376 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 8.4427 | 1,2 | 12.5222 | 20.965 | 0.83019 | 43147.8376 | 60.4908 | 4857.5042 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.2568 | 1.3092 | 1.5187 | 0.15846 | 0.15846 | 0.15212 | 0.15212 | 0.10142 | 0.08874 | 0.41849 | 2 | 0.060827 | 0.060827 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.3304 | 0.64401 | 7.0028 | 1.0818 | 0.39745 | 0.10199 | 3.2107 | 0.50984 | 7.7923 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.22 | 0.061 | 1 | 4.3 | 13.6 |  |  |  | 7.45 | 0.056 | 1 | 3.8 | 13.8 |  |  |  | 4.2 | 3.6 | 3.3 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 240 | 250 | 290 | 250 | 250 | 240 | 240 | 160 | 140 | 220 |  | 980 | 980 | 970 | 80 | 98 | 12 | 1420 | 240 | 408 | 40 | 39 | 6 | 520 | 95 | 227 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.68 | 22 | 20 | 25.4 | 63 | 222 | 14.3 | 0.288 |  | 6.12 | 10 | 0.057 | 6.05 | 10 |  | 6.07 | 10 | [8 empty] | 0.046 | [14 empty] | 0.034 | 1 | 0.48 |  | 0.044 | 0.02 | 1 | 0.56 |  | 0.047 | 1 | 0.49 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.1 | [9 empty] | 6.13 | 0.344 | 4 | 0.69 | 14.3 | 9 | 0.65066 |  | 6.14 | 0.376 | 4 | 0.76 | 14 | 9 | 0.65066 | 6.18 | 0.39 | 5 | 0.66 | 15.6 | 9 | 0.45333 |  |  |  | 0.009 | [9 empty] | 7.52 | 0.063 | 1 | 4.1 | 13.7 | 23 | 45 | 0.019 | 7.67 | 0.06 | 1 | 3.8 | 13.7 | 23 | 45 | 0.016 | 4.2 | 3.6 | 3.4 | [55 empty] | 9:00 | 0.69 | 9 | 28.2667 | 19.504 | 6.13 | 14.3 | 15 | 1.3003 | 10 | 6.5 | 0.53066 | 9:00 | 0.76 | 9 | 28.2667 | 21.4827 | 6.14 | 14 | 15 | 1.4322 | 10 | 6.5 | 0.53066 | 9:00 | 0.66 | 9 | 30 | 19.8 | 6.18 | 15.6 | 10 | 1.98 | 15 | 6.5 | 0.33333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.65 | 22 | 20 | 25.7 | 59 | 213 | 14.4 | 0.289 |  | 5.9 | 9 | 0.071 | 5.92 | 9 |  | 5.9 | 9 | [8 empty] | 0.051 | [14 empty] | 0.034 | 1 | 0.46 |  | 0.048 | 0.023 | 1 | 0.53 |  | 0.044 | 1 | 0.46 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.98 | 0.336 | 4 | 0.64 | 15 | 9 | 0.40302 |  | 5.96 | 0.369 | 4 | 0.69 | 14.7 | 9 | 0.57991 | 5.94 | 0.373 | 4 | 0.7 | 16 | 9 | 0.38667 | [13 empty] | 7.62 | 0.062 | 1 | 4.8 | 14 |  |  |  | 7.47 | 0.059 | 1 | 4.1 | 14.5 |  |  |  | 4.2 | 3.4 | 3.2 | [55 empty] | 13:00 | 0.64 | 9 | 28.2667 | 18.0907 | 5.98 | 15 | 8 | 2.2613 | 15 | 6 | 0.28302 | 13:00 | 0.69 | 9 | 28.2667 | 19.504 | 5.96 | 14.7 | 13 | 1.5003 | 10 | 6 | 0.45991 | 13:00 | 0.7 | 9 | 30 | 21 | 5.94 | 16 | 8 | 2.625 | 15 | 6 | 0.26667
14:00 | [126 empty] | 248 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.68 | 22 | 20 | 24.3 | 57 | 218 | 14.5 | 0.278 |  | 6.14 | 9 | 0.052 | 6.15 | 9 |  | 6.05 | 9 | [8 empty] | 0.037 | [14 empty] | 0.034 | 1 | 0.43 |  | 0.041 | 0.023 | 1 | 0.5 |  | 0.048 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.59 | 0.063 | 1 | 4.6 | 14.1 |  |  |  | 7.58 | 0.06 | 1 | 4 | 14.5 |  |  |  | 4.2 | 3.2 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.73 | 21 | 20 | 24.6 | 53 | 200 | 14.6 | 0.266 |  | 5.94 | 10 | 0.045 | 6.94 | 11 |  | 5.94 | 10 | [8 empty] | 0.034 | [14 empty] | 0.031 | 1 | 0.5 |  | 0.037 | 0.018 | 1 | 0.57 |  | 0.04 | 1 | 0.44 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.106 | [9 empty] | 6.11 | 0.362 | 4 | 0.67 | 14.7 | 9 | 0.65066 |  | 6.09 | 0.397 | 4 | 0.77 | 14.5 | 9 | 0.65066 | 6.13 | 0.42 | 4 | 0.62 | 16.2 | 9 | 0.45333 |  |  |  | 0.013 | [9 empty] | 7.48 | 0.059 | 1 | 4.5 | 13.8 | 21 | 41 | 0.022 | 7.5 | 0.063 | 1 | 3.7 | 14 | 20 | 44 | 0.022 | 4.2 | 3.1 | 2.9 | [55 empty] | 21:00 | 0.67 | 9 | 28.2667 | 18.9387 | 6.11 | 14.7 | 15 | 1.2626 | 10 | 6.5 | 0.53066 | 21:00 | 0.77 | 9 | 28.2667 | 21.7653 | 6.09 | 14.5 | 15 | 1.451 | 10 | 6.5 | 0.53066 | 21:00 | 0.62 | 9 | 30 | 18.6 | 6.13 | 16.2 | 10 | 1.86 | 15 | 6.5 | 0.33333
22:00 | [72 empty] | DOSE |  | TOTAL | 27 | 27 | 27 | 81 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 22.0738 | 0 | 43.7947 | 65.8685 | 2.581 | TOTAL | 181.563 | 12420.4536 | 0 | 2000 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.1894 | 4.7131 | 4.6084 | 0.48807 | 0.48173 | 0.46271 | 0.46271 | 0.34228 | 0.31059 | 2.2827 | 3 | 0.18062 | 0.18062 | 0.17938 | 3.2454 | 1.4981 | 0.30597 | 12.366 | 1.9589 | 20.8023 | 3.2454 | 1.1923 | 0.30597 | 9.7295 | 1.5564 | 23.3769 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.7 | 21 | 21 | 23.1 | 49 | 195 | 14.7 | 0.252 |  | 6 | 10 | 0.049 | 6.15 | 10 |  | 6.06 | 10 | [8 empty] | 0.042 | [14 empty] | 0.028 | 1 | 0.48 |  | 0.045 | 0.013 | 1 | 0.55 |  | 0.039 | 1 | 0.43 | [22 empty] | AVERAGE | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 7.3579 |  | 14.5982 | 21.9562 | 0.86034 | AVERAGE | 60.521 | 4140.1512 |  | 666.6667 | #N/A | #N/A | #N/A |  |  |  | 1.3965 | 1.571 | 1.5361 | 0.16269 | 0.16058 | 0.15424 | 0.15424 | 0.11409 | 0.10353 | 0.7609 | 1 | 0.060206 | 0.060206 | 0.059792 | 1.0818 | 0.49935 | 0.10199 | 4.122 | 0.65295 | 6.9341 | 1.0818 | 0.39745 | 0.10199 | 3.2432 | 0.51879 | 7.7923 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.16 | 130 | 121 | 149 | 339 | 1266 | 86.8 | 1.669 | 0.206 | 36.11 | 59 | 0.32 | 37.26 | 60 | 0 | 36.1 | 60 | 0 | 24.27 | 1.478 | 16 | 2.67 | 58.5 | 36 | 2.355 | 0.25 | 24.3 | 1.647 | 17 | 3.03 | 57.4 | 36 | 2.5319 | 24.4 | 1.614 | 17 | 2.69 | 63.4 | 36 | 1.7467 | 0.199 | 6 | 2.82 | 0.022 | 0.257 | 0.119 | 6 | 3.25 | 0 | 0.265 | 6 | 2.64 | 0 | 44.67 | 0.365 | 6 | 26.5 | 82.9 | 44 | 86 | 0.041 | 45.21 | 0.357 | 6 | 22.9 | 84.4 | 43 | 89 | 0.038 | 25.3 | 20.3 | 18.8 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 5.1883 |  | 12.5222 | 20.965 | 0.73728 | MINIMUM | 60.4908 | 3750.731 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.2045 | 1.3092 | 1.5187 | 0.15846 | 0.15846 | 0.14579 | 0.15212 | 0.10142 | 0.08874 | 0.41849 | 0 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 3.9139 | 0.64401 | 6.7968 | 1.0818 | 0.39745 | 0.10199 | 3.2107 | 0.50984 | 7.7923 |  | MIN | 0.67 | 9 | 28.2667 | 18.9387 | 6.05 | 14.5 | 15 | 1.2626 |  |  |  | MIN | 0.76 | 9 | 28.2667 | 21.4827 | 6.14 | 14 | 15 | 1.4322 |  |  |  | MIN | 0.62 | 9 | 30 | 18.6 | 6.13 | 16.2 | 10 | 1.86 |  |  |  | 1.2626
AVERAGE | 6.6933 | 21.6667 | 20.1667 | 24.8333 | 56.5 | 211 | 14.4667 | 0.27817 | 0.103 | 6.0183 | 9.8333 | 0.053333 | 6.21 | 10 |  | 6.0167 | 10 |  | 6.0675 | 0.3695 | 4 | 0.6675 | 14.625 | 9 | 0.58875 | 0.041667 | 6.075 | 0.41175 | 4.25 | 0.7575 | 14.35 | 9 | 0.63297 | 6.1 | 0.4035 | 4.25 | 0.6725 | 15.85 | 9 | 0.43667 | 0.033167 | 1 | 0.47 | 0.011 | 0.042833 | 0.019833 | 1 | 0.54167 |  | 0.044167 | 1 | 0.44 |  | 7.445 | 0.060833 | 1 | 4.4167 | 13.8167 | 22 | 43 | 0.0205 | 7.535 | 0.0595 | 1 | 3.8167 | 14.0667 | 21.5 | 44.5 | 0.019 | 4.2167 | 3.3833 | 3.1333 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 8.4427 |  | 18.7502 | 23.9386 | 1.0135 | MAXIMUM | 60.5814 | 4857.5042 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.7281 | 1.8329 | 1.571 | 0.1648 | 0.1648 | 0.1648 | 0.15846 | 0.12677 | 0.12677 | 1.4267 | 2 | 0.060827 | 0.060827 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.3304 | 0.67084 | 7.0028 | 1.0818 | 0.39745 | 0.10199 | 3.308 | 0.53668 | 7.7923
MINIMUM | 6.65 | 21 | 20 | 23.1 | 49 | 195 | 14.3 | 0.252 | 0.1 | 5.9 | 9 | 0.045 | 5.92 | 9 |  | 5.9 | 9 |  | 5.98 | 0.336 | 4 | 0.64 | 14.3 | 9 | 0.40302 | 0.034 | 5.96 | 0.369 | 4 | 0.69 | 14 | 9 | 0.57991 | 5.94 | 0.373 | 4 | 0.62 | 15.6 | 9 | 0.38667 | 0.028 | 1 | 0.43 | 0.009 | 0.037 | 0.013 | 1 | 0.5 |  | 0.039 | 1 | 0.4 |  | 7.22 | 0.057 | 1 | 4.1 | 13.6 | 21 | 41 | 0.019 | 7.45 | 0.056 | 1 | 3.5 | 13.7 | 20 | 44 | 0.016 | 4.2 | 3.1 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 20050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 900 | 880 | 770 | 760 | 730 | 730 | 540 | 490 | 1200 | 0 | 2910 | 2910 | 2890 | 240 | 294 | 36 | 4150 | 730 | 1212 | 120 | 117 | 18 | 1580 | 290 | 681
MAXIMUM | 6.73 | 22 | 21 | 25.9 | 63 | 222 | 14.7 | 0.296 | 0.106 | 6.14 | 11 | 0.071 | 6.94 | 11 |  | 6.08 | 12 |  | 6.13 | 0.436 | 4 | 0.69 | 15 | 9 | 0.65066 | 0.051 | 6.14 | 0.505 | 5 | 0.81 | 14.7 | 9 | 0.65066 | 6.18 | 0.431 | 5 | 0.71 | 16.2 | 9 | 0.45333 | 0.038 | 1 | 0.5 | 0.013 | 0.048 | 0.023 | 1 | 0.57 |  | 0.048 | 1 | 0.49 |  | 7.62 | 0.063 | 1 | 4.8 | 14.1 | 23 | 45 | 0.022 | 7.67 | 0.063 | 1 | 4.1 | 14.5 | 23 | 45 | 0.022 | 4.3 | 3.6 | 3.4 | [17 empty] | AVERAGE | 6683.3333 | [9 empty] | 266.6667 | 300 | 293.3333 | 256.6667 | 253.3333 | 243.3333 | 243.3333 | 180 | 163.3333 | 400 |  | 970 | 970 | 963.3333 | 80 | 98 | 12 | 1383.3333 | 243.3333 | 404 | 40 | 39 | 6 | 526.6667 | 96.6667 | 227
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0817 |  | TOTAL AVG COAG ALK: |  |  |  | 9.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.505 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.62 | [5 empty] | 6.0808 |  |  |  |  | 0.048 |  |  |  |  | 0.62 | [6 empty] | 0.048 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 6680 | [9 empty] | 230 | 250 | 290 | 250 | 250 | 230 | 240 | 160 | 140 | 220 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1330 | 240 | 396 | 40 | 39 | 6 | 520 | 95 | 227
[90 empty] | MAXIMUM | 6690 | [9 empty] | 330 | 350 | 300 | 260 | 260 | 260 | 250 | 200 | 200 | 750 |  | 980 | 980 | 970 | 80 | 98 | 12 | 1420 | 250 | 408 | 40 | 39 | 6 | 540 | 100 | 227
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.995 |  | TOTAL MGD: |  | 5.261 |  |  | FINISHED SOUTH 1 |  | START: | 23123764 |  | END: | 23129025 |  |  | Alum | 8910 |  | 10200 |  | 0 | [45 empty] | 0.67 | 9 | 28.2667 | 18.9387 | 6.05 | 14.5 | 15 | 1.2626
[73 empty] | FINISHED 2 | 14.323 |  | TOTAL MGD: |  | 5.734 |  |  | FINISHED SOUTH 2 |  | START: | 40985880 |  | END: | 40991614 |  |  | Caustic | 6768 |  | 4840
[73 empty] | TOTAL RAW | 27.109 |  | TOTAL MGD: |  | 4.251 |  |  | FINISHED CONWAY |  | START: | 8728259 |  | END: | 8732510 |  |  | Hypochlorite | 13 |  | 30
[76 empty] | TOTAL MGD: |  | 10.072 |  |  | FINISHED PERRY |  | START: | 30451574 |  | END: | 30461646 |  |  | Phosphate | 2524
[76 empty] | TOTAL MGD: |  | 9.039 |  |  | RAW PLANT 1 |  | START: | 27974172 |  | END: | 27983211 |  |  | Fluoride | 1500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.047 |  |  | RAW PLANT 2 |  | START: | 27921530 |  | END: | 27930577 |  |  | Cal~Flo | 14.63 | 0 | 0 | 11.61 | 2542.84 | 25
[76 empty] | TOTAL MGD: |  | 9.023 |  |  | RAW PLANT 3 |  | START: | 4235649 |  | END: | 4244672 |  |  | Zinc | 3199
[76 empty] | TOTAL MGD: |  | 0.936 |  |  | DECANT |  | START: | 1395205 |  | END: | 1396141 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.55233 |  |  | BLOW DOWN |  | START: | 8767.1771 |  | END: | 8767.7294 |  |  | NH3 | 11.54
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2506 | Phosphate | 44
[90 empty] | Caustic 1 | 154 | Fluoride | 0
[90 empty] | Caustic 2 | 94 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1
[91 empty] | FINISHED SOUTH 1 |  | END: | 23129025
[91 empty] | FINISHED SOUTH 2 |  | END: | 40991614
[91 empty] | FINISHED CONWAY |  | END: | 8732510
[91 empty] | FINISHED PERRY |  | END: | 30461646
[91 empty] | RAW PLANT 1 |  | END: | 27983211
[91 empty] | RAW PLANT 2 |  | END: | 27930577
[91 empty] | RAW PLANT 3 |  | END: | 4244672
[91 empty] | DECANT |  | END: | 1396141
[91 empty] | BLOW DOWN |  | END: | 8767.7294
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 17
DATE: | 2018-02-17 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-17 | [23 empty] | DATE: | 2018-02-17
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-17 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43148.0037 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 8.4427 | 1,2 | 12.5222 | 20.965 | 0.85274 | 43148.0037 | 60.4908 | 4857.5042 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.3616 | 1.3877 | 1.5187 | 0.15846 | 0.15846 | 0.15212 | 0.15212 | 0.10142 | 0.095078 | 0.41849 | 0 | 0.060827 | 0.060827 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.3304 | 0.64401 | 7.0028 | 1.0818 | 0.39745 | 0.10199 | 3.2107 | 0.50984 | 7.7923 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.381 | 4 | 0.6 | 14.9 | 9 | 0.65066 |  | 6.19 | 0.449 | 4 | 0.67 | 14.7 | 9 | 0.65066 | 6.17 | 0.361 | 4 | 0.8 | 16.3 | 9 | 0.45333 | [13 empty] | 7.38 | 0.056 | 1 | 4.4 | 14.4 |  |  |  | 7.44 | 0.065 | 1 | 3.7 | 14.2 |  |  |  | 4.1 | 3.1 | 3 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 260 | 265 | 290 | 250 | 250 | 240 | 240 | 160 | 150 | 220 |  | 980 | 980 | 970 | 80 | 98 | 12 | 1420 | 240 | 408 | 40 | 39 | 6 | 520 | 95 | 227 |  | 1:00 | 0.6 | 9 | 28.2667 | 16.96 | 6.06 | 14.9 | 15 | 1.1307 | 10 | 6.5 | 0.53066 | 1:00 | 0.67 | 9 | 28.2667 | 18.9387 | 6.19 | 14.7 | 15 | 1.2626 | 10 | 6.5 | 0.53066 | 1:00 | 0.8 | 9 | 30 | 24 | 6.17 | 16.3 | 10 | 2.4 | 15 | 6.5 | 0.33333
2:00 | [72 empty] | 43148.325 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.9619 | 1,2 | 9.9734 | 19.9354 | 1.2341 | 43148.325 | 60.4908 | 3627.7562 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.6758 | 1.5187 | 0.15846 | 0.15846 | 0.15212 | 0.15212 | 0.10142 | 0.10142 | 1.4267 | 1 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.3659 | 0.67084 | 7.0028 | 1.0818 | 0.39745 | 0.10199 | 3.137 | 0.59034 | 7.7923 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.73 | 22 | 20 | 21.2 | 51 | 183 | 14.6 | 0.25 |  | 6.11 | 12 | 0.045 | 6.21 | 12 |  | 6.22 | 12 | [8 empty] | 0.039 | [14 empty] | 0.062 | 1 | 0.38 |  | 0.046 | 0.037 | 1 | 0.57 |  | 0.066 | 1 | 0.4 | [38 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 300 | 320 | 290 | 250 | 250 | 240 | 240 | 160 | 160 | 750 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1450 | 250 | 408 | 40 | 39 | 6 | 510 | 110 | 227 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43148.8359 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.9619 | 1,2 | 9.9734 | 19.9354 | 1.4482 | 43148.8359 | 60.4908 | 3443.294 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4663 | 1.4663 | 1.4977 | 0.1648 | 0.1648 | 0.15846 | 0.15846 | 0.10142 | 0.10142 | 1.2174 | 4 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.0976 | 0.72451 | 6.7796 | 1.1359 | 0.39745 | 0.10199 | 3.7811 | 0.50984 | 7.0714 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 8.13 | 0.074 | 1 | 4.4 | 14.1 |  |  |  | 8.04 | 0.07 | 1 | 3.6 | 14 |  |  |  | 4 | 3.1 | 2.8 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 286 | 260 | 260 | 250 | 250 | 160 | 160 | 640 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1350 | 270 | 395 | 42 | 39 | 6 | 630 | 95 | 206 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.77 | 22 | 20 | 21.1 | 43 | 180 | 14.7 | 0.231 |  | 6.2 | 10 | 0.034 | 6.19 | 10 |  | 6.17 | 10 | [8 empty] | 0.03 | [14 empty] | 0.042 | 1 | 0.4 |  | 0.039 | 0.024 | 1 | 0.5 |  | 0.047 | 1 | 0.6 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.084 | [9 empty] | 6.28 | 0.33 | 4 | 0.6 | 14.5 | 9 | 0.65066 |  | 6.31 | 0.44 | 4 | 0.66 | 14.2 | 9 | 0.65066 | 6.32 | 0.475 | 4 | 0.83 | 16 | 9 | 0.45333 |  |  |  | 0.01 | [9 empty] | 8 | 0.073 | 1 | 4.5 | 14 | 24 | 40 | 0.012 | 8 | 0.069 | 1 | 2.8 | 14.1 | 24 | 43 | 0.004 | 3.9 | 3.1 | 2.9 | [55 empty] | 9:00 | 0.6 | 9 | 28.2667 | 16.96 | 6.28 | 14.5 | 15 | 1.1307 | 10 | 6.5 | 0.53066 | 9:00 | 0.66 | 9 | 28.2667 | 18.656 | 6.31 | 14.2 | 15 | 1.2437 | 10 | 6.5 | 0.53066 | 9:00 | 0.83 | 9 | 30 | 24.9 | 6.32 | 16 | 10 | 2.49 | 15 | 6.5 | 0.33333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.74 | 22 | 20 | 20 | 54 | 170 | 14.8 | 0.278 |  | 6.21 | 10 | 0.062 | 6.13 | 10 |  | 6.11 | 10 | [8 empty] | 0.052 | [14 empty] | 0.04 | 1 | 0.4 |  | 0.053 | 0.024 | 0.5 | 0.5 |  | 0.05 | 1 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.26 | 0.348 | 4 | 0.62 | 14.4 | 9 | 0.65066 |  | 6.22 | 0.396 | 4 | 0.63 | 14.2 | 9 | 0.65066 | 6.29 | 0.409 | 4 | 0.71 | 16 | 9 | 0.45333 | [13 empty] | 7.69 | 0.069 | 1 | 4.8 | 14.1 |  |  |  | 7.94 | 0.07 | 1 | 3.9 | 14.1 |  |  |  | 4 | 3 | 3.4 | [55 empty] | 13:00 | 0.62 | 9 | 28.2667 | 17.5253 | 6.26 | 14.4 | 15 | 1.1684 | 10 | 6.5 | 0.53066 | 13:00 | 0.63 | 9 | 28.2667 | 17.808 | 6.22 | 14.2 | 15 | 1.1872 | 10 | 6.5 | 0.53066 | 13:00 | 0.71 | 9 | 30 | 21.3 | 6.29 | 16 | 10 | 2.13 | 15 | 6.5 | 0.33333
14:00 | [126 empty] | 247 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.72 | 22 | 20 | 21.3 | 56 | 175 | 14.7 | 0.268 |  | 6.27 | 10 | 0.055 | 6.14 | 10 |  | 6.12 | 10 | [8 empty] | 0.05 | [14 empty] | 0.035 | 1 | 0.39 |  | 0.05 | 0.024 | 1 | 0.46 |  | 0.044 | 1 | 0.46 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.7 | 0.07 | 1 | 4.6 | 14.2 |  |  |  | 7.78 | 0.069 | 1 | 3.8 | 14.1 |  |  |  | 4 | 3 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.72 | 21 | 19 | 20 | 52 | 170 | 14.5 | 0.241 |  | 6.08 | 12 | 0.047 | 6.08 | 12 |  | 6.09 | 12 | [8 empty] | 0.045 | [14 empty] | 0.032 | 1 | 0.46 |  | 0.05 | 0.028 | 1 | 0.54 |  | 0.073 | 1 | 0.51 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.082 | [9 empty] | 6.09 | 0.34 | 4 | 0.69 | 14.6 | 9 | 0.65066 |  | 6.16 | 0.44 | 4 | 0.7 | 14.3 | 9 | 0.65066 | 6.24 | 0.372 | 4 | 0.65 | 16 | 9 | 0.45333 |  |  |  | 0.01 | [9 empty] | 7.7 | 0.063 | 1 | 4.6 | 14.1 | 23 | 36 | 0.018 | 7.66 | 0.058 | 1 | 4.2 | 13.9 | 22 | 34 | 0.013 | 4.1 | 2.9 | 5 | [55 empty] | 21:00 | 0.69 | 9 | 28.2667 | 19.504 | 6.09 | 14.6 | 15 | 1.3003 | 10 | 6.5 | 0.53066 | 21:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.16 | 14.3 | 15 | 1.3191 | 10 | 6.5 | 0.53066 | 21:00 | 0.65 | 9 | 30 | 19.5 | 6.24 | 16 | 10 | 1.95 | 15 | 6.5 | 0.33333
22:00 | [72 empty] | DOSE |  | TOTAL | 27 | 27 | 27 | 81 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 28.3666 | 0 | 32.4691 | 60.8357 | 3.535 | TOTAL | 181.4724 | 11928.5544 | 0 | 1950 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.3989 | 4.5298 | 4.535 | 0.48173 | 0.48173 | 0.46271 | 0.46271 | 0.30425 | 0.29791 | 3.0626 | 5 | 0.18 | 0.18 | 0.17938 | 3.2454 | 1.4981 | 0.30597 | 12.7938 | 2.0394 | 20.7852 | 3.2995 | 1.1923 | 0.30597 | 10.1288 | 1.61 | 22.656 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.75 | 23 | 20 | 18.9 | 54 | 161 | 14.7 | 0.266 |  | 6.06 | 11 | 0.05 | 6.1 | 11 |  | 6.08 | 11 | [8 empty] | 0.044 | [14 empty] | 0.031 | 1 | 0.47 |  | 0.046 | 0.024 | 1 | 0.52 |  | 0.063 | 1 | 0.49 | [22 empty] | AVERAGE | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.4555 |  | 10.823 | 20.2786 | 1.1783 | AVERAGE | 60.4908 | 3976.1848 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.4663 | 1.5099 | 1.5117 | 0.16058 | 0.16058 | 0.15424 | 0.15424 | 0.10142 | 0.099304 | 1.0209 | 1.6667 | 0.059999 | 0.059999 | 0.059792 | 1.0818 | 0.49935 | 0.10199 | 4.2646 | 0.67979 | 6.9284 | 1.0998 | 0.39745 | 0.10199 | 3.3763 | 0.53668 | 7.552 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.43 | 132 | 119 | 122.5 | 310 | 1039 | 88 | 1.534 | 0.166 | 36.93 | 65 | 0.293 | 36.85 | 65 | 0 | 5.942 | 5 | 0 | 24.69 | 1.399 | 16 | 2.51 | 58.4 | 36 | 2.6026 | 0.26 | 24.88 | 1.725 | 16 | 2.66 | 57.4 | 36 | 2.6026 | 25.02 | 1.617 | 16 | 2.99 | 64.3 | 36 | 1.8133 | 0.242 | 6 | 2.5 | 0.02 | 0.284 | 0.161 | 5.5 | 3.09 | 0 | 0.1 | 6 | 2.96 | 0 | 46.6 | 0.405 | 6 | 27.3 | 84.9 | 47 | 76 | 0.03 | 46.86 | 0.401 | 6 | 22 | 84.4 | 46 | 77 | 0.017 | 24.1 | 18.2 | 20.5 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 8.4427 |  | 9.9734 | 19.9354 | 0.85274 | MINIMUM | 60.4908 | 3443.294 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.3616 | 1.3877 | 1.4977 | 0.15846 | 0.15846 | 0.15212 | 0.15212 | 0.10142 | 0.095078 | 0.41849 | 0 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.0976 | 0.64401 | 6.7796 | 1.0818 | 0.39745 | 0.10199 | 3.137 | 0.50984 | 7.0714 |  | MIN | 0.6 | 9 | 28.2667 | 16.96 | 6.06 | 14.9 | 15 | 1.1307 |  |  |  | MIN | 0.63 | 9 | 28.2667 | 17.808 | 6.22 | 14.2 | 15 | 1.1872 |  |  |  | MIN | 0.65 | 9 | 30 | 19.5 | 6.24 | 16 | 10 | 1.95 |  |  |  | 1.1307
AVERAGE | 6.7383 | 22 | 19.8333 | 20.4167 | 51.6667 | 173.1667 | 14.6667 | 0.25567 | 0.083 | 6.155 | 10.8333 | 0.048833 | 6.1417 | 10.8333 |  | 6.1317 | 10.8333 |  | 6.1725 | 0.34975 | 4 | 0.6275 | 14.6 | 9 | 0.65066 | 0.043333 | 6.22 | 0.43125 | 4 | 0.665 | 14.35 | 9 | 0.65066 | 6.255 | 0.40425 | 4 | 0.7475 | 16.075 | 9 | 0.45333 | 0.040333 | 1 | 0.41667 | 0.01 | 0.047333 | 0.026833 | 0.91667 | 0.515 |  | 0.057167 | 1 | 0.49333 |  | 7.7667 | 0.0675 | 1 | 4.55 | 14.15 | 23.5 | 38 | 0.015 | 7.81 | 0.066833 | 1 | 3.6667 | 14.0667 | 23 | 38.5 | 0.0085 | 4.0167 | 3.0333 | 3.4167 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.9619 |  | 12.5222 | 20.965 | 1.4482 | MAXIMUM | 60.4908 | 4857.5042 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.6758 | 1.5187 | 0.1648 | 0.1648 | 0.15846 | 0.15846 | 0.10142 | 0.10142 | 1.4267 | 4 | 0.060827 | 0.060827 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.3659 | 0.72451 | 7.0028 | 1.1359 | 0.39745 | 0.10199 | 3.7811 | 0.59034 | 7.7923
MINIMUM | 6.72 | 21 | 19 | 18.9 | 43 | 161 | 14.5 | 0.231 | 0.082 | 6.06 | 10 | 0.034 | 6.08 | 10 |  | 6.08 | 10 |  | 6.06 | 0.33 | 4 | 0.6 | 14.4 | 9 | 0.65066 | 0.03 | 6.16 | 0.396 | 4 | 0.63 | 14.2 | 9 | 0.65066 | 6.17 | 0.361 | 4 | 0.65 | 16 | 9 | 0.45333 | 0.031 | 1 | 0.38 | 0.01 | 0.039 | 0.024 | 0.5 | 0.46 |  | 0.044 | 1 | 0.4 |  | 7.38 | 0.056 | 1 | 4.4 | 14 | 23 | 36 | 0.012 | 7.44 | 0.058 | 1 | 2.8 | 13.9 | 22 | 34 | 0.004 | 3.9 | 2.9 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 20040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 865 | 866 | 760 | 760 | 730 | 730 | 480 | 470 | 1610 | 0 | 2900 | 2900 | 2890 | 240 | 294 | 36 | 4220 | 760 | 1211 | 122 | 117 | 18 | 1660 | 300 | 660
MAXIMUM | 6.77 | 23 | 20 | 21.3 | 56 | 183 | 14.8 | 0.278 | 0.084 | 6.27 | 12 | 0.062 | 6.21 | 12 |  | 6.22 | 12 |  | 6.28 | 0.381 | 4 | 0.69 | 14.9 | 9 | 0.65066 | 0.052 | 6.31 | 0.449 | 4 | 0.7 | 14.7 | 9 | 0.65066 | 6.32 | 0.475 | 4 | 0.83 | 16.3 | 9 | 0.45333 | 0.062 | 1 | 0.47 | 0.01 | 0.053 | 0.037 | 1 | 0.57 |  | 0.073 | 1 | 0.6 |  | 8.13 | 0.074 | 1 | 4.8 | 14.4 | 24 | 40 | 0.018 | 8.04 | 0.07 | 1 | 4.2 | 14.2 | 24 | 43 | 0.013 | 4.1 | 3.1 | 5 | [17 empty] | AVERAGE | 6680 | [9 empty] | 280 | 288.3333 | 288.6667 | 253.3333 | 253.3333 | 243.3333 | 243.3333 | 160 | 156.6667 | 536.6667 |  | 966.6667 | 966.6667 | 963.3333 | 80 | 98 | 12 | 1406.6667 | 253.3333 | 403.6667 | 40.6667 | 39 | 6 | 553.3333 | 100 | 220
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1428 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.475 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.6 | [5 empty] | 6.2158 |  |  |  |  | 0.073 |  |  |  |  | 0.6 | [6 empty] | 0.073 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 6680 | [9 empty] | 260 | 265 | 286 | 250 | 250 | 240 | 240 | 160 | 150 | 220 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1350 | 240 | 395 | 40 | 39 | 6 | 510 | 95 | 206
[90 empty] | MAXIMUM | 6680 | [9 empty] | 300 | 320 | 290 | 260 | 260 | 250 | 250 | 160 | 160 | 750 |  | 980 | 980 | 970 | 80 | 98 | 12 | 1450 | 270 | 408 | 42 | 39 | 6 | 630 | 110 | 227
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.093 |  | TOTAL MGD: |  | 5.231 |  |  | FINISHED SOUTH 1 |  | START: | 23129025 |  | END: | 23134256 |  |  | Alum | 8223 |  | 9470 |  | 0 | [45 empty] | 0.6 | 9 | 28.2667 | 16.96 | 6.06 | 14.9 | 15 | 1.1307
[73 empty] | FINISHED 2 | 14.258 |  | TOTAL MGD: |  | 5.862 |  |  | FINISHED SOUTH 2 |  | START: | 40991614 |  | END: | 40997476 |  |  | Caustic | 6626 |  | 4741
[73 empty] | TOTAL RAW | 26.743 |  | TOTAL MGD: |  | 4.521 |  |  | FINISHED CONWAY |  | START: | 8732510 |  | END: | 8737031 |  |  | Hypochlorite | 11.75 |  | 29
[76 empty] | TOTAL MGD: |  | 9.737 |  |  | FINISHED PERRY |  | START: | 30461646 |  | END: | 30471383 |  |  | Phosphate | 2441
[76 empty] | TOTAL MGD: |  | 8.785 |  |  | RAW PLANT 1 |  | START: | 27983211 |  | END: | 27991996 |  |  | Fluoride | 1600 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.81 |  |  | RAW PLANT 2 |  | START: | 27930577 |  | END: | 27939387 |  |  | Cal~Flo | 11.61 | 0 | 0 | 9.75 | 1566.12 | 25
[76 empty] | TOTAL MGD: |  | 9.148 |  |  | RAW PLANT 3 |  | START: | 4244672 |  | END: | 4253820 |  |  | Zinc | 3205
[76 empty] | TOTAL MGD: |  | 1.413 |  |  | DECANT |  | START: | 1396141 |  | END: | 1397554 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.54314 |  |  | BLOW DOWN |  | START: | 8767.7294 |  | END: | 8768.2726 |  |  | NH3 | 11.37
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 600
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2992 | Phosphate | 34
[90 empty] | Caustic 1 | 154 | Fluoride | 0
[90 empty] | Caustic 2 | 93 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23134256
[91 empty] | FINISHED SOUTH 2 |  | END: | 40997476
[91 empty] | FINISHED CONWAY |  | END: | 8737031
[91 empty] | FINISHED PERRY |  | END: | 30471383
[91 empty] | RAW PLANT 1 |  | END: | 27991996
[91 empty] | RAW PLANT 2 |  | END: | 27939387
[91 empty] | RAW PLANT 3 |  | END: | 4253820
[91 empty] | DECANT |  | END: | 1397554
[91 empty] | BLOW DOWN |  | END: | 8768.2726
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 18
DATE: | 2018-02-18 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-18 | [23 empty] | DATE: | 2018-02-18
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-18 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [7 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  | 5.625 |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43149.0055 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.9619 | 1,2 | 9.9734 | 19.9354 | 0.95111 | 43149.0055 | 60.4908 | 3443.294 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4663 | 1.3616 | 1.4977 | 0.1648 | 0.1648 | 0.15846 | 0.15846 | 0.10142 | 0.10142 | 1.2174 | 0 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.0976 | 0.64401 | 6.7796 | 1.1359 | 0.39745 | 0.10199 | 3.7811 | 0.50984 | 7.0714 |  |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.13 | 0.365 | 4 | 0.58 | 14.7 | 9 | 0.65066 |  | 6.19 | 0.476 | 4 | 0.71 | 14.4 | 9 | 0.65066 | 6.2 | 0.432 | 4 | 0.68 | 15.9 | 9 | 0.45333 | [13 empty] | 7.58 | 0.063 | 1 | 4.2 | 14.3 |  |  |  | 7.48 | 0.05 | 1 | 3.3 | 14 |  |  |  | 4.1 | 3 | 3 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 280 | 260 | 286 | 260 | 260 | 250 | 250 | 160 | 160 | 640 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1350 | 240 | 395 | 42 | 39 | 6 | 630 | 95 | 206 |  |  | 1:00 | 0.58 | 9 | 28.2667 | 16.3947 | 6.13 | 14.7 | 15 | 1.093 | 10 | 6.5 | 0.53066 | 1:00 | 0.71 | 9 | 28.2667 | 20.0693 | 6.19 | 14.4 | 15 | 1.338 | 10 | 6.5 | 0.53066 | 1:00 | 0.68 | 9 | 30 | 20.4 | 6.2 | 15.9 | 10 | 2.04 | 15 | 6.5 | 0.33333
2:00 | [72 empty] | 43149.3243 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 11.101 | 1,2 | 9.3557 | 20.4566 | 0.88992 | 43149.3243 | 60.4908 | 3320.3192 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.6758 | 1.571 | 0.1648 | 0.1648 | 0.15846 | 0.15846 | 0.10142 | 0.11409 | 1.2365 | 4.5 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 3.9876 | 0.64401 | 6.7968 | 1.0818 | 0.39745 | 0.10199 | 3.157 | 0.53668 | 7.0714 |  |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.73 | 22 | 20 | 17.5 | 50 | 158 | 14.7 | 0.241 |  | 6.1 | 11 | 0.045 | 6.09 | 11 |  | 6.09 | 10 | [8 empty] | 0.036 | [14 empty] | 0.027 | 1 | 0.47 |  | 0.046 | 0.023 | 1 | 0.5 |  | 0.057 | 1 | 0.5 | [38 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 300 | 320 | 300 | 260 | 260 | 250 | 250 | 160 | 180 | 650 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1350 | 240 | 396 | 40 | 39 | 6 | 510 | 100 | 206 |  |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43149.8501 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 11.101 | 1 | 9.3557 | 20.4566 | 1.833 | 43149.8501 | 60.4908 | 3504.7814 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5187 | 1.4663 | 1.5187 | 0.15846 | 0.1648 | 0.15846 | 0.15846 | 0.095078 | 0.095078 | 1.5598 | 5 | 0.060827 | 0.060827 | 0.060206 | 1.1089 | 0.49935 | 0.10199 | 4.1344 | 0.63059 | 6.7968 | 1.1359 | 0.39745 | 0.10199 | 3.1834 | 0.50984 | 7.0714 |  |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.29 | 0.06 | 1 | 4.3 | 14.1 |  |  |  | 7.32 | 0.054 | 1 | 3.9 | 14 |  |  |  | 4.1 | 3.1 | 2.5 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 290 | 280 | 290 | 250 | 260 | 250 | 250 | 150 | 150 | 820 |  | 980 | 980 | 970 | 82 | 98 | 12 | 1360 | 235 | 396 | 42 | 39 | 6 | 500 | 95 | 206 |  |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [128 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.72 | 22 | 20 | 17.3 | 49 | 150 | 14.7 | 0.274 |  | 6.09 | 10 | 0.05 | 6.09 | 10 |  | 6.07 | 10 | [8 empty] | 0.043 | [14 empty] | 0.026 | 1 | 0.5 |  | 0.046 | 0.021 | 1 | 0.5 |  | 0.048 | 1 | 0.53 | [76 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [128 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.075 | [9 empty] | 6.15 | 0.278 | 4 | 0.7 | 14.7 | 9 | 0.65066 |  | 6.17 | 0.347 | 4 | 0.7 | 14.4 | 9 | 0.65066 | 6.19 | 0.438 | 4 | 0.73 | 15.9 | 9 | 0.45333 |  |  |  | 0.015 | [9 empty] | 7.49 | 0.06 | 1 | 4.5 | 14.1 | 23 | 36 | 0.029 | 7.45 | 0.059 | 1 | 3.3 | 14.1 | 23 | 36 | 0.016 | 4 | 2.9 | 2.6 | [56 empty] | 9:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.15 | 14.7 | 15 | 1.3191 | 10 | 6.5 | 0.53066 | 9:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.17 | 14.4 | 15 | 1.3191 | 10 | 6.5 | 0.53066 | 9:00 | 0.73 | 9 | 30 | 21.9 | 6.19 | 15.9 | 10 | 2.19 | 15 | 6.5 | 0.33333
10:00 | [128 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.69 | 21 | 20 | 18.6 | 55 | 160 | 14.9 | 0.289 |  | 6.01 | 10 | 0.052 | 6 | 10 |  | 6 | 10 | [8 empty] | 0.042 | [14 empty] | 0.025 | 1 | 0.46 |  | 0.042 | 0.022 | 1 | 0.46 |  | 0.044 | 1 | 0.5 | [76 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [128 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.13 | 0.296 | 4 | 0.7 | 15.2 | 9 | 0.47377 |  | 6.13 | 0.296 | 4 | 0.66 | 15.2 | 9 | 0.47377 | 6.15 | 0.429 | 4 | 0.73 | 16 | 9 | 0.45333 | [13 empty] | 7.38 | 0.063 | 1 | 4.3 | 14.4 |  |  |  | 7.4 | 0.056 | 1 | 3.7 | 14.4 |  |  |  | 4 | 2.9 | 2.6 | [56 empty] | 13:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.13 | 15.2 | 10 | 1.9787 | 15 | 6.5 | 0.35377 | 13:00 | 0.66 | 9 | 28.2667 | 18.656 | 6.13 | 15.2 | 10 | 1.8656 | 15 | 6.5 | 0.35377 | 13:00 | 0.73 | 9 | 30 | 21.9 | 6.15 | 16 | 10 | 2.19 | 15 | 6.5 | 0.33333
14:00 | [126 empty] | 231 |  | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.67 | 21 | 20 | 18.8 | 54 | 158 | 14.9 | 0.279 |  | 6.16 | 10 | 0.052 | 6.12 | 10 |  | 6.05 | 10 | [8 empty] | 0.04 | [14 empty] | 0.024 | 1 | 0.46 |  | 0.04 | 0.023 | 1 | 0.43 |  | 0.045 | 1 | 0.5 | [76 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [128 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.56 | 0.063 | 1 | 4.5 | 14.3 |  |  |  | 7.46 | 0.06 | 1 | 3.1 | 14.3 |  |  |  | 4 | 2.9 | 2.7 | [56 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [128 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 21 | 18 | 16.6 | 55 | 145 | 15 | 0.268 |  | 6.01 | 11 | 0.052 | 6 | 11 |  | 6.04 | 11 | [8 empty] | 0.041 | [14 empty] | 0.048 | 1 | 0.51 |  | 0.043 | 0.018 | 1 | 0.58 |  | 0.05 | 1 | 0.58 | [76 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [128 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.071 | [9 empty] | 6.02 | 0.352 | 4 | 0.7 | 15 | 9 | 0.47377 |  | 6.08 | 0.443 | 4 | 0.87 | 14.8 | 9 | 0.65066 | 6.08 | 0.354 | 4 | 0.69 | 14.8 | 9 | 0.62 |  |  |  | 0.01 | [9 empty] | 7.43 | 0.061 | 1 | 4.4 | 14.3 | 22 | 31 | 0.025 | 7.45 | 0.061 | 1 | 3.6 | 14.2 | 23 | 32 | 0.02 | 4.1 | 3 | 2.6 | [56 empty] | 21:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.02 | 15 | 10 | 1.9787 | 15 | 6.5 | 0.35377 | 21:00 | 0.87 | 9 | 28.2667 | 24.592 | 6.08 | 14.8 | 15 | 1.6395 | 10 | 6.5 | 0.53066 | 21:00 | 0.69 | 9 | 30 | 20.7 | 6.08 | 14.8 | 15 | 1.38 | 10 | 6.5 | 0.5
22:00 | [72 empty] | DOSE |  | TOTAL | 27 | 27 | 27 | 81 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 32.1638 | 1 | 28.6848 | 60.8486 | 3.674 | TOTAL | 181.4724 | 10268.3946 | 0 | 2000 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.556 | 4.5036 | 4.5874 | 0.48807 | 0.49441 | 0.47539 | 0.47539 | 0.29791 | 0.31059 | 4.0137 | 9.5 | 0.18 | 0.18 | 0.17938 | 3.2725 | 1.4981 | 0.30597 | 12.2195 | 1.9186 | 20.3732 | 3.3536 | 1.1923 | 0.30597 | 10.1215 | 1.5564 | 21.2143 |  |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.64 | 21 | 19 | 15.9 | 51 | 152 | 15.1 | 0.268 |  | 5.86 | 10 | 0.054 | 5.85 | 10 |  | 5.94 | 10 | [8 empty] | 0.043 | [14 empty] | 0.045 | 1 | 0.51 |  | 0.042 | 0.022 | 1 | 0.54 |  | 0.049 | 1 | 0.55 | [22 empty] | AVERAGE | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.7213 | 1 | 9.5616 | 20.2829 | 1.2247 | AVERAGE | 60.4908 | 3422.7982 |  | 666.6667 | #N/A | #N/A | #N/A |  |  |  | 1.5187 | 1.5012 | 1.5291 | 0.16269 | 0.1648 | 0.15846 | 0.15846 | 0.099304 | 0.10353 | 1.3379 | 3.1667 | 0.059999 | 0.059999 | 0.059792 | 1.0908 | 0.49935 | 0.10199 | 4.0732 | 0.63954 | 6.7911 | 1.1179 | 0.39745 | 0.10199 | 3.3738 | 0.51879 | 7.0714 |  |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.07 | 128 | 117 | 104.7 | 314 | 923 | 89.3 | 1.619 | 0.146 | 36.23 | 62 | 0.305 | 36.15 | 62 | 0 | 36.19 | 61 | 0 | 24.43 | 1.291 | 16 | 2.68 | 59.6 | 36 | 2.2489 | 0.245 | 24.57 | 1.562 | 16 | 2.94 | 58.8 | 36 | 2.4258 | 24.62 | 1.653 | 16 | 2.83 | 62.6 | 36 | 1.98 | 0.195 | 6 | 2.91 | 0.025 | 0.259 | 0.129 | 6 | 3.01 | 0 | 0.293 | 6 | 3.16 | 0 | 44.73 | 0.37 | 6 | 26.2 | 85.5 | 45 | 67 | 0.054 | 44.56 | 0.34 | 6 | 20.9 | 85 | 46 | 68 | 0.036 | 24.3 | 17.8 | 16 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.9619 | 1 | 9.3557 | 19.9354 | 0.88992 | MINIMUM | 60.4908 | 3320.3192 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.4663 | 1.3616 | 1.4977 | 0.15846 | 0.1648 | 0.15846 | 0.15846 | 0.095078 | 0.095078 | 1.2174 | 0 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 3.9876 | 0.63059 | 6.7796 | 1.0818 | 0.39745 | 0.10199 | 3.157 | 0.50984 | 7.0714 |  |  | MIN | 0.58 | 9 | 28.2667 | 16.3947 | 6.13 | 14.7 | 15 | 1.093 |  |  |  | MIN | 0.7 | 9 | 28.2667 | 19.7867 | 6.17 | 14.4 | 15 | 1.3191 |  |  |  | MIN | 0.69 | 9 | 30 | 20.7 | 6.08 | 14.8 | 15 | 1.38 |  |  |  | 1.093
AVERAGE | 6.6783 | 21.3333 | 19.5 | 17.45 | 52.3333 | 153.8333 | 14.8833 | 0.26983 | 0.073 | 6.0383 | 10.3333 | 0.050833 | 6.025 | 10.3333 |  | 6.0317 | 10.1667 |  | 6.1075 | 0.32275 | 4 | 0.67 | 14.9 | 9 | 0.56222 | 0.040833 | 6.1425 | 0.3905 | 4 | 0.735 | 14.7 | 9 | 0.60644 | 6.155 | 0.41325 | 4 | 0.7075 | 15.65 | 9 | 0.495 | 0.0325 | 1 | 0.485 | 0.0125 | 0.043167 | 0.0215 | 1 | 0.50167 |  | 0.048833 | 1 | 0.52667 |  | 7.455 | 0.061667 | 1 | 4.3667 | 14.25 | 22.5 | 33.5 | 0.027 | 7.4267 | 0.056667 | 1 | 3.4833 | 14.1667 | 23 | 34 | 0.018 | 4.05 | 2.9667 | 2.6667 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 11.101 | 1 | 9.9734 | 20.4566 | 1.833 | MAXIMUM | 60.4908 | 3504.7814 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.6758 | 1.571 | 0.1648 | 0.1648 | 0.15846 | 0.15846 | 0.10142 | 0.11409 | 1.5598 | 5 | 0.060827 | 0.060827 | 0.060206 | 1.1089 | 0.49935 | 0.10199 | 4.1344 | 0.64401 | 6.7968 | 1.1359 | 0.39745 | 0.10199 | 3.7811 | 0.53668 | 7.0714
MINIMUM | 6.62 | 21 | 18 | 15.9 | 49 | 145 | 14.7 | 0.241 | 0.071 | 5.86 | 10 | 0.045 | 5.85 | 10 |  | 5.94 | 10 |  | 6.02 | 0.278 | 4 | 0.58 | 14.7 | 9 | 0.47377 | 0.036 | 6.08 | 0.296 | 4 | 0.66 | 14.4 | 9 | 0.47377 | 6.08 | 0.354 | 4 | 0.68 | 14.8 | 9 | 0.45333 | 0.024 | 1 | 0.46 | 0.01 | 0.04 | 0.018 | 1 | 0.43 |  | 0.044 | 1 | 0.5 |  | 7.29 | 0.06 | 1 | 4.2 | 14.1 | 22 | 31 | 0.025 | 7.32 | 0.05 | 1 | 3.1 | 14 | 23 | 32 | 0.016 | 4 | 2.9 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 20040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 860 | 876 | 770 | 780 | 750 | 750 | 470 | 490 | 2110 | 0 | 2900 | 2900 | 2890 | 242 | 294 | 36 | 4060 | 715 | 1187 | 124 | 117 | 18 | 1640 | 290 | 618
MAXIMUM | 6.73 | 22 | 20 | 18.8 | 55 | 160 | 15.1 | 0.289 | 0.075 | 6.16 | 11 | 0.054 | 6.12 | 11 |  | 6.09 | 11 |  | 6.15 | 0.365 | 4 | 0.7 | 15.2 | 9 | 0.65066 | 0.043 | 6.19 | 0.476 | 4 | 0.87 | 15.2 | 9 | 0.65066 | 6.2 | 0.438 | 4 | 0.73 | 16 | 9 | 0.62 | 0.048 | 1 | 0.51 | 0.015 | 0.046 | 0.023 | 1 | 0.58 |  | 0.057 | 1 | 0.58 |  | 7.58 | 0.063 | 1 | 4.5 | 14.4 | 23 | 36 | 0.029 | 7.48 | 0.061 | 1 | 3.9 | 14.4 | 23 | 36 | 0.02 | 4.1 | 3.1 | 3 | [17 empty] | AVERAGE | 6680 | [9 empty] | 290 | 286.6667 | 292 | 256.6667 | 260 | 250 | 250 | 156.6667 | 163.3333 | 703.3333 |  | 966.6667 | 966.6667 | 963.3333 | 80.6667 | 98 | 12 | 1353.3333 | 238.3333 | 395.6667 | 41.3333 | 39 | 6 | 546.6667 | 96.6667 | 206
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0317 |  | TOTAL AVG COAG ALK: |  |  |  | 10.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.476 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.58 | [5 empty] | 6.135 |  |  |  |  | 0.057 |  |  |  |  | 0.58 | [6 empty] | 0.057 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 6680 | [9 empty] | 280 | 260 | 286 | 250 | 260 | 250 | 250 | 150 | 150 | 640 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1350 | 235 | 395 | 40 | 39 | 6 | 500 | 95 | 206
[90 empty] | MAXIMUM | 6680 | [9 empty] | 300 | 320 | 300 | 260 | 260 | 250 | 250 | 160 | 180 | 820 |  | 980 | 980 | 970 | 82 | 98 | 12 | 1360 | 240 | 396 | 42 | 39 | 6 | 630 | 100 | 206
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [51 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.975 |  | TOTAL MGD: |  | 4.979 |  |  | FINISHED SOUTH 1 |  | START: | 23134256 |  | END: | 23139235 |  |  | Alum | 7591 |  | 8901 |  | 0 | [46 empty] | 0.58 | 9 | 28.2667 | 16.3947 | 6.13 | 14.7 | 15 | 1.093
[73 empty] | FINISHED 2 | 13.286 |  | TOTAL MGD: |  | 5.996 |  |  | FINISHED SOUTH 2 |  | START: | 40997476 |  | END: | 41003472 |  |  | Caustic | 6455 |  | 4644
[73 empty] | TOTAL RAW | 26.522 |  | TOTAL MGD: |  | 4.111 |  |  | FINISHED CONWAY |  | START: | 8737031 |  | END: | 8741142 |  |  | Hypochlorite | 10 |  | 28.5
[76 empty] | TOTAL MGD: |  | 9.175 |  |  | FINISHED PERRY |  | START: | 30471383 |  | END: | 30480558 |  |  | Phosphate | 2434
[76 empty] | TOTAL MGD: |  | 8.755 |  |  | RAW PLANT 1 |  | START: | 27991996 |  | END: | 28000751 |  |  | Fluoride | 1600 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.782 |  |  | RAW PLANT 2 |  | START: | 27939387 |  | END: | 27948169 |  |  | Cal~Flo | 9.75 | 0 | 0 | 8.09 | 1397.72 | 25
[76 empty] | TOTAL MGD: |  | 8.985 |  |  | RAW PLANT 3 |  | START: | 4253820 |  | END: | 4262805 |  |  | Zinc | 3199
[76 empty] | TOTAL MGD: |  | 1.501 |  |  | DECANT |  | START: | 1397554 |  | END: | 1399055 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.53351 |  |  | BLOW DOWN |  | START: | 8768.2726 |  | END: | 8768.8061 |  |  | NH3 | 11.2
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 600
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2496 | Phosphate | 47
[90 empty] | Caustic 1 | 145 | Fluoride | 0
[90 empty] | Caustic 2 | 86 | Zinc | 7
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1
[91 empty] | FINISHED SOUTH 1 |  | END: | 23139235
[91 empty] | FINISHED SOUTH 2 |  | END: | 41003472
[91 empty] | FINISHED CONWAY |  | END: | 8741142
[91 empty] | FINISHED PERRY |  | END: | 30480558
[91 empty] | RAW PLANT 1 |  | END: | 28000751
[91 empty] | RAW PLANT 2 |  | END: | 27948169
[91 empty] | RAW PLANT 3 |  | END: | 4262805
[91 empty] | DECANT |  | END: | 1399055
[91 empty] | BLOW DOWN |  | END: | 8768.8061
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 19
DATE: | 2018-02-19 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-19 | [23 empty] | DATE: | 2018-02-19
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-19 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43150.0086 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 11.101 | 1 | 9.3557 | 20.4566 | 1.3652 | 43150.0086 | 60.4908 | 3504.7814 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5187 | 1.4663 | 1.5187 | 0.15846 | 0.1648 | 0.15846 | 0.15846 | 0.095078 | 0.095078 | 1.5598 | 0 | 0.060827 | 0.060827 | 0.060206 | 1.1089 | 0.49935 | 0.10199 | 3.9734 | 0.63059 | 6.7968 | 1.1359 | 0.39745 | 0.10199 | 3.1834 | 0.50984 | 7.0714 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.07 | 0.395 | 4 | 0.7 | 15.1 | 9 | 0.47377 |  | 6.14 | 0.432 | 4 | 0.81 | 14.9 | 9 | 0.65066 | 6.14 | 0.368 | 4 | 0.71 | 16.1 | 9 | 0.45333 | [13 empty] | 7.46 | 0.06 | 1 | 4 | 14.5 |  |  |  | 7.49 | 0.057 | 1 | 3.5 | 14.2 |  |  |  | 4.1 | 3 | 3 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 290 | 280 | 290 | 250 | 260 | 250 | 250 | 150 | 150 | 820 |  | 980 | 980 | 970 | 82 | 98 | 12 | 1300 | 235 | 396 | 42 | 39 | 6 | 500 | 95 | 206 |  | 1:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.07 | 15.1 | 10 | 1.9787 | 15 | 6.5 | 0.35377 | 1:00 | 0.81 | 9 | 28.2667 | 22.896 | 6.14 | 14.9 | 15 | 1.5264 | 10 | 6.5 | 0.53066 | 1:00 | 0.71 | 9 | 30 | 21.3 | 6.14 | 16.1 | 10 | 2.13 | 15 | 6.5 | 0.33333
2:00 | [72 empty] | 43150.3072 | 2,3,5 | 37 | 8.7 | 8.7 | 8.7 | 26.1 | 8.2 | 8.2 | 8.2 | 24.6 | 7,1 | 12.9283 | 1 | 11.4293 | 24.3576 | 0.82656 | 43150.3072 | 59.9537 | 3443.294 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6285 | 1.5742 | 1.5199 | 0.16393 | 0.16393 | 0.16393 | 0.16393 | 0.098357 | 0.098357 | 1.5218 | 5 | 0.061122 | 0.061122 | 0.061122 | 1.0934 | 0.50178 | 0.10572 | 4.116 | 0.66757 | 6.7964 | 1.1214 | 0.39086 | 0.10572 | 3.3115 | 0.55631 | 7.081 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.68 | 21 | 20 | 15.4 | 48 | 150 | 15.1 | 0.254 |  | 6.03 | 11 | 0.048 | 6.11 | 11 |  | 6.08 | 11 | [8 empty] | 0.04 | [14 empty] | 0.039 | 1 | 0.49 |  | 0.037 | 0.022 | 1 | 0.51 |  | 0.047 | 1 | 0.53 | [38 empty] | 6400 | [6 empty] | 0 | 0 | 0 | 300 | 290 | 280 | 250 | 250 | 250 | 250 | 150 | 150 | 800 |  | 950 | 950 | 950 | 78 | 95 | 12 | 1300 | 240 | 382 | 40 | 37 | 6 | 500 | 100 | 199 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43150.5941 | 2,3,5 | 37 | 10.3 | 9.8 | 6 | 26.1 | 9.8 | 9.3 | 5.5 | 24.6 | 7,1 | 12.9283 | 1 | 11.4293 | 24.3576 | 0.82656 | 43150.5941 | 59.9537 | 3443.294 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.3626 | 1.388 | 1.214 | 0.13846 | 0.13846 | 0.14553 | 0.14553 | 0.095078 | 0.14262 | 1.5218 | 5 | 0.051143 | 0.053892 | 0.091127 | 0.9388 | 0.43085 | 0.090777 | 3.6048 | 0.5732 | 5.8356 | 1.6719 | 0.58273 | 0.15762 | 4.677 | 0.82941 | 10.5572 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.31 | 0.057 | 1 | 4.1 | 14.4 |  |  |  | 7.38 | 0.059 | 1 | 3.6 | 14.2 |  |  |  | 3.9 | 2.9 | 3 | [18 empty] | 6400 | [6 empty] | 0 | 0 | 0 | 300 | 290 | 150 | 250 | 250 | 250 | 250 | 100 | 150 | 800 |  | 950 | 950 | 950 | 78 | 95 | 12 | 1300 | 240 | 382 | 40 | 37 | 6 | 500 | 100 | 199 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43150.8508 | 2,3,5 | 37 | 10.2 | 10.2 | 5.6 | 26 | 8.1 | 8.1 | 8.1 | 24.3 | 7,1 | 12.9283 | 1 | 11.4293 | 24.3576 | 1.8539 | 43150.8508 | 50.2163 | 4058.168 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5387 | 1.5387 | 0.87926 | 0.13982 | 0.13423 | 0.12864 | 0.14541 | 0.10187 | 0.10187 | 1.1033 | 1 | 0.061225 | 0.061225 | 0.059922 | 1.1352 | 0.50263 | 0.10703 | 4.1043 | 0.64765 | 6.8803 | 1.1352 | 0.39568 | 0.10703 | 3.2051 | 0.53502 | 7.1685 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.65 | 21 | 20 | 15 | 55 | 150 | 15 | 0.275 |  | 5.95 | 10 | 0.05 | 5.94 | 10 |  | 5.97 | 10 | [8 empty] | 0.045 | [14 empty] | 0.039 | 1 | 0.46 |  | 0.048 | 0.022 | 1 | 0.5 |  | 0.046 | 1 | 0.5 | [38 empty] | 5340 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 160 | 250 | 240 | 230 | 260 | 100 | 100 | 580 |  | 940 | 940 | 920 | 80 | 94 | 12 | 1280 | 230 | 382 | 40 | 37 | 6 | 475 | 95 | 199 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.069 | [9 empty] | 6.14 | 0.363 | 4 | 0.72 | 15 | 8.7 | 0.46198 |  | 6.07 | 0.373 | 4 | 0.62 | 14.8 | 8.7 | 0.63297 | 6.14 | 0.336 | 4 | 0.59 | 16 | 8.7 | 0.44222 |  |  |  | 0.01 | [9 empty] | 7.45 | 0.06 | 1 | 4.4 | 14.7 | 26 | 40 | 0.014 | 7.4 | 0.055 | 1 | 3.7 | 14.3 | 29 | 42 | 0.01 | 3.8 | 2.7 | 2.7 | [55 empty] | 9:00 | 0.72 | 8.7 | 29.2414 | 21.0538 | 6.14 | 15 | 10 | 2.1054 | 15 | 6.5 | 0.34198 | 9:00 | 0.62 | 8.7 | 29.2414 | 18.1297 | 6.07 | 14.8 | 15 | 1.2086 | 10 | 6.5 | 0.51297 | 9:00 | 0.59 | 8.7 | 31.0345 | 18.3103 | 6.14 | 16 | 10 | 1.831 | 15 | 6.5 | 0.32222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.66 | 21 | 20 | 15.6 | 53 | 149 | 15.3 | 0.284 |  | 6 | 10 | 0.055 | 6 | 10 |  | 6 | 10 | [8 empty] | 0.043 | [14 empty] | 0.039 | 1 | 0.43 |  | 0.043 | 0.022 | 1 | 0.46 |  | 0.048 | 1 | 0.43 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.327 | 4 | 0.51 | 15 | 10.3 | 0.52487 |  | 6.03 | 0.3 | 4 | 0.6 | 14.9 | 9.4 | 0.67425 | 6.04 | 0.4 | 4 | 0.6 | 16.1 | 6 | 0.34222 | [13 empty] | 7.2 | 0.059 | 1 | 4.2 | 14.5 |  |  |  | 7.3 | 0.056 | 1 | 3.5 | 14.5 |  |  |  | 3.8 | 2.8 | 2.7 | [55 empty] | 13:00 | 0.51 | 10.3 | 24.699 | 12.5965 | 6.12 | 15 | 10 | 1.2597 | 15 | 6.5 | 0.40487 | 13:00 | 0.6 | 9.4 | 27.0638 | 16.2383 | 6.03 | 14.9 | 15 | 1.0826 | 10 | 6.5 | 0.55425 | 13:00 | 0.6 | 6 | 45 | 27 | 6.04 | 16.1 | 10 | 2.7 | 15 | 6.5 | 0.22222
14:00 | [126 empty] | 234 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.69 | 22 | 20 | 15.9 | 55 | 149 | 15.2 | 0.264 |  | 6.14 | 10 | 0.048 | 6.06 | 10 |  | 6.04 | 10 | [8 empty] | 0.042 | [14 empty] | 0.036 | 1 | 0.48 |  | 0.042 | 0.023 | 1 | 0.46 |  | 0.045 | 1 | 0.46 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.29 | 0.06 | 1 | 4.1 | 14.5 |  |  |  | 7.32 | 0.059 | 1 | 3.6 | 14.6 |  |  |  | 3.8 | 2.8 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 22 | 20 | 13.8 | 53 | 142 | 15.4 | 0.291 |  | 6.14 | 11 | 0.051 | 6.15 | 12 |  | 6.1 | 12 | [8 empty] | 0.044 | [14 empty] | 0.04 | 1 | 0.46 |  | 0.045 | 0.031 | 1 | 0.45 |  | 0.049 | 1 | 0.43 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.064 | [9 empty] | 6.08 | 0.444 | 4 | 0.47 | 15.5 | 10.2 | 0.52094 |  | 6.09 | 0.471 | 5 | 0.62 | 15.4 | 10.2 | 0.52094 | 6.11 | 0.374 | 4 | 0.77 | 16.4 | 5.6 | 0.32741 |  |  |  | 0.006 | [9 empty] | 7.23 | 0.067 | 1 | 4.1 | 14.6 | 22 | 32 | 0.02 | 7.31 | 0.059 | 1 | 3.8 | 14.5 | 20 | 30 | 0.018 | 3.8 | 3 | 3 | [55 empty] | 21:00 | 0.47 | 10.2 | 24.9412 | 11.7224 | 6.08 | 15.5 | 10 | 1.1722 | 15 | 6.5 | 0.40094 | 21:00 | 0.62 | 10.2 | 24.9412 | 15.4635 | 6.09 | 15.4 | 10 | 1.5464 | 15 | 6.5 | 0.40094 | 21:00 | 0.77 | 5.6 | 48.2143 | 37.125 | 6.11 | 16.4 | 10 | 3.7125 | 15 | 6.5 | 0.20741
22:00 | [72 empty] | DOSE |  | TOTAL | 38.2 | 37.7 | 29.3 | 105.2 | 34.6 | 34.1 | 30.3 | 99 | 0 | 49.8859 | 4 | 43.6435 | 93.5294 | 4.8722 | TOTAL | 230.6145 | 14449.5374 | 0 | 2600 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 6.0485 | 5.9673 | 5.1318 | 0.60068 | 0.60142 | 0.59655 | 0.61333 | 0.39038 | 0.43792 | 5.7067 | 11 | 0.23432 | 0.23707 | 0.27238 | 4.2762 | 1.9346 | 0.40552 | 15.7986 | 2.519 | 26.3091 | 5.0644 | 1.7667 | 0.47236 | 14.3771 | 2.4306 | 31.8781 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.64 | 21 | 20 | 14.2 | 56 | 144 | 15.5 | 0.288 |  | 6.02 | 11 | 0.051 | 6.01 | 11 |  | 6.08 | 11 | [8 empty] | 0.048 | [14 empty] | 0.063 | 1 | 0.35 |  | 0.049 | 0.048 | 1 | 0.03 |  | 0.072 | 1 | 0.28 | [22 empty] | AVERAGE | 9.55 | 9.425 | 7.325 | 26.3 | 8.65 | 8.525 | 7.575 | 24.75 |  | 12.4715 | 1 | 10.9109 | 23.3824 | 1.2181 | AVERAGE | 57.6536 | 3612.3843 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.5121 | 1.4918 | 1.283 | 0.15017 | 0.15036 | 0.14914 | 0.15333 | 0.097596 | 0.10948 | 1.4267 | 2.75 | 0.058579 | 0.059266 | 0.068094 | 1.0691 | 0.48365 | 0.10138 | 3.9496 | 0.62976 | 6.5773 | 1.2661 | 0.44168 | 0.11809 | 3.5943 | 0.60764 | 7.9695 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.94 | 128 | 120 | 89.9 | 320 | 884 | 91.5 | 1.656 | 0.133 | 36.28 | 63 | 0.303 | 36.27 | 64 | 0 | 36.27 | 64 | 0 | 24.41 | 1.529 | 16 | 2.4 | 60.6 | 38.2 | 1.9816 | 0.262 | 24.33 | 1.576 | 17 | 2.65 | 60 | 37.3 | 2.4788 | 24.43 | 1.478 | 16 | 2.67 | 64.6 | 29.3 | 1.5652 | 0.256 | 6 | 2.67 | 0.016 | 0.264 | 0.168 | 6 | 2.41 | 0 | 0.307 | 6 | 2.63 | 0 | 43.94 | 0.363 | 6 | 24.9 | 87.2 | 48 | 72 | 0.034 | 44.2 | 0.345 | 6 | 21.7 | 86.3 | 49 | 72 | 0.028 | 23.2 | 17.2 | 17.1 |  |  | MINIMUM | 8.7 | 8.7 | 5.6 | 26 | 8.1 | 8.1 | 5.5 | 24.3 |  | 11.101 | 1 | 9.3557 | 20.4566 | 0.82656 | MINIMUM | 50.2163 | 3443.294 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.3626 | 1.388 | 0.87926 | 0.13846 | 0.13423 | 0.12864 | 0.14541 | 0.095078 | 0.095078 | 1.1033 | 0 | 0.051143 | 0.053892 | 0.059922 | 0.9388 | 0.43085 | 0.090777 | 3.6048 | 0.5732 | 5.8356 | 1.1214 | 0.39086 | 0.10199 | 3.1834 | 0.50984 | 7.0714 |  | MIN | 0.47 | 10.2 | 24.9412 | 11.7224 | 6.08 | 15.5 | 10 | 1.1722 |  |  |  | MIN | 0.6 | 9.4 | 27.0638 | 16.2383 | 6.03 | 14.9 | 15 | 1.0826 |  |  |  | MIN | 0.59 | 8.7 | 31.0345 | 18.3103 | 6.14 | 16 | 10 | 1.831 |  |  |  | 1.0826
AVERAGE | 6.6567 | 21.3333 | 20 | 14.9833 | 53.3333 | 147.3333 | 15.25 | 0.276 | 0.0665 | 6.0467 | 10.5 | 0.0505 | 6.045 | 10.6667 |  | 6.045 | 10.6667 |  | 6.1025 | 0.38225 | 4 | 0.6 | 15.15 | 9.55 | 0.49539 | 0.043667 | 6.0825 | 0.394 | 4.25 | 0.6625 | 15 | 9.325 | 0.61971 | 6.1075 | 0.3695 | 4 | 0.6675 | 16.15 | 7.325 | 0.3913 | 0.042667 | 1 | 0.445 | 0.008 | 0.044 | 0.028 | 1 | 0.40167 |  | 0.051167 | 1 | 0.43833 |  | 7.3233 | 0.0605 | 1 | 4.15 | 14.5333 | 24 | 36 | 0.017 | 7.3667 | 0.0575 | 1 | 3.6167 | 14.3833 | 24.5 | 36 | 0.014 | 3.8667 | 2.8667 | 2.85 |  |  | MAXIMUM | 10.3 | 10.2 | 9 | 27 | 9.8 | 9.3 | 8.5 | 25.5 |  | 12.9283 | 1 | 11.4293 | 24.3576 | 1.8539 | MAXIMUM | 60.4908 | 4058.168 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.6285 | 1.5742 | 1.5199 | 0.16393 | 0.1648 | 0.16393 | 0.16393 | 0.10187 | 0.14262 | 1.5598 | 5 | 0.061225 | 0.061225 | 0.091127 | 1.1352 | 0.50263 | 0.10703 | 4.116 | 0.66757 | 6.8803 | 1.6719 | 0.58273 | 0.15762 | 4.677 | 0.82941 | 10.5572
MINIMUM | 6.62 | 21 | 20 | 13.8 | 48 | 142 | 15 | 0.254 | 0.064 | 5.95 | 10 | 0.048 | 5.94 | 10 |  | 5.97 | 10 |  | 6.07 | 0.327 | 4 | 0.47 | 15 | 8.7 | 0.46198 | 0.04 | 6.03 | 0.3 | 4 | 0.6 | 14.8 | 8.7 | 0.52094 | 6.04 | 0.336 | 4 | 0.59 | 16 | 5.6 | 0.32741 | 0.036 | 1 | 0.35 | 0.006 | 0.037 | 0.022 | 1 | 0.03 |  | 0.045 | 1 | 0.28 |  | 7.2 | 0.057 | 1 | 4 | 14.4 | 22 | 32 | 0.014 | 7.3 | 0.055 | 1 | 3.5 | 14.2 | 20 | 30 | 0.01 | 3.8 | 2.7 | 2.7 | [15 empty] | MIL/MIN |  | TOTAL | 24820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 1140 | 880 | 1000 | 1000 | 980 | 1010 | 500 | 550 | 3000 | 0 | 3820 | 3820 | 3790 | 318 | 382 | 48 | 5180 | 945 | 1542 | 162 | 150 | 24 | 1975 | 390 | 803
MAXIMUM | 6.69 | 22 | 20 | 15.9 | 56 | 150 | 15.5 | 0.291 | 0.069 | 6.14 | 11 | 0.055 | 6.15 | 12 |  | 6.1 | 12 |  | 6.14 | 0.444 | 4 | 0.72 | 15.5 | 10.3 | 0.52487 | 0.048 | 6.14 | 0.471 | 5 | 0.81 | 15.4 | 10.2 | 0.67425 | 6.14 | 0.4 | 4 | 0.77 | 16.4 | 9 | 0.45333 | 0.063 | 1 | 0.49 | 0.01 | 0.049 | 0.048 | 1 | 0.51 |  | 0.072 | 1 | 0.53 |  | 7.46 | 0.067 | 1 | 4.4 | 14.7 | 26 | 40 | 0.02 | 7.49 | 0.059 | 1 | 3.8 | 14.6 | 29 | 42 | 0.018 | 4.1 | 3 | 3 | [17 empty] | AVERAGE | 6205 | [9 empty] | 292.5 | 285 | 220 | 250 | 250 | 245 | 252.5 | 125 | 137.5 | 750 |  | 955 | 955 | 947.5 | 79.5 | 95.5 | 12 | 1295 | 236.25 | 385.5 | 40.5 | 37.5 | 6 | 493.75 | 97.5 | 200.75
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0456 |  | TOTAL AVG COAG ALK: |  |  |  | 10.6111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.471 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.0975 |  |  |  |  | 0.072 |  |  |  |  | 0.47 | [6 empty] | 0.072 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 5340 | [9 empty] | 280 | 280 | 150 | 250 | 240 | 230 | 250 | 100 | 100 | 580 |  | 940 | 940 | 920 | 78 | 94 | 12 | 1280 | 230 | 382 | 40 | 37 | 6 | 475 | 95 | 199
[90 empty] | MAXIMUM | 6680 | [9 empty] | 300 | 290 | 290 | 250 | 260 | 250 | 260 | 150 | 150 | 820 |  | 980 | 980 | 970 | 82 | 98 | 12 | 1300 | 240 | 396 | 42 | 39 | 6 | 500 | 100 | 206
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.753 |  | TOTAL MGD: |  | 4.816 |  |  | FINISHED SOUTH 1 |  | START: | 23139235 |  | END: | 23144051 |  |  | Alum | 9093 |  | 8470 |  | 0 | [45 empty] | 0.6 | 9.4 | 27.0638 | 16.2383 | 6.03 | 14.9 | 15 | 1.0826
[73 empty] | FINISHED 2 | 13.374 |  | TOTAL MGD: |  | 5.937 |  |  | FINISHED SOUTH 2 |  | START: | 41003472 |  | END: | 41009409 |  |  | Caustic | 6295 |  | 4543
[73 empty] | TOTAL RAW | 26.638 |  | TOTAL MGD: |  | 4.444 |  |  | FINISHED CONWAY |  | START: | 8741142 |  | END: | 8745586 |  |  | Hypochlorite | 8.5 |  | 27
[76 empty] | TOTAL MGD: |  | 8.93 |  |  | FINISHED PERRY |  | START: | 30480558 |  | END: | 30489488 |  |  | Phosphate | 2322
[76 empty] | TOTAL MGD: |  | 9.643 |  |  | RAW PLANT 1 |  | START: | 28000751 |  | END: | 28010394 |  |  | Fluoride | 1500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.422 |  |  | RAW PLANT 2 |  | START: | 27948169 |  | END: | 27957591 |  |  | Cal~Flo | 8.09 | 0 | 0 | 6.51 | 1330.36 | 25
[76 empty] | TOTAL MGD: |  | 7.573 |  |  | RAW PLANT 3 |  | START: | 4262805 |  | END: | 4270378 |  |  | Zinc | 3209
[76 empty] | TOTAL MGD: |  | 1.332 |  |  | DECANT |  | START: | 1399055 |  | END: | 1400387 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.54931 |  |  | BLOW DOWN |  | START: | 8768.8061 |  | END: | 8769.3554 |  |  | NH3 | 11.03
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 600
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2448 | Phosphate | 47
[90 empty] | Caustic 1 | 143 | Fluoride | 0
[90 empty] | Caustic 2 | 91 | Zinc | 9
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 2.5
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 1.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23144051
[91 empty] | FINISHED SOUTH 2 |  | END: | 41009409
[91 empty] | FINISHED CONWAY |  | END: | 8745586
[91 empty] | FINISHED PERRY |  | END: | 30489488
[91 empty] | RAW PLANT 1 |  | END: | 28010394
[91 empty] | RAW PLANT 2 |  | END: | 27957591
[91 empty] | RAW PLANT 3 |  | END: | 4270378
[91 empty] | DECANT |  | END: | 1400387
[91 empty] | BLOW DOWN |  | END: | 8769.3554
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 20
DATE: | 2018-02-20 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-20 | [23 empty] | DATE: | 2018-02-20
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-20 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43151.0711 | 2,3,5 | 39 | 9.5 | 9.5 | 5 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 10.2398 | 1,2 | 10.1736 | 20.4134 | 0.20016 | 43151.0711 | 50.0204 | 2951.3948 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4838 | 1.4838 | 0.7122 | 0.15012 | 0.15012 | 0.15012 | 0.15012 | 0 | 0.11409 | 1.3316 | 1 | 0.063309 | 0.063309 | 0.063309 | 1.1034 | 0.50241 | 0.10596 | 4.1969 | 0.7907 | 6.9055 | 0.91954 | 0.38114 | 0.096324 | 3.4612 | 0.5839 | 7.3918 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.99 | 0.564 | 4 | 0.45 | 15.5 | 10.2 | 0.44075 |  | 6.05 | 0.469 | 4 | 0.62 | 15.3 | 10.2 | 0.52094 | 6.14 | 0.44 | 4 | 0.37 | 16.4 | 5.6 | 0.32741 | [13 empty] | 7.35 | 0.067 | 1 | 4 | 14.8 |  |  |  | 7.58 | 0.071 | 1 | 3.5 | 14.6 |  |  |  | 3.8 | 3 | 3.3 | [18 empty] | 4910 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 120 | 250 | 250 | 250 | 250 | 0 | 100 | 700 |  | 900 | 900 | 900 | 72 | 87 | 11 | 1260 | 260 | 355 | 30 | 33 | 5 | 500 | 96 | 190 |  | 1:00 | 0.45 | 10.2 | 24.9412 | 11.2235 | 5.99 | 15.5 | 8 | 1.4029 | 15 | 6 | 0.32075 | 1:00 | 0.62 | 10.2 | 24.9412 | 15.4635 | 6.05 | 15.3 | 10 | 1.5464 | 15 | 6.5 | 0.40094 | 1:00 | 0.37 | 5.6 | 48.2143 | 17.8393 | 6.14 | 16.4 | 10 | 1.7839 | 15 | 6.5 | 0.20741
2:00 | [72 empty] | 43151.3912 | 2,3,5 | 39 | 9.5 | 9.5 | 5 | 24 | 7.5 | 7.5 | 7.5 | 22.5 | 7,1 | 10.2398 | 1 | 10.1736 | 20.4134 | 0.20016 | 43151.3912 | 50.0204 | 2951.3948 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4838 | 1.4838 | 0.7122 | 0.15012 | 0.15012 | 0.15012 | 0.15012 | 0 | 0.11409 | 1.3316 | 1 | 0.063309 | 0.063309 | 0.063309 | 1.1034 | 0.50241 | 0.10596 | 4.0969 | 0.7907 | 6.9055 | 0.91954 | 0.38114 | 0.096324 | 3.3112 | 0.5839 | 7.3918 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.68 | 21 | 20 | 14 | 54 | 140 | 15.5 | 0.267 |  | 5.88 | 10 | 0.046 | 5.96 | 11 |  | 5.96 | 11 | [8 empty] | 0.045 | [14 empty] | 0.029 | 1 | 0.33 |  | 0.044 | 0.024 | 1 | 0.3 |  | 0.044 | 1 | 0.27 | [38 empty] | 4910 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 120 | 250 | 250 | 250 | 250 | 0 | 100 | 700 |  | 900 | 900 | 900 | 72 | 87 | 11 | 1260 | 260 | 355 | 30 | 33 | 5 | 500 | 96 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43151.5643 | 2,3,5 | 39 | 8.8 | 8.8 | 4.6 | 22.2 | 6.9 | 6.9 | 6.9 | 20.7 | 7,1 | 10.2398 | 1 | 10.1736 | 20.4134 | 0.20016 | 43151.5643 | 49.5606 | 2828.42 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.8063 | 1.8063 | 0.77413 | 0.16206 | 0.16206 | 0.16206 | 0.16206 | 0 | 0.12401 | 1.712 | 1 | 0.061168 | 0.061168 | 0.061168 | 1.0995 | 0.50216 | 0.1047 | 4.0995 | 0.77682 | 6.8717 | 1.0995 | 0.50216 | 0.1047 | 3.245 | 0.39667 | 7.4003 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.25 | 0.058 | 1 | 4 | 14.8 |  |  |  | 7.31 | 0.074 | 1 | 3.6 | 14.7 |  |  |  | 3.8 | 3.1 | 4.4 | [18 empty] | 4500 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 120 | 250 | 250 | 250 | 250 | 0 | 100 | 900 |  | 800 | 800 | 800 | 66 | 80 | 10 | 1160 | 235 | 325 | 33 | 40 | 5 | 450 | 60 | 175 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43151.8293 | 2,3,5 | 39 | 8.8 | 8.8 | 4.6 | 22.2 | 6.9 | 6.9 | 6.9 | 20.7 | 7,1 | 10.2398 | 1 | 10.1736 | 20.4134 | 1.3337 | 43151.8293 | 50.2214 | 2213.546 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.6128 | 1.6128 | 0.70962 | 0.19448 | 0.19448 | 0.18151 | 0.18151 | 0 | 0.24803 | 1.712 | 2.5 | 0.061168 | 0.061168 | 0.059639 | 1.0828 | 0.50216 | 0.1047 | 4.2317 | 0.76029 | 6.5334 | 1.1661 | 0.37662 | 0.12564 | 3.1789 | 0.56195 | 6.4699 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.64 | 21 | 20 | 13.4 | 56 | 137 | 15.4 | 0.286 |  | 6.02 | 10 | 0.046 | 5.97 | 10 |  | 5.96 | 10 | [8 empty] | 0.041 | [14 empty] | 0.034 | 1 | 0.38 |  | 0.042 | 0.028 | 1 | 0.33 |  | 0.044 | 1 | 0.3 | [38 empty] | 4560 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 110 | 300 | 300 | 280 | 280 | 0 | 200 | 900 |  | 800 | 800 | 780 | 65 | 80 | 10 | 1200 | 230 | 309 | 35 | 30 | 6 | 440 | 85 | 153 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.058 | [9 empty] | 6.1 | 0.505 | 4 | 0.53 | 15.6 | 9.5 | 0.49343 |  | 6.1 | 0.439 | 4 | 0.51 | 15.3 | 9.5 | 0.49343 | 6.13 | 0.404 | 4 | 0.49 | 16.3 | 5 | 0.30519 |  |  |  | 0.012 | [9 empty] | 7.3 | 0.054 | 1 | 4.4 | 14.9 | 29 | 37 | 0.017 | 7.82 | 0.05 | 1 | 3.7 | 14.7 | 29 | 36 | 0.009 | 3.8 | 3.1 | 4.2 | [55 empty] | 9:00 | 0.53 | 9.5 | 26.7789 | 14.1928 | 6.1 | 15.6 | 10 | 1.4193 | 15 | 6.5 | 0.37343 | 9:00 | 0.51 | 9.5 | 26.7789 | 13.6573 | 6.1 | 15.3 | 10 | 1.3657 | 15 | 6.5 | 0.37343 | 9:00 | 0.49 | 5 | 54 | 26.46 | 6.13 | 16.3 | 10 | 2.646 | 15 | 6.5 | 0.18519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.58 | 25 | 20 | 13.4 | 55 | 139 | 15.7 | 0.261 |  | 6.13 | 10 | 0.026 | 6.12 | 10 |  | 6.08 | 10 | [8 empty] | 0.014 | [14 empty] | 0.024 | 1 | 0.28 |  | 0.016 | 0.029 | 1 | 0.26 |  | 0.043 | 1 | 0.2 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.389 | 3 | 0.5 | 15.8 | 9 | 0.47377 |  | 6.06 | 0.436 | 4 | 0.5 | 15.5 | 9 | 0.47377 | 6.04 | 0.403 | 3 | 0.48 | 16.9 | 4.9 | 0.30148 | [13 empty] | 7.63 | 0.059 | 1 | 3.9 | 15.1 |  |  |  | 7.98 | 0.056 | 1 | 3.8 | 15.2 |  |  |  | 3.7 | 3.1 | 2.4 | [55 empty] | 13:00 | 0.5 | 9 | 28.2667 | 14.1333 | 6.03 | 15.8 | 10 | 1.4133 | 15 | 6.5 | 0.35377 | 13:00 | 0.5 | 9 | 28.2667 | 14.1333 | 6.06 | 15.5 | 10 | 1.4133 | 15 | 6.5 | 0.35377 | 13:00 | 0.48 | 4.9 | 55.102 | 26.449 | 6.04 | 16.9 | 10 | 2.6449 | 15 | 6.5 | 0.18148
14:00 | [126 empty] | 190 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.71 | 26 | 20 | 12.3 | 57 | 131 | 16 | 0.297 |  | 6.2 | 10 | 0.058 | 6.18 | 10 |  | 6.18 | 10 | [8 empty] | 0.045 | [14 empty] | 0.033 | 1 | 0.28 |  | 0.042 | 0.039 | 1 | 0.25 |  | 0.048 | 1 | 0.22 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.64 | 0.069 | 1 | 4.4 | 15.4 |  |  |  | 7.93 | 0.07 | 1 | 3.7 | 15.9 |  |  |  | 3.7 | 3.2 | 2.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.65 | 24 | 19 | 12.2 | 55 | 125 | 16.2 | 0.293 |  | 5.9 | 9 | 0.048 | 5.79 | 9 |  | 6.01 | 9 | [8 empty] | 0.048 | [14 empty] | 0.043 | 1 | 0.32 |  | 0.048 | 0.044 | 1 | 0.31 |  | 0.058 | 1 | 0.26 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.052 | [9 empty] | 6.16 | 0.361 | 4 | 0.57 | 16.3 | 8.8 | 0.46591 |  | 6.16 | 0.525 | 4 | 0.63 | 16.1 | 8.8 | 0.46591 | 6.19 | 0.583 | 4 | 0.3 | 17.2 | 4.6 | 0.29037 |  |  |  | 0.011 | [9 empty] | 7.41 | 0.067 | 1 | 4.3 | 15.4 | 23 | 27 | 0.02 | 7.5 | 0.065 | 1 | 4 | 15.1 | 22 | 31 | 0.01 | 3.6 | 3.2 | 2.4 | [55 empty] | 21:00 | 0.57 | 8.8 | 28.9091 | 16.4782 | 6.16 | 16.3 | 10 | 1.6478 | 15 | 6.5 | 0.34591 | 21:00 | 0.63 | 8.8 | 28.9091 | 18.2127 | 6.16 | 16.1 | 10 | 1.8213 | 15 | 6.5 | 0.34591 | 21:00 | 0.3 | 4.6 | 58.6957 | 17.6087 | 6.19 | 17.2 | 10 | 1.7609 | 15 | 6.5 | 0.17037
22:00 | [72 empty] | DOSE |  | TOTAL | 36.6 | 36.6 | 19.2 | 92.4 | 28.8 | 28.8 | 28.8 | 86.4 | 0 | 40.9594 | 3 | 40.6944 | 81.6538 | 1.9342 | TOTAL | 199.8227 | 10944.7556 | 0 | 2650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 6.3866 | 6.3866 | 2.9082 | 0.65679 | 0.65679 | 0.64382 | 0.64382 | 0 | 0.60023 | 6.0872 | 5.5 | 0.24896 | 0.24896 | 0.24743 | 4.3891 | 2.0091 | 0.42131 | 16.625 | 3.1185 | 27.2161 | 4.1046 | 1.6411 | 0.42299 | 13.1963 | 2.1264 | 28.6538 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.63 | 23 | 19 | 12.3 | 52 | 120 | 16.3 | 0.292 |  | 5.94 | 11 | 0.051 | 6.01 | 11 |  | 5.89 | 11 | [8 empty] | 0.042 | [14 empty] | 0.028 | 1 | 0.3 |  | 0.043 | 0.037 | 1 | 0.29 |  | 0.041 | 1 | 0.26 | [22 empty] | AVERAGE | 9.15 | 9.15 | 4.8 | 23.1 | 7.2 | 7.2 | 7.2 | 21.6 |  | 10.2398 | 1 | 10.1736 | 20.4134 | 0.48355 | AVERAGE | 49.9557 | 2736.1889 |  | 662.5 | #N/A | #N/A | #N/A |  |  |  | 1.5966 | 1.5966 | 0.72704 | 0.1642 | 0.1642 | 0.16096 | 0.16096 |  | 0.15006 | 1.5218 | 1.375 | 0.062239 | 0.062239 | 0.061857 | 1.0973 | 0.50229 | 0.10533 | 4.1562 | 0.77963 | 6.804 | 1.0262 | 0.41027 | 0.10575 | 3.2991 | 0.53161 | 7.1635 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.89 | 140 | 118 | 77.6 | 329 | 792 | 95.1 | 1.696 | 0.11 | 36.07 | 60 | 0.275 | 36.03 | 61 | 0 | 36.08 | 61 | 0 | 24.28 | 1.819 | 15 | 2.05 | 63.2 | 37.5 | 1.8739 | 0.235 | 24.37 | 1.869 | 16 | 2.26 | 62.2 | 37.5 | 1.9541 | 24.5 | 1.83 | 15 | 1.64 | 66.8 | 20.1 | 1.2244 | 0.191 | 6 | 1.89 | 0.023 | 0.235 | 0.201 | 6 | 1.74 | 0 | 0.278 | 6 | 1.51 | 0 | 44.58 | 0.374 | 6 | 25 | 90.4 | 52 | 64 | 0.037 | 46.12 | 0.386 | 6 | 22.3 | 90.2 | 51 | 67 | 0.019 | 22.4 | 18.7 | 19.2 |  |  | MINIMUM | 8.8 | 8.8 | 4.6 | 22.2 | 6.9 | 6.9 | 6.9 | 20.7 |  | 10.2398 | 1 | 10.1736 | 20.4134 | 0.20016 | MINIMUM | 49.5606 | 2213.546 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.4838 | 1.4838 | 0.70962 | 0.15012 | 0.15012 | 0.15012 | 0.15012 |  | 0.11409 | 1.3316 | 1 | 0.061168 | 0.061168 | 0.059639 | 1.0828 | 0.50216 | 0.1047 | 4.0969 | 0.76029 | 6.5334 | 0.91954 | 0.37662 | 0.096324 | 3.1789 | 0.39667 | 6.4699 |  | MIN | 0.45 | 10.2 | 24.9412 | 11.2235 | 5.99 | 15.5 | 8 | 1.4029 |  |  |  | MIN | 0.51 | 9.5 | 26.7789 | 13.6573 | 6.1 | 15.3 | 10 | 1.3657 |  |  |  | MIN | 0.3 | 4.6 | 58.6957 | 17.6087 | 6.19 | 17.2 | 10 | 1.7609 |  |  |  | 1.3657
AVERAGE | 6.6483 | 23.3333 | 19.6667 | 12.9333 | 54.8333 | 132 | 15.85 | 0.28267 | 0.055 | 6.0117 | 10 | 0.045833 | 6.005 | 10.1667 |  | 6.0133 | 10.1667 |  | 6.07 | 0.45475 | 3.75 | 0.5125 | 15.8 | 9.375 | 0.46847 | 0.039167 | 6.0925 | 0.46725 | 4 | 0.565 | 15.55 | 9.375 | 0.48851 | 6.125 | 0.4575 | 3.75 | 0.41 | 16.7 | 5.025 | 0.30611 | 0.031833 | 1 | 0.315 | 0.0115 | 0.039167 | 0.0335 | 1 | 0.29 |  | 0.046333 | 1 | 0.25167 |  | 7.43 | 0.062333 | 1 | 4.1667 | 15.0667 | 26 | 32 | 0.0185 | 7.6867 | 0.064333 | 1 | 3.7167 | 15.0333 | 25.5 | 33.5 | 0.0095 | 3.7333 | 3.1167 | 3.2 |  |  | MAXIMUM | 9.5 | 9.5 | 5 | 24 | 7.5 | 7.5 | 7.5 | 22.5 |  | 10.2398 | 1 | 10.1736 | 20.4134 | 1.3337 | MAXIMUM | 50.2214 | 2951.3948 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.8063 | 1.8063 | 0.77413 | 0.19448 | 0.19448 | 0.18151 | 0.18151 |  | 0.24803 | 1.712 | 2.5 | 0.063309 | 0.063309 | 0.063309 | 1.1034 | 0.50241 | 0.10596 | 4.2317 | 0.7907 | 6.9055 | 1.1661 | 0.50216 | 0.12564 | 3.4612 | 0.5839 | 7.4003
MINIMUM | 6.58 | 21 | 19 | 12.2 | 52 | 120 | 15.4 | 0.261 | 0.052 | 5.88 | 9 | 0.026 | 5.79 | 9 |  | 5.89 | 9 |  | 5.99 | 0.361 | 3 | 0.45 | 15.5 | 8.8 | 0.44075 | 0.014 | 6.05 | 0.436 | 4 | 0.5 | 15.3 | 8.8 | 0.46591 | 6.04 | 0.403 | 3 | 0.3 | 16.3 | 4.6 | 0.29037 | 0.024 | 1 | 0.28 | 0.011 | 0.016 | 0.024 | 1 | 0.25 |  | 0.041 | 1 | 0.2 |  | 7.25 | 0.054 | 1 | 3.9 | 14.8 | 23 | 27 | 0.017 | 7.31 | 0.05 | 1 | 3.5 | 14.6 | 22 | 31 | 0.009 | 3.6 | 3 | 2.4 | [15 empty] | MIL/MIN |  | TOTAL | 18880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 1030 | 470 | 1050 | 1050 | 1030 | 1030 | 0 | 500 | 3200 | 0 | 3400 | 3400 | 3380 | 275 | 334 | 42 | 4880 | 985 | 1344 | 128 | 136 | 21 | 1890 | 337 | 708
MAXIMUM | 6.71 | 26 | 20 | 14 | 57 | 140 | 16.3 | 0.297 | 0.058 | 6.2 | 11 | 0.058 | 6.18 | 11 |  | 6.18 | 11 |  | 6.16 | 0.564 | 4 | 0.57 | 16.3 | 10.2 | 0.49343 | 0.048 | 6.16 | 0.525 | 4 | 0.63 | 16.1 | 10.2 | 0.52094 | 6.19 | 0.583 | 4 | 0.49 | 17.2 | 5.6 | 0.32741 | 0.043 | 1 | 0.38 | 0.012 | 0.048 | 0.044 | 1 | 0.33 |  | 0.058 | 1 | 0.3 |  | 7.64 | 0.069 | 1 | 4.4 | 15.4 | 29 | 37 | 0.02 | 7.98 | 0.074 | 1 | 4 | 15.9 | 29 | 36 | 0.01 | 3.8 | 3.2 | 4.4 | [17 empty] | AVERAGE | 4720 | [9 empty] | 257.5 | 257.5 | 117.5 | 262.5 | 262.5 | 257.5 | 257.5 |  | 125 | 800 |  | 850 | 850 | 845 | 68.75 | 83.5 | 10.5 | 1220 | 246.25 | 336 | 32 | 34 | 5.25 | 472.5 | 84.25 | 177
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.01 |  | TOTAL AVG COAG ALK: |  |  |  | 10.1111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.583 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.3 | [5 empty] | 6.0958 |  |  |  |  | 0.058 |  |  |  |  | 0.3 | [6 empty] | 0.058 | [16 empty] | Pump Station MIN |  | 2.4 | [17 empty] | MINIMUM | 4500 | [9 empty] | 250 | 250 | 110 | 250 | 250 | 250 | 250 |  | 100 | 700 |  | 800 | 800 | 780 | 65 | 80 | 10 | 1160 | 230 | 309 | 30 | 30 | 5 | 440 | 60 | 153
[90 empty] | MAXIMUM | 4910 | [9 empty] | 280 | 280 | 120 | 300 | 300 | 280 | 280 |  | 200 | 900 |  | 900 | 900 | 900 | 72 | 87 | 11 | 1260 | 260 | 355 | 35 | 40 | 6 | 500 | 96 | 190
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.101 |  | TOTAL MGD: |  | 5.105 |  |  | FINISHED SOUTH 1 |  | START: | 23144051 |  | END: | 23149156 |  |  | Alum | 8626 |  | 10200 |  | 0 | [45 empty] | 0.51 | 9.5 | 26.7789 | 13.6573 | 6.1 | 15.3 | 10 | 1.3657
[73 empty] | FINISHED 2 | 12.039 |  | TOTAL MGD: |  | 5.996 |  |  | FINISHED SOUTH 2 |  | START: | 41009409 |  | END: | 41015405 |  |  | Caustic | 6166 |  | 4450
[73 empty] | TOTAL RAW | 23.989 |  | TOTAL MGD: |  | 4.199 |  |  | FINISHED CONWAY |  | START: | 8745586 |  | END: | 8749785 |  |  | Hypochlorite | 13 |  | 30.25
[76 empty] | TOTAL MGD: |  | 7.84 |  |  | FINISHED PERRY |  | START: | 30489488 |  | END: | 30497328 |  |  | Phosphate | 2240
[76 empty] | TOTAL MGD: |  | 9.479 |  |  | RAW PLANT 1 |  | START: | 28010394 |  | END: | 28019873 |  |  | Fluoride | 1500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.383 |  |  | RAW PLANT 2 |  | START: | 27957591 |  | END: | 27966974 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 5.127 |  |  | RAW PLANT 3 |  | START: | 4270378 |  | END: | 4275505 |  |  | Zinc | 3208
[76 empty] | TOTAL MGD: |  | 1.732 |  |  | DECANT |  | START: | 1400387 |  | END: | 1402119 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.63307 |  |  | BLOW DOWN |  | START: | 8769.3554 |  | END: | 8769.9885 |  |  | NH3 | 10.89
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 600
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 1992 | Phosphate | 42
[90 empty] | Caustic 1 | 137 | Fluoride | 0
[90 empty] | Caustic 2 | 53 | Zinc | 8
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 1
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 3
[91 empty] | FINISHED SOUTH 1 |  | END: | 23149156
[91 empty] | FINISHED SOUTH 2 |  | END: | 41015405
[91 empty] | FINISHED CONWAY |  | END: | 8749785
[91 empty] | FINISHED PERRY |  | END: | 30497328
[91 empty] | RAW PLANT 1 |  | END: | 28019873
[91 empty] | RAW PLANT 2 |  | END: | 27966974
[91 empty] | RAW PLANT 3 |  | END: | 4275505
[91 empty] | DECANT |  | END: | 1402119
[91 empty] | BLOW DOWN |  | END: | 8769.9885
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 21
DATE: | 2018-02-21 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-21 | [23 empty] | DATE: | 2018-02-21
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-21 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43152.0217 | 2,3,5 | 39 | 9 | 9 | 4.9 | 22.9 | 7.1 | 7.1 | 7.1 | 21.3 | 7,1 | 10.2398 | 1 | 10.1736 | 20.4134 | 1.2467 | 43152.0217 | 50.181 | 2582.4704 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.63 | 1.63 | 0.75232 | 0.19649 | 0.19649 | 0.18382 | 0.18382 | 0 | 0.24449 | 0 | 0 | 0.059445 | 0.059445 | 0.059445 | 1.1009 | 0.50022 | 0.10175 | 4.2485 | 0.771 | 6.6165 | 1.1332 | 0.37821 | 0.1221 | 3.1612 | 0.57825 | 6.4932 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.07 | 0.326 | 4 | 0.53 | 16.5 | 9 | 0.47377 |  | 6.13 | 0.465 | 4 | 0.61 | 16.3 | 9 | 0.47377 | 6.12 | 0.392 | 4 | 0.33 | 17.4 | 4.9 | 0.30148 | [13 empty] | 7 | 0.062 | 1 | 4.3 | 15.6 |  |  |  | 7.32 | 0.069 | 1 | 3.8 | 15.3 |  |  |  | 3.7 | 3.3 | 3 | [18 empty] | 4700 | [6 empty] | 0 | 0 | 0 | 260 | 260 | 120 | 310 | 310 | 290 | 290 | 0 | 210 | 0 |  | 800 | 800 | 800 | 68 | 82 | 10 | 1240 | 240 | 322 | 35 | 31 | 6 | 450 | 90 | 158 |  | 1:00 | 0.53 | 9 | 28.2667 | 14.9813 | 6.07 | 16.5 | 10 | 1.4981 | 15 | 6.5 | 0.35377 | 1:00 | 0.61 | 9 | 28.2667 | 17.2427 | 6.13 | 16.3 | 10 | 1.7243 | 15 | 6.5 | 0.35377 | 1:00 | 0.33 | 4.9 | 55.102 | 18.1837 | 6.12 | 17.4 | 10 | 1.8184 | 15 | 6.5 | 0.18148
2:00 | [72 empty] | 43152.3196 | 2,3,5 | 39 | 10 | 10 | 5 | 25 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 8.4053 | 1 | 10.8014 | 19.2067 | 0 | 43152.3196 | 55.7457 | 2398.0082 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.712 | 1.7691 | 0.82748 | 0.19966 | 0.19966 | 0.18825 | 0.19966 | 0 | 0.25101 | 1.5218 | 1 | 0.060874 | 0.060874 | 0.060874 | 1.1052 | 0.49975 | 0.10188 | 4.1065 | 0.77491 | 6.6025 | 1.0905 | 0.38869 | 0.09262 | 3.2142 | 0.58484 | 6.509 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.64 | 23 | 20 | 12 | 58 | 128 | 16.4 | 0.256 |  | 5.95 | 11 | 0.044 | 5.96 | 11 |  | 5.97 | 11 | [8 empty] | 0.037 | [14 empty] | 0.027 | 1 | 0.29 |  | 0.041 | 0.026 | 1 | 0.32 |  | 0.043 | 1 | 0.29 | [38 empty] | 5700 | [6 empty] | 0 | 0 | 0 | 300 | 310 | 145 | 350 | 350 | 330 | 350 | 0 | 220 | 800 |  | 900 | 900 | 900 | 75 | 90 | 11 | 1300 | 265 | 353 | 37 | 35 | 5 | 500 | 100 | 174 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43152.8706 | 2,3,5 | 39 | 11 | 11 | 6 | 28 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 10.6675 | 1 | 14.5152 | 25.1827 | 1.62 | 43152.8706 | 55.0122 | 2643.9578 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.712 | 1.712 | 1.712 | 0.20226 | 0.20226 | 0.18151 | 0.18151 | 0.20917 | 0.2377 | 1.5218 | 1 | 0.060874 | 0.060874 | 0.060874 | 1.12 | 0.49975 | 0.09262 | 4.1037 | 0.76029 | 7.4816 | 1.12 | 0.38869 | 0.11114 | 3.1942 | 0.59654 | 7.4816 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.2 | 0.057 | 1 | 4.3 | 15.6 |  |  |  | 7.3 | 0.062 | 1 | 3.9 | 15.2 |  |  |  | 3.7 | 3.4 | 2.8 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 390 | 390 | 350 | 350 | 220 | 250 | 800 |  | 900 | 900 | 900 | 76 | 90 | 10 | 1270 | 260 | 400 | 38 | 35 | 6 | 500 | 102 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.61 | 25 | 20 | 12.8 | 52 | 132 | 16.5 | 0.277 |  | 5.91 | 14 | 0.046 | 5.91 | 14 |  | 5.95 | 12 | [8 empty] | 0.041 | [14 empty] | 0.026 | 1 | 0.32 |  | 0.05 | 0.026 | 1 | 0.45 |  | 0.041 | 1 | 0.24 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.057 | [9 empty] | 6.05 | 0.461 | 6 | 0.53 | 16.3 | 10 | 0.51308 |  | 6.07 | 0.434 | 6 | 0.61 | 16.1 | 10 | 0.51308 | 6.07 | 0.331 | 5 | 0.53 | 17.3 | 5 | 0.30519 |  |  |  | 0.019 | [9 empty] | 7.18 | 0.058 | 2 | 4.3 | 15.8 | 28 | 35 | 0.022 | 7.26 | 0.057 | 2 | 3.8 | 15.2 | 27 | 40 | 0.017 | 3.8 | 3.4 | 3 | [55 empty] | 9:00 | 0.53 | 10 | 25.44 | 13.4832 | 6.05 | 16.3 | 10 | 1.3483 | 15 | 6.5 | 0.39308 | 9:00 | 0.61 | 10 | 25.44 | 15.5184 | 6.07 | 16.1 | 10 | 1.5518 | 15 | 6.5 | 0.39308 | 9:00 | 0.53 | 5 | 54 | 28.62 | 6.07 | 17.3 | 10 | 2.862 | 15 | 6.5 | 0.18519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.61 | 24 | 20 | 12.2 | 54 | 130 | 16.5 | 0.292 |  | 6.02 | 11 | 0.046 | 5.99 | 11 |  | 5.99 | 11 | [8 empty] | 0.041 | [14 empty] | 0.026 | 1 | 0.31 |  | 0.047 | 0.026 | 1 | 0.45 |  | 0.042 | 1 | 0.19 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.261 | 4 | 0.61 | 17.2 | 10 | 0.51308 |  | 6.04 | 0.313 | 4 | 0.7 | 16.8 | 10 | 0.51308 | 6.09 | 0.437 | 3 | 0.41 | 17.6 | 5.3 | 0.3163 | [13 empty] | 7.24 | 0.049 | 1 | 4.6 | 15.9 |  |  |  | 7.43 | 0.046 | 1 | 3.3 | 15.9 |  |  |  | 3.8 | 3.4 | 3 | [55 empty] | 13:00 | 0.61 | 10 | 25.44 | 15.5184 | 6.03 | 17.2 | 10 | 1.5518 | 15 | 6.5 | 0.39308 | 13:00 | 0.7 | 10 | 25.44 | 17.808 | 6.04 | 16.8 | 10 | 1.7808 | 15 | 6.5 | 0.39308 | 13:00 | 0.41 | 5.3 | 50.9434 | 20.8868 | 6.09 | 17.6 | 10 | 2.0887 | 15 | 6.5 | 0.1963
14:00 | [126 empty] | 206 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.68 | 20 | 21 | 12.1 | 54 | 135 | 16.8 | 0.287 |  | 6.01 | 11 | 0.045 | 5.98 | 11 |  | 5.92 | 10 | [8 empty] | 0.044 | [14 empty] | 0.032 | 1 | 0.38 |  | 0.047 | 0.034 | 1 | 0.4 |  | 0.044 | 1 | 0.27 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17;00 | [53 empty] | 7.21 | 0.055 | 1 | 4.4 | 16.5 |  |  |  | 7.32 | 0.049 | 1 | 3.4 | 15.8 |  |  |  | 3.8 | 3.5 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 5.67 | 20 | 20 | 10.8 | 55 | 112 | 17.4 | 0.281 |  | 6.06 | 10 | 0.055 | 6 | 10 |  | 5.96 | 10 | [8 empty] | 0.043 | [14 empty] | 0.038 | 1 | 0.25 |  | 0.045 | 0.034 | 1 | 0.39 |  | 0.032 | 1 | 0.42 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.046 | [9 empty] | 6.09 | 0.288 | 3 | 0.49 | 17.5 | 11 | 0.55239 |  | 6.1 | 0.317 | 3 | 0.54 | 17.5 | 11 | 0.55239 | 6.11 | 0.43 | 3 | 0.58 | 18 | 6 | 0.34222 |  |  |  | 0.013 | [9 empty] | 7.11 | 0.048 | 1 | 3.8 | 16.1 | 24 | 30 | 0.02 | 7.25 | 0.05 | 1 | 3.7 | 16.2 | 23 | 33 | 0.014 | 3.8 | 3.4 | 3.2 | [55 empty] | 21:00 | 0.49 | 11 | 23.1273 | 11.3324 | 6.09 | 17.5 | 10 | 1.1332 | 15 | 6.5 | 0.43239 | 21:00 | 0.54 | 11 | 23.1273 | 12.4887 | 6.1 | 17.5 | 10 | 1.2489 | 15 | 6.5 | 0.43239 | 21:00 | 0.58 | 6 | 45 | 26.1 | 6.11 | 18 | 10 | 2.61 | 15 | 6.5 | 0.22222
22:00 | [72 empty] | DOSE |  | TOTAL | 30 | 30 | 15.9 | 75.9 | 22.7 | 22.7 | 22.7 | 68.1 | 0 | 29.3126 | 3 | 35.4902 | 64.8029 | 2.8667 | TOTAL | 160.9389 | 7624.4364 | 0 | 2000 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 5.0541 | 5.1111 | 3.2918 | 0.59842 | 0.59842 | 0.55359 | 0.56499 | 0.20917 | 0.73319 | 3.0436 | 2 | 0.18119 | 0.18119 | 0.18119 | 3.326 | 1.4997 | 0.29625 | 12.4587 | 2.3062 | 20.7005 | 3.3437 | 1.1556 | 0.32586 | 9.5696 | 1.7596 | 20.4837 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.65 | 23 | 19 | 8.45 | 57 | 109 | 17.5 | 0.281 |  | 5.94 | 9 | 0.064 | 5.95 | 9 |  | 5.91 | 10 | [8 empty] | 0.043 | [14 empty] | 0.033 | 1 | 0.24 |  | 0.041 | 0.037 | 1 | 0.37 |  | 0.041 | 1.47 | 0.47 | [22 empty] | AVERAGE | 10 | 10 | 5.3 | 25.3 | 7.5667 | 7.5667 | 7.5667 | 22.7 |  | 9.7709 | 1 | 11.8301 | 21.601 | 0.95556 | AVERAGE | 53.6463 | 2541.4788 |  | 666.6667 | #N/A | #N/A | #N/A |  |  |  | 1.6847 | 1.7037 | 1.0973 | 0.19947 | 0.19947 | 0.18453 | 0.18833 | 0.069724 | 0.2444 | 1.0145 | 0.66667 | 0.060398 | 0.060398 | 0.060398 | 1.1087 | 0.4999 | 0.098751 | 4.1529 | 0.76873 | 6.9002 | 1.1146 | 0.3852 | 0.10862 | 3.1899 | 0.58654 | 6.8279 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.86 | 135 | 120 | 68.35 | 330 | 746 | 101.1 | 1.674 | 0.103 | 35.89 | 66 | 0.3 | 35.79 | 66 | 0 | 35.7 | 64 | 0 | 24.24 | 1.336 | 17 | 2.16 | 67.5 | 40 | 2.0523 | 0.249 | 24.34 | 1.529 | 17 | 2.46 | 66.7 | 40 | 2.0523 | 24.39 | 1.59 | 15 | 1.85 | 70.3 | 21.2 | 1.2652 | 0.182 | 6 | 1.79 | 0.032 | 0.271 | 0.183 | 6 |  | 0 | 0.243 | 6.47 | 1.88 | 0 | 42.94 | 0.329 | 7 | 25.7 | 95.5 | 52 | 65 | 0.042 | 43.88 | 0.333 | 7 | 21.9 | 93.6 | 50 | 73 | 0.031 | 22.6 | 20.4 | 18.1 |  |  | MINIMUM | 9 | 9 | 4.9 | 22.9 | 7.1 | 7.1 | 7.1 | 21.3 |  | 8.4053 | 1 | 10.1736 | 19.2067 | 0 | MINIMUM | 50.181 | 2398.0082 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.63 | 1.63 | 0.75232 | 0.19649 | 0.19649 | 0.18151 | 0.18151 | 0 | 0.2377 | 0 | 0 | 0.059445 | 0.059445 | 0.059445 | 1.1009 | 0.49975 | 0.09262 | 4.1037 | 0.76029 | 6.6025 | 1.0905 | 0.37821 | 0.09262 | 3.1612 | 0.57825 | 6.4932 |  | MIN | 0.49 | 11 | 23.1273 | 11.3324 | 6.09 | 17.5 | 10 | 1.1332 |  |  |  | MIN | 0.54 | 11 | 23.1273 | 12.4887 | 6.1 | 17.5 | 10 | 1.2489 |  |  |  | MIN | 0.33 | 4.9 | 55.102 | 18.1837 | 6.12 | 17.4 | 10 | 1.8184 |  |  |  | 1.1332
AVERAGE | 6.4767 | 22.5 | 20 | 11.3917 | 55 | 124.3333 | 16.85 | 0.279 | 0.0515 | 5.9817 | 11 | 0.05 | 5.965 | 11 |  | 5.95 | 10.6667 |  | 6.06 | 0.334 | 4.25 | 0.54 | 16.875 | 10 | 0.51308 | 0.0415 | 6.085 | 0.38225 | 4.25 | 0.615 | 16.675 | 10 | 0.51308 | 6.0975 | 0.3975 | 3.75 | 0.4625 | 17.575 | 5.3 | 0.3163 | 0.030333 | 1 | 0.29833 | 0.016 | 0.045167 | 0.0305 | 1 |  |  | 0.0405 | 1.0783 | 0.31333 |  | 7.1567 | 0.054833 | 1.1667 | 4.2833 | 15.9167 | 26 | 32.5 | 0.021 | 7.3133 | 0.0555 | 1.1667 | 3.65 | 15.6 | 25 | 36.5 | 0.0155 | 3.7667 | 3.4 | 3.0167 |  |  | MAXIMUM | 11 | 11 | 6 | 28 | 7.8 | 7.8 | 7.8 | 23.4 |  | 10.6675 | 1 | 14.5152 | 25.1827 | 1.62 | MAXIMUM | 55.7457 | 2643.9578 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.712 | 1.7691 | 1.712 | 0.20226 | 0.20226 | 0.18825 | 0.19966 | 0.20917 | 0.25101 | 1.5218 | 1 | 0.060874 | 0.060874 | 0.060874 | 1.12 | 0.50022 | 0.10188 | 4.2485 | 0.77491 | 7.4816 | 1.1332 | 0.38869 | 0.1221 | 3.2142 | 0.59654 | 7.4816
MINIMUM | 5.67 | 20 | 19 | 8.45 | 52 | 109 | 16.4 | 0.256 | 0.046 | 5.91 | 9 | 0.044 | 5.91 | 9 |  | 5.91 | 10 |  | 6.03 | 0.261 | 3 | 0.49 | 16.3 | 9 | 0.47377 | 0.037 | 6.04 | 0.313 | 3 | 0.54 | 16.1 | 9 | 0.47377 | 6.07 | 0.331 | 3 | 0.33 | 17.3 | 4.9 | 0.30148 | 0.026 | 1 | 0.24 | 0.013 | 0.041 | 0.026 | 1 |  |  | 0.032 | 1 | 0.19 |  | 7 | 0.048 | 1 | 3.8 | 15.6 | 24 | 30 | 0.02 | 7.25 | 0.046 | 1 | 3.3 | 15.2 | 23 | 33 | 0.014 | 3.7 | 3.3 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 16700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 870 | 565 | 1050 | 1050 | 970 | 990 | 220 | 680 | 1600 | 0 | 2600 | 2600 | 2600 | 219 | 262 | 31 | 3810 | 765 | 1075 | 110 | 101 | 17 | 1450 | 292 | 532
MAXIMUM | 6.68 | 25 | 21 | 12.8 | 58 | 135 | 17.5 | 0.292 | 0.057 | 6.06 | 14 | 0.064 | 6 | 14 |  | 5.99 | 12 |  | 6.09 | 0.461 | 6 | 0.61 | 17.5 | 11 | 0.55239 | 0.044 | 6.13 | 0.465 | 6 | 0.7 | 17.5 | 11 | 0.55239 | 6.12 | 0.437 | 5 | 0.58 | 18 | 6 | 0.34222 | 0.038 | 1 | 0.38 | 0.019 | 0.05 | 0.037 | 1 |  |  | 0.044 | 1.47 | 0.47 |  | 7.24 | 0.062 | 2 | 4.6 | 16.5 | 28 | 35 | 0.022 | 7.43 | 0.069 | 2 | 3.9 | 16.2 | 27 | 40 | 0.017 | 3.8 | 3.5 | 3.2 | [17 empty] | AVERAGE | 5566.6667 | [9 empty] | 286.6667 | 290 | 188.3333 | 350 | 350 | 323.3333 | 330 | 73.3333 | 226.6667 | 533.3333 |  | 866.6667 | 866.6667 | 866.6667 | 73 | 87.3333 | 10.3333 | 1270 | 255 | 358.3333 | 36.6667 | 33.6667 | 5.6667 | 483.3333 | 97.3333 | 177.3333
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9656 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.465 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.33 | [5 empty] | 6.0808 |  |  |  |  | 0.044 |  |  |  |  | 0.33 | [6 empty] | 0.044 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 4700 | [9 empty] | 260 | 260 | 120 | 310 | 310 | 290 | 290 | 0 | 210 | 0 |  | 800 | 800 | 800 | 68 | 82 | 10 | 1240 | 240 | 322 | 35 | 31 | 5 | 450 | 90 | 158
[90 empty] | MAXIMUM | 6300 | [9 empty] | 300 | 310 | 300 | 390 | 390 | 350 | 350 | 220 | 250 | 800 |  | 900 | 900 | 900 | 76 | 90 | 11 | 1300 | 265 | 400 | 38 | 35 | 6 | 500 | 102 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.399 |  | TOTAL MGD: |  | 4.879 |  |  | FINISHED SOUTH 1 |  | START: | 23149156 |  | END: | 23154035 |  |  | Alum | 10100 |  | 9510 |  | 0 | [45 empty] | 0.49 | 11 | 23.1273 | 11.3324 | 6.09 | 17.5 | 10 | 1.1332
[73 empty] | FINISHED 2 | 13.187 |  | TOTAL MGD: |  | 5.52 |  |  | FINISHED SOUTH 2 |  | START: | 41015405 |  | END: | 41020925 |  |  | Caustic | 6015 |  | 4443
[73 empty] | TOTAL RAW | 24.843 |  | TOTAL MGD: |  | 4.11 |  |  | FINISHED CONWAY |  | START: | 8749785 |  | END: | 8753895 |  |  | Hypochlorite | 12 |  | 30
[76 empty] | TOTAL MGD: |  | 9.077 |  |  | FINISHED PERRY |  | START: | 30497328 |  | END: | 30506405 |  |  | Phosphate | 2235
[76 empty] | TOTAL MGD: |  | 9.822 |  |  | RAW PLANT 1 |  | START: | 28019873 |  | END: | 28029695 |  |  | Fluoride | 1250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.746 |  |  | RAW PLANT 2 |  | START: | 27966974 |  | END: | 27976720 |  |  | Cal~Flo | 13.64 | 0 | 0 | 12.42 | 1027.24 | 25
[76 empty] | TOTAL MGD: |  | 5.275 |  |  | RAW PLANT 3 |  | START: | 4275505 |  | END: | 4280780 |  |  | Zinc | 3202
[76 empty] | TOTAL MGD: |  | 1.299 |  |  | DECANT |  | START: | 1402119 |  | END: | 1403418 |  |  | Polymer | 10 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.73948 |  |  | BLOW DOWN |  | START: | 8769.9885 |  | END: | 8770.7279 |  |  | NH3 | 10.73
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 700
[90 empty] | BI-SULFITE | 850 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2134 | Phosphate | 40
[90 empty] | Caustic 1 | 133 | Fluoride | 48
[90 empty] | Caustic 2 | 73 | Zinc | 7
[90 empty] | Hypochlorite 1 | 346 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 680 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23154035
[91 empty] | FINISHED SOUTH 2 |  | END: | 41020925
[91 empty] | FINISHED CONWAY |  | END: | 8753895
[91 empty] | FINISHED PERRY |  | END: | 30506405
[91 empty] | RAW PLANT 1 |  | END: | 28029695
[91 empty] | RAW PLANT 2 |  | END: | 27976720
[91 empty] | RAW PLANT 3 |  | END: | 4280780
[91 empty] | DECANT |  | END: | 1403418
[91 empty] | BLOW DOWN |  | END: | 8770.7279
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 22
DATE: | 2018-02-22 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-22 | [23 empty] | DATE: | 2018-02-22
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-22 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43153.0141 | 2,3,5 | 52 | 11 | 11 | 6 | 28 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 11.0952 | 1 | 14.3093 | 25.4045 | 1.2931 | 43153.0141 | 55.0122 | 2643.9578 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.712 | 1.712 | 1.712 | 0.20226 | 0.20226 | 0.18151 | 0.18151 | 0.20917 | 0.2377 | 1.5218 | 1.5 | 0.060874 | 0.060874 | 0.060874 | 1.12 | 0.49975 | 0.09262 | 4.1037 | 0.76029 | 7.4816 | 1.12 | 0.38869 | 0.11114 | 3.1942 | 0.59654 | 7.4816 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.31 | 3 | 0.52 | 17.2 | 11.4 | 0.56811 |  | 6.02 | 0.32 | 3 | 0.57 | 17.1 | 11.3 | 0.56418 | 6.05 | 0.44 | 4 | 0.71 | 18.1 | 6.1 | 0.34593 | [13 empty] | 7.07 | 0.047 | 1 | 3.4 | 16.2 |  |  |  | 7.1 | 0.048 | 1 | 3.4 | 16.3 |  |  |  | 3.7 | 3.3 | 3.4 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 390 | 390 | 350 | 350 | 220 | 250 | 800 |  | 900 | 900 | 900 | 76 | 90 | 10 | 1270 | 260 | 400 | 38 | 35 | 6 | 500 | 102 | 200 |  | 1:00 | 0.52 | 11.4 | 22.3158 | 11.6042 | 6.01 | 17.2 | 10 | 1.1604 | 15 | 6.5 | 0.44811 | 1:00 | 0.57 | 11.3 | 22.5133 | 12.8326 | 6.02 | 17.1 | 10 | 1.2833 | 15 | 6.5 | 0.44418 | 1:00 | 0.71 | 6.1 | 44.2623 | 31.4262 | 6.05 | 18.1 | 10 | 3.1426 | 15 | 6.5 | 0.22593
2:00 | [72 empty] | 43153.3342 | 2,3,5 | 60 | 11 | 11 | 6 | 28 | 8.8 | 8.8 | 8.8 | 26.4 | 7,1 | 8.2584 | 1,2 | 16.5312 | 24.7896 | 1.6612 | 43153.3342 | 55.1869 | 2828 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5933 | 1.5175 | 1.6692 | 0.19707 | 0.18151 | 0.17114 | 0.1867 | 0.2377 | 0.19016 | 1.2365 | 1.5 | 0.059952 | 0.059952 | 0.06295 | 1.0972 | 0.50202 | 0.098514 | 3.9418 | 0.76461 | 5.8025 | 1.0972 | 0.40358 | 0.098514 | 3.2192 | 0.49246 | 7.4603 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.61 | 22 | 18 | 9.01 | 56 | 112 | 17.5 | 0.281 |  | 5.95 | 10 | 0.06 | 5.98 | 10 |  | 5.96 | 10 | [8 empty] | 0.047 | [14 empty] | 0.029 | 1 | 0.38 |  | 0.045 | 0.032 | 1 | 0.35 |  | 0.04 | 1 | 0.42 | [38 empty] | 6320 | [6 empty] | 0 | 0 | 0 | 315 | 300 | 330 | 380 | 350 | 330 | 360 | 250 | 200 | 650 |  | 1000 | 1000 | 1050 | 84 | 102 | 12 | 1380 | 295 | 350 | 42 | 41 | 6 | 540 | 95 | 225 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43153.8387 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.3427 | 1,2 | 15.1085 | 24.4512 | 1.967 | 43153.8387 | 55.0122 | 2643.9578 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.19016 | 0.17748 | 0.17748 | 0.17748 | 0.19016 | 0.15846 | 1.2365 | 1.5 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.0931 | 0.75671 | 7.552 | 1.0818 | 0.50955 | 0.10199 | 3.176 | 0.53668 | 7.7236 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.02 | 0.048 | 1 | 3.5 | 16.3 |  |  |  | 7.16 | 0.051 | 1 | 3.4 | 16.2 |  |  |  | 3.4 | 3.6 | 3.4 | [18 empty] | 6075 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 300 | 250 | 650 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1380 | 282 | 440 | 40 | 50 | 6 | 480 | 100 | 225 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.6 | 20 | 17 | 8.45 | 60 | 113 | 16.8 | 0.293 |  | 5.92 | 10 | 0.055 | 5.93 | 10 |  | 5.98 | 10 | [8 empty] | 0.046 | [14 empty] | 0.033 | 1 | 0.023 |  | 0.043 | 0.034 | 1 | 0.34 |  | 0.042 | 1 | 0.46 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.07 | 0.512 | 7 | 0.48 | 16.7 | 11.1 | 0.55632 |  | 6.08 | 0.592 | 5 | 0.46 | 16.5 | 11.1 | 0.55632 | 6.08 | 0.569 | 4 | 0.6 | 17.7 | 6 | 0.34222 |  |  |  | 0.017 | [9 empty] | 7.1 | 0.064 | 1 | 4.3 | 16 | 23 | 34 | 0.017 | 7.28 | 0.057 | 2 | 3.5 | 15.7 | 28 | 34 | 0.02 | 3.5 | 3.6 | 3.4 | [55 empty] | 9:00 | 0.48 | 11.1 | 22.9189 | 11.0011 | 6.07 | 16.7 | 10 | 1.1001 | 15 | 6.5 | 0.43632 | 9:00 | 0.46 | 11.1 | 22.9189 | 10.5427 | 6.08 | 16.5 | 10 | 1.0543 | 15 | 6.5 | 0.43632 | 9:00 | 0.6 | 6 | 45 | 27 | 6.08 | 17.7 | 10 | 2.7 | 15 | 6.5 | 0.22222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.67 | 24 | 20 | 8.64 | 70 | 115 | 16.8 | 0.307 |  | 5.91 | 10 | 0.053 | 5.93 | 10 |  | 6.01 | 10 | [8 empty] | 0.044 | [14 empty] | 0.038 | 1 | 0.29 |  | 0.046 | 0.05 | 1 | 0.37 |  | 0.054 | 1 | 0.57 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.95 | 0.576 | 4 | 0.56 | 17.6 | 11.1 | 0.46906 |  | 6.05 | 0.495 | 4 | 0.52 | 17.4 | 11.1 | 0.55632 | 6.09 | 0.419 | 4 | 0.89 | 18 | 6 | 0.34222 | [13 empty] | 7.01 | 0.065 | 1 | 4.1 | 16.7 |  |  |  | 7.36 | 0.057 | 1 | 3.4 | 17 |  |  |  | 3.5 | 3.3 | 3.5 | [55 empty] | 13:00 | 0.56 | 11.1 | 22.9189 | 12.8346 | 5.95 | 17.6 | 8 | 1.6043 | 15 | 6 | 0.34906 | 13:00 | 0.52 | 11.1 | 22.9189 | 11.9178 | 6.05 | 17.4 | 10 | 1.1918 | 15 | 6.5 | 0.43632 | 13:00 | 0.89 | 6 | 45 | 40.05 | 6.09 | 18 | 10 | 4.005 | 15 | 6.5 | 0.22222
14:00 | [126 empty] | 242 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.61 | 24 | 20 | 8.08 | 58 | 111 | 17.1 | 0.308 |  | 5.96 | 10 | 0.052 | 5.98 | 10 |  | 5.99 | 10 | [8 empty] | 0.041 | [14 empty] | 0.036 | 1 | 0.28 |  | 0.041 | 0.041 | 1 | 0.5 |  | 0.061 | 1 | 0.6 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 6.97 | 0.064 | 1 | 4 | 16.7 |  |  |  | 7.27 | 0.064 | 1 | 3.9 | 16.3 |  |  |  | 3.5 | 3.3 | 3.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 25 | 20 | 7.79 | 55 | 106 | 18 | 0.278 |  | 5.98 | 10 | 0.055 | 5.96 | 10 |  | 5.97 | 10 | [8 empty] | 0.042 | [14 empty] | 0.034 | 1 | 0.34 |  | 0.042 | 0.045 | 1 | 0.56 |  | 0.056 | 1 | 0.69 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.042 | [9 empty] | 6.1 | 0.288 | 3 | 0.54 | 18 | 9 | 0.47377 |  | 6.08 | 0.215 | 3 | 0.65 | 18 | 9 | 0.47377 | 6.09 | 0.43 | 4 | 0.79 | 18 | 9 | 0.45333 |  |  |  | 0.014 | [9 empty] | 7.15 | 0.055 | 1 | 3.7 | 16.6 | 24 | 29 | 0.018 | 7.34 | 0.057 | 1 | 3.6 | 16.7 | 21 | 31 | 0.013 | 3.5 | 3.3 | 3.3 | [55 empty] | 21:00 | 0.54 | 9 | 28.2667 | 15.264 | 6.1 | 18 | 10 | 1.5264 | 15 | 6.5 | 0.35377 | 21:00 | 0.65 | 9 | 28.2667 | 18.3733 | 6.08 | 18 | 10 | 1.8373 | 15 | 6.5 | 0.35377 | 21:00 | 0.79 | 9 | 30 | 23.7 | 6.09 | 18 | 10 | 2.37 | 15 | 6.5 | 0.33333
22:00 | [72 empty] | DOSE |  | TOTAL | 31 | 31 | 21 | 83 | 25.1 | 25.1 | 25.1 | 75.3 | 0 | 28.6963 | 1 | 45.949 | 74.6453 | 4.9213 | TOTAL | 165.2113 | 8115.9156 | 0 | 2100 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.8764 | 4.8005 | 4.9523 | 0.58948 | 0.56125 | 0.53013 | 0.54569 | 0.63702 | 0.58632 | 3.9947 | 4.5 | 0.17979 | 0.17979 | 0.18279 | 3.2989 | 1.5011 | 0.29312 | 12.1386 | 2.2816 | 20.8361 | 3.2989 | 1.3018 | 0.31165 | 9.5895 | 1.6257 | 22.6655 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.61 | 23 | 19 | 8.75 | 57 | 112 | 17.9 | 0.273 |  | 5.96 | 11 | 0.062 | 5.97 | 10 |  | 5.94 | 11 | [8 empty] | 0.044 | [14 empty] | 0.029 | 1 | 0.27 |  | 0.041 | 0.04 | 1 | 0.46 |  | 0.049 | 1 | 0.52 | [22 empty] | AVERAGE | 10.3333 | 10.3333 | 7 | 27.6667 | 8.3667 | 8.3667 | 8.3667 | 25.1 |  | 9.5654 | 1 | 15.3163 | 24.8818 | 1.6404 | AVERAGE | 55.0704 | 2705.3052 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.6255 | 1.6002 | 1.6508 | 0.19649 | 0.18708 | 0.17671 | 0.1819 | 0.21234 | 0.19544 | 1.3316 | 1.5 | 0.05993 | 0.05993 | 0.06093 | 1.0996 | 0.50037 | 0.097708 | 4.0462 | 0.76054 | 6.9454 | 1.0996 | 0.43394 | 0.10388 | 3.1965 | 0.54189 | 7.5552 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.72 | 138 | 114 | 50.72 | 356 | 669 | 104.1 | 1.74 | 0.083 | 35.68 | 61 | 0.337 | 35.75 | 60 | 0 | 35.85 | 61 | 0 | 24.13 | 1.686 | 17 | 2.1 | 69.5 | 42.6 | 2.0673 | 0.264 | 24.23 | 1.622 | 15 | 2.2 | 69 | 42.5 | 2.1506 | 24.31 | 1.858 | 16 | 2.99 | 71.8 | 27.1 | 1.4837 | 0.199 | 6 | 1.583 | 0.031 | 0.258 | 0.242 | 6 | 2.58 | 0 | 0.302 | 6 | 3.26 | 0 | 42.32 | 0.343 | 6 | 23 | 98.5 | 47 | 63 | 0.035 | 43.51 | 0.334 | 7 | 21.2 | 98.2 | 49 | 65 | 0.033 | 21.1 | 20.4 | 20.7 |  |  | MINIMUM | 9 | 9 | 6 | 27 | 7.8 | 7.8 | 7.8 | 23.4 |  | 8.2584 | 1 | 14.3093 | 24.4512 | 1.2931 | MINIMUM | 55.0122 | 2643.9578 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.5175 | 1.571 | 0.19016 | 0.17748 | 0.17114 | 0.17748 | 0.19016 | 0.15846 | 1.2365 | 1.5 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.09262 | 3.9418 | 0.75671 | 5.8025 | 1.0818 | 0.38869 | 0.098514 | 3.176 | 0.49246 | 7.4603 |  | MIN | 0.48 | 11.1 | 22.9189 | 11.0011 | 6.07 | 16.7 | 10 | 1.1001 |  |  |  | MIN | 0.46 | 11.1 | 22.9189 | 10.5427 | 6.08 | 16.5 | 10 | 1.0543 |  |  |  | MIN | 0.79 | 9 | 30 | 23.7 | 6.09 | 18 | 10 | 2.37 |  |  |  | 1.0543
AVERAGE | 6.62 | 23 | 19 | 8.4533 | 59.3333 | 111.5 | 17.35 | 0.29 | 0.0415 | 5.9467 | 10.1667 | 0.056167 | 5.9583 | 10 |  | 5.975 | 10.1667 |  | 6.0325 | 0.4215 | 4.25 | 0.525 | 17.375 | 10.65 | 0.51682 | 0.044 | 6.0575 | 0.4055 | 3.75 | 0.55 | 17.25 | 10.625 | 0.53765 | 6.0775 | 0.4645 | 4 | 0.7475 | 17.95 | 6.775 | 0.37093 | 0.033167 | 1 | 0.26383 | 0.0155 | 0.043 | 0.040333 | 1 | 0.43 |  | 0.050333 | 1 | 0.54333 |  | 7.0533 | 0.057167 | 1 | 3.8333 | 16.4167 | 23.5 | 31.5 | 0.0175 | 7.2517 | 0.055667 | 1.1667 | 3.5333 | 16.3667 | 24.5 | 32.5 | 0.0165 | 3.5167 | 3.4 | 3.45 |  |  | MAXIMUM | 11 | 11 | 9 | 28 | 8.8 | 8.8 | 8.8 | 26.4 |  | 11.0952 | 1 | 16.5312 | 25.4045 | 1.967 | MAXIMUM | 55.1869 | 2828 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.712 | 1.712 | 1.712 | 0.20226 | 0.20226 | 0.18151 | 0.1867 | 0.2377 | 0.2377 | 1.5218 | 1.5 | 0.060874 | 0.060874 | 0.06295 | 1.12 | 0.50202 | 0.10199 | 4.1037 | 0.76461 | 7.552 | 1.12 | 0.50955 | 0.11114 | 3.2192 | 0.59654 | 7.7236
MINIMUM | 6.6 | 20 | 17 | 7.79 | 55 | 106 | 16.8 | 0.273 | 0.041 | 5.91 | 10 | 0.052 | 5.93 | 10 |  | 5.94 | 10 |  | 5.95 | 0.288 | 3 | 0.48 | 16.7 | 9 | 0.46906 | 0.041 | 6.02 | 0.215 | 3 | 0.46 | 16.5 | 9 | 0.47377 | 6.05 | 0.419 | 4 | 0.6 | 17.7 | 6 | 0.34222 | 0.029 | 1 | 0.023 | 0.014 | 0.041 | 0.032 | 1 | 0.34 |  | 0.04 | 1 | 0.42 |  | 6.97 | 0.047 | 1 | 3.4 | 16 | 23 | 29 | 0.017 | 7.1 | 0.048 | 1 | 3.4 | 15.7 | 21 | 31 | 0.013 | 3.4 | 3.3 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 18695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915 | 900 | 930 | 1070 | 1020 | 960 | 990 | 770 | 700 | 2100 | 0 | 2850 | 2850 | 2900 | 240 | 290 | 34 | 4030 | 837 | 1190 | 120 | 126 | 18 | 1520 | 297 | 650
MAXIMUM | 6.67 | 25 | 20 | 9.01 | 70 | 115 | 18 | 0.308 | 0.042 | 5.98 | 11 | 0.062 | 5.98 | 10 |  | 6.01 | 11 |  | 6.1 | 0.576 | 7 | 0.56 | 18 | 11.4 | 0.56811 | 0.047 | 6.08 | 0.592 | 5 | 0.65 | 18 | 11.3 | 0.56418 | 6.09 | 0.569 | 4 | 0.89 | 18.1 | 9 | 0.45333 | 0.038 | 1 | 0.38 | 0.017 | 0.046 | 0.05 | 1 | 0.56 |  | 0.061 | 1 | 0.69 |  | 7.15 | 0.065 | 1 | 4.3 | 16.7 | 24 | 34 | 0.018 | 7.36 | 0.064 | 2 | 3.9 | 17 | 28 | 34 | 0.02 | 3.7 | 3.6 | 3.7 | [17 empty] | AVERAGE | 6231.6667 | [9 empty] | 305 | 300 | 310 | 356.6667 | 340 | 320 | 330 | 256.6667 | 233.3333 | 700 |  | 950 | 950 | 966.6667 | 80 | 96.6667 | 11.3333 | 1343.3333 | 279 | 396.6667 | 40 | 42 | 6 | 506.6667 | 99 | 216.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.96 |  | TOTAL AVG COAG ALK: |  |  |  | 10.1111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.592 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.0558 |  |  |  |  | 0.061 |  |  |  |  | 0.46 | [6 empty] | 0.061 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 6075 | [9 empty] | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 220 | 200 | 650 |  | 900 | 900 | 900 | 76 | 90 | 10 | 1270 | 260 | 350 | 38 | 35 | 6 | 480 | 95 | 200
[90 empty] | MAXIMUM | 6320 | [9 empty] | 315 | 300 | 330 | 390 | 390 | 350 | 360 | 300 | 250 | 800 |  | 1000 | 1000 | 1050 | 84 | 102 | 12 | 1380 | 295 | 440 | 42 | 50 | 6 | 540 | 102 | 225
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.76 |  | TOTAL MGD: |  | 5.73 |  |  | FINISHED SOUTH 1 |  | START: | 23154035 |  | END: | 23159765 |  |  | Alum | 10500 |  | 10900 |  | 0 | [45 empty] | 0.46 | 11.1 | 22.9189 | 10.5427 | 6.08 | 16.5 | 10 | 1.0543
[73 empty] | FINISHED 2 | 14.16 |  | TOTAL MGD: |  | 6.03 |  |  | FINISHED SOUTH 2 |  | START: | 41020925 |  | END: | 41026955 |  |  | Caustic | 5868 |  | 4340
[73 empty] | TOTAL RAW | 28.185 |  | TOTAL MGD: |  | 4.48 |  |  | FINISHED CONWAY |  | START: | 8753895 |  | END: | 8758375 |  |  | Hypochlorite | 10.5 |  | 28
[76 empty] | TOTAL MGD: |  | 9.68 |  |  | FINISHED PERRY |  | START: | 30506405 |  | END: | 30516085 |  |  | Phosphate | 2222
[76 empty] | TOTAL MGD: |  | 10.895 |  |  | RAW PLANT 1 |  | START: | 28029695 |  | END: | 28040590 |  |  | Fluoride | 850 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.78 |  |  | RAW PLANT 2 |  | START: | 27976720 |  | END: | 27987500 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 6.51 |  |  | RAW PLANT 3 |  | START: | 4280780 |  | END: | 4287290 |  |  | Zinc | 3193
[76 empty] | TOTAL MGD: |  | 1.793 |  |  | DECANT |  | START: | 1403418 |  | END: | 1405211 |  |  | Polymer | 12 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.99554 |  |  | BLOW DOWN |  | START: | 8770.7279 |  | END: | 8771.7235 |  |  | NH3 | 10.55
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 700
[90 empty] | BI-SULFITE | 850 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 3169 | Phosphate | 44
[90 empty] | Caustic 1 | 147 | Fluoride | 57
[90 empty] | Caustic 2 | 95 | Zinc | 8
[90 empty] | Hypochlorite 1 | 346 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 714 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23159765
[91 empty] | FINISHED SOUTH 2 |  | END: | 41026955
[91 empty] | FINISHED CONWAY |  | END: | 8758375
[91 empty] | FINISHED PERRY |  | END: | 30516085
[91 empty] | RAW PLANT 1 |  | END: | 28040590
[91 empty] | RAW PLANT 2 |  | END: | 27987500
[91 empty] | RAW PLANT 3 |  | END: | 4287290
[91 empty] | DECANT |  | END: | 1405211
[91 empty] | BLOW DOWN |  | END: | 8771.7235
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 23
DATE: | 2018-02-23 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-23 | [23 empty] | DATE: | 2018-02-23
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-23 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43154.0055 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.3427 | 1,2 | 15.1085 | 24.4512 | 1.2787 | 43154.0055 | 55.0122 | 2643.9578 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.19016 | 0.17748 | 0.17748 | 0.17748 | 0.19016 | 0.15846 | 0.99868 | 2 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.0931 | 0.75671 | 8.3244 | 1.0818 | 0.50955 | 0.10199 | 3.176 | 0.53668 | 7.7236 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.268 | 3 | 0.51 | 17.6 | 9.1 | 0.4777 |  | 6.04 | 0.195 | 3 | 0.62 | 17.6 | 9.2 | 0.48164 | 6.05 | 0.41 | 4 | 0.55 | 18.6 | 9.5 | 0.47185 | [13 empty] | 7.29 | 0.049 | 1 | 3.4 | 16.6 |  |  |  | 7.29 | 0.051 | 1 | 3.2 | 16.7 |  |  |  | 3.5 | 3.3 | 2.6 | [18 empty] | 6075 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 300 | 250 | 525 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1380 | 282 | 485 | 40 | 50 | 6 | 480 | 100 | 225 |  | 1:00 | 0.51 | 9.1 | 27.956 | 14.2576 | 6.01 | 17.6 | 10 | 1.4258 | 15 | 6.5 | 0.3577 | 1:00 | 0.62 | 9.2 | 27.6522 | 17.1443 | 6.04 | 17.6 | 10 | 1.7144 | 15 | 6.5 | 0.36164 | 1:00 | 0.55 | 9.5 | 28.4211 | 15.6316 | 6.05 | 18.6 | 10 | 1.5632 | 15 | 6.5 | 0.35185
2:00 | [72 empty] | 43154.3365 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.3427 | 1,2 | 15.1085 | 24.4512 | 1.9086 | 43154.3365 | 57.4119 | 2705.4452 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.5187 | 1.4663 | 1.571 | 0.20283 | 0.20283 | 0.19016 | 0.20283 | 0.19016 | 0.17748 | 0.80845 | 0 | 0.060827 | 0.060827 | 0.062068 | 1.0818 | 0.49935 | 0.10199 | 4.2141 | 0.75135 | 8.3244 | 1.1359 | 0.39745 | 0.10199 | 3.1634 | 0.53668 | 7.552 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.62 | 25 | 18 | 8.91 | 58 | 115 | 18 | 0.286 |  | 5.98 | 12 | 0.057 | 5.97 | 11 |  | 5.95 | 12 | [8 empty] | 0.042 | [14 empty] | 0.033 | 1 | 0.28 |  | 0.043 | 0.032 | 1 | 0.42 |  | 0.045 | 1 | 0.48 | [38 empty] | 6340 | [6 empty] | 0 | 0 | 0 | 290 | 280 | 300 | 320 | 320 | 300 | 320 | 300 | 280 | 425 |  | 980 | 980 | 1000 | 80 | 98 | 12 | 1440 | 280 | 485 | 42 | 39 | 6 | 500 | 100 | 220 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43154.8278 | 2,3,5 | 46 | 9.4 | 9.3 | 9.4 | 28.1 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 11.975 | 1,2 | 12.4272 | 24.4022 | 1.44 | 43154.8278 | 54.8165 | 2828.42 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.18206 | 0.18206 | 0.18402 | 0.18402 | 0.18206 | 0.18206 | 0.80845 | 1 | 0.060827 | 0.060827 | 0.060827 | 1.0818 | 0.50955 | 0.10199 | 4.2914 | 0.81038 | 8.5818 | 1.0818 | 0.50955 | 0.10199 | 3.1834 | 0.54741 | 7.552 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.32 | 0.054 | 1 | 3.8 | 16.8 |  |  |  | 7.37 | 0.056 | 1 | 3.3 | 16.7 |  |  |  | 3.6 | 3.2 | 2.8 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 425 |  | 980 | 980 | 980 | 80 | 100 | 12 | 1480 | 302 | 500 | 40 | 50 | 6 | 500 | 102 | 220 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.58 | 23 | 18 | 8.76 | 55 | 116 | 17.1 | 0.312 |  | 5.81 | 10 | 0.048 | 5.84 | 10 |  | 5.89 | 11 | [8 empty] | 0.044 | [14 empty] | 0.028 | 1 | 0.27 |  | 0.047 | 0.039 | 1 | 0.49 |  | 0.05 | 1 | 0.44 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.044 | [9 empty] | 6 | 0.232 | 3 | 0.53 | 17.1 | 9 | 0.40302 |  | 6.03 | 0.244 | 3 | 0.67 | 17 | 9 | 0.47377 | 6.04 | 0.281 | 3 | 0.76 | 18.1 | 9 | 0.45333 |  |  |  | 0.014 | [9 empty] | 7.76 | 0.061 | 1 | 4.6 | 16.8 | 27 | 37 | 0.017 | 7.84 | 0.057 | 2 | 4.1 | 16 | 28 | 34 | 0.017 | 3.7 | 3.2 | 3 | [55 empty] | 9:00 | 0.53 | 9 | 28.2667 | 14.9813 | 6 | 17.1 | 8 | 1.8727 | 15 | 6 | 0.28302 | 9:00 | 0.67 | 9 | 28.2667 | 18.9387 | 6.03 | 17 | 10 | 1.8939 | 15 | 6.5 | 0.35377 | 9:00 | 0.76 | 9 | 30 | 22.8 | 6.04 | 18.1 | 10 | 2.28 | 15 | 6.5 | 0.33333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.63 | 23 | 18 | 8.54 | 55 | 114 | 17.2 | 0.295 |  | 6.01 | 11 | 0.049 | 5.95 | 11 |  | 5.99 | 11 | [8 empty] | 0.046 | [14 empty] | 0.054 | 1 | 0.3 |  | 0.046 | 0.052 | 1 | 0.49 |  | 0.055 | 1 | 0.48 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.02 | 0.247 | 3 | 0.55 | 18 | 9 | 0.47377 |  | 6.03 | 0.249 | 3 | 0.71 | 17.8 | 9 | 0.47377 | 6.03 | 0.286 | 3 | 0.74 | 18.2 | 9 | 0.45333 | [13 empty] | 7.63 | 0.064 | 1 | 4.3 | 16.9 |  |  |  | 7.66 | 0.059 | 1 | 4.2 | 16.7 |  |  |  | 3.9 | 3.4 | 3 | [55 empty] | 13:00 | 0.55 | 9 | 28.2667 | 15.5467 | 6.02 | 18 | 10 | 1.5547 | 15 | 6.5 | 0.35377 | 13:00 | 0.71 | 9 | 28.2667 | 20.0693 | 6.03 | 17.8 | 10 | 2.0069 | 15 | 6.5 | 0.35377 | 13:00 | 0.74 | 9 | 30 | 22.2 | 6.03 | 18.2 | 10 | 2.22 | 15 | 6.5 | 0.33333
14:00 | [126 empty] | 281 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.58 | 23 | 19 | 8.81 | 57 | 114 | 17.5 | 0.299 |  | 5.99 | 11 | 0.047 | 5.96 | 11 |  | 6.03 | 11 | [8 empty] | 0.04 | [14 empty] | 0.053 | 1 | 0.24 |  | 0.045 | 0.044 | 1 | 0.4 |  | 0.053 | 1 | 0.5 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.79 | 0.055 | 1 | 4.4 | 16.9 |  |  |  | 7.69 | 0.066 | 1 | 4.2 | 16.8 |  |  |  | 3.6 | 3.2 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 24 | 20 | 8.5 | 56 | 112 | 18 | 0.291 |  | 5.96 | 12 | 0.061 | 5.97 | 12 |  | 5.97 | 12 | [8 empty] | 0.045 | [14 empty] | 0.05 | 1 | 0.32 |  | 0.049 | 0.038 | 1 | 0.48 |  | 0.053 | 1 | 0.54 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.045 | [9 empty] | 6.07 | 0.237 | 3 | 0.47 | 18 | 9.4 | 0.4895 |  | 6.03 | 0.264 | 3 | 0.59 | 18 | 9.3 | 0.48557 | 6.04 | 0.321 | 3 | 0.86 | 18.5 | 9.4 | 0.46815 |  |  |  | 0.014 | [9 empty] | 7.64 | 0.054 | 1 | 4 | 17.1 | 25 | 28 | 0.019 | 7.58 | 0.056 | 1 | 3.7 | 17.1 | 23 | 29 | 0.018 | 3.7 | 3.4 | 2.9 | [55 empty] | 21:00 | 0.47 | 9.4 | 27.0638 | 12.72 | 6.07 | 18 | 10 | 1.272 | 15 | 6.5 | 0.3695 | 21:00 | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.03 | 18 | 10 | 1.6139 | 15 | 6.5 | 0.36557 | 21:00 | 0.86 | 9.4 | 28.7234 | 24.7021 | 6.04 | 18.5 | 10 | 2.4702 | 15 | 6.5 | 0.34815
22:00 | [72 empty] | DOSE |  | TOTAL | 27.4 | 27.3 | 27.4 | 82.1 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 30.6605 | 0 | 42.6442 | 73.3046 | 4.6273 | TOTAL | 167.2406 | 8177.823 | 0 | 2100 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.6607 | 4.6084 | 4.7131 | 0.57505 | 0.56238 | 0.55166 | 0.56433 | 0.56238 | 0.51801 | 2.6156 | 3 | 0.18062 | 0.18062 | 0.18186 | 3.2454 | 1.5083 | 0.30597 | 12.5985 | 2.3184 | 25.2305 | 3.2995 | 1.4165 | 0.30597 | 9.5228 | 1.6208 | 22.8276 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.67 | 22 | 21 | 8.3 | 57 | 113 | 18.2 | 0.283 |  | 5.98 | 13 | 0.056 | 5.94 | 12 |  | 6.02 | 12 | [8 empty] | 0.046 | [14 empty] | 0.048 | 1 | 0.26 |  | 0.045 | 0.04 | 1 | 0.38 |  | 0.05 | 1 | 0.36 | [22 empty] | AVERAGE | 9.1333 | 9.1 | 9.1333 | 27.3667 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.2202 |  | 14.2147 | 24.4349 | 1.5424 | AVERAGE | 55.7469 | 2725.941 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.5536 | 1.5361 | 1.571 | 0.19168 | 0.18746 | 0.18389 | 0.18811 | 0.18746 | 0.17267 | 0.87186 | 1 | 0.060206 | 0.060206 | 0.06062 | 1.0818 | 0.50275 | 0.10199 | 4.1995 | 0.77281 | 8.4102 | 1.0998 | 0.47218 | 0.10199 | 3.1743 | 0.54025 | 7.6092 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.7 | 140 | 114 | 51.82 | 338 | 684 | 106 | 1.766 | 0.089 | 35.73 | 69 | 0.318 | 35.63 | 67 | 0 | 35.85 | 69 | 0 | 24.1 | 0.984 | 12 | 2.06 | 70.7 | 36.5 | 1.844 | 0.263 | 24.13 | 0.952 | 12 | 2.59 | 70.4 | 36.5 | 1.9147 | 24.16 | 1.298 | 13 | 2.91 | 73.4 | 36.9 | 1.8467 | 0.266 | 6 | 1.67 | 0.028 | 0.275 | 0.245 | 6 | 2.66 | 0 | 0.306 | 6 | 2.8 | 0 | 45.43 | 0.337 | 6 | 24.5 | 101.1 | 52 | 65 | 0.036 | 45.43 | 0.345 | 7 | 22.7 | 100 | 51 | 63 | 0.035 | 22 | 19.7 | 17 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.3427 |  | 12.4272 | 24.4022 | 1.2787 | MINIMUM | 54.8165 | 2643.9578 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.5187 | 1.4663 | 1.571 | 0.18206 | 0.17748 | 0.17748 | 0.17748 | 0.18206 | 0.15846 | 0.80845 | 0 | 0.058965 | 0.058965 | 0.058965 | 1.0818 | 0.49935 | 0.10199 | 4.0931 | 0.75135 | 8.3244 | 1.0818 | 0.39745 | 0.10199 | 3.1634 | 0.53668 | 7.552 |  | MIN | 0.47 | 9.4 | 27.0638 | 12.72 | 6.07 | 18 | 10 | 1.272 |  |  |  | MIN | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.03 | 18 | 10 | 1.6139 |  |  |  | MIN | 0.55 | 9.5 | 28.4211 | 15.6316 | 6.05 | 18.6 | 10 | 1.5632 |  |  |  | 1.272
AVERAGE | 6.6167 | 23.3333 | 19 | 8.6367 | 56.3333 | 114 | 17.6667 | 0.29433 | 0.0445 | 5.955 | 11.5 | 0.053 | 5.9383 | 11.1667 |  | 5.975 | 11.5 |  | 6.025 | 0.246 | 3 | 0.515 | 17.675 | 9.125 | 0.461 | 0.043833 | 6.0325 | 0.238 | 3 | 0.6475 | 17.6 | 9.125 | 0.47869 | 6.04 | 0.3245 | 3.25 | 0.7275 | 18.35 | 9.225 | 0.46167 | 0.044333 | 1 | 0.27833 | 0.014 | 0.045833 | 0.040833 | 1 | 0.44333 |  | 0.051 | 1 | 0.46667 |  | 7.5717 | 0.056167 | 1 | 4.0833 | 16.85 | 26 | 32.5 | 0.018 | 7.5717 | 0.0575 | 1.1667 | 3.7833 | 16.6667 | 25.5 | 31.5 | 0.0175 | 3.6667 | 3.2833 | 2.8333 |  |  | MAXIMUM | 9.4 | 9.3 | 9.4 | 28.1 | 8.5 | 8.5 | 8.5 | 25.5 |  | 11.975 |  | 15.1085 | 24.4512 | 1.9086 | MAXIMUM | 57.4119 | 2828.42 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.571 | 1.571 | 0.20283 | 0.20283 | 0.19016 | 0.20283 | 0.19016 | 0.18206 | 0.99868 | 2 | 0.060827 | 0.060827 | 0.062068 | 1.0818 | 0.50955 | 0.10199 | 4.2914 | 0.81038 | 8.5818 | 1.1359 | 0.50955 | 0.10199 | 3.1834 | 0.54741 | 7.7236
MINIMUM | 6.58 | 22 | 18 | 8.3 | 55 | 112 | 17.1 | 0.283 | 0.044 | 5.81 | 10 | 0.047 | 5.84 | 10 |  | 5.89 | 11 |  | 6 | 0.232 | 3 | 0.47 | 17.1 | 9 | 0.40302 | 0.04 | 6.03 | 0.195 | 3 | 0.59 | 17 | 9 | 0.47377 | 6.03 | 0.281 | 3 | 0.55 | 18.1 | 9 | 0.45333 | 0.028 | 1 | 0.24 | 0.014 | 0.043 | 0.032 | 1 | 0.38 |  | 0.045 | 1 | 0.36 |  | 7.29 | 0.049 | 1 | 3.4 | 16.6 | 25 | 28 | 0.017 | 7.29 | 0.051 | 1 | 3.2 | 16 | 23 | 29 | 0.017 | 3.5 | 3.2 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 18715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890 | 880 | 900 | 920 | 900 | 880 | 900 | 900 | 830 | 1375 | 0 | 2910 | 2910 | 2930 | 240 | 296 | 36 | 4300 | 864 | 1470 | 122 | 139 | 18 | 1480 | 302 | 665
MAXIMUM | 6.67 | 25 | 21 | 8.91 | 58 | 116 | 18.2 | 0.312 | 0.045 | 6.01 | 13 | 0.061 | 5.97 | 12 |  | 6.03 | 12 |  | 6.07 | 0.268 | 3 | 0.55 | 18 | 9.4 | 0.4895 | 0.046 | 6.04 | 0.264 | 3 | 0.71 | 18 | 9.3 | 0.48557 | 6.05 | 0.41 | 4 | 0.86 | 18.6 | 9.5 | 0.47185 | 0.054 | 1 | 0.32 | 0.014 | 0.049 | 0.052 | 1 | 0.49 |  | 0.055 | 1 | 0.54 |  | 7.79 | 0.064 | 1 | 4.6 | 17.1 | 27 | 37 | 0.019 | 7.84 | 0.066 | 2 | 4.2 | 17.1 | 28 | 34 | 0.018 | 3.9 | 3.4 | 3 | [17 empty] | AVERAGE | 6238.3333 | [9 empty] | 296.6667 | 293.3333 | 300 | 306.6667 | 300 | 293.3333 | 300 | 300 | 276.6667 | 458.3333 |  | 970 | 970 | 976.6667 | 80 | 98.6667 | 12 | 1433.3333 | 288 | 490 | 40.6667 | 46.3333 | 6 | 493.3333 | 100.6667 | 221.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9561 |  | TOTAL AVG COAG ALK: |  |  |  | 11.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.41 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.0325 |  |  |  |  | 0.055 |  |  |  |  | 0.47 | [6 empty] | 0.055 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 6075 | [9 empty] | 290 | 280 | 300 | 300 | 280 | 280 | 280 | 300 | 250 | 425 |  | 950 | 950 | 950 | 80 | 98 | 12 | 1380 | 280 | 485 | 40 | 39 | 6 | 480 | 100 | 220
[90 empty] | MAXIMUM | 6340 | [9 empty] | 300 | 300 | 300 | 320 | 320 | 300 | 320 | 300 | 300 | 525 |  | 980 | 980 | 1000 | 80 | 100 | 12 | 1480 | 302 | 500 | 42 | 50 | 6 | 500 | 102 | 225
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.31 |  | TOTAL MGD: |  | 5.44 |  |  | FINISHED SOUTH 1 |  | START: | 23159765 |  | END: | 23165205 |  |  | Alum | 9798 |  | 10200 |  | 0 | [45 empty] | 0.47 | 9.4 | 27.0638 | 12.72 | 6.07 | 18 | 10 | 1.272
[73 empty] | FINISHED 2 | 13.55 |  | TOTAL MGD: |  | 5.87 |  |  | FINISHED SOUTH 2 |  | START: | 41026955 |  | END: | 41032825 |  |  | Caustic | 5682 |  | 4233
[73 empty] | TOTAL RAW | 27.575 |  | TOTAL MGD: |  | 4.2 |  |  | FINISHED CONWAY |  | START: | 8758375 |  | END: | 8762575 |  |  | Hypochlorite | 14 |  | 34.5
[76 empty] | TOTAL MGD: |  | 9.35 |  |  | FINISHED PERRY |  | START: | 30516085 |  | END: | 30525435 |  |  | Phosphate | 2149
[76 empty] | TOTAL MGD: |  | 9.17 |  |  | RAW PLANT 1 |  | START: | 28040590 |  | END: | 28049760 |  |  | Fluoride | 750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.095 |  |  | RAW PLANT 2 |  | START: | 27987500 |  | END: | 27996595 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 9.31 |  |  | RAW PLANT 3 |  | START: | 4287290 |  | END: | 4296600 |  |  | Zinc | 3194
[76 empty] | TOTAL MGD: |  | 1.501 |  |  | DECANT |  | START: | 1405211 |  | END: | 1406712 |  |  | Polymer | 12 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.85647 |  |  | BLOW DOWN |  | START: | 8771.7235 |  | END: | 8772.5799 |  |  | NH3 | 10.35
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2363 | Phosphate | 58
[90 empty] | Caustic 1 | 184 | Fluoride | 58
[90 empty] | Caustic 2 | 97 | Zinc | 8
[90 empty] | Hypochlorite 1 | 346 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 760 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23165205
[91 empty] | FINISHED SOUTH 2 |  | END: | 41032825
[91 empty] | FINISHED CONWAY |  | END: | 8762575
[91 empty] | FINISHED PERRY |  | END: | 30525435
[91 empty] | RAW PLANT 1 |  | END: | 28049760
[91 empty] | RAW PLANT 2 |  | END: | 27996595
[91 empty] | RAW PLANT 3 |  | END: | 4296600
[91 empty] | DECANT |  | END: | 1406712
[91 empty] | BLOW DOWN |  | END: | 8772.5799
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 24
DATE: | 2018-02-24 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 20 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 20 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 20
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-24 | [23 empty] | DATE: | 2018-02-24
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-24 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43155.0029 | 2,3,5 | 46 | 9.4 | 9.3 | 9.4 | 28.1 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 11.975 | 1,2 | 12.4272 | 24.4022 | 1.1693 | 43155.0029 | 54.8165 | 2828.42 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.18206 | 0.18206 | 0.18402 | 0.18402 | 0.18206 | 0.18206 | 0.80845 | 1 | 0.060827 | 0.060827 | 0.060827 | 1.0818 | 0.50955 | 0.10199 | 4.2914 | 0.81038 | 8.5818 | 1.0818 | 0.50955 | 0.10199 | 3.1834 | 0.54741 | 7.552 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.269 | 3 | 0.53 | 17.9 | 9.3 | 0.48557 |  | 6.07 | 0.213 | 3 | 0.63 | 17.9 | 9.4 | 0.4895 | 6.04 | 0.389 | 3 | 0.64 | 18.8 | 9.6 | 0.47556 | [13 empty] | 7.48 | 0.051 | 1 | 3.7 | 17.1 |  |  |  | 7.41 | 0.053 | 1 | 3.4 | 16.4 |  |  |  | 3.7 | 3.5 | 3.3 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 425 |  | 980 | 980 | 980 | 80 | 100 | 12 | 1480 | 302 | 500 | 40 | 50 | 6 | 500 | 102 | 220 |  | 1:00 | 0.53 | 9.3 | 27.3548 | 14.4981 | 6.06 | 17.9 | 10 | 1.4498 | 15 | 6.5 | 0.36557 | 1:00 | 0.63 | 9.4 | 27.0638 | 17.0502 | 6.07 | 17.9 | 10 | 1.705 | 15 | 6.5 | 0.3695 | 1:00 | 0.64 | 9.6 | 28.125 | 18 | 6.04 | 18.8 | 10 | 1.8 | 15 | 6.5 | 0.35556
2:00 | [72 empty] | 43155.3528 | 2,3,5 | 42 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 11.975 | 1,2 | 12.4272 | 24.4022 | 0 | 43155.3528 | 57.4119 | 2766.9326 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.4663 | 1.6758 | 0.21551 | 0.20283 | 0.20283 | 0.21551 | 0.19016 | 0.1648 | 0.80845 | 2 | 0.060827 | 0.060206 | 0.059585 | 1.1089 | 0.49935 | 0.10199 | 4.2982 | 0.81843 | 8.5818 | 1.0818 | 0.39745 | 0.10199 | 3.2107 | 0.59034 | 7.552 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.63 | 24 | 20 | 8.24 | 60 | 115 | 18.2 | 0.3 |  | 5.99 | 12 | 0.06 | 5.98 | 12 |  | 6 | 12 | [8 empty] | 0.045 | [14 empty] | 0.038 | 1 | 0.24 |  | 0.044 | 0.04 | 1 | 0.36 |  | 0.044 | 1 | 0.42 | [38 empty] | 6340 | [6 empty] | 0 | 0 | 0 | 300 | 280 | 320 | 340 | 320 | 320 | 340 | 300 | 260 | 425 |  | 980 | 970 | 960 | 82 | 98 | 12 | 1490 | 305 | 500 | 40 | 39 | 6 | 520 | 110 | 220 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43155.826 | 2,3,5 | 42 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.311 | 1,2 | 19.1966 | 28.5077 | 1.9368 | 43155.826 | 55.0122 | 2766.9326 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.80845 | 1.5 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.2964 | 0.81038 | 7.8095 | 1.0818 | 0.50955 | 0.10199 | 3.177 | 0.55814 | 6.8655 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.35 | 0.053 | 1 | 3.9 | 17.3 |  |  |  | 7.5 | 0.054 | 1 | 3.5 | 17.2 |  |  |  | 3.6 | 3.5 | 3.4 | [18 empty] | 6075 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 425 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1480 | 302 | 455 | 40 | 50 | 6 | 510 | 104 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.64 | 20 | 19 | 7.77 | 57 | 113 | 17.6 | 0.297 |  | 5.92 | 10 | 0.054 | 5.9 | 10 |  | 5.93 | 10 | [8 empty] | 0.044 | [14 empty] | 0.042 | 1 | 0.24 |  | 0.047 | 0.039 | 1 | 0.43 |  | 0.052 | 1 | 0.53 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.048 | [9 empty] | 6.13 | 0.234 | 3 | 0.46 | 17.4 | 9 | 0.47377 |  | 6.11 | 0.195 | 3 | 0.66 | 17.3 | 9 | 0.47377 | 6.1 | 0.397 | 3 | 0.7 | 18.3 | 9 | 0.45333 |  |  |  | 0.011 | [9 empty] | 7.54 | 0.063 | 2 | 4.9 | 17 | 24 | 29 | 0.017 | 8.04 | 0.058 | 2 | 4.9 | 16.3 | 25 | 32 | 0.019 | 3.7 | 3.4 | 3.2 | [55 empty] | 9:00 | 0.46 | 9 | 28.2667 | 13.0027 | 6.13 | 17.4 | 10 | 1.3003 | 15 | 6.5 | 0.35377 | 9:00 | 0.66 | 9 | 28.2667 | 18.656 | 6.11 | 17.3 | 10 | 1.8656 | 15 | 6.5 | 0.35377 | 9:00 | 0.7 | 9 | 30 | 21 | 6.1 | 18.3 | 10 | 2.1 | 15 | 6.5 | 0.33333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.64 | 21 | 19 | 7.51 | 55 | 108 | 17.9 | 0.291 |  | 5.98 | 8 | 0.051 | 5.97 | 8 |  | 5.94 | 9 | [8 empty] | 0.044 | [14 empty] | 0.038 | 1 | 0.31 |  | 0.046 | 0.034 | 1 | 0.46 |  | 0.052 | 1 | 0.55 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.02 | 0.209 | 3 | 0.55 | 18.5 | 9 | 0.47377 |  | 6.02 | 0.197 | 3 | 0.66 | 17.8 | 9 | 0.47377 | 6.04 | 0.235 | 4 | 0.7 | 18.6 | 9 | 0.45333 | [13 empty] | 8.21 | 0.052 | 2 | 5 | 17.1 |  |  |  | 8.1 | 0.052 | 2 | 3.4 | 17 |  |  |  | 3.7 | 3.4 | 3.1 | [55 empty] | 13:00 | 0.55 | 9 | 28.2667 | 15.5467 | 6.02 | 18.5 | 10 | 1.5547 | 15 | 6.5 | 0.35377 | 13:00 | 0.66 | 9 | 28.2667 | 18.656 | 6.02 | 17.8 | 10 | 1.8656 | 15 | 6.5 | 0.35377 | 13:00 | 0.7 | 9 | 30 | 21 | 6.04 | 18.6 | 10 | 2.1 | 15 | 6.5 | 0.33333
14:00 | [126 empty] | 275 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.61 | 18 | 17 | 7.62 | 58 | 112 | 18.4 | 0.307 |  | 6 | 9 | 0.069 | 5.95 | 8 |  | 5.97 | 9 | [8 empty] | 0.052 | [14 empty] | 0.032 | 1 | 0.27 |  | 0.038 | 0.034 | 1 | 0.38 |  | 0.047 | 1 | 0.42 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.49 | 0.051 | 1 | 4.2 | 17.1 |  |  |  | 8.16 | 0.054 | 1 | 4.4 | 16.9 |  |  |  | 3.8 | 3.4 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 22 | 18 | 7.54 | 58 | 108 | 18.8 | 0.317 |  | 5.99 | 10 | 0.064 | 5.96 | 10 |  | 5.95 | 10 | [8 empty] | 0.046 | [14 empty] | 0.034 | 1 | 0.27 |  | 0.046 | 0.033 | 1 | 0.37 |  | 0.052 | 1 | 0.44 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.04 | [9 empty] | 6 | 0.225 | 3 | 0.55 | 18.5 | 9 | 0.40302 |  | 6 | 0.205 | 3 | 0.57 | 18.5 | 9 | 0.40302 | 6.04 | 0.436 | 4 | 0.58 | 19 | 9 | 0.45333 |  |  |  | 0.008 | [9 empty] | 7.31 | 0.049 | 1 | 4 | 17.4 | 20 | 30 | 0.023 | 7.46 | 0.053 | 1 | 3.7 | 17.6 | 21 | 28 | 0.019 | 3.9 | 3.5 | 3.1 | [55 empty] | 21:00 | 0.55 | 9 | 28.2667 | 15.5467 | 6 | 18.5 | 8 | 1.9433 | 15 | 6 | 0.28302 | 21:00 | 0.57 | 9 | 28.2667 | 16.112 | 6 | 18.5 | 8 | 2.014 | 15 | 6 | 0.28302 | 21:00 | 0.58 | 9 | 30 | 17.4 | 6.04 | 19 | 10 | 1.74 | 15 | 6.5 | 0.33333
22:00 | [72 empty] | DOSE |  | TOTAL | 27.4 | 27.3 | 27.4 | 82.1 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 33.2611 | 0 | 44.051 | 77.3122 | 3.1061 | TOTAL | 167.2406 | 8362.2852 | 0 | 2100 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.7131 | 4.6084 | 4.8178 | 0.58773 | 0.57505 | 0.57701 | 0.58969 | 0.56238 | 0.53702 | 2.4254 | 4.5 | 0.18186 | 0.18124 | 0.18062 | 3.2725 | 1.5083 | 0.30597 | 12.886 | 2.4392 | 24.9731 | 3.2454 | 1.4165 | 0.30597 | 9.5711 | 1.6959 | 21.9695 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.6 | 21 | 18 | 7.46 | 60 | 109 | 18.7 | 0.302 |  | 6.01 | 11 | 0.065 | 6.1 | 10 |  | 6.04 | 11 | [8 empty] | 0.05 | [14 empty] | 0.037 | 1 | 0.26 |  | 0.048 | 0.039 | 1 | 0.36 |  | 0.05 | 1 | 0.31 | [22 empty] | AVERAGE | 9.1333 | 9.1 | 9.1333 | 27.3667 | 8.5 | 8.5 | 8.5 | 25.5 |  | 11.087 |  | 14.6837 | 25.7707 | 1.0354 | AVERAGE | 55.7469 | 2787.4284 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.5361 | 1.6059 | 0.19591 | 0.19168 | 0.19234 | 0.19656 | 0.18746 | 0.17901 | 0.80845 | 1.5 | 0.06062 | 0.060413 | 0.060206 | 1.0908 | 0.50275 | 0.10199 | 4.2953 | 0.81306 | 8.3244 | 1.0818 | 0.47218 | 0.10199 | 3.1904 | 0.5653 | 7.3232 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.74 | 126 | 111 | 46.14 | 348 | 665 | 109.6 | 1.814 | 0.088 | 35.89 | 60 | 0.363 | 35.86 | 58 | 0 | 35.83 | 61 | 0 | 24.21 | 0.937 | 12 | 2.09 | 72.3 | 36.3 | 1.8361 | 0.281 | 24.2 | 0.81 | 12 | 2.52 | 71.5 | 36.4 | 1.8401 | 24.22 | 1.457 | 14 | 2.62 | 74.7 | 36.6 | 1.8356 | 0.221 | 6 | 1.59 | 0.019 | 0.269 | 0.219 | 6 | 2.36 | 0 |  | 6 | 2.67 | 0 | 45.38 | 0.319 | 8 | 25.7 | 103 | 44 | 59 | 0.04 | 46.67 | 0.324 | 8 | 23.3 | 101.4 | 46 | 60 | 0.038 | 22.4 | 20.7 | 19.1 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.311 |  | 12.4272 | 24.4022 | 0 | MINIMUM | 54.8165 | 2766.9326 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.4663 | 1.571 | 0.18206 | 0.18206 | 0.18402 | 0.18402 | 0.18206 | 0.1648 | 0.80845 | 1 | 0.060206 | 0.060206 | 0.059585 | 1.0818 | 0.49935 | 0.10199 | 4.2914 | 0.81038 | 7.8095 | 1.0818 | 0.39745 | 0.10199 | 3.177 | 0.54741 | 6.8655 |  | MIN | 0.46 | 9 | 28.2667 | 13.0027 | 6.13 | 17.4 | 10 | 1.3003 |  |  |  | MIN | 0.63 | 9.4 | 27.0638 | 17.0502 | 6.07 | 17.9 | 10 | 1.705 |  |  |  | MIN | 0.58 | 9 | 30 | 17.4 | 6.04 | 19 | 10 | 1.74 |  |  |  | 1.3003
AVERAGE | 6.6233 | 21 | 18.5 | 7.69 | 58 | 110.8333 | 18.2667 | 0.30233 | 0.044 | 5.9817 | 10 | 0.0605 | 5.9767 | 9.6667 |  | 5.9717 | 10.1667 |  | 6.0525 | 0.23425 | 3 | 0.5225 | 18.075 | 9.075 | 0.45903 | 0.046833 | 6.05 | 0.2025 | 3 | 0.63 | 17.875 | 9.1 | 0.46002 | 6.055 | 0.36425 | 3.5 | 0.655 | 18.675 | 9.15 | 0.45889 | 0.036833 | 1 | 0.265 | 0.0095 | 0.044833 | 0.0365 | 1 | 0.39333 |  |  | 1 | 0.445 |  | 7.5633 | 0.053167 | 1.3333 | 4.2833 | 17.1667 | 22 | 29.5 | 0.02 | 7.7783 | 0.054 | 1.3333 | 3.8833 | 16.9 | 23 | 30 | 0.019 | 3.7333 | 3.45 | 3.1833 |  |  | MAXIMUM | 9.4 | 9.3 | 9.4 | 28.1 | 8.5 | 8.5 | 8.5 | 25.5 |  | 11.975 |  | 19.1966 | 28.5077 | 1.9368 | MAXIMUM | 57.4119 | 2828.42 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.571 | 1.6758 | 0.21551 | 0.20283 | 0.20283 | 0.21551 | 0.19016 | 0.19016 | 0.80845 | 2 | 0.060827 | 0.060827 | 0.060827 | 1.1089 | 0.50955 | 0.10199 | 4.2982 | 0.81843 | 8.5818 | 1.0818 | 0.50955 | 0.10199 | 3.2107 | 0.59034 | 7.552
MINIMUM | 6.6 | 18 | 17 | 7.46 | 55 | 108 | 17.6 | 0.291 | 0.04 | 5.92 | 8 | 0.051 | 5.9 | 8 |  | 5.93 | 9 |  | 6 | 0.209 | 3 | 0.46 | 17.4 | 9 | 0.40302 | 0.044 | 6 | 0.195 | 3 | 0.57 | 17.3 | 9 | 0.40302 | 6.04 | 0.235 | 3 | 0.58 | 18.3 | 9 | 0.45333 | 0.032 | 1 | 0.24 | 0.008 | 0.038 | 0.033 | 1 | 0.36 |  |  | 1 | 0.31 |  | 7.31 | 0.049 | 1 | 3.7 | 17 | 20 | 29 | 0.017 | 7.41 | 0.052 | 1 | 3.4 | 16.3 | 21 | 28 | 0.019 | 3.6 | 3.4 | 3 | [15 empty] | MIL/MIN |  | TOTAL | 18715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 880 | 920 | 940 | 920 | 920 | 940 | 900 | 860 | 1275 | 0 | 2930 | 2920 | 2910 | 242 | 296 | 36 | 4450 | 909 | 1455 | 120 | 139 | 18 | 1530 | 316 | 640
MAXIMUM | 6.64 | 24 | 20 | 8.24 | 60 | 115 | 18.8 | 0.317 | 0.048 | 6.01 | 12 | 0.069 | 6.1 | 12 |  | 6.04 | 12 |  | 6.13 | 0.269 | 3 | 0.55 | 18.5 | 9.3 | 0.48557 | 0.052 | 6.11 | 0.213 | 3 | 0.66 | 18.5 | 9.4 | 0.4895 | 6.1 | 0.436 | 4 | 0.7 | 19 | 9.6 | 0.47556 | 0.042 | 1 | 0.31 | 0.011 | 0.048 | 0.04 | 1 | 0.46 |  |  | 1 | 0.55 |  | 8.21 | 0.063 | 2 | 5 | 17.4 | 24 | 30 | 0.023 | 8.16 | 0.058 | 2 | 4.9 | 17.6 | 25 | 32 | 0.019 | 3.9 | 3.5 | 3.4 | [17 empty] | AVERAGE | 6238.3333 | [9 empty] | 300 | 293.3333 | 306.6667 | 313.3333 | 306.6667 | 306.6667 | 313.3333 | 300 | 286.6667 | 425 |  | 976.6667 | 973.3333 | 970 | 80.6667 | 98.6667 | 12 | 1483.3333 | 303 | 485 | 40 | 46.3333 | 6 | 510 | 105.3333 | 213.3333
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9767 |  | TOTAL AVG COAG ALK: |  |  |  | 9.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.436 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.0525 |  |  |  |  | 0.042 |  |  |  |  | 0.46 | [6 empty] | 0.042 | [16 empty] | Pump Station MIN |  | 3 | [17 empty] | MINIMUM | 6075 | [9 empty] | 300 | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 260 | 425 |  | 970 | 970 | 960 | 80 | 98 | 12 | 1480 | 302 | 455 | 40 | 39 | 6 | 500 | 102 | 200
[90 empty] | MAXIMUM | 6340 | [9 empty] | 300 | 300 | 320 | 340 | 320 | 320 | 340 | 300 | 300 | 425 |  | 980 | 980 | 980 | 82 | 100 | 12 | 1490 | 305 | 500 | 40 | 50 | 6 | 520 | 110 | 220
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.7 |  | TOTAL MGD: |  | 5.165 |  |  | FINISHED SOUTH 1 |  | START: | 23165205 |  | END: | 23170370 |  |  | Alum | 9249 |  | 9734 |  | 0 | [45 empty] | 0.46 | 9 | 28.2667 | 13.0027 | 6.13 | 17.4 | 10 | 1.3003
[73 empty] | FINISHED 2 | 14.11 |  | TOTAL MGD: |  | 5.535 |  |  | FINISHED SOUTH 2 |  | START: | 41032825 |  | END: | 41038360 |  |  | Caustic | 5546 |  | 4138
[73 empty] | TOTAL RAW | 26.96 |  | TOTAL MGD: |  | 3.99 |  |  | FINISHED CONWAY |  | START: | 8762575 |  | END: | 8766565 |  |  | Hypochlorite | 12 |  | 33
[76 empty] | TOTAL MGD: |  | 10.12 |  |  | FINISHED PERRY |  | START: | 30525435 |  | END: | 30535555 |  |  | Phosphate | 2162
[76 empty] | TOTAL MGD: |  | 8.935 |  |  | RAW PLANT 1 |  | START: | 28049760 |  | END: | 28058695 |  |  | Fluoride | 750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.905 |  |  | RAW PLANT 2 |  | START: | 27996595 |  | END: | 28005500 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 9.12 |  |  | RAW PLANT 3 |  | START: | 4296600 |  | END: | 4305720 |  |  | Zinc | 3206
[76 empty] | TOTAL MGD: |  | 1.783 |  |  | DECANT |  | START: | 1406712 |  | END: | 1408495 |  |  | Polymer | 12 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.8739 |  |  | BLOW DOWN |  | START: | 8772.5799 |  | END: | 8773.4538 |  |  | NH3 | 10.15
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 700
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2355 | Phosphate | 45
[90 empty] | Caustic 1 | 184 | Fluoride | 57
[90 empty] | Caustic 2 | 91 | Zinc | 8
[90 empty] | Hypochlorite 1 | 346 | Polymer 1 | 2
[90 empty] | Hypochlorite 2 | 764 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23170370
[91 empty] | FINISHED SOUTH 2 |  | END: | 41038360
[91 empty] | FINISHED CONWAY |  | END: | 8766565
[91 empty] | FINISHED PERRY |  | END: | 30535555
[91 empty] | RAW PLANT 1 |  | END: | 28058695
[91 empty] | RAW PLANT 2 |  | END: | 28005500
[91 empty] | RAW PLANT 3 |  | END: | 4305720
[91 empty] | DECANT |  | END: | 1408495
[91 empty] | BLOW DOWN |  | END: | 8773.4538
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 25
DATE: | 2018-02-25 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 20 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 20 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 20
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-25 | [23 empty] | DATE: | 2018-02-25
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-25 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43156.0032 | 2,3,5 | 42 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.7963 | 1,2 | 14.3179 | 24.1142 | 1.3824 | 43156.0032 | 55.0122 | 2766.9326 | 0 | 700 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.80845 | 2 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.2964 | 0.81038 | 7.8095 | 1.0818 | 0.50955 | 0.10199 | 3.177 | 0.55814 | 6.8655 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.298 | 3 | 0.53 | 18.3 | 9.1 | 0.4777 |  | 6.07 | 0.244 | 3 | 0.48 | 18.3 | 9 | 0.47377 | 6.09 | 0.333 | 3 | 0.7 | 19.2 | 9.2 | 0.46074 | [13 empty] | 7.52 | 0.052 | 1 | 3.9 | 17.5 |  |  |  | 7.46 | 0.054 | 1 | 3.8 | 17.4 |  |  |  | 3.9 | 3.8 | 3.9 | [18 empty] | 6075 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 425 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1480 | 302 | 455 | 40 | 50 | 6 | 510 | 104 | 200 |  | 1:00 | 0.53 | 9.1 | 27.956 | 14.8167 | 6.01 | 18.3 | 10 | 1.4817 | 15 | 6.5 | 0.3577 | 1:00 | 0.48 | 9 | 28.2667 | 13.568 | 6.07 | 18.3 | 10 | 1.3568 | 15 | 6.5 | 0.35377 | 1:00 | 0.7 | 9.2 | 29.3478 | 20.5435 | 6.09 | 19.2 | 10 | 2.0543 | 15 | 6.5 | 0.34074
2:00 | [72 empty] | 43156.326 | 2,3,5 | 42 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.7963 | 1,2 | 14.3179 | 24.1142 | 0 | 43156.326 | 55.465 | 2766.9326 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.4663 | 1.571 | 1.6758 | 0.20917 | 0.20283 | 0.20283 | 0.21551 | 0.19016 | 0.17114 | 0.80845 | 2.5 | 0.060516 | 0.060827 | 0.062068 | 1.0818 | 0.50445 | 0.10199 | 4.3051 | 0.81843 | 7.8095 | 1.1359 | 0.39745 | 0.10199 | 3.178 | 0.61718 | 6.8655 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.67 | 24 | 18 | 7.55 | 64 | 114 | 18.5 | 0.268 |  | 6.04 | 12 | 0.057 | 6.02 | 12 |  | 6.01 | 12 | [8 empty] | 0.041 | [14 empty] | 0.038 | 1 | 0.24 |  | 0.041 | 0.038 | 1 | 0.32 |  | 0.044 | 1 | 0.28 | [38 empty] | 6125 | [6 empty] | 0 | 0 | 0 | 280 | 300 | 320 | 330 | 320 | 320 | 340 | 300 | 270 | 425 |  | 975 | 980 | 1000 | 80 | 99 | 12 | 1500 | 305 | 455 | 42 | 39 | 6 | 540 | 115 | 200 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43156.8446 | 2,3,5 | 42 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 12.2098 | 1,2 | 15.0005 | 27.2102 | 1.2341 | 43156.8446 | 55.0122 | 2766.9326 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.571 | 1.571 | 0.20283 | 0.20283 | 0.19016 | 0.19016 | 0.19016 | 0.17748 | 0.80845 | 3 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.50955 | 0.10199 | 4.2651 | 0.82648 | 7.8095 | 1.0818 | 0.40764 | 0.10199 | 3.1944 | 0.57961 | 6.8655 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.48 | 0.054 | 1 | 4.2 | 17.4 |  |  |  | 7.34 | 0.056 | 1 | 3.7 | 17.3 |  |  |  | 3.8 | 3.8 | 4.2 | [18 empty] | 6075 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 320 | 320 | 300 | 300 | 300 | 280 | 425 |  | 970 | 970 | 970 | 80 | 100 | 12 | 1500 | 308 | 455 | 40 | 40 | 6 | 530 | 108 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.63 | 21 | 17 | 7.54 | 65 | 114 | 18.3 | 0.328 |  | 6.03 | 8 | 0.059 | 5.97 | 10 |  | 6.01 | 9 | [8 empty] | 0.045 | [14 empty] | 0.042 | 2 | 0.28 |  | 0.047 | 0.038 | 2 | 0.26 |  | 0.059 | 2 | 0.32 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.034 | [9 empty] | 6.09 | 0.341 | 4 | 0.47 | 18.1 | 9 | 0.47377 |  | 6.07 | 0.291 | 4 | 0.41 | 18 | 9 | 0.47377 | 6.08 | 0.27 | 4 | 0.5 | 18.9 | 9 | 0.45333 |  |  |  | 0.01 | [9 empty] | 7.46 | 0.054 | 1 | 4.1 | 17.6 | 20 | 26 | 0.013 | 7.44 | 0.055 | 2 | 3.6 | 16.7 | 25 | 26 | 0.013 | 3.8 | 3.7 | 3.8 | [55 empty] | 9:00 | 0.47 | 9 | 28.2667 | 13.2853 | 6.09 | 18.1 | 10 | 1.3285 | 15 | 6.5 | 0.35377 | 9:00 | 0.41 | 9 | 28.2667 | 11.5893 | 6.07 | 18 | 10 | 1.1589 | 15 | 6.5 | 0.35377 | 9:00 | 0.5 | 9 | 30 | 15 | 6.08 | 18.9 | 10 | 1.5 | 15 | 6.5 | 0.33333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.61 | 20 | 15 | 6.22 | 65 | 107 | 18.5 | 0.335 |  | 5.99 | 9 | 0.061 | 5.94 | 9 |  | 5.95 | 9 | [8 empty] | 0.055 | [14 empty] | 0.037 | 2 | 0.36 |  | 0.052 | 0.037 | 2 | 0.25 |  | 0.057 | 2 | 0.38 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.91 | 0.261 | 4 | 0.48 | 18.8 | 9 | 0.40302 |  | 5.94 | 0.225 | 3 | 0.55 | 18.7 | 9 | 0.40302 | 5.93 | 0.339 | 3 | 0.57 | 19 | 9 | 0.38667 | [13 empty] | 7.5 | 0.059 | 1 | 4.3 | 17.8 |  |  |  | 7.57 | 0.056 | 2 | 3.9 | 17.5 |  |  |  | 3.8 | 3.6 | 3 | [55 empty] | 13:00 | 0.48 | 9 | 28.2667 | 13.568 | 5.91 | 18.8 | 8 | 1.696 | 15 | 6 | 0.28302 | 13:00 | 0.55 | 9 | 28.2667 | 15.5467 | 5.94 | 18.7 | 8 | 1.9433 | 15 | 6 | 0.28302 | 13:00 | 0.57 | 9 | 30 | 17.1 | 5.93 | 19 | 8 | 2.1375 | 15 | 6 | 0.26667
14:00 | [126 empty] | 253 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.63 | 21 | 15 | 7.2 | 65 | 114 | 18.6 | 0.331 |  | 6.09 | 9 | 0.061 | 6.07 | 9 |  | 6.03 | 9 | [8 empty] | 0.049 | [14 empty] | 0.033 | 1 | 0.16 |  | 0.05 | 0.043 | 1 | 0.32 |  | 0.052 | 1 | 0.35 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.55 | 0.051 | 1 | 4.3 | 17.8 |  |  |  | 7.45 | 0.057 | 1 | 3.7 | 17.3 |  |  |  | 3.9 | 3.4 | 2.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.68 | 22 | 16 | 7.27 | 65 | 117 | 19.5 | 0.283 |  | 5.9 | 10 | 0.066 | 5.92 | 10 |  | 5.95 | 10 | [8 empty] | 0.052 | [14 empty] | 0.033 | 1 | 0.14 |  | 0.05 | 0.04 | 1 | 0.3 |  | 0.051 | 1 | 0.26 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.01 | 0.312 | 3 | 0.48 | 19 | 9 | 0.47377 |  | 6.04 | 0.209 | 3 | 0.57 | 19 | 9 | 0.47377 | 5.95 | 0.369 | 3 | 0.61 | 20 | 9 | 0.32 |  |  |  | 0.017 | [9 empty] | 7.36 | 0.053 | 1 | 4.2 | 18.2 | 20 | 32 | 0.023 | 7.56 | 0.059 | 1 | 4 | 17.6 | 21 | 30 | 0.012 | 3.9 | 3.5 | 2.9 | [55 empty] | 21:00 | 0.48 | 9 | 28.2667 | 13.568 | 6.01 | 19 | 10 | 1.3568 | 15 | 6.5 | 0.35377 | 21:00 | 0.57 | 9 | 28.2667 | 16.112 | 6.04 | 19 | 10 | 1.6112 | 15 | 6.5 | 0.35377 | 21:00 | 0.61 | 9 | 30 | 18.3 | 5.95 | 20 | 6 | 3.05 | 20 | 6 | 0.2
22:00 | [72 empty] | DOSE |  | TOTAL | 27 | 27 | 27 | 81 | 25.5 | 25.5 | 25.5 | 76.5 | 0 | 31.8024 | 0 | 43.6363 | 75.4387 | 2.6165 | TOTAL | 165.4895 | 8300.7978 | 0 | 2050 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 4.6084 | 4.7131 | 4.8178 | 0.60216 | 0.59582 | 0.58315 | 0.59582 | 0.57047 | 0.53878 | 2.4254 | 7.5 | 0.18093 | 0.18124 | 0.18248 | 3.2454 | 1.5133 | 0.30597 | 12.8665 | 2.4553 | 23.4284 | 3.2995 | 1.3146 | 0.30597 | 9.5495 | 1.7549 | 20.5964 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.57 | 20 | 16 | 7.05 | 71 | 119 | 19.5 | 0.353 |  | 5.91 | 11 | 0.069 | 6 | 9 |  | 5.97 | 10 | [8 empty] | 0.05 | [14 empty] | 0.04 | 1 | 0.18 |  | 0.048 | 0.037 | 1 | 0.37 |  | 0.052 | 1 | 0.33 | [22 empty] | AVERAGE | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.6008 |  | 14.5454 | 25.1462 | 0.87216 | AVERAGE | 55.1632 | 2766.9326 |  | 683.3333 | #N/A | #N/A | #N/A |  |  |  | 1.5361 | 1.571 | 1.6059 | 0.20072 | 0.19861 | 0.19438 | 0.19861 | 0.19016 | 0.17959 | 0.80845 | 2.5 | 0.060309 | 0.060413 | 0.060827 | 1.0818 | 0.50445 | 0.10199 | 4.2888 | 0.81843 | 7.8095 | 1.0998 | 0.43821 | 0.10199 | 3.1832 | 0.58498 | 6.8655 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.79 | 128 | 97 | 42.83 | 395 | 685 | 112.9 | 1.898 | 0.077 | 35.96 | 59 | 0.373 | 35.92 | 59 | 0 | 35.92 | 59 | 0 | 24.02 | 1.212 | 14 | 1.96 | 74.2 | 36.1 | 1.8283 | 0.292 | 24.12 | 0.969 | 13 | 2.01 | 74 | 36 | 1.8243 | 24.05 | 1.311 | 13 | 2.38 | 77.1 | 36.2 | 1.6207 | 0.223 | 8 | 1.36 | 0.027 | 0.288 | 0.233 | 8 | 1.82 | 0 | 0.315 | 8 | 1.92 | 0 | 44.87 | 0.323 | 6 | 25 | 106.3 | 40 | 58 | 0.036 | 44.82 | 0.337 | 8 | 22.7 | 103.8 | 46 | 56 | 0.025 | 23.1 | 21.8 | 20.7 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.7963 |  | 14.3179 | 24.1142 | 0 | MINIMUM | 55.0122 | 2766.9326 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.4663 | 1.571 | 1.571 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.19016 | 0.17114 | 0.80845 | 2 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.49935 | 0.10199 | 4.2651 | 0.81038 | 7.8095 | 1.0818 | 0.39745 | 0.10199 | 3.177 | 0.55814 | 6.8655 |  | MIN | 0.47 | 9 | 28.2667 | 13.2853 | 6.09 | 18.1 | 10 | 1.3285 |  |  |  | MIN | 0.41 | 9 | 28.2667 | 11.5893 | 6.07 | 18 | 10 | 1.1589 |  |  |  | MIN | 0.5 | 9 | 30 | 15 | 6.08 | 18.9 | 10 | 1.5 |  |  |  | 1.1589
AVERAGE | 6.6317 | 21.3333 | 16.1667 | 7.1383 | 65.8333 | 114.1667 | 18.8167 | 0.31633 | 0.0385 | 5.9933 | 9.8333 | 0.062167 | 5.9867 | 9.8333 |  | 5.9867 | 9.8333 |  | 6.005 | 0.303 | 3.5 | 0.49 | 18.55 | 9.025 | 0.45707 | 0.048667 | 6.03 | 0.24225 | 3.25 | 0.5025 | 18.5 | 9 | 0.45608 | 6.0125 | 0.32775 | 3.25 | 0.595 | 19.275 | 9.05 | 0.40519 | 0.037167 | 1.3333 | 0.22667 | 0.0135 | 0.048 | 0.038833 | 1.3333 | 0.30333 |  | 0.0525 | 1.3333 | 0.32 |  | 7.4783 | 0.053833 | 1 | 4.1667 | 17.7167 | 20 | 29 | 0.018 | 7.47 | 0.056167 | 1.3333 | 3.7833 | 17.3 | 23 | 28 | 0.0125 | 3.85 | 3.6333 | 3.45 |  |  | MAXIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 12.2098 |  | 15.0005 | 27.2102 | 1.3824 | MAXIMUM | 55.465 | 2766.9326 |  | 700 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.571 | 1.6758 | 0.20917 | 0.20283 | 0.20283 | 0.21551 | 0.19016 | 0.19016 | 0.80845 | 3 | 0.060516 | 0.060827 | 0.062068 | 1.0818 | 0.50955 | 0.10199 | 4.3051 | 0.82648 | 7.8095 | 1.1359 | 0.50955 | 0.10199 | 3.1944 | 0.61718 | 6.8655
MINIMUM | 6.57 | 20 | 15 | 6.22 | 64 | 107 | 18.3 | 0.268 | 0.034 | 5.9 | 8 | 0.057 | 5.92 | 9 |  | 5.95 | 9 |  | 5.91 | 0.261 | 3 | 0.47 | 18.1 | 9 | 0.40302 | 0.041 | 5.94 | 0.209 | 3 | 0.41 | 18 | 9 | 0.40302 | 5.93 | 0.27 | 3 | 0.5 | 18.9 | 9 | 0.32 | 0.033 | 1 | 0.14 | 0.01 | 0.041 | 0.037 | 1 | 0.25 |  | 0.044 | 1 | 0.26 |  | 7.36 | 0.051 | 1 | 3.9 | 17.4 | 20 | 26 | 0.013 | 7.34 | 0.054 | 1 | 3.6 | 16.7 | 21 | 26 | 0.012 | 3.8 | 3.4 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 18275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 900 | 920 | 950 | 940 | 920 | 940 | 900 | 850 | 1275 | 0 | 2915 | 2920 | 2940 | 240 | 297 | 36 | 4480 | 915 | 1365 | 122 | 129 | 18 | 1580 | 327 | 600
MAXIMUM | 6.68 | 24 | 18 | 7.55 | 71 | 119 | 19.5 | 0.353 | 0.043 | 6.09 | 12 | 0.069 | 6.07 | 12 |  | 6.03 | 12 |  | 6.09 | 0.341 | 4 | 0.53 | 19 | 9.1 | 0.4777 | 0.055 | 6.07 | 0.291 | 4 | 0.57 | 19 | 9 | 0.47377 | 6.09 | 0.369 | 4 | 0.7 | 20 | 9.2 | 0.46074 | 0.042 | 2 | 0.36 | 0.017 | 0.052 | 0.043 | 2 | 0.37 |  | 0.059 | 2 | 0.38 |  | 7.55 | 0.059 | 1 | 4.3 | 18.2 | 20 | 32 | 0.023 | 7.57 | 0.059 | 2 | 4 | 17.6 | 25 | 30 | 0.013 | 3.9 | 3.8 | 4.2 | [17 empty] | AVERAGE | 6091.6667 | [9 empty] | 293.3333 | 300 | 306.6667 | 316.6667 | 313.3333 | 306.6667 | 313.3333 | 300 | 283.3333 | 425 |  | 971.6667 | 973.3333 | 980 | 80 | 99 | 12 | 1493.3333 | 305 | 455 | 40.6667 | 43 | 6 | 526.6667 | 109 | 200
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9889 |  | TOTAL AVG COAG ALK: |  |  |  | 9.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.369 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.41 | [5 empty] | 6.0158 |  |  |  |  | 0.059 |  |  |  |  | 0.41 | [6 empty] | 0.059 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 6075 | [9 empty] | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 425 |  | 970 | 970 | 970 | 80 | 98 | 12 | 1480 | 302 | 455 | 40 | 39 | 6 | 510 | 104 | 200
[90 empty] | MAXIMUM | 6125 | [9 empty] | 300 | 300 | 320 | 330 | 320 | 320 | 340 | 300 | 300 | 425 |  | 975 | 980 | 1000 | 80 | 100 | 12 | 1500 | 308 | 455 | 42 | 50 | 6 | 540 | 115 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.09 |  | TOTAL MGD: |  | 5.48 |  |  | FINISHED SOUTH 1 |  | START: | 23170370 |  | END: | 23175850 |  |  | Alum | 8410 |  | 8998 |  | 0 | [45 empty] | 0.41 | 9 | 28.2667 | 11.5893 | 6.07 | 18 | 10 | 1.1589
[73 empty] | FINISHED 2 | 13.74 |  | TOTAL MGD: |  | 5.61 |  |  | FINISHED SOUTH 2 |  | START: | 41038360 |  | END: | 41043970 |  |  | Caustic | 5319 |  | 4037
[73 empty] | TOTAL RAW | 26.315 |  | TOTAL MGD: |  | 4.4 |  |  | FINISHED CONWAY |  | START: | 8766565 |  | END: | 8770965 |  |  | Hypochlorite | 10 |  | 31
[76 empty] | TOTAL MGD: |  | 9.34 |  |  | FINISHED PERRY |  | START: | 30535555 |  | END: | 30544895 |  |  | Phosphate | 2079
[76 empty] | TOTAL MGD: |  | 8.705 |  |  | RAW PLANT 1 |  | START: | 28058695 |  | END: | 28067400 |  |  | Fluoride | 500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.64 |  |  | RAW PLANT 2 |  | START: | 28005500 |  | END: | 28014140 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 8.97 |  |  | RAW PLANT 3 |  | START: | 4305720 |  | END: | 4314690 |  |  | Zinc | 3194
[76 empty] | TOTAL MGD: |  | 1.287 |  |  | DECANT |  | START: | 1408495 |  | END: | 1409782 |  |  | Polymer | 11 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.88021 |  |  | BLOW DOWN |  | START: | 8773.4538 |  | END: | 8774.3341 |  |  | NH3 | 9.95
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 700
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2297 | Phosphate | 45
[90 empty] | Caustic 1 | 168 | Fluoride | 54
[90 empty] | Caustic 2 | 85 | Zinc | 8
[90 empty] | Hypochlorite 1 | 346 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 780 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23175850
[91 empty] | FINISHED SOUTH 2 |  | END: | 41043970
[91 empty] | FINISHED CONWAY |  | END: | 8770965
[91 empty] | FINISHED PERRY |  | END: | 30544895
[91 empty] | RAW PLANT 1 |  | END: | 28067400
[91 empty] | RAW PLANT 2 |  | END: | 28014140
[91 empty] | RAW PLANT 3 |  | END: | 4314690
[91 empty] | DECANT |  | END: | 1409782
[91 empty] | BLOW DOWN |  | END: | 8774.3341
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2BCOperator:
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. BuildingBCOperator:
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1BCOperator:
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 26
DATE: | 2018-02-26 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 20 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 20 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 20
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-26 | [23 empty] | DATE: | 2018-02-26
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-26 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43157.0028 | 2,3,5 | 42 | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 12.2098 | 1,2 | 15.0005 | 27.2102 | 1.0627 | 43157.0028 | 55.0122 | 2766.9326 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.702 | 1.702 | 1.571 | 0.20102 | 0.20102 | 0.18472 | 0.18472 | 0.3613 | 0 | 0.80845 | 3.5 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.50955 | 0.10199 | 4.2651 | 0.82648 | 7.8095 | 1.0818 | 0.40764 | 0.10199 | 3.1944 | 0.57961 | 6.8655 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.99 | 0.371 | 3 | 0.46 | 19.2 | 10.3 | 0.4439 |  | 6.05 | 0.308 | 3 | 0.51 | 19.1 | 10.6 | 0.53667 | 6 | 0.362 | 3 | 0.36 | 19.9 | 6 | 0.29778 | [13 empty] | 7.25 | 0.053 | 2 | 3.9 | 18.2 |  |  |  | 7.29 | 0.055 | 2 | 3.5 | 17.7 |  |  |  | 3.9 | 3.6 | 3.1 | [18 empty] | 6075 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 300 | 370 | 370 | 340 | 340 | 380 | 0 | 425 |  | 970 | 970 | 970 | 80 | 100 | 12 | 1500 | 308 | 455 | 40 | 40 | 6 | 530 | 108 | 200 |  | 1:00 | 0.46 | 10.3 | 24.699 | 11.3616 | 5.99 | 19.2 | 8 | 1.4202 | 15 | 6 | 0.3239 | 1:00 | 0.51 | 10.6 | 24 | 12.24 | 6.05 | 19.1 | 10 | 1.224 | 15 | 6.5 | 0.41667 | 1:00 | 0.36 | 6 | 45 | 16.2 | 6 | 19.9 | 8 | 2.025 | 15 | 6 | 0.17778
2:00 | [72 empty] | 43157.1343 | 2,3,5 | 42 | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.8827 | 1,2 | 12.9974 | 22.8802 | 0 | 43157.1343 | 59.7664 | 2766.9326 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.702 | 1.702 | 1.571 | 0.20102 | 0.20102 | 0.18472 | 0.18472 | 0.3613 | 0 | 0.80845 | 0 | 0.060206 | 0.060206 | 0.060206 | 1.0818 | 0.50955 | 0.10199 | 4.2651 | 0.82648 | 7.8095 | 1.0818 | 0.40764 | 0.10199 | 3.1944 | 0.57961 | 6.8655 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.57 | 22 | 16 | 7.39 | 72 | 123 | 19.8 | 0.313 |  | 6.02 | 11 | 0.06 | 6.01 | 11 |  | 5.99 | 12 | [8 empty] | 0.055 | [14 empty] | 0.04 | 1 | 0.2 |  | 0.054 | 0.042 | 1 | 0.34 |  | 0.044 | 1 | 0.3 | [38 empty] | 6600 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 300 | 370 | 370 | 340 | 340 | 380 | 0 | 425 |  | 970 | 970 | 970 | 80 | 100 | 12 | 1500 | 308 | 455 | 40 | 40 | 6 | 530 | 108 | 200 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43157.3404 | 2,3,5 | 47 | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.8827 | 1,2 | 12.9974 | 22.8802 | 0 | 43157.3404 | 65.0186 | 3074.3696 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.2568 | 0.22819 | 0.21732 | 0.23905 | 0.26079 | 0.38031 | 0 | 1.9498 | 4 | 0.060827 | 0.060827 | 0.059585 | 1.0818 | 0.50445 | 0.10199 | 4.2951 | 0.81843 | 7.8095 | 1.0818 | 0.39745 | 0.10199 | 3.198 | 0.59034 | 6.8655 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.21 | 0.055 | 2 | 3.7 | 18.4 |  |  |  | 7.26 | 0.057 | 2 | 3.5 | 17.6 |  |  |  | 3.9 | 3.6 | 3.2 | [18 empty] | 7180 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 240 | 420 | 400 | 440 | 480 | 400 | 0 | 1025 |  | 980 | 980 | 960 | 80 | 99 | 12 | 1500 | 305 | 455 | 40 | 39 | 6 | 540 | 110 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43157.6333 | 2,3,5 | 47 | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.8827 | 1,2 | 12.9974 | 22.8802 | 0 | 43157.6333 | 69.9538 | 3074.3696 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.2568 | 0.22819 | 0.21732 | 0.23905 | 0.26079 | 0.38031 | 0 | 1.9498 | 4 | 0.060827 | 0.060827 | 0.059585 | 1.0818 | 0.50445 | 0.10199 | 4.2951 | 0.81843 | 7.8095 | 1.0818 | 0.39745 | 0.10199 | 3.198 | 0.59034 | 6.8655 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.55 | 20 | 17 | 7.41 | 71 | 123 | 18.7 | 0.367 |  | 5.71 | 8 | 0.061 | 5.78 | 8 |  | 5.89 | 8 | [8 empty] | 0.051 | [14 empty] | 0.042 | 1 | 0.16 |  | 0.057 | 0.04 | 1 | 0.29 |  | 0.051 | 1 | 0.14 | [38 empty] | 7725 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 240 | 420 | 400 | 440 | 480 | 400 | 0 | 1025 |  | 980 | 980 | 960 | 80 | 99 | 12 | 1500 | 305 | 455 | 40 | 39 | 6 | 540 | 110 | 200 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43157.8454 | 2,3,5 | 47 | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 9.9288 | 1,2 | 16.0301 | 25.9589 | 1.9411 | 43157.8454 | 70.0896 | 3689.2436 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.702 | 1.702 | 1.1783 | 0.20646 | 0.20646 | 0.19016 | 0.19016 | 0.3613 | 0 | 0.80845 | 1.5 | 0.060827 | 0.060827 | 0.060827 | 1.0818 | 0.50955 | 0.10199 | 4.3201 | 0.81575 | 7.8095 | 1.0818 | 0.50955 | 0.10199 | 3.1654 | 0.62254 | 6.8655 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.049 | [9 empty] | 5.89 | 0.478 | 4 | 0.4 | 18.8 | 10.5 | 0.45019 |  | 5.96 | 0.363 | 4 | 0.47 | 18.7 | 10.5 | 0.45019 | 5.97 | 0.259 | 4 | 0.42 | 19.5 | 6 | 0.29778 |  |  |  | 0.017 | [9 empty] | 7.22 | 0.067 | 2 | 4.2 | 18.1 | 25 | 45 | 0.021 | 7.37 | 0.065 | 2 | 3.9 | 17.2 | 27 | 43 | 0.026 | 3.8 | 3.5 | 3.3 | [18 empty] | 7740 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 225 | 380 | 380 | 350 | 350 | 380 | 0 | 425 |  | 980 | 980 | 980 | 80 | 100 | 12 | 1500 | 304 | 455 | 40 | 50 | 6 | 560 | 116 | 200 |  | 9:00 | 0.4 | 10.5 | 24.2286 | 9.6914 | 5.89 | 18.8 | 8 | 1.2114 | 15 | 6 | 0.33019 | 9:00 | 0.47 | 10.5 | 24.2286 | 11.3874 | 5.96 | 18.7 | 8 | 1.4234 | 15 | 6 | 0.33019 | 9:00 | 0.42 | 6 | 45 | 18.9 | 5.97 | 19.5 | 8 | 2.3625 | 15 | 6 | 0.17778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.56 | 25 | 18 | 7.01 | 74 | 122 | 18.7 | 0.371 |  | 5.96 | 10 | 0.06 | 6.02 | 10 |  | 5.93 | 10 | [8 empty] | 0.05 | [14 empty] | 0.039 | 1 | 0.19 |  | 0.055 | 0.054 | 1 | 0.32 |  | 0.049 | 1 | 0.16 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.02 | 0.501 | 5 | 0.47 | 18.9 | 10.5 | 0.53274 |  | 6.01 | 0.389 | 5 | 0.47 | 18.8 | 10.5 | 0.53274 | 6 | 0.278 | 4 | 0.42 | 19.6 | 6 | 0.29778 | [13 empty] | 7.3 | 0.07 | 2 | 3.8 | 18.3 |  |  |  | 7.43 | 0.06 | 2 | 3.4 | 17.3 |  |  |  | 3.8 | 3.4 | 3.3 | [55 empty] | 13:00 | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.02 | 18.9 | 10 | 1.1387 | 15 | 6.5 | 0.41274 | 13:00 | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.01 | 18.8 | 10 | 1.1387 | 15 | 6.5 | 0.41274 | 13:00 | 0.42 | 6 | 45 | 18.9 | 6 | 19.6 | 8 | 2.3625 | 15 | 6 | 0.17778
14:00 | [126 empty] | 258 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.61 | 21 | 17 | 7.71 | 68 | 120 | 18.8 | 0.353 |  | 6.09 | 9 | 0.062 | 5.95 | 10 |  | 5.99 | 9 | [8 empty] | 0.055 | [14 empty] | 0.046 | 1 | 0.27 |  | 0.052 | 0.059 | 2 | 0.32 |  | 0.051 | 1 | 0.16 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.29 | 0.067 | 1 | 3.7 | 18.1 |  |  |  | 7.35 | 0.061 | 1 | 3.4 | 17.1 |  |  |  | 3.8 | 3.4 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.59 | 22 | 18 | 8.3 | 70 | 125 | 19.6 | 0.348 |  | 5.95 | 10 | 0.065 | 5.95 | 10 |  | 5.98 | 10 | [8 empty] | 0.05 | [14 empty] | 0.037 | 1 | 0.28 |  | 0.048 | 0.039 | 2 | 0.37 |  | 0.042 | 2 | 0.14 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.048 | [9 empty] | 6 | 0.293 | 4 | 0.57 | 19.5 | 10.5 | 0.45019 |  | 6.01 | 0.244 | 4 | 0.65 | 19.5 | 10.5 | 0.53274 | 6 | 0.354 | 4 | 0.44 | 20 | 6 | 0.25333 |  |  |  | 0.016 | [9 empty] | 7.44 | 0.055 | 2 | 5 | 18.5 | 27 | 33 | 0.021 | 7.42 | 0.057 | 2 | 4.7 | 17.7 | 24 | 35 | 0.015 | 3.7 | 3.5 | 3.1 | [55 empty] | 21:00 | 0.57 | 10.5 | 24.2286 | 13.8103 | 6 | 19.5 | 8 | 1.7263 | 15 | 6 | 0.33019 | 21:00 | 0.65 | 10.5 | 24.2286 | 15.7486 | 6.01 | 19.5 | 10 | 1.5749 | 15 | 6.5 | 0.41274 | 21:00 | 0.44 | 6 | 45 | 19.8 | 6 | 20 | 6 | 3.3 | 20 | 6 | 0.13333
22:00 | [72 empty] | DOSE |  | TOTAL | 52.5 | 52.5 | 30 | 135 | 42.5 | 42.5 | 42.5 | 127.5 | 0 | 51.7867 | 0 | 70.0229 | 121.8096 | 3.0038 | TOTAL | 319.8406 | 15371.848 | 0 | 3375 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 8.6669 | 8.6669 | 6.834 | 1.0649 | 1.0431 | 1.0377 | 1.0812 | 1.8445 | 0 | 6.325 | 13 | 0.30289 | 0.30289 | 0.30041 | 5.4091 | 2.5375 | 0.50995 | 21.4403 | 4.1056 | 39.0473 | 5.4091 | 2.1197 | 0.50995 | 15.9502 | 2.9624 | 34.3273 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.57 | 22 | 17 | 8.18 | 77 | 130 | 19.5 | 0.355 |  | 5.94 | 11 | 0.061 | 5.91 | 11 |  | 5.93 | 10 | [8 empty] | 0.046 | [14 empty] | 0.032 | 1 | 0.24 |  | 0.043 | 0.04 | 2 | 0.4 |  | 0.04 | 2 | 0.18 | [22 empty] | AVERAGE | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.3573 |  | 14.0046 | 24.3619 | 0.60077 | AVERAGE | 63.9681 | 3074.3696 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.7334 | 1.7334 | 1.3668 | 0.21297 | 0.20863 | 0.20754 | 0.21623 | 0.3689 |  | 1.265 | 2.6 | 0.060578 | 0.060578 | 0.060082 | 1.0818 | 0.50751 | 0.10199 | 4.2881 | 0.82111 | 7.8095 | 1.0818 | 0.42394 | 0.10199 | 3.19 | 0.59249 | 6.8655 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.45 | 132 | 103 | 46 | 432 | 743 | 115.1 | 2.107 | 0.097 | 35.67 | 59 | 0.369 | 35.62 | 60 | 0 | 35.71 | 59 | 0 | 23.9 | 1.643 | 16 | 1.9 | 76.4 | 41.8 | 1.877 | 0.307 | 24.03 | 1.304 | 16 | 2.1 | 76.1 | 42.1 | 2.0523 | 23.97 | 1.253 | 15 | 1.64 | 79 | 24 | 1.1467 | 0.236 | 6 | 1.34 | 0.033 | 0.309 | 0.274 | 9 | 2.04 | 0 | 0.277 | 8 | 1.08 | 0 | 43.71 | 0.367 | 11 | 24.3 | 109.6 | 52 | 78 | 0.042 | 44.12 | 0.355 | 11 | 22.4 | 104.6 | 51 | 78 | 0.041 | 22.9 | 21 | 19.1 |  |  | MINIMUM | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.8827 |  | 12.9974 | 22.8802 | 0 | MINIMUM | 55.0122 | 2766.9326 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.702 | 1.702 | 1.1783 | 0.20102 | 0.20102 | 0.18472 | 0.18472 | 0.3613 |  | 0.80845 | 0 | 0.060206 | 0.060206 | 0.059585 | 1.0818 | 0.50445 | 0.10199 | 4.2651 | 0.81575 | 7.8095 | 1.0818 | 0.39745 | 0.10199 | 3.1654 | 0.57961 | 6.8655 |  | MIN | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.02 | 18.9 | 10 | 1.1387 |  |  |  | MIN | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.01 | 18.8 | 10 | 1.1387 |  |  |  | MIN | 0.36 | 6 | 45 | 16.2 | 6 | 19.9 | 8 | 2.025 |  |  |  | 1.1387
AVERAGE | 6.575 | 22 | 17.1667 | 7.6667 | 72 | 123.8333 | 19.1833 | 0.35117 | 0.0485 | 5.945 | 9.8333 | 0.0615 | 5.9367 | 10 |  | 5.9517 | 9.8333 |  | 5.975 | 0.41075 | 4 | 0.475 | 19.1 | 10.45 | 0.46925 | 0.051167 | 6.0075 | 0.326 | 4 | 0.525 | 19.025 | 10.525 | 0.51308 | 5.9925 | 0.31325 | 3.75 | 0.41 | 19.75 | 6 | 0.28667 | 0.039333 | 1 | 0.22333 | 0.0165 | 0.0515 | 0.045667 | 1.5 | 0.34 |  | 0.046167 | 1.3333 | 0.18 |  | 7.285 | 0.061167 | 1.8333 | 4.05 | 18.2667 | 26 | 39 | 0.021 | 7.3533 | 0.059167 | 1.8333 | 3.7333 | 17.4333 | 25.5 | 39 | 0.0205 | 3.8167 | 3.5 | 3.1833 |  |  | MAXIMUM | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 12.2098 |  | 16.0301 | 27.2102 | 1.9411 | MAXIMUM | 70.0896 | 3689.2436 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.7805 | 1.7805 | 1.571 | 0.22819 | 0.21732 | 0.23905 | 0.26079 | 0.38031 |  | 1.9498 | 4 | 0.060827 | 0.060827 | 0.060827 | 1.0818 | 0.50955 | 0.10199 | 4.3201 | 0.82648 | 7.8095 | 1.0818 | 0.50955 | 0.10199 | 3.198 | 0.62254 | 6.8655
MINIMUM | 6.55 | 20 | 16 | 7.01 | 68 | 120 | 18.7 | 0.313 | 0.048 | 5.71 | 8 | 0.06 | 5.78 | 8 |  | 5.89 | 8 |  | 5.89 | 0.293 | 3 | 0.4 | 18.8 | 10.3 | 0.4439 | 0.046 | 5.96 | 0.244 | 3 | 0.47 | 18.7 | 10.5 | 0.45019 | 5.97 | 0.259 | 3 | 0.36 | 19.5 | 6 | 0.25333 | 0.032 | 1 | 0.16 | 0.016 | 0.043 | 0.039 | 1 | 0.29 |  | 0.04 | 1 | 0.14 |  | 7.21 | 0.053 | 1 | 3.7 | 18.1 | 25 | 33 | 0.021 | 7.26 | 0.055 | 1 | 3.4 | 17.1 | 24 | 35 | 0.015 | 3.7 | 3.4 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 35320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1655 | 1655 | 1305 | 1960 | 1920 | 1910 | 1990 | 1940 | 0 | 3325 | 0 | 4880 | 4880 | 4840 | 400 | 498 | 60 | 7500 | 1530 | 2275 | 200 | 208 | 30 | 2700 | 552 | 1000
MAXIMUM | 6.61 | 25 | 18 | 8.3 | 77 | 130 | 19.8 | 0.371 | 0.049 | 6.09 | 11 | 0.065 | 6.02 | 11 |  | 5.99 | 12 |  | 6.02 | 0.501 | 5 | 0.57 | 19.5 | 10.5 | 0.53274 | 0.055 | 6.05 | 0.389 | 5 | 0.65 | 19.5 | 10.6 | 0.53667 | 6 | 0.362 | 4 | 0.44 | 20 | 6 | 0.29778 | 0.046 | 1 | 0.28 | 0.017 | 0.057 | 0.059 | 2 | 0.4 |  | 0.051 | 2 | 0.3 |  | 7.44 | 0.07 | 2 | 5 | 18.5 | 27 | 45 | 0.021 | 7.43 | 0.065 | 2 | 4.7 | 17.7 | 27 | 43 | 0.026 | 3.9 | 3.6 | 3.3 | [17 empty] | AVERAGE | 7064 | [9 empty] | 331 | 331 | 261 | 392 | 384 | 382 | 398 | 388 |  | 665 |  | 976 | 976 | 968 | 80 | 99.6 | 12 | 1500 | 306 | 455 | 40 | 41.6 | 6 | 540 | 110.4 | 200
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9444 |  | TOTAL AVG COAG ALK: |  |  |  | 9.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.501 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.36 | [5 empty] | 5.9917 |  |  |  |  | 0.059 |  |  |  |  | 0.36 | [6 empty] | 0.059 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 6075 | [9 empty] | 325 | 325 | 225 | 370 | 370 | 340 | 340 | 380 |  | 425 |  | 970 | 970 | 960 | 80 | 99 | 12 | 1500 | 304 | 455 | 40 | 39 | 6 | 530 | 108 | 200
[90 empty] | MAXIMUM | 7740 | [9 empty] | 340 | 340 | 300 | 420 | 400 | 440 | 480 | 400 |  | 1025 |  | 980 | 980 | 980 | 80 | 100 | 12 | 1500 | 308 | 455 | 40 | 50 | 6 | 560 | 116 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.495 |  | TOTAL MGD: |  | 5 |  |  | FINISHED SOUTH 1 |  | START: | 23175850 |  | END: | 23180850 |  |  | Alum | 7637 |  | 8140 |  | 0 | [45 empty] | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.02 | 18.9 | 10 | 1.1387
[73 empty] | FINISHED 2 | 14.315 |  | TOTAL MGD: |  | 5.495 |  |  | FINISHED SOUTH 2 |  | START: | 41043970 |  | END: | 41049465 |  |  | Caustic | 5155 |  | 4040
[73 empty] | TOTAL RAW | 27.465 |  | TOTAL MGD: |  | 4.085 |  |  | FINISHED CONWAY |  | START: | 8770965 |  | END: | 8775050 |  |  | Hypochlorite | 9 |  | 30
[76 empty] | TOTAL MGD: |  | 10.23 |  |  | FINISHED PERRY |  | START: | 30544895 |  | END: | 30555125 |  |  | Phosphate | 2115
[76 empty] | TOTAL MGD: |  | 10.7 |  |  | RAW PLANT 1 |  | START: | 28067400 |  | END: | 28078100 |  |  | Fluoride | 500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.58 |  |  | RAW PLANT 2 |  | START: | 28014140 |  | END: | 28024720 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 6.185 |  |  | RAW PLANT 3 |  | START: | 4314690 |  | END: | 4320875 |  |  | Zinc | 3223
[76 empty] | TOTAL MGD: |  | 1.738 |  |  | DECANT |  | START: | 1409782 |  | END: | 1411520 |  |  | Polymer | 10 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.75495 |  |  | BLOW DOWN |  | START: | 8774.3341 |  | END: | 8775.089 |  |  | NH3 | 9.75
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 700
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2717 | Phosphate | 44
[90 empty] | Caustic 1 | 172 | Fluoride | 54
[90 empty] | Caustic 2 | 86 | Zinc | 7
[90 empty] | Hypochlorite 1 | 336 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 791 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23180850
[91 empty] | FINISHED SOUTH 2 |  | END: | 41049465
[91 empty] | FINISHED CONWAY |  | END: | 8775050
[91 empty] | FINISHED PERRY |  | END: | 30555125
[91 empty] | RAW PLANT 1 |  | END: | 28078100
[91 empty] | RAW PLANT 2 |  | END: | 28024720
[91 empty] | RAW PLANT 3 |  | END: | 4320875
[91 empty] | DECANT |  | END: | 1411520
[91 empty] | BLOW DOWN |  | END: | 8775.089
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 27
DATE: | 2018-02-27 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 20 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 20 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 20
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-02-27 | [23 empty] | DATE: | 2018-02-27
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-27 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43158.0022 | 2,3,5 | 47 | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.4731 | 1,2 | 15.2741 | 25.7472 | 1.6877 | 43158.0022 | 70.0896 | 3689.2436 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.702 | 1.702 | 1.1783 | 0.20646 | 0.20646 | 0.19016 | 0.19016 | 0.3613 | 0 | 0.80845 | 1.5 | 0.060827 | 0.060827 | 0.060827 | 1.0818 | 0.50955 | 0.10199 | 4.3201 | 0.81575 | 7.8095 | 1.0818 | 0.50955 | 0.10199 | 3.1654 | 0.62254 | 6.8655 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.361 | 4 | 0.44 | 19.1 | 10.3 | 0.4439 |  | 6 | 0.298 | 3 | 0.56 | 18.9 | 10.6 | 0.45333 | 6.01 | 0.397 | 4 | 0.34 | 19.7 | 6.1 | 0.34593 | [13 empty] | 7.43 | 0.054 | 1 | 4.8 | 18.4 |  |  |  | 7.4 | 0.055 | 2 | 4.4 | 17.6 |  |  |  | 3.7 | 3.5 | 3.3 | [18 empty] | 7740 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 225 | 380 | 380 | 350 | 350 | 380 | 0 | 425 |  | 980 | 980 | 980 | 80 | 100 | 12 | 1500 | 304 | 455 | 40 | 50 | 6 | 560 | 116 | 200 |  | 1:00 | 0.44 | 10.3 | 24.699 | 10.8676 | 5.96 | 19.1 | 8 | 1.3584 | 15 | 6 | 0.3239 | 1:00 | 0.56 | 10.6 | 24 | 13.44 | 6 | 18.9 | 8 | 1.68 | 15 | 6 | 0.33333 | 1:00 | 0.34 | 6.1 | 44.2623 | 15.0492 | 6.01 | 19.7 | 10 | 1.5049 | 15 | 6.5 | 0.22593
2:00 | [72 empty] | 43158.3076 | 2,3,5 | 32 | 9.7 | 9.7 | 5.6 | 25 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 10.4731 | 1,2 | 15.2741 | 25.7472 | 0 | 43158.4326 | 70.0244 | 3812.2184 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.9403 | 1.9403 | 1.0272 | 0.23524 | 0.23524 | 0.23524 | 0.27053 | 0.44823 | 0 | 0.95112 | 2 | 0.060198 | 0.060198 | 0.060198 | 1.12 | 0.49975 | 0.10188 | 4.2961 | 0.81877 | 8.5103 | 1.061 | 0.49975 | 0.09262 | 3.2412 | 0.61408 | 7.4816 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.59 | 22 | 18 | 9.9 | 72 | 140 | 19.4 | 0.358 |  | 5.97 | 12 | 0.068 | 5.95 | 12 |  | 5.98 | 12 | [8 empty] | 0.054 | [14 empty] | 0.034 | 1 | 0.22 |  | 0.051 | 0.037 | 1 | 0.36 |  | 0.04 | 1 | 0.2 | [38 empty] | 7160 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 180 | 400 | 400 | 400 | 460 | 440 | 0 | 500 |  | 890 | 890 | 890 | 76 | 90 | 11 | 1370 | 280 | 455 | 36 | 45 | 5 | 520 | 105 | 200 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43158.8224 | 2,3,5 | 32 | 9.6 | 9.6 | 6 | 25.2 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 10.6157 | 1,2 | 13.1818 | 23.7974 | 1.6315 | 43158.8224 | 69.8568 | 3750.731 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.712 | 1.712 | 1.712 | 0.20798 | 0.20798 | 0.18421 | 0.18421 | 0.19016 | 0.28523 | 0.95112 | 2 | 0.060198 | 0.060198 | 0.060198 | 1.12 | 0.49975 | 0.09262 | 4.2861 | 0.81877 | 7.5751 | 1.12 | 0.44422 | 0.11114 | 3.1742 | 0.59654 | 5.6112 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.23 | 0.048 | 1 | 4.7 | 18.4 |  |  |  | 7.45 | 0.05 | 1 | 4.2 | 17.5 |  |  |  | 3.7 | 3.5 | 3.2 | [18 empty] | 7200 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 350 | 350 | 310 | 310 | 200 | 300 | 500 |  | 890 | 890 | 890 | 76 | 90 | 10 | 1370 | 280 | 405 | 38 | 40 | 6 | 500 | 102 | 150 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.57 | 27 | 20 | 9.02 | 74 | 133 | 18.1 | 0.371 |  | 5.89 | 12 | 0.064 | 5.8 | 11 |  | 5.88 | 12 | [8 empty] | 0.046 | [14 empty] | 0.032 | 1 | 0.24 |  | 0.045 | 0.029 | 1 | 0.3 |  | 0.041 | 1 | 0.2 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.049 | [9 empty] | 5.97 | 0.264 | 3 | 0.49 | 17.9 | 9.7 | 0.42503 |  | 5.98 | 0.259 | 3 | 0.57 | 17.8 | 9.7 | 0.42503 | 5.99 | 0.436 | 4 | 0.46 | 18.8 | 5.6 | 0.28593 |  |  |  | 0.019 | [9 empty] | 7.49 | 0.06 | 3 | 4.7 | 17.7 | 29 | 44 | 0.022 | 8.09 | 0.06 | 2 | 4 | 16.8 | 35 | 39 | 0.027 | 3.8 | 3.5 | 3.3 | [55 empty] | 9:00 | 0.49 | 9.7 | 26.2268 | 12.8511 | 5.97 | 17.9 | 8 | 1.6064 | 15 | 6 | 0.30503 | 9:00 | 0.57 | 9.7 | 26.2268 | 14.9493 | 5.98 | 17.8 | 8 | 1.8687 | 15 | 6 | 0.30503 | 9:00 | 0.46 | 5.6 | 48.2143 | 22.1786 | 5.99 | 18.8 | 8 | 2.7723 | 15 | 6 | 0.16593
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.58 | 22 | 20 | 7.52 | 79 | 130 | 18.1 | 0.409 |  | 5.92 | 11 | 0.062 | 5.94 | 11 |  | 5.9 | 11 | [8 empty] | 0.045 | [14 empty] | 0.027 | 1 | 0.36 |  | 0.045 | 0.044 | 1 | 0.4 |  | 0.052 | 1 | 0.24 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.561 | 4 | 0.56 | 18.4 | 9.2 | 0.40931 |  | 6.02 | 0.421 | 3 | 0.55 | 18.3 | 9.2 | 0.48164 | 6.03 | 0.322 | 3 | 0.4 | 18.7 | 5.5 | 0.3237 | [13 empty] | 8.21 | 0.056 | 1 | 4.1 | 17.7 |  |  |  | 8.32 | 0.055 | 1 | 3.9 | 17.2 |  |  |  | 3.6 | 3.6 | 3.3 | [55 empty] | 13:00 | 0.56 | 9.2 | 27.6522 | 15.4852 | 6 | 18.4 | 8 | 1.9357 | 15 | 6 | 0.28931 | 13:00 | 0.55 | 9.2 | 27.6522 | 15.2087 | 6.02 | 18.3 | 10 | 1.5209 | 15 | 6.5 | 0.36164 | 13:00 | 0.4 | 5.5 | 49.0909 | 19.6364 | 6.03 | 18.7 | 10 | 1.9636 | 15 | 6.5 | 0.2037
14:00 | [126 empty] | 236 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.52 | 22 | 16 | 8.18 | 77 | 130 | 18.2 | 0.389 |  | 5.92 | 10 | 0.062 | 5.89 | 10 |  | 5.89 | 10 | [8 empty] | 0.05 | [14 empty] | 0.022 | 1 | 0.25 |  | 0.047 | 0.028 | 1 | 0.31 |  | 0.068 | 1 | 0.25 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.23 | 0.052 | 1 | 4.5 | 17.7 |  |  |  | 7.27 | 0.052 | 1 | 4.3 | 16.7 |  |  |  | 3.7 | 3.6 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 22 | 20 | 9.29 | 65 | 127 | 19 | 0.323 |  | 5.95 | 10 | 0.064 | 5.94 | 10 |  | 5.98 | 10 | [8 empty] | 0.051 | [14 empty] | 0.023 | 1 | 0.3 |  | 0.049 | 0.033 | 1 | 0.49 |  | 0.06 | 1 | 0.48 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.056 | [9 empty] | 6 | 0.237 | 4 | 0.49 | 18.5 | 9.6 | 0.42189 |  | 6 | 0.225 | 4 | 0.55 | 18.5 | 9.6 | 0.42189 | 6 | 0.388 | 4 | 0.45 | 19 | 6 | 0.29778 |  |  |  | 0.019 | [9 empty] | 7.1 | 0.05 | 1 | 5 | 18.1 | 22 | 32 | 0.021 | 7.19 | 0.049 | 1 | 4.7 | 17.3 | 24 | 37 | 0.022 | 3.7 | 3.8 | 4.1 | [55 empty] | 21:00 | 0.49 | 9.6 | 26.5 | 12.985 | 6 | 18.5 | 8 | 1.6231 | 15 | 6 | 0.30189 | 21:00 | 0.55 | 9.6 | 26.5 | 14.575 | 6 | 18.5 | 8 | 1.8219 | 15 | 6 | 0.30189 | 21:00 | 0.45 | 6 | 45 | 20.25 | 6 | 19 | 8 | 2.5312 | 15 | 6 | 0.17778
22:00 | [72 empty] | DOSE |  | TOTAL | 29.8 | 29.8 | 17.6 | 77.2 | 24.1 | 24.1 | 24.1 | 72.3 | 0 | 31.5619 | 0 | 43.7299 | 75.2918 | 3.3192 | TOTAL | 209.9709 | 11252.193 | 0 | 2000 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 5.3543 | 5.3543 | 3.9175 | 0.64968 | 0.64968 | 0.60961 | 0.6449 | 0.99968 | 0.28523 | 2.7107 | 5.5 | 0.18122 | 0.18122 | 0.18122 | 3.3217 | 1.509 | 0.29649 | 12.9024 | 2.4533 | 23.8949 | 3.2628 | 1.4535 | 0.30575 | 9.5807 | 1.8332 | 19.9582 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.63 | 23 | 19 | 7.71 | 75 | 122 | 18.5 | 0.357 |  | 5.99 | 11 | 0.07 | 5.97 | 11 |  | 5.95 | 10 | [8 empty] | 0.042 | [14 empty] | 0.024 | 1 | 0.24 |  | 0.041 | 0.034 | 1 | 0.31 |  | 0.056 | 1 | 0.48 | [22 empty] | AVERAGE | 9.9333 | 9.9333 | 5.8667 | 25.7333 | 8.0333 | 8.0333 | 8.0333 | 24.1 |  | 10.5206 |  | 14.5766 | 25.0973 | 1.1064 | AVERAGE | 69.9903 | 3750.731 |  | 666.6667 | #N/A | #N/A | #N/A |  |  |  | 1.7848 | 1.7848 | 1.3058 | 0.21656 | 0.21656 | 0.2032 | 0.21497 | 0.33323 | 0.095078 | 0.90357 | 1.8333 | 0.060408 | 0.060408 | 0.060408 | 1.1072 | 0.50301 | 0.098831 | 4.3008 | 0.81776 | 7.965 | 1.0876 | 0.4845 | 0.10192 | 3.1936 | 0.61105 | 6.6527 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.51 | 138 | 113 | 51.62 | 442 | 782 | 111.3 | 2.207 | 0.105 | 35.64 | 66 | 0.39 | 35.49 | 65 | 0 | 35.58 | 65 | 0 | 23.93 | 1.423 | 15 | 1.98 | 73.9 | 38.8 | 1.7001 | 0.288 | 24 | 1.203 | 13 | 2.23 | 73.5 | 39.1 | 1.7819 | 24.03 | 1.543 | 15 | 1.65 | 76.2 | 23.2 | 1.2533 | 0.162 | 6 | 1.61 | 0.038 | 0.278 | 0.205 | 6 | 2.17 | 0 | 0.317 | 6 | 1.85 | 0 | 44.69 | 0.32 | 8 | 27.8 | 108 | 51 | 76 | 0.043 | 45.72 | 0.321 | 8 | 25.5 | 103.1 | 59 | 76 | 0.049 | 22.2 | 21.5 | 21 |  |  | MINIMUM | 9.6 | 9.6 | 5.6 | 25 | 7.8 | 7.8 | 7.8 | 23.4 |  | 10.4731 |  | 13.1818 | 23.7974 | 0 | MINIMUM | 69.8568 | 3689.2436 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.702 | 1.702 | 1.0272 | 0.20646 | 0.20646 | 0.18421 | 0.18421 | 0.19016 | 0 | 0.80845 | 1.5 | 0.060198 | 0.060198 | 0.060198 | 1.0818 | 0.49975 | 0.09262 | 4.2861 | 0.81575 | 7.5751 | 1.061 | 0.44422 | 0.09262 | 3.1654 | 0.59654 | 5.6112 |  | MIN | 0.44 | 10.3 | 24.699 | 10.8676 | 5.96 | 19.1 | 8 | 1.3584 |  |  |  | MIN | 0.55 | 9.2 | 27.6522 | 15.2087 | 6.02 | 18.3 | 10 | 1.5209 |  |  |  | MIN | 0.34 | 6.1 | 44.2623 | 15.0492 | 6.01 | 19.7 | 10 | 1.5049 |  |  |  | 1.3584
AVERAGE | 6.585 | 23 | 18.8333 | 8.6033 | 73.6667 | 130.3333 | 18.55 | 0.36783 | 0.0525 | 5.94 | 11 | 0.065 | 5.915 | 10.8333 |  | 5.93 | 10.8333 |  | 5.9825 | 0.35575 | 3.75 | 0.495 | 18.475 | 9.7 | 0.42503 | 0.048 | 6 | 0.30075 | 3.25 | 0.5575 | 18.375 | 9.775 | 0.44547 | 6.0075 | 0.38575 | 3.75 | 0.4125 | 19.05 | 5.8 | 0.31333 | 0.027 | 1 | 0.26833 | 0.019 | 0.046333 | 0.034167 | 1 | 0.36167 |  | 0.052833 | 1 | 0.30833 |  | 7.4483 | 0.053333 | 1.3333 | 4.6333 | 18 | 25.5 | 38 | 0.0215 | 7.62 | 0.0535 | 1.3333 | 4.25 | 17.1833 | 29.5 | 38 | 0.0245 | 3.7 | 3.5833 | 3.5 |  |  | MAXIMUM | 10.5 | 10.5 | 6 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.6157 |  | 15.2741 | 25.7472 | 1.6877 | MAXIMUM | 70.0896 | 3812.2184 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.9403 | 1.9403 | 1.712 | 0.23524 | 0.23524 | 0.23524 | 0.27053 | 0.44823 | 0.28523 | 0.95112 | 2 | 0.060827 | 0.060827 | 0.060827 | 1.12 | 0.50955 | 0.10199 | 4.3201 | 0.81877 | 8.5103 | 1.12 | 0.50955 | 0.11114 | 3.2412 | 0.62254 | 7.4816
MINIMUM | 6.52 | 22 | 16 | 7.52 | 65 | 122 | 18.1 | 0.323 | 0.049 | 5.89 | 10 | 0.062 | 5.8 | 10 |  | 5.88 | 10 |  | 5.96 | 0.237 | 3 | 0.44 | 17.9 | 9.2 | 0.40931 | 0.042 | 5.98 | 0.225 | 3 | 0.55 | 17.8 | 9.2 | 0.42189 | 5.99 | 0.322 | 3 | 0.34 | 18.7 | 5.5 | 0.28593 | 0.022 | 1 | 0.22 | 0.019 | 0.041 | 0.028 | 1 | 0.3 |  | 0.04 | 1 | 0.2 |  | 7.1 | 0.048 | 1 | 4.1 | 17.7 | 22 | 32 | 0.021 | 7.19 | 0.049 | 1 | 3.9 | 16.7 | 24 | 37 | 0.022 | 3.6 | 3.5 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 22100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 965 | 965 | 705 | 1130 | 1130 | 1060 | 1120 | 1020 | 300 | 1425 | 0 | 2760 | 2760 | 2760 | 232 | 280 | 33 | 4240 | 864 | 1315 | 114 | 135 | 17 | 1580 | 323 | 550
MAXIMUM | 6.63 | 27 | 20 | 9.9 | 79 | 140 | 19.4 | 0.409 | 0.056 | 5.99 | 12 | 0.07 | 5.97 | 12 |  | 5.98 | 12 |  | 6 | 0.561 | 4 | 0.56 | 19.1 | 10.3 | 0.4439 | 0.054 | 6.02 | 0.421 | 4 | 0.57 | 18.9 | 10.6 | 0.48164 | 6.03 | 0.436 | 4 | 0.46 | 19.7 | 6.1 | 0.34593 | 0.034 | 1 | 0.36 | 0.019 | 0.051 | 0.044 | 1 | 0.49 |  | 0.068 | 1 | 0.48 |  | 8.21 | 0.06 | 3 | 5 | 18.4 | 29 | 44 | 0.022 | 8.32 | 0.06 | 2 | 4.7 | 17.6 | 35 | 39 | 0.027 | 3.8 | 3.8 | 4.1 | [17 empty] | AVERAGE | 7366.6667 | [9 empty] | 321.6667 | 321.6667 | 235 | 376.6667 | 376.6667 | 353.3333 | 373.3333 | 340 | 100 | 475 |  | 920 | 920 | 920 | 77.3333 | 93.3333 | 11 | 1413.3333 | 288 | 438.3333 | 38 | 45 | 5.6667 | 526.6667 | 107.6667 | 183.3333
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9283 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.561 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.34 | [5 empty] | 5.9967 |  |  |  |  | 0.068 |  |  |  |  | 0.34 | [6 empty] | 0.068 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 7160 | [9 empty] | 300 | 300 | 180 | 350 | 350 | 310 | 310 | 200 | 0 | 425 |  | 890 | 890 | 890 | 76 | 90 | 10 | 1370 | 280 | 405 | 36 | 40 | 5 | 500 | 102 | 150
[90 empty] | MAXIMUM | 7740 | [9 empty] | 340 | 340 | 300 | 400 | 400 | 400 | 460 | 440 | 300 | 500 |  | 980 | 980 | 980 | 80 | 100 | 12 | 1500 | 304 | 455 | 40 | 50 | 6 | 560 | 116 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.095 |  | TOTAL MGD: |  | 4.805 |  |  | FINISHED SOUTH 1 |  | START: | 23180850 |  | END: | 23185655 |  |  | Alum | 7037 |  | 7392 |  | 0 | [45 empty] | 0.44 | 10.3 | 24.699 | 10.8676 | 5.96 | 19.1 | 8 | 1.3584
[73 empty] | FINISHED 2 | 13.935 |  | TOTAL MGD: |  | 5.29 |  |  | FINISHED SOUTH 2 |  | START: | 41049465 |  | END: | 41054755 |  |  | Caustic | 4979 |  | 3921
[73 empty] | TOTAL RAW | 25.18 |  | TOTAL MGD: |  | 4.885 |  |  | FINISHED CONWAY |  | START: | 8775050 |  | END: | 8779935 |  |  | Hypochlorite | 12.5 |  | 19
[76 empty] | TOTAL MGD: |  | 9.05 |  |  | FINISHED PERRY |  | START: | 30555125 |  | END: | 30564175 |  |  | Phosphate | 1994
[76 empty] | TOTAL MGD: |  | 9.74 |  |  | RAW PLANT 1 |  | START: | 28078100 |  | END: | 28087840 |  |  | Fluoride | 500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.63 |  |  | RAW PLANT 2 |  | START: | 28024720 |  | END: | 28034350 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 5.81 |  |  | RAW PLANT 3 |  | START: | 4320875 |  | END: | 4326685 |  |  | Zinc | 3208
[76 empty] | TOTAL MGD: |  | 1.793 |  |  | DECANT |  | START: | 1411520 |  | END: | 1413313 |  |  | Polymer | 10 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 0.80996 |  |  | BLOW DOWN |  | START: | 8775.089 |  | END: | 8775.899 |  |  | NH3 | 9.55
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
[90 empty] | BI-SULFITE | 800 | PUMP SPEED | 17
DAY TANK Chemical Inventory
[90 empty] | Alum | 2722 | Phosphate | 44
[90 empty] | Caustic 1 | 164 | Fluoride | 50
[90 empty] | Caustic 2 | 72 | Zinc | 7
[90 empty] | Hypochlorite 1 | 345 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 718 | Polymer 2 | 2
[91 empty] | FINISHED SOUTH 1 |  | END: | 23185655
[91 empty] | FINISHED SOUTH 2 |  | END: | 41054755
[91 empty] | FINISHED CONWAY |  | END: | 8779935
[91 empty] | FINISHED PERRY |  | END: | 30564175
[91 empty] | RAW PLANT 1 |  | END: | 28087840
[91 empty] | RAW PLANT 2 |  | END: | 28034350
[91 empty] | RAW PLANT 3 |  | END: | 4326685
[91 empty] | DECANT |  | END: | 1413313
[91 empty] | BLOW DOWN |  | END: | 8775.899
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 28
DATE: | 2018-02-28 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 5 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 5 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 5 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-02-28 | [23 empty] | DATE: | 2018-02-28
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-02-28 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43159.0054 | 2,3,5 | 32 | 9.6 | 9.6 | 6 | 25.2 | 7.8 | 7.8 | 7.8 | 23.4 | 7,1 | 10.6157 | 1,2 | 13.1818 | 23.7974 | 1.5782 | 43159.0054 | 69.8568 | 3750.731 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.712 | 1.712 | 1.712 | 0.20798 | 0.20798 | 0.18421 | 0.18421 | 0.19016 | 0.28523 | 0.95112 | 2 | 0.060198 | 0.060198 | 0.060198 | 1.12 | 0.49975 | 0.09262 | 4.2861 | 0.81877 | 7.5751 | 1.12 | 0.44422 | 0.11114 | 3.1742 | 0.59654 | 5.6112 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6 | 0.294 | 3 | 0.48 | 18.1 | 9.8 | 0.42818 |  | 6.05 | 0.245 | 3 | 0.51 | 17.9 | 9.9 | 0.50915 | 6.03 | 0.476 | 4 | 0.43 | 18.9 | 6.2 | 0.34963 | [13 empty] | 7.12 | 0.048 | 1 | 4.7 | 17.8 |  |  |  | 7.1 | 0.05 | 1 | 4.6 | 17.1 |  |  |  | 3.7 | 3.9 | 2.7 | [18 empty] | 7200 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 350 | 350 | 310 | 310 | 200 | 300 | 500 |  | 890 | 890 | 890 | 76 | 90 | 10 | 1370 | 280 | 405 | 38 | 40 | 6 | 500 | 102 | 150 |  | 1:00 | 0.48 | 9.8 | 25.9592 | 12.4604 | 6 | 18.1 | 8 | 1.5576 | 15 | 6 | 0.30818 | 1:00 | 0.51 | 9.9 | 25.697 | 13.1055 | 6.05 | 17.9 | 10 | 1.3105 | 15 | 6.5 | 0.38915 | 1:00 | 0.43 | 6.2 | 43.5484 | 18.7258 | 6.03 | 18.9 | 10 | 1.8726 | 15 | 6.5 | 0.22963
2:00 | [72 empty] | 43159.3289 | 2,3,5 | 32 | 10.3 | 10.3 | 6.3 | 26.9 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.6157 | 1,2 | 13.1818 | 23.7974 | 1.5631 | 43159.3289 | 70.3502 | 3873.7058 | 0 | 650 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.7281 | 1.6758 | 1.702 | 0.21046 | 0.22154 | 0.21046 | 0.22154 | 0.38031 | 0.099606 | 1.8452 | 3 | 0.058965 | 0.058965 | 0.060206 | 1.217 | 0.49935 | 0.10199 | 4.2732 | 0.73793 | 7.5177 | 1.1359 | 0.39745 | 0.10199 | 3.3517 | 0.53668 | 6.5222 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.56 | 24 | 18 | 7.79 | 72 | 133 | 18.5 | 0.323 |  | 5.99 | 12 | 0.07 | 5.98 | 12 |  | 6 | 12 | [8 empty] | 0.054 | [14 empty] | 0.028 | 1 | 0.22 |  | 0.049 | 0.034 | 1 | 0.32 |  | 0.048 | 1 | 0.4 | [38 empty] | 7740 | [6 empty] | 0 | 0 | 0 | 330 | 320 | 325 | 380 | 400 | 380 | 400 | 420 | 110 | 970 |  | 950 | 950 | 970 | 90 | 98 | 12 | 1490 | 275 | 438 | 42 | 39 | 6 | 550 | 100 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43159.7928 | 2,3,5 | 48 | 10.3 | 10.3 | 6.3 | 26.9 | 8.5 | 8.5 | 8.5 | 25.5 | 7,1 | 10.6157 | 1,2 | 13.1818 | 23.7974 | 0 | 43159.7928 | 75.4401 | 4242.6302 | 0 | 675 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1.571 | 1.7805 | 1.7281 | 0.19939 | 0.18277 | 0.21046 | 0.20493 | 0.38484 | 0.090551 | 0.95112 | 0 | 0.059585 | 0.059585 | 0.058965 | 1.2306 | 0.49935 | 0.10199 | 4.3101 | 0.81843 | 8.2385 | 1.0818 | 0.39745 | 0.10199 | 3.1907 | 0.56351 | 6.5222 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.17 | 0.05 | 1 | 5 | 17.9 |  |  |  | 7.19 | 0.053 | 1 | 4.3 | 17.1 |  |  |  | 3.8 | 3.9 | 3 | [18 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 300 | 340 | 330 | 360 | 330 | 380 | 370 | 425 | 100 | 500 |  | 960 | 960 | 950 | 91 | 98 | 12 | 1500 | 305 | 480 | 40 | 39 | 6 | 520 | 105 | 190 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.61 | 24 | 19 | 7.43 | 71 | 123 | 17.4 | 0.369 |  | 5.88 | 10 | 0.056 | 5.87 | 11 |  | 5.89 | 12 | [8 empty] | 0.041 | [14 empty] | 0.073 | 1 | 0.37 |  | 0.042 | 0.034 | 1 | 0.39 |  | 0.049 | 1 | 0.4 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.053 | [9 empty] | 6.06 | 0.368 | 4 | 0.47 | 17.1 | 10.3 | 0.52487 |  | 6.04 | 0.316 | 3 | 0.51 | 17 | 10.2 | 0.52094 | 6.05 | 0.308 | 4 | 0.5 | 18.1 | 6.5 | 0.36074 |  |  |  | 0.019 | [9 empty] | 7.38 | 0.058 | 1 | 4.7 | 17 | 28 | 49 | 0.022 | 7.53 | 0.058 | 1 | 4.4 | 16.1 | 27 | 49 | 0.015 | 3.8 | 3.7 | 3.2 | [55 empty] | 9:00 | 0.47 | 10.3 | 24.699 | 11.6085 | 6.06 | 17.1 | 10 | 1.1609 | 15 | 6.5 | 0.40487 | 9:00 | 0.51 | 10.2 | 24.9412 | 12.72 | 6.04 | 17 | 10 | 1.272 | 15 | 6.5 | 0.40094 | 9:00 | 0.5 | 6.5 | 41.5385 | 20.7692 | 6.05 | 18.1 | 10 | 2.0769 | 15 | 6.5 | 0.24074
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.62 | 23 | 20 | 7.73 | 67 | 120 | 17.4 | 0.387 |  | 6.02 | 12 | 0.052 | 6.06 | 12 |  | 6 | 12 | [8 empty] | 0.04 | [14 empty] | 0.061 | 1 | 0.35 |  | 0.042 | 0.029 | 1 | 0.34 |  | 0.053 | 1 | 0.37 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.82 | 0.411 | 4 | 0.45 | 17.3 | 10.3 | 0.4439 |  | 5.93 | 0.332 | 4 | 0.4 | 17.2 | 10.3 | 0.4439 | 6.05 | 0.311 | 4 | 0.51 | 18 | 6.3 | 0.35333 | [13 empty] | 7.2 | 0.075 | 1 | 4.4 | 16.8 |  |  |  | 7.73 | 0.072 | 1 | 4.6 | 16.3 |  |  |  | 3.8 | 3.6 | 3.1 | [55 empty] | 13:00 | 0.45 | 10.3 | 24.699 | 11.1146 | 5.82 | 17.3 | 8 | 1.3893 | 15 | 6 | 0.3239 | 13:00 | 0.4 | 10.3 | 24.699 | 9.8796 | 5.93 | 17.2 | 8 | 1.235 | 15 | 6 | 0.3239 | 13:00 | 0.51 | 6.3 | 42.8571 | 21.8571 | 6.05 | 18 | 10 | 2.1857 | 15 | 6.5 | 0.23333
14:00 | [126 empty] | 241 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.57 | 24 | 20 | 7.08 | 84 | 129 | 17.4 | 0.425 |  | 5.95 | 12 | 0.097 | 5.91 | 12 |  | 6.01 | 12 | [8 empty] | 0.055 | [14 empty] | 0.055 | 1 | 0.3 |  | 0.056 | 0.035 | 1 | 0.27 |  | 0.054 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.37 | 0.067 | 1 | 4.6 | 16.8 |  |  |  | 7.23 | 0.061 | 1 | 4.7 | 16.3 |  |  |  | 3.9 | 3.6 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.6 | 24 | 20 | 8.4 | 78 | 130 | 17.4 | 0.384 |  | 6.1 | 12 | 0.064 | 6.11 | 12 |  | 6 | 12 | [8 empty] | 0.053 | [14 empty] | 0.051 | 1 | 0.36 |  | 0.048 | 0.037 | 1 | 0.39 |  | 0.06 | 1 | 0.43 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.054 | [9 empty] | 6.006 | 0.35 | 5 | 0.45 | 17.2 | 10.3 | 0.52487 |  | 6.05 | 0.259 | 4 | 0.54 | 17.1 | 10.1 | 0.51701 | 6.08 | 0.457 | 4 | 0.62 | 18.1 | 6.4 | 0.35704 |  |  |  | 0.011 | [9 empty] | 7.61 | 0.066 | 1 | 4.2 | 16.8 | 28 | 49 | 0.021 | 7.77 | 0.063 | 1 | 4.4 | 16.2 | 28 | 49 | 0.008 | 3.9 | 3.6 | 3.1 | [55 empty] | 21:00 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.006 | 17.2 | 10 | 1.1115 | 15 | 6.5 | 0.40487 | 21:00 | 0.54 | 10.1 | 25.1881 | 13.6016 | 6.05 | 17.1 | 10 | 1.3602 | 15 | 6.5 | 0.39701 | 21:00 | 0.62 | 6.4 | 42.1875 | 26.1562 | 6.08 | 18.1 | 10 | 2.6156 | 15 | 6.5 | 0.23704
22:00 | [72 empty] | DOSE |  | TOTAL | 30.2 | 30.2 | 18.6 | 79 | 24.8 | 24.8 | 24.8 | 74.4 | 0 | 31.847 | 0 | 39.5453 | 71.3923 | 3.1414 | TOTAL | 215.6471 | 11867.067 | 0 | 1975 | #N/A | #N/A | #N/A | 0 | 0 | 0 | 5.0112 | 5.1683 | 5.1421 | 0.61783 | 0.6123 | 0.60514 | 0.61068 | 0.95531 | 0.47539 | 3.7474 | 5 | 0.17875 | 0.17875 | 0.17937 | 3.5676 | 1.4985 | 0.2966 | 12.8694 | 2.3751 | 23.3313 | 3.3377 | 1.2391 | 0.31512 | 9.7166 | 1.6967 | 18.6556 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.65 | 24 | 20 | 7.8 | 76 | 129 | 17.2 | 0.365 |  | 6 | 12 | 0.07 | 6 | 12 |  | 6 | 12 | [8 empty] | 0.058 | [14 empty] | 0.05 | 1 | 0.39 |  | 0.056 | 0.035 | 1 | 0.39 |  | 0.06 | 1 | 0.46 | [22 empty] | AVERAGE | 10.0667 | 10.0667 | 6.2 | 26.3333 | 8.2667 | 8.2667 | 8.2667 | 24.8 |  | 10.6157 |  | 13.1818 | 23.7974 | 1.0471 | AVERAGE | 71.8824 | 3955.689 |  | 658.3333 | #N/A | #N/A | #N/A |  |  |  | 1.6704 | 1.7228 | 1.714 | 0.20594 | 0.2041 | 0.20171 | 0.20356 | 0.31844 | 0.15846 | 1.2491 | 1.6667 | 0.059583 | 0.059583 | 0.05979 | 1.1892 | 0.49949 | 0.098867 | 4.2898 | 0.79171 | 7.7771 | 1.1126 | 0.41304 | 0.10504 | 3.2389 | 0.56557 | 6.2185 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.61 | 143 | 117 | 46.23 | 448 | 764 | 105.3 | 2.253 | 0.107 | 35.94 | 70 | 0.409 | 35.93 | 71 | 0 | 35.9 | 72 | 0 | 23.886 | 1.423 | 16 | 1.85 | 69.7 | 40.7 | 1.9218 | 0.301 | 24.07 | 1.152 | 14 | 1.96 | 69.2 | 40.5 | 1.991 | 24.21 | 1.552 | 16 | 2.06 | 73.1 | 25.4 | 1.4207 | 0.318 | 6 | 1.99 | 0.03 | 0.293 | 0.204 | 6 | 2.1 | 0 | 0.324 | 6 | 2.46 | 0 | 43.85 | 0.364 | 6 | 27.6 | 103.1 | 56 | 98 | 0.043 | 44.55 | 0.357 | 6 | 27 | 99.1 | 55 | 98 | 0.023 | 22.9 | 22.3 | 18.2 |  |  | MINIMUM | 9.6 | 9.6 | 6 | 25.2 | 7.8 | 7.8 | 7.8 | 23.4 |  | 10.6157 |  | 13.1818 | 23.7974 | 0 | MINIMUM | 69.8568 | 3750.731 |  | 650 | #N/A | #N/A | #N/A |  |  |  | 1.571 | 1.6758 | 1.702 | 0.19939 | 0.18277 | 0.18421 | 0.18421 | 0.19016 | 0.090551 | 0.95112 | 0 | 0.058965 | 0.058965 | 0.058965 | 1.12 | 0.49935 | 0.09262 | 4.2732 | 0.73793 | 7.5177 | 1.0818 | 0.39745 | 0.10199 | 3.1742 | 0.53668 | 5.6112 |  | MIN | 0.45 | 10.3 | 24.699 | 11.1146 | 6.006 | 17.2 | 10 | 1.1115 |  |  |  | MIN | 0.4 | 10.3 | 24.699 | 9.8796 | 5.93 | 17.2 | 8 | 1.235 |  |  |  | MIN | 0.43 | 6.2 | 43.5484 | 18.7258 | 6.03 | 18.9 | 10 | 1.8726 |  |  |  | 1.1115
AVERAGE | 6.6017 | 23.8333 | 19.5 | 7.705 | 74.6667 | 127.3333 | 17.55 | 0.3755 | 0.0535 | 5.99 | 11.6667 | 0.068167 | 5.9883 | 11.8333 |  | 5.9833 | 12 |  | 5.9715 | 0.35575 | 4 | 0.4625 | 17.425 | 10.175 | 0.48046 | 0.050167 | 6.0175 | 0.288 | 3.5 | 0.49 | 17.3 | 10.125 | 0.49775 | 6.0525 | 0.388 | 4 | 0.515 | 18.275 | 6.35 | 0.35519 | 0.053 | 1 | 0.33167 | 0.015 | 0.048833 | 0.034 | 1 | 0.35 |  | 0.054 | 1 | 0.41 |  | 7.3083 | 0.060667 | 1 | 4.6 | 17.1833 | 28 | 49 | 0.0215 | 7.425 | 0.0595 | 1 | 4.5 | 16.5167 | 27.5 | 49 | 0.0115 | 3.8167 | 3.7167 | 3.0333 |  |  | MAXIMUM | 10.3 | 10.3 | 6.3 | 26.9 | 8.5 | 8.5 | 8.5 | 25.5 |  | 10.6157 |  | 13.1818 | 23.7974 | 1.5782 | MAXIMUM | 75.4401 | 4242.6302 |  | 675 | #N/A | #N/A | #N/A |  |  |  | 1.7281 | 1.7805 | 1.7281 | 0.21046 | 0.22154 | 0.21046 | 0.22154 | 0.38484 | 0.28523 | 1.8452 | 3 | 0.060198 | 0.060198 | 0.060206 | 1.2306 | 0.49975 | 0.10199 | 4.3101 | 0.81877 | 8.2385 | 1.1359 | 0.44422 | 0.11114 | 3.3517 | 0.59654 | 6.5222
MINIMUM | 6.56 | 23 | 18 | 7.08 | 67 | 120 | 17.2 | 0.323 | 0.053 | 5.88 | 10 | 0.052 | 5.87 | 11 |  | 5.89 | 12 |  | 5.82 | 0.294 | 3 | 0.45 | 17.1 | 9.8 | 0.42818 | 0.04 | 5.93 | 0.245 | 3 | 0.4 | 17 | 9.9 | 0.4439 | 6.03 | 0.308 | 4 | 0.43 | 18 | 6.2 | 0.34963 | 0.028 | 1 | 0.22 | 0.011 | 0.042 | 0.029 | 1 | 0.27 |  | 0.048 | 1 | 0.37 |  | 7.12 | 0.048 | 1 | 4.2 | 16.8 | 28 | 49 | 0.021 | 7.1 | 0.05 | 1 | 4.3 | 16.1 | 27 | 49 | 0.008 | 3.7 | 3.6 | 2.7 | [15 empty] | MIL/MIN |  | TOTAL | 23240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 960 | 955 | 1090 | 1080 | 1070 | 1080 | 1045 | 510 | 1970 | 0 | 2800 | 2800 | 2810 | 257 | 286 | 34 | 4360 | 860 | 1323 | 120 | 118 | 18 | 1570 | 307 | 530
MAXIMUM | 6.65 | 24 | 20 | 8.4 | 84 | 133 | 18.5 | 0.425 | 0.054 | 6.1 | 12 | 0.097 | 6.11 | 12 |  | 6.01 | 12 |  | 6.06 | 0.411 | 5 | 0.48 | 18.1 | 10.3 | 0.52487 | 0.058 | 6.05 | 0.332 | 4 | 0.54 | 17.9 | 10.3 | 0.52094 | 6.08 | 0.476 | 4 | 0.62 | 18.9 | 6.5 | 0.36074 | 0.073 | 1 | 0.39 | 0.019 | 0.056 | 0.037 | 1 | 0.39 |  | 0.06 | 1 | 0.46 |  | 7.61 | 0.075 | 1 | 5 | 17.9 | 28 | 49 | 0.022 | 7.77 | 0.072 | 1 | 4.7 | 17.1 | 28 | 49 | 0.015 | 3.9 | 3.9 | 3.2 | [17 empty] | AVERAGE | 7746.6667 | [9 empty] | 310 | 320 | 318.3333 | 363.3333 | 360 | 356.6667 | 360 | 348.3333 | 170 | 656.6667 |  | 933.3333 | 933.3333 | 936.6667 | 85.6667 | 95.3333 | 11.3333 | 1453.3333 | 286.6667 | 441 | 40 | 39.3333 | 6 | 523.3333 | 102.3333 | 176.6667
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9872 |  | TOTAL AVG COAG ALK: |  |  |  | 11.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.476 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.4 | [5 empty] | 6.0138 |  |  |  |  | 0.073 |  |  |  |  | 0.4 | [6 empty] | 0.073 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 7200 | [9 empty] | 300 | 300 | 300 | 350 | 330 | 310 | 310 | 200 | 100 | 500 |  | 890 | 890 | 890 | 76 | 90 | 10 | 1370 | 275 | 405 | 38 | 39 | 6 | 500 | 100 | 150
[90 empty] | MAXIMUM | 8300 | [9 empty] | 330 | 340 | 330 | 380 | 400 | 380 | 400 | 425 | 300 | 970 |  | 960 | 960 | 970 | 91 | 98 | 12 | 1500 | 305 | 480 | 42 | 40 | 6 | 550 | 105 | 190
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 8.197 |  | TOTAL MGD: |  | 3.957 |  |  | FINISHED SOUTH 1 |  | START: | 23185655 |  | END: | 23189612 |  |  | Alum | 9022 |  | 6466 |  | 0 | [45 empty] | 0.45 | 10.3 | 24.699 | 11.1146 | 6.006 | 17.2 | 10 | 1.1115
[73 empty] | FINISHED 2 | 10.278 |  | TOTAL MGD: |  | 4.24 |  |  | FINISHED SOUTH 2 |  | START: | 41054755 |  | END: | 41058995 |  |  | Caustic | 4818 |  | 3817
[73 empty] | TOTAL RAW | 22.15 |  | TOTAL MGD: |  | 2.669 |  |  | FINISHED CONWAY |  | START: | 8779935 |  | END: | 8782604 |  |  | Hypochlorite | 10'/422 |  | 23'
[76 empty] | TOTAL MGD: |  | 7.609 |  |  | FINISHED PERRY |  | START: | 30564175 |  | END: | 30571784 |  |  | Phosphate | 1904
[76 empty] | TOTAL MGD: |  | 8.592 |  |  | RAW PLANT 1 |  | START: | 28087840 |  | END: | 28096432 |  |  | Fluoride | 0 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.539 |  |  | RAW PLANT 2 |  | START: | 28034350 |  | END: | 28042889 |  |  | Cal~Flo | 8.09 | 5.85 | 14.16 | 13.64 | 2323.92 | 25
[76 empty] | TOTAL MGD: |  | 5.019 |  |  | RAW PLANT 3 |  | START: | 4326685 |  | END: | 4331704 |  |  | Zinc | 3213
[76 empty] | TOTAL MGD: |  | 1.37 |  |  | DECANT |  | START: | 1413313 |  | END: | 1414683 |  |  | Polymer | 0 |  | DRUMS
[76 empty] | TOTAL MGD: |  | 1.0227 |  |  | BLOW DOWN |  | START: | 8775.899 |  | END: | 8776.9217 |  |  | NH3 | 9.39
[87 empty] | 0 |  |  | Lime | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 675
[90 empty] | BI-SULFITE | 0 | PUMP SPEED | 0
DAY TANK Chemical Inventory
[90 empty] | Alum | 2791 | Phosphate | 34
[90 empty] | Caustic 1 | 166 | Fluoride | 0
[90 empty] | Caustic 2 | 75 | Zinc | 4
[90 empty] | Hypochlorite 1 | 0 | Polymer 1 | 3
[90 empty] | Hypochlorite 2 | 0 | Polymer 2 | 2.5
[91 empty] | FINISHED SOUTH 1 |  | END: | 23189612
[91 empty] | FINISHED SOUTH 2 |  | END: | 41058995
[91 empty] | FINISHED CONWAY |  | END: | 8782604
[91 empty] | FINISHED PERRY |  | END: | 30571784
[91 empty] | RAW PLANT 1 |  | END: | 28096432
[91 empty] | RAW PLANT 2 |  | END: | 28042889
[91 empty] | RAW PLANT 3 |  | END: | 4331704
[91 empty] | DECANT |  | END: | 1414683
[91 empty] | BLOW DOWN |  | END: | 8776.9217
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 29
DATE: | 2018-03-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 | [10 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 | [28 empty] | 6:00 - 18:00 |  | 0 |  | 0 | [37 empty] | 6:00 - 18:00 |  | 0 |  | 0
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 0 |  | 0 | [37 empty] | 18:00 - 6:00 |  | 0 |  | 0
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2018-03-01 | [23 empty] | DATE: | 2018-03-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-03-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [127 empty] | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [127 empty] | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
2:00 | [127 empty] | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | [127 empty] | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [127 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | [127 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [127 empty] | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | [127 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [127 empty] | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
14:00 | [126 empty] | 0 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | [127 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [127 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | [127 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [127 empty] | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
22:00 | [72 empty] | DOSE |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | [74 empty] | AVERAGE | [14 empty] | AVERAGE | [37 empty] | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MINIMUM | [14 empty] | MINIMUM | [37 empty] | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | 0
AVERAGE | [74 empty] | MAXIMUM | [14 empty] | MAXIMUM
MINIMUM | [87 empty] | MIL/MIN |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAXIMUM | [89 empty] | AVERAGE
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [7 empty] | TOTAL AVG COAG ALK: | [5 empty] | TOTAL MAX SETTLED NTU: | [6 empty] | TOTAL MIN SETTLED DISEN.: |  |  | 0 | [10 empty] | 0 | [28 empty] | Pump Station MIN |  | 0 | [17 empty] | MINIMUM
[63 empty] | 0 | [26 empty] | MAXIMUM
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | -64248.607 |  | TOTAL MGD: |  | -23189.612 |  |  | FINISHED SOUTH 1 |  | START: | 23189612 |  | END: | 0 |  |  | Alum | [57 empty] | 0
[73 empty] | FINISHED 2 | -39354.388 |  | TOTAL MGD: |  | -41058.995 |  |  | FINISHED SOUTH 2 |  | START: | 41058995 |  | END: | 0 |  |  | Caustic
[73 empty] | TOTAL RAW | -60471.025 |  | TOTAL MGD: |  | -8782.604 |  |  | FINISHED CONWAY |  | START: | 8782604 |  | END: | 0 |  |  | Hypochlorite
[76 empty] | TOTAL MGD: |  | -30571.784 |  |  | FINISHED PERRY |  | START: | 30571784 |  | END: | 0 |  |  | Phosphate
[76 empty] | TOTAL MGD: |  | -28096.432 |  |  | RAW PLANT 1 |  | START: | 28096432 |  | END: | 0 |  |  | Fluoride | [5 empty] | cal %
[76 empty] | TOTAL MGD: |  | -28042.889 |  |  | RAW PLANT 2 |  | START: | 28042889 |  | END: | 0 |  |  | Cal~Flo | [5 empty] | 25
[76 empty] | TOTAL MGD: |  | -4331.704 |  |  | RAW PLANT 3 |  | START: | 4331704 |  | END: | 0 |  |  | Zinc
[76 empty] | TOTAL MGD: |  | -1414.683 |  |  | DECANT |  | START: | 1414683 |  | END: | 0 |  |  | Polymer
[76 empty] | TOTAL MGD: |  | -8776.9217 |  |  | BLOW DOWN |  | START: | 8776.9217 |  | END: | 0 |  |  | NH3
[87 empty] | 0 |  |  | Lime
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon
DAY TANK Chemical Inventory
[90 empty] | Alum |  | Phosphate
[90 empty] | Caustic 1 |  | Fluoride
[90 empty] | Caustic 2 |  | Zinc
[90 empty] | Hypochlorite 1 |  | Polymer 1
[90 empty] | Hypochlorite 2 |  | Polymer 2
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 30
DATE: | 2018-03-02 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 | [10 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 | [28 empty] | 6:00 - 18:00 |  | 0 |  | 0 | [37 empty] | 6:00 - 18:00 |  | 0 |  | 0
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 0 |  | 0 | [37 empty] | 18:00 - 6:00 |  | 0 |  | 0
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2018-03-02 | [23 empty] | DATE: | 2018-03-02
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-03-02 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [127 empty] | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [127 empty] | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
2:00 | [127 empty] | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | [127 empty] | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [127 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | [127 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [127 empty] | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | [127 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [127 empty] | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
14:00 | [126 empty] | 0 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | [127 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [127 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | [127 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [127 empty] | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
22:00 | [72 empty] | DOSE |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | [74 empty] | AVERAGE | [14 empty] | AVERAGE | [37 empty] | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MINIMUM | [14 empty] | MINIMUM | [37 empty] | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | 0
AVERAGE | [74 empty] | MAXIMUM | [14 empty] | MAXIMUM
MINIMUM | [87 empty] | MIL/MIN |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAXIMUM | [89 empty] | AVERAGE
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [7 empty] | TOTAL AVG COAG ALK: | [5 empty] | TOTAL MAX SETTLED NTU: | [6 empty] | TOTAL MIN SETTLED DISEN.: |  |  | 0 | [10 empty] | 0 | [28 empty] | Pump Station MIN |  | 0 | [17 empty] | MINIMUM
MAXIMUM
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 0 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 0 |  | END: | 0 |  |  | Alum | [57 empty] | 0
[73 empty] | FINISHED 2 | 0 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 2 |  | START: | 0 |  | END: | 0 |  |  | Caustic
[73 empty] | TOTAL RAW | 0 |  | TOTAL MGD: |  | 0 |  |  | FINISHED CONWAY |  | START: | 0 |  | END: | 0 |  |  | Hypochlorite
[76 empty] | TOTAL MGD: |  | 0 |  |  | FINISHED PERRY |  | START: | 0 |  | END: | 0 |  |  | Phosphate
[76 empty] | TOTAL MGD: |  | 0 |  |  | RAW PLANT 1 |  | START: | 0 |  | END: | 0 |  |  | Fluoride | [5 empty] | cal %
[76 empty] | TOTAL MGD: |  | 0 |  |  | RAW PLANT 2 |  | START: | 0 |  | END: | 0 |  |  | Cal~Flo | [5 empty] | 25
[76 empty] | TOTAL MGD: |  | 0 |  |  | RAW PLANT 3 |  | START: | 0 |  | END: | 0 |  |  | Zinc
[76 empty] | TOTAL MGD: |  | 0 |  |  | DECANT |  | START: | 0 |  | END: | 0 |  |  | Polymer
[76 empty] | TOTAL MGD: |  | 0 |  |  | BLOW DOWN |  | START: | 0 |  | END: | 0 |  |  | NH3
[87 empty] | 0 |  |  | Lime
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon
DAY TANK Chemical Inventory
[90 empty] | Alum |  | Phosphate
[90 empty] | Caustic 1 |  | Fluoride
[90 empty] | Caustic 2 |  | Zinc
[90 empty] | Hypochlorite 1 |  | Polymer 1
[90 empty] | Hypochlorite 2 |  | Polymer 2
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 31
DATE: | 2018-03-03 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 | [10 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 | [28 empty] | 6:00 - 18:00 |  | 0 |  | 0 | [37 empty] | 6:00 - 18:00 |  | 0 |  | 0
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 0 |  | 0 | [37 empty] | 18:00 - 6:00 |  | 0 |  | 0
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2018-03-03 | [23 empty] | DATE: | 2018-03-03
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-03-03 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [127 empty] | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [127 empty] | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
2:00 | [127 empty] | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | [127 empty] | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [127 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | [127 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [127 empty] | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | [127 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [127 empty] | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
14:00 | [126 empty] | 0 | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | [127 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [127 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | [127 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [127 empty] | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
22:00 | [72 empty] | DOSE |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | [74 empty] | AVERAGE | [14 empty] | AVERAGE | [37 empty] | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MINIMUM | [14 empty] | MINIMUM | [37 empty] | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | 0
AVERAGE | [74 empty] | MAXIMUM | [14 empty] | MAXIMUM
MINIMUM | [87 empty] | MIL/MIN |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAXIMUM | [89 empty] | AVERAGE
# 0F DAYS IN THE MONTH |  | 28 |  |  |  | TOTAL AVG COAG PH: | [7 empty] | TOTAL AVG COAG ALK: | [5 empty] | TOTAL MAX SETTLED NTU: | [6 empty] | TOTAL MIN SETTLED DISEN.: |  |  | 0 | [10 empty] | 0 | [28 empty] | Pump Station MIN |  | 0 | [17 empty] | MINIMUM
MAXIMUM
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 0 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 0 |  | END: | 0 |  |  | Alum | [57 empty] | 0
[73 empty] | FINISHED 2 | 0 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 2 |  | START: | 0 |  | END: | 0 |  |  | Caustic
[73 empty] | TOTAL RAW | 0 |  | TOTAL MGD: |  | 0 |  |  | FINISHED CONWAY |  | START: | 0 |  | END: | 0 |  |  | Hypochlorite
[76 empty] | TOTAL MGD: |  | 0 |  |  | FINISHED PERRY |  | START: | 0 |  | END: | 0 |  |  | Phosphate
[76 empty] | TOTAL MGD: |  | 0 |  |  | RAW PLANT 1 |  | START: | 0 |  | END: | 0 |  |  | Fluoride | [5 empty] | cal %
[76 empty] | TOTAL MGD: |  | 0 |  |  | RAW PLANT 2 |  | START: | 0 |  | END: | 0 |  |  | Cal~Flo | [5 empty] | 25
[76 empty] | TOTAL MGD: |  | 0 |  |  | RAW PLANT 3 |  | START: | 0 |  | END: | 0 |  |  | Zinc
[76 empty] | TOTAL MGD: |  | 0 |  |  | DECANT |  | START: | 0 |  | END: | 0 |  |  | Polymer
[76 empty] | TOTAL MGD: |  | 0 |  |  | BLOW DOWN |  | START: | 0 |  | END: | 0 |  |  | NH3
[87 empty] | 0 |  |  | Lime
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon
Alum
Caustic 1
Caustic 2
Hypochlorite 1
Hypochlorite 2
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN MONTH
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## BULK TANK LEVEL
cal-flow | 0 | 0 | 0.10024 | 0.43102 | 1.263 | 2.2052 | 2.0148 | 1.5938 | 1.263 | 0.91217 | 0.95226 | 1.263 | 1.1828 | 1.7742 | 1.5537 | 3.0272 | 1.8644 | 1.664 | 1.5838 | 2.7666 | 1.2229 | 2.7666 | 2.7666 | 2.7666 | 2.7666 | 2.7666 | 2.7666 | 2.7666 | 0 | 0 | 0
| Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday
| 2018-02-01 | 2018-02-02 | 2018-02-03 | 2018-02-04 | 2018-02-05 | 2018-02-06 | 2018-02-07 | 2018-02-08 | 2018-02-09 | 2018-02-10 | 2018-02-11 | 2018-02-12 | 2018-02-13 | 2018-02-14 | 2018-02-15 | 2018-02-16 | 2018-02-17 | 2018-02-18 | 2018-02-19 | 2018-02-20 | 2018-02-21 | 2018-02-22 | 2018-02-23 | 2018-02-24 | 2018-02-25 | 2018-02-26 | 2018-02-27 | 2018-02-28 | 2018-03-01 | 2018-03-02 | 2018-03-03
Alum1 | 6403 | 6006 | 5522 | 5052 | 6867 | 5876 | 7604 | 6815 | 6196 | 5645 | 5061 | 6805 | 6196 | 7560 | 9447 | 8910 | 8223 | 7591 | 9093 | 8626 | 10100 | 10500 | 9798 | 9249 | 8410 | 7637 | 7037 | 9022 | 0 | 0 | 0
Alum2 | 6745 | 6385 | 5964 | 5543 | 5085 | 6580 | 6048 | 7715 | 7155 | 6660 | 6140 | 5620 | 7430 | 9198 | 8420 | 10200 | 9470 | 8901 | 8470 | 10200 | 9510 | 10900 | 10200 | 9734 | 8998 | 8140 | 7392 | 6466 | 0 | 0 | 0
Alum Tower | bar: 2018-02-01 to 2018-03-03
Caustic | 5677 | 5528 | 5294 | 5118 | 4913 | 4656 | 4531 | 4360 | 4255 | 4118 | 3874 | 3793 | 3654 | 7064 | 6921 | 6768 | 6626 | 6455 | 6295 | 6166 | 6015 | 5868 | 5682 | 5546 | 5319 | 5155 | 4979 | 4818 | 0 | 0 | 0
Caustic | 5883 | 5883 | 5790 | 5693 | 5591 | 5573 | 5483 | 5481 | 5391 | 5272 | 5277 | 5181 | 5075 | 5063 | 4959 | 4840 | 4741 | 4644 | 4543 | 4450 | 4443 | 4340 | 4233 | 4138 | 4037 | 4040 | 3921 | 3817 | 0 | 0 | 0
Hypochlorite | 12 | 13 | 12 | 11 | 9 | 8 | 6'/416 | 4.5'/396 | 13'/379 | 12'/354 | 10'/442 | 14'/397 | 13' | 11.75 | 10 | 13 | 11.75 | 10 | 8.5 | 13 | 12 | 10.5 | 14 | 12 | 10 | 9 | 12.5 | 10'/422 | 0 | 0 | 0
Hypochlorite | 27.5 | 34 | 33 | 31.5 | 30 | 29 | 38.5' | 37' | 26.5' | 24.5' | 23' | 5.5' | 16.5' | 27 | 26 | 30 | 29 | 28.5 | 27 | 30.25 | 30 | 28 | 34.5 | 33 | 31 | 30 | 19 | 23' | 0 | 0 | 0
Phosphate | 100 | 3082 | 3067 | 2974 | 2974 | 2862 | 2896 | 2880 | 2800 | 2825 | 2696 | 2697 | 2704 | 2526 | 2516 | 2524 | 2441 | 2434 | 2322 | 2240 | 2235 | 2222 | 2149 | 2162 | 2079 | 2115 | 1994 | 1904 | 0 | 0 | 0
Fluoride | 2500 | 2450 | 2450 | 2400 | 2400 | 2150 | 0 | 0 | 2000 | 2000 | 2000 | 2000 | 1600 | 1600 | 1600 | 1500 | 1600 | 1600 | 1500 | 1500 | 1250 | 850 | 750 | 750 | 500 | 500 | 500 | 0 | 0 | 0 | 0
Cal~Flo | 0 | 0 | 84.2 | 362.06 | 1060.92 | 1852.4 | 1692.42 | 1338.78 | 1060.92 | 766.22 | 799.9 | 1060.92 | 993.56 | 1490.34 | 1305.1 | 2542.84 | 1566.12 | 1397.72 | 1330.36 | 2323.92 | 1027.24 | 2323.92 | 2323.92 | 2323.92 | 2323.92 | 2323.92 | 2323.92 | 2323.92 | 0 | 0 | 0
Zinc | 472 | 3648 | 3640 | 3.1 | 3140 | 3140 | 3201 | 3185 | 3178 | 3199 | 3207 | 3212 | 3220 | 3200 | 3191 | 3199 | 3205 | 3199 | 3209 | 3208 | 3202 | 3193 | 3194 | 3206 | 3194 | 3223 | 3208 | 3213 | 0 | 0 | 0
Polymer | 9 | 9 | 8 | 8 | 8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 12 | 12 | 11 | 10 | 10 | 0 | 0 | 0 | 0
NH3 | 7.31 | 6.71 | 654 | 6.33 | 6.15 | 5.97 | 13.29 | 13.08 | 12.89 | 12.71 | 12.5 | 12.32 | 12.14 | 11.88 | 11.7 | 11.54 | 11.37 | 11.2 | 11.03 | 10.89 | 10.73 | 10.55 | 10.35 | 10.15 | 9.95 | 9.75 | 9.55 | 9.39 | 0 | 0 | 0
Lime | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cabon | 650 | 650 | 650 | 650 | 650 | 650 | 715 | 640 | 600 | 675 | 650 | 575 | 650 | 375 | 375 | 650 | 600 | 600 | 600 | 600 | 700 | 700 | 0 | 700 | 700 | 700 | 650 | 675 | 0 | 0 | 0
filter aid | 2018-02-01: 2.6452

## AWOP 2018
| Raw | Settled | Filter
Average | 10.6526 | 0.57842 | 0.052677
Max | 33 | 1 | 0.09
Count |  | 1 | 0 | Average Raw
AWOP Count |  | 0 | 0 | Per day
2017-01-01 | 6.46 | 0.453 | 0.079 |  | 9.7717
2017-01-02 | 6.52 | 0.369 | 0.05 |  | 29.85
2017-01-03 | 6.47 | 0.627 | 0.048 |  | 34.4667
2017-01-04 | 7.07 | 0.451 | 0.038 |  | 26.5833
2017-01-05 | 8.09 | 0.675 | 0.076 |  | 22.1333
2017-01-06 | 17.8 | 0.465 | 0.054 |  | 19.75
2017-01-07 | 22.1 | 0.54 | 0.055 |  | 24.3167
2017-01-08 | 21.2 | 0.489 | 0.053 |  | 29.9667
2017-01-09 | 22.7 | 0.648 | 0.089 |  | 37.4
2017-01-10 | 22.8 | 0.871 | 0.063 |  | 30.5333
2017-01-11 | 26.5 | 0.99 | 0.07 |  | 40.3833
2017-01-12 | 21.5 | 0.762 | 0.055 |  | 39.4667
2017-01-13 | 15.6 | 0.799 | 0.06 |  | 30.2
2017-01-14 | 12.9 | 0.663 | 0.067 |  | 27.25
2017-01-15 | 10.9 | 0.702 | 0.066 |  | 27.0667
2017-01-16 | 9.67 | 0.707 | 0.071 |  | 24.8333
2017-01-17 | 8.39 | 0.545 | 0.047 |  | 20.4167
2017-01-18 | 9.8 | 0.612 | 0.058 |  | 17.45
2017-01-19 | 5.64 | 0.71 | 0.038 |  | 14.9833
2017-01-20 | 5.4 | 0.671 | 0.045 |  | 12.9333
2017-01-21 | 5.26 | 0.524 | 0.044 |  | 11.3917
2017-01-22 | 5.65 | 0.384 | 0.066 |  | 8.4533
2017-01-23 | 5.85 | 0.574 | 0.044 |  | 8.6367
2017-01-24 | 5.35 | 0.428 | 0.028 |  | 7.69
2017-01-25 | 5.5 | 0.476 | 0.042 |  | 7.1383
2017-01-26 | 9.47 | 0.43 | 0.04 |  | 7.6667
2017-01-27 | 16.4 | 0.478 | 0.073 |  | 8.6033
2017-01-28 | 24.6 | 0.618 | 0.061 |  | 7.705
2017-01-29 | 16.5 | 0.527 | 0.053
2017-01-30 | 13.5 | 0.567 | 0.05
2017-01-31 | 12.3 | 0.474 | 0.07
2017-02-01 | 11.5 | 0.436 | 0.053
2017-02-02 | 10.1 | 0.511 | 0.048
2017-02-03 | 9.41 | 0.57 | 0.084
2017-02-04 | 9.44 | 0.664 | 0.074
2017-02-05 | 7.68 | 0.68 | 0.058
2017-02-06 | 7.8 | 0.614 | 0.07
2017-02-07 | 9.61 | 0.764 | 0.053
2017-02-08 | 8.42 | 0.859 | 0.062
2017-02-09 | 8.27 | 0.9 | 0.076
2017-02-10 | 8.83 | 0.56 | 0.042
2017-02-11 | 10.4 | 0.44 | 0.04
2017-02-12 | 9.62 | 0.437 | 0.054
2017-02-13 | 9.38 | 0.472 | 0.072
2017-02-14 | 8.98 | 0.488 | 0.076
2017-02-15 | 8.88 | 0.31 | 0.05
2017-02-16 | 9.13 | 0.434 | 0.048
2017-02-17 | 9.03 | 0.404 | 0.047
2017-02-18 | 8.86 | 0.438 | 0.042
2017-02-19 | 9.1 | 0.541 | 0.07
2017-02-20 | 9.27 | 0.408 | 0.05
2017-02-21 | 10.2 | 0.389 | 0.046
2017-02-22 | 10.1 | 0.463 | 0.08
2017-02-23 | 9.62 | 0.594 | 0.07
2017-02-24 | 8.31 | 0.598 | 0.05
2017-02-25 | 9.64 | 0.637 | 0.05
2017-02-26 | 10.3 | 0.573 | 0.041
2017-02-27 | 9.4 | 0.659 | 0.041
2017-02-28 | 8.26 | 0.475 | 0.089
2017-03-01 | 8.5 | 0.592 | 0.062
2017-03-02 | 8.88 | 0.827 | 0.054
2017-03-03 | 9.49 | 0.523 | 0.045
2017-03-04 | 9.16 | 0.558 | 0.038
2017-03-05 | 9.45 | 0.482 | 0.066
2017-03-06 | 8.72 | 0.49 | 0.057
2017-03-07 | 8.01 | 0.452 | 0.05
2017-03-08 | 7.33 | 0.506 | 0.042
2017-03-09 | 8.57 | 0.568 | 0.036
2017-03-10 | 10.4 | 0.47 | 0.065
2017-03-11 | 10.1 | 0.638 | 0.057
2017-03-12 | 7.54 | 0.62 | 0.051
2017-03-13 | 7.29 | 0.499 | 0.062
2017-03-14 | 7.83 | 0.46 | 0.039
2017-03-15 | 13.9 | 0.515 | 0.035
2017-03-16 | 9.75 | 0.536 | 0.056
2017-03-17 | 10.5 | 0.7 | 0.078
2017-03-18 | 10.8 | 0.67 | 0.049
2017-03-19 | 10.3 | 0.648 | 0.058
2017-03-20 | 11.2 | 0.754 | 0.06
2017-03-21 | 9.22 | 0.83 | 0.087
2017-03-22 | 9.23 | 0.873 | 0.068
2017-03-23 | 9.26 | 0.723 | 0.087
2017-03-24 | 7.74 | 0.494 | 0.06
2017-03-25 | 11.7 | 0.767 | 0.081
2017-03-26 | 9.8 | 0.546 | 0.05
2017-03-27 | 20 | 0.371 | 0.082
2017-03-28 | 10.2 | 0.557 | 0.06
2017-03-29 | 11.3 | 0.574 | 0.046
2017-03-30 | 9.07 | 0.457 | 0.036
2017-03-31 | 8.86 | 0.388 | 0.059
2017-04-01 | 9.39 | 0.53 | 0.05
2017-04-02 | 10.5 | 0.498 | 0.04
2017-04-03 | 8.99 | 0.624 | 0.043
2017-04-04 | 10.2 | 0.591 | 0.049
2017-04-05 | 11.2 | 0.497 | 0.039
2017-04-06 | 9.85 | 0.933 | 0.039
2017-04-07 | 12.6 | 0.789 | 0.067
2017-04-08 | 13.2 | 0.696 | 0.039
2017-04-09 | 16.3 | 0.707 | 0.061
2017-04-10 | 18.2 | 0.609 | 0.089
2017-04-11 | 17.2 | 0.757 | 0.036
2017-04-12 | 17.1 | 0.667 | 0.055
2017-04-13 | 20.7 | 0.716 | 0.05
2017-04-14 | 17.9 | 0.667 | 0.042
2017-04-15 | 16.9 | 0.562 | 0.061
2017-04-16 | 20.2 | 0.58 | 0.078
2017-04-17 | 16.4 | 0.797 | 0.048
2017-04-18 | 15.4 | 0.802 | 0.053
2017-04-19 | 17.2 | 0.832 | 0.083
2017-04-20 | 9.6 | 0.571 | 0.04
2017-04-21 | 10.6 | 0.598 | 0.064
2017-04-22 | 10.7 | 0.659 | 0.052
2017-04-23 | 9.67 | 0.711 | 0.051
2017-04-24 | 9.45 | 0.481 | 0.043
2017-04-25 | 8.84 | 0.452 | 0.051
2017-04-26 | 10.2 | 0.455 | 0.055
2017-04-27 | 11.7 | 0.479 | 0.035
2017-04-28 | 19.5 | 0.412 | 0.033
2017-04-29 | 18.5 | 0.628 | 0.039
2017-04-30 | 18 | 0.645 | 0.039
2017-05-01 | 16.1 | 0.652 | 0.048
2017-05-02 | 11.8 | 0.767 | 0.049
2017-05-03 | 12.1 | 0.682 | 0.049
2017-05-04 | 11.4 | 0.559 | 0.042
2017-05-05 | 7.45 | 0.581 | 0.037
2017-05-06 | 7.49 | 0.894 | 0.057
2017-05-07 | 9.17 | 0.807 | 0.051
2017-05-08 | 10.1 | 0.762 | 0.065
2017-05-09 | 10.4 | 0.676 | 0.037
2017-05-10 | 11 | 0.61 | 0.051
2017-05-11 | 10 | 0.666 | 0.067
2017-05-12 | 10.6 | 0.85 | 0.041
2017-05-13 | 9.86 | 0.579 | 0.039
2017-05-14 | 10.5 | 0.683 | 0.033
2017-05-15 | 12.5 | 0.691 | 0.05
2017-05-16 | 12.2 | 0.682 | 0.062
2017-05-17 | 13.6 | 0.8 | 0.048
2017-05-18 | 12.8 | 0.61 | 0.049
2017-05-19 | 12.9 | 0.447 | 0.066
2017-05-20 | 12.1 | 0.496 | 0.055
2017-05-21 | 13.1 | 0.57 | 0.044
2017-05-22 | 14.9 | 0.353 | 0.038
2017-05-23 | 13.9 | 0.244 | 0.028
2017-05-24 | 15.2 | 0.501 | 0.028
2017-05-25 | 15.8 | 0.839 | 0.034
2017-05-26 | 18.8 | 0.552 | 0.035
2017-05-27 | 27.9 | 0.502 | 0.031
2017-05-28 | 33 | 0.466 | 0.057
2017-05-29 | 30.2 | 0.635 | 0.04
2017-05-30 | 24.8 | 0.506 | 0.048
2017-05-31 | 19.4 | 0.33 | 0.04
2017-06-01 | 16.8 | 0.398 | 0.037
2017-06-02 | 15.2 | 0.418 | 0.05
2017-06-03 | 16.5 | 0.446 | 0.044
2017-06-04 | 10.6 | 0.449 | 0.041
2017-06-05 | 10.2 | 0.339 | 0.06
2017-06-06 | 6.65 | 0.331 | 0.035
2017-06-07 | 6.83 | 0.325 | 0.05
2017-06-08 | 7.1 | 0.428 | 0.041
2017-06-09 | 8.99 | 0.48 | 0.041
2017-06-10 | 11.4 | 0.43 | 0.051
2017-06-11 | 14.2 | 0.403 | 0.07
2017-06-12 | 17.3 | 0.458 | 0.056
2017-06-13 | 13.5 | 0.516 | 0.04
2017-06-14 | 14.6 | 0.452 | 0.035
2017-06-15 | 13.2 | 0.403 | 0.052
2017-06-16 | 13.5 | 0.48 | 0.043
2017-06-17 | 15.1 | 0.41 | 0.038
2017-06-18 | 17.2 | 0.555 | 0.037
2017-06-19 | 16 | 0.432 | 0.056
2017-06-20 | 12.7 | 0.422 | 0.056
2017-06-21 | 13.7 | 0.302 | 0.042
2017-06-22 | 16.4 | 0.465 | 0.04
2017-06-23 | 16.4 | 0.394 | 0.045
2017-06-24 | 22.6 | 0.521 | 0.035
2017-06-25 | 19.2 | 0.382 | 0.048
2017-06-26 | 16.4 | 0.492 | 0.057
2017-06-27 | 16.4 | 0.495 | 0.045
2017-06-28 | 18.1 | 0.538 | 0.065
2017-06-29 | 18.6 | 0.485 | 0.044
2017-06-30 | 18.6 | 0.432 | 0.06
2017-07-01 | 17.7 | 0.369 | 0.053
2017-07-02 | 15.8 | 0.529 | 0.045
2017-07-03 | 14.7 | 0.448 | 0.05
2017-07-04 | 12 | 0.468 | 0.042
2017-07-05 | 15.1 | 0.58 | 0.04
2017-07-06 | 19.4 | 0.5 | 0.051
2017-07-07 | 19.4 | 0.577 | 0.039
2017-07-08 | 22.9 | 0.569 | 0.05
2017-07-09 | 18.4 | 0.83 | 0.04
2017-07-10 | 15.2 | 0.466 | 0.06
2017-07-11 | 12.8 | 0.586 | 0.05
2017-07-12 | 12.2 | 0.898 | 0.06
2017-07-13 | 10.8 | 0.874 | 0.036
2017-07-14 | 9.6 | 0.59 | 0.046
2017-07-15 | 10.2 | 0.791 | 0.04
2017-07-16 | 8.49 | 0.581 | 0.033
2017-07-17 | 8.42 | 0.752 | 0.03
2017-07-18 | 8.15 | 0.608 | 0.049
2017-07-19 | 8.76 | 0.6 | 0.038
2017-07-20 | 8.6 | 0.8 | 0.05
2017-07-21 | 11.1 | 0.495 | 0.039
2017-07-22 | 10.3 | 0.505 | 0.04
2017-07-23 | 9.57 | 0.878 | 0.07
2017-07-24 | 11.3 | 0.492 | 0.056
2017-07-25 | 10.5 | 0.41 | 0.05
2017-07-26 | 12.8 | 0.469 | 0.042
2017-07-27 | 11.1 | 0.51 | 0.055
2017-07-28 | 14.7 | 0.592 | 0.052
2017-07-29 | 12.5 | 0.587 | 0.046
2017-07-30 | 10.1 | 0.591 | 0.033
2017-07-31 | 10.5 | 0.852 | 0.045
2017-08-01 | 7.89 | 0.441 | 0.046
2017-08-02 | 8.24 | 0.686 | 0.041
2017-08-03 | 7.38 | 0.738 | 0.046
2017-08-04 | 7.24 | 0.99 | 0.06
2017-08-05 | 7.06 | 0.717 | 0.056
2017-08-06 | 7.93 | 0.605 | 0.043
2017-08-07 | 8.01 | 0.644 | 0.05
2017-08-08 | 8.02 | 0.554 | 0.035
2017-08-09 | 7.58 | 0.792 | 0.048
2017-08-10 | 8.42 | 0.492 | 0.048
2017-08-11 | 7.39 | 0.712 | 0.05
2017-08-12 | 7.67 | 0.504 | 0.05
2017-08-13 | 7.99 | 0.624 | 0.035
2017-08-14 | 8.18 | 0.519 | 0.09
2017-08-15 | 9.55 | 0.946 | 0.068
2017-08-16 | 8.17 | 0.863 | 0.04
2017-08-17 | 8.2 | 0.763 | 0.038
2017-08-18 | 7.65 | 0.483 | 0.04
2017-08-19 | 12.4 | 0.474 | 0.04
2017-08-20 | 10.6 | 0.429 | 0.071
2017-08-21 | 12.8 | 0.514 | 0.042
2017-08-22 | 14.1 | 0.456 | 0.04
2017-08-23 | 13.6 | 0.902 | 0.032
2017-08-24 | 13.2 | 0.906 | 0.042
2017-08-25 | 13.3 | 0.965 | 0.059
2017-08-26 | 14.6 | 0.396 | 0.04
2017-08-27 | 14.1 | 0.645 | 0.035
2017-08-28 | 12.6 | 0.832 | 0.036
2017-08-29 | 7.08 | 0.605 | 0.034
2017-08-30 | 6.71 | 0.782 | 0.068
2017-08-31 | 8.6 | 0.915 | 0.06
2017-09-01 | 8.18 | 0.92 | 0.05
2017-09-02 | 10.3 | 0.768 | 0.043
2017-09-03 | 9.74 | 0.99 | 0.04
2017-09-04 | 13.5 | 1 | 0.04
2017-09-05 | 12.3 | 0.986 | 0.05
2017-09-06 | 8.67 | 0.64 | 0.042
2017-09-07 | 16.3 | 0.747 | 0.071
2017-09-08 | 7.63 | 0.813 | 0.05
2017-09-09 | 6.75 | 0.982 | 0.05
2017-09-10 | 6.11 | 0.576 | 0.031
2017-09-11 | 7.15 | 0.463 | 0.034
2017-09-12 | 5.71 | 0.293 | 0.046
2017-09-13 | 7.22 | 0.277 | 0.04
2017-09-14 | 7.44 | 0.396 | 0.04
2017-09-15 | 9.03 | 0.426 | 0.043
2017-09-16 | 9 | 0.47 | 0.039
2017-09-17 | 7.87 | 0.549 | 0.048
2017-09-18 | 9.02 | 0.61 | 0.061
2017-09-19 | 7.41 | 0.522 | 0.05
2017-09-20 | 6.77 | 0.52 | 0.06
2017-09-21 | 7.01 | 0.651 | 0.054
2017-09-22 | 7.12 | 0.693 | 0.057
2017-09-23 | 6.63 | 0.554 | 0.06
2017-09-24 | 5.54 | 0.525 | 0.048
2017-09-25 | 8 | 0.57 | 0.053
2017-09-26 | 5.76 | 0.508 | 0.039
2017-09-27 | 5.88 | 0.49 | 0.05
2017-09-28 | 5.57 | 0.63 | 0.059
2017-09-29 | 8.54 | 0.58 | 0.05
2017-09-30 | 6.56 | 0.98 | 0.043
2017-10-01 | 9.65 | 0.733 | 0.06
2017-10-02 | 7.23 | 0.475 | 0.042
2017-10-03 | 5.94 | 0.549 | 0.058
2017-10-04 | 6.88 | 0.583 | 0.042
2017-10-05 | 6.11 | 0.386 | 0.053
2017-10-06 | 5.96 | 0.482 | 0.042
2017-10-07 | 5.18 | 0.342 | 0.051
2017-10-08 | 5.71 | 0.26 | 0.064
2017-10-09 | 5.27 | 0.298 | 0.05
2017-10-10 | 4.7 | 0.277 | 0.042
2017-10-11 | 5.7 | 0.367 | 0.043
2017-10-12 | 6.32 | 0.676 | 0.042
2017-10-13 | 6.98 | 0.554 | 0.042
2017-10-14 | 6.22 | 0.62 | 0.048
2017-10-15 | 7.11 | 0.456 | 0.05
2017-10-16 | 7.49 | 0.494 | 0.046
2017-10-17 | 6.34 | 0.81 | 0.046
2017-10-18 | 6.02 | 0.558 | 0.09
2017-10-19 | 5.43 | 0.551 | 0.046
2017-10-20 | 6.29 | 0.383 | 0.08
2017-10-21 | 5.96 | 0.459 | 0.055
2017-10-22 | 7.83 | 0.459 | 0.054
2017-10-23 | 8.11 | 0.453 | 0.052
2017-10-24 | 6.5 | 0.414 | 0.028
2017-10-25 | 8.14 | 0.43 | 0.06
2017-10-26 | 7.91 | 0.481 | 0.06
2017-10-27 | 8.92 | 0.556 | 0.054
2017-10-28 | 9.2 | 0.696 | 0.053
2017-10-29 | 6.74 | 0.575 | 0.06
2017-10-30 | 7.68 | 0.574 | 0.06
2017-10-31 | 8.22 | 0.439 | 0.052
2017-11-01 | 7.56 | 0.595 | 0.052
2017-11-02 | 8.95 | 0.444 | 0.074
2017-11-03 | 8.24 | 0.48 | 0.057
2017-11-04 | 7.15 | 0.4 | 0.054
2017-11-05 | 8.46 | 0.397 | 0.052
2017-11-06 | 6.65 | 0.393 | 0.07
2017-11-07 | 7.19 | 0.375 | 0.059
2017-11-08 | 6.47 | 0.562 | 0.06
2017-11-09 | 5.57 | 0.589 | 0.052
2017-11-10 | 7.75 | 0.596 | 0.055
2017-11-11 | 7.4 | 0.647 | 0.064
2017-11-12 | 8.32 | 0.617 | 0.063
2017-11-13 | 7.93 | 0.597 | 0.059
2017-11-14 | 9.09 | 0.437 | 0.059
2017-11-15 | 10.7 | 0.438 | 0.058
2017-11-16 | 8.28 | 0.38 | 0.06
2017-11-17 | 7.97 | 0.466 | 0.063
2017-11-18 | 7.35 | 0.541 | 0.057
2017-11-19 | 6.91 | 0.491 | 0.05
2017-11-20 | 6.59 | 0.543 | 0.056
2017-11-21 | 6.02 | 0.443 | 0.056
2017-11-22 | 7.95 | 0.57 | 0.051
2017-11-23 | 6.21 | 0.555 | 0.069
2017-11-24 | 6.2 | 0.563 | 0.03
2017-11-25 | 5.87 | 0.502 | 0.07
2017-11-26 | 6.06 | 0.492 | 0.079
2017-11-27 | 5.82 | 0.468 | 0.071
2017-11-28 | 5.76 | 0.501 | 0.07
2017-11-29 | 5.12 | 0.525 | 0.068
2017-11-30 | 5.08 | 0.463 | 0.058
2017-12-01 | 5.52 | 0.491 | 0.056
2017-12-02 | 5.4 | 0.535 | 0.048
2017-12-03 | 5.39 | 0.507 | 0.05
2017-12-04 | 5.55 | 0.612 | 0.045
2017-12-05 | 5.45 | 0.411 | 0.06
2017-12-06 | 5.06 | 0.43 | 0.081
2017-12-07 | 5 | 0.593 | 0.073
2017-12-08 | 4.44 | 0.572 | 0.07
2017-12-09 | 4.4 | 0.664 | 0.084
2017-12-10 | 4.71 | 0.517 | 0.08
2017-12-11 | 5.84 | 0.72 | 0.069
2017-12-12 | 7.16 | 0.663 | 0.069
2017-12-13 | 8.66 | 0.61 | 0.069
2017-12-14 | 15.7 | 0.766 | 0.08
2017-12-15 | 21.6 | 0.498 | 0.062
2017-12-16 | 18.8 | 0.579 | 0.063
2017-12-17 | 18.2 | 0.517 | 0.052
2017-12-18 | 15.1 | 0.567 | 0.048
2017-12-19 | 10.8 | 0.629 | 0.049
2017-12-20 | 8.84 | 0.598 | 0.069
2017-12-21 | 8.67 | 0.817 | 0.07
2017-12-22 | 9.1 | 0.804 | 0.063
2017-12-23 | 9.78 | 0.656 | 0.06
2017-12-24 | 9.2 | 0.754 | 0.039
2017-12-25 | 10.2 | 0.78 | 0.068
2017-12-26 | 10.2 | 0.684 | 0.059
2017-12-27 | 9.38 | 0.643 | 0.056
2017-12-28 | 8.12 | 0.823 | 0.07
2017-12-29 | 7.29 | 0.597 | 0.061
2017-12-30 | 6.92 | 0.579 | 0.052
2017-12-31 | 6.53 | 0.574 | 0.055
2018-01-01 | 6.9083 | 0.653 | 0.066
2018-01-02 | 6.895 | 0.593 | 0.07
2018-01-03 | 6.9283 | 0.755 | 0.075
2018-01-04 | 6.9317 | 0.796 | 0.076
2018-01-05 | 7.0217 | 0.857 | 0.08
2018-01-06 | 6.9867 | 0.709 | 0.066
2018-01-07 | 7.0983 | 0.64 | 0.063
2018-01-08 | 7.0633 | 0.643 | 0.063
2018-01-09 | 7.0133 | 0.496 | 0.059
2018-01-10 | 6.935 | 0.47 | 0.053
2018-01-11 | 6.9667 | 0.494 | 0.047
2018-01-12 | 6.9333 | 0.468 | 0.058
2018-01-13 | 6.915 | 0.9 | 0.053
2018-01-14 | 6.9317 | 0.428 | 0.046
2018-01-15 | 6.935 | 0.504 | 0.038
2018-01-16 | 6.9733 | 0.51 | 0.037
2018-01-17 | 6.8267 | 0.608 | 0.036
2018-01-18 | 7.0233 | 0.642 | 0.047
2018-01-19 | 7.0767 | 0.642 | 0.042
2018-01-20 | 7.0717 | 0.651 | 0.043
2018-01-21 | 7.1367 | 0.777 | 0.04
2018-01-22 | 7.0483 | 0.745 | 0.04
2018-01-23 | 7.0167 | 0.924 | 0.04
2018-01-24 | 6.975 | 0.834 | 0.042
2018-01-25 | 6.9283 | 0.835 | 0.093
2018-01-26 | 6.8733 | 0.624 | 0.042
2018-01-27 | 6.9167 | 0.506 | 0.053
2018-01-28 | 6.915 | 0.499 | 0.04
2018-01-29 | 6.9583 | 0.56 | 0.043
2018-01-30 | 6.895 | 0.525 | 0.035
2018-01-31 | 6.865 | 0.59 | 0.066
2018-02-01 | 12.1 | 0.563 | 0.05
2018-02-02 | 42.3 | 0.504 | 0.042
2018-02-03 | 41.5 | 0.471 | 0.05
2018-02-04 | 30.1 | 0.593 | 0.045
2018-02-05 | 25.9 | 0.899 | 0.059
2018-02-06 | 21.8 | 0.589 | 0.048
2018-02-07 | 28.2 | 0.722 | 0.06
2018-02-08 | 33.6 | 0.571 | 0.062
2018-02-09 | 40.8 | 0.505 | 0.053
2018-02-10 | 35 | 0.737 | 0.07
2018-02-11 | 44.9 | 0.661 | 0.052
2018-02-12 | 44.2 | 0.664 | 0.089
2018-02-13 | 33 | 0.495 | 0.062
2018-02-14 | 29.2 | 0.599 | 0.055
2018-02-15 | 28.7 | 0.479 | 0.049
2018-02-16 | 25.9 | 0.505 | 0.048
2018-02-17 | 21.3 | 0.475 | 0.073
2018-02-18 | 18.8 | 0.476 | 0.057
2018-02-19 | 15.9 | 0.471 | 0.072
2018-02-20 | 14 | 0.583 | 0.058
2018-02-21 | 12.8 | 0.465 | 0.044
2018-02-22 | 9.01 | 0.592 | 0.061
2018-02-23 | 8.91 | 0.41 | 0.055
2018-02-24 | 8.24 | 0.436 | 0.042
2018-02-25 | 7.55 | 0.369 | 0.059
2018-02-26 | 8.3 | 0.501 | 0.059
2018-02-27 | 9.9 | 0.561 | 0.068
2018-02-28 | 8.4 | 0.476 | 0.073
2018-03-01
2018-03-02
2018-03-03
2018-03-04

## Sheet1 (2) (hidden)
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10 | Running Avg. Treated UV254
2015-01-19 | 1530 | 120 | 5.8 | 0.4 | 0.016 | 96% |  |  | 11.5942 | 10.35 | 1.2 | 0.58 | 0.016
2015-01-19 | 1925 | 120 | 5.534 | 0.344 | -0.033 | 109.6% | 12.4% |  | 9.971 | 12.0349 | 1.2 | 0.5534 | -0.0085
2015-01-19 | 2315 | 120 | 5.936 | 0.355 | 0.028 | 92.11% | -18.98% |  | 10.2899 | 11.662 | 1.2 | 0.5936 | 0.0036667
2015-01-20 | 320 | 120 | 5.815 | 0.333 | 0.032 | 90.39% | -1.905% |  | 9.6522 | 12.4324 | 1.2 | 0.5815 | 0.01075
2015-01-20 | 820 | 110 | 5.96 | 0.342 | 0.066 | 80.7% | -12.01% |  | 9.913 | 11.0965 | 1.1 | 0.596 | 0.0218
2015-01-20 | 1020 | 110 | 5.757 | 0.361 | 0.03 | 91.69% | 11.98% |  | 10.4638 | 10.5125 | 1.1 | 0.5757 | 0.023167
2015-01-20 | 1200 | 110 | 6.057 | 0.366 | 0.036 | 90.16% | -1.692% |  | 10.6087 | 10.3689 | 1.1 | 0.6057 | 0.025
2015-01-20 | 1245 | 110 | 6.2 | 0.32 | 0.014 | 95.62% | 5.711% |  | 9.2754 | 11.8594 | 1.1 | 0.62 | 0.023625
2015-01-20 | 1330 | 110 | 6.13 | 0.347 | 0.029 | 91.64% | -4.346% |  | 10.058 | 10.9366 | 1.1 | 0.613 | 0.024222
2015-01-20 | 1410 | 110 | 6.16 | 0.343 | 0.035 | 89.8% | -2.057% |  | 9.942 | 11.0641 | 1.1 | 0.616 | 0.0253
2015-01-20 | 1440 | 110 | 6.32 | 0.351 | 0.033 | 90.6% | 0.8856% |  | 10.1739 | 10.812 | 1.1 | 0.632 | 0.026
2015-01-20 | 1510 | 110 | 6.317 | 0.347 | 0.033 | 90.49% | -0.1198% |  | 10.058 | 10.9366 | 1.1 | 0.6317 | 0.026583
2015-01-20 | 1550 | 110 | 6.16 | 0.348 | 0.035 | 89.94% | -0.6086% |  | 10.087 | 10.9052 | 1.1 | 0.616 | 0.027231
2015-01-20 | 1830 | 110 | 6.095 | 0.237 | 0.019 | 91.98% | 2.218% |  | 6.8696 | 16.0127 | 1.1 | 0.6095 | 0.026643
2015-01-20 | 2050 | 110 | 5.808 | 0.397 | 0.073 | 81.61% | -12.71% |  | 11.5072 | 9.5592 | 1.1 | 0.5808 | 0.029733
2015-01-20 | 2300 | 110 | 6.073 | 0.351 | 0.052 | 85.19% | 4.195% |  | 10.1739 | 10.812 | 1.1 | 0.6073 | 0.031125 | [6 empty] | Treated | Raw
2015-01-21 | 100 | 110 | 6.318 | 0.339 | 0.049 | 85.55% | 0.4215% |  | 9.8261 | 11.1947 | 1.1 | 0.6318 | 0.032176 |  |  |  |  | 2015-01-19 | 99.24% | 0.022
2015-01-21 | 315 | 110 | 6.171 | 0.413 | 0.094 | 77.24% | -10.75% |  | 11.971 | 9.1889 | 1.1 | 0.6171 | 0.035611 |  |  |  |  | 2015-01-20 | 89.22% | 0.037462
2015-01-21 | 530 | 110 | 6.148 | 0.358 | 0.042 | 88.27% | 12.49% |  | 10.3768 | 10.6006 | 1.1 | 0.6148 | 0.035947 | Stdev | 0.010573 |  |  | 2015-01-21 | 89.47% | 0.037136
2015-01-21 | 705 | 105 | 6.181 | 0.36 | 0.031 | 91.39% | 3.415% |  | 10.4348 | 10.0625 | 1.05 | 0.6181 | 0.0357 | Median | 0.030429 |  |  | 2015-01-22 | 89.99% | 0.036611
2015-01-21 | 800 | 105 | 6.246 | 0.381 | 0.048 | 87.4% | -4.562% |  | 11.0435 | 9.5079 | 1.05 | 0.6246 | 0.036286 |  |  |  |  | 2015-01-23 | 90.48% | 0.036235
2015-01-21 | 900 | 105 | 6.24 | 0.383 | 0.017 | 95.56% | 8.539% |  | 11.1014 | 9.4582 | 1.05 | 0.624 | 0.035409 |  |  | Treated | Raw | 2015-01-24 | 92.01% | 0.031571
2015-01-21 | 910 | 105 | 6.284 | 0.359 | 0.021 | 94.15% | -1.499% |  | 10.4058 | 10.0905 | 1.05 | 0.6284 | 0.034783 | 120 | 92.83% | 0.025333 | 0.36267 | 2015-01-25 | 90.25% | 0.039267
2015-01-21 | 1000 | 105 | 6.095 | 0.365 | 0.027 | 92.6% | -1.671% |  | 10.5797 | 9.9247 | 1.05 | 0.6095 | 0.034458 | 110 | 88.56% | 0.042667 | 0.348 | 2015-01-26 | 91.21% | 0.03525
2015-01-21 | 1100 | 105 | 6.218 | 0.359 | 0.068 | 81.06% | -14.24% |  | 10.4058 | 10.0905 | 1.05 | 0.6218 | 0.0358 | 105 | 91.36% | 0.031111 | 0.35722 | 2015-01-27 | 93.67%
2015-01-21 | 1120 | 105 | 6.056 | 0.355 | 0.035 | 90.14% | 10.08% |  | 10.2899 | 10.2042 | 1.05 | 0.6056 | 0.035769 | 115 | 88.91% | 0.038563 | 0.34931 | 2015-01-28 | 93.29%
2015-01-21 | 1200 | 105 | 6.018 | 0.334 | 0.023 | 93.11% | 3.193% |  | 9.6812 | 10.8458 | 1.05 | 0.6018 | 0.035296 | 105 | 90.28% | 0.0345 | 0.3525
2015-01-21 | 1330 | 105 | 6.297 | 0.319 | 0.01 | 96.87% | 3.873% |  | 9.2464 | 11.3558 | 1.05 | 0.6297 | 0.034393 | 95 | 91% | 0.035286 | 0.39201
2015-01-21 | 1415 | 115 | 6.33 | 0.331 | 0.062 | 81.27% | -19.19% |  | 9.5942 | 11.9864 | 1.15 | 0.633 | 0.035345 | 85 | 91.86% | 0.031667 | 0.388
2015-01-21 | 1500 | 115 | 6.273 | 0.342 | 0.069 | 79.82% | -1.809% |  | 9.913 | 11.6009 | 1.15 | 0.6273 | 0.036467 | 80 | 92.5% | 0.029455 | 0.39291
2015-01-21 | 1550 | 115 | 6.373 | 0.324 | 0.025 | 92.28% | 13.5% |  | 9.3913 | 12.2454 | 1.15 | 0.6373 | 0.036097 | 70 | 93.51% | 0.023667 | 0.38733
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10 |  |  |  | Raw | Treated
2015-01-21 | 1650 | 115 | 6.356 | 0.303 | 0.022 | 92.74% | 0.491% |  | 8.7826 | 13.0941 | 1.15 | 0.6356 |  | 60 | 90.83% | 0.35839 | 0.033826
2015-01-21 | 1730 | 115 | 6.298 | 0.312 | 0.011 | 96.47% | 3.872% |  | 9.0435 | 12.7163 | 1.15 | 0.6298 |  | 63 | 91.9% | 0.3538 | 0.029267 | Raw | Treated | % Removal
2015-01-21 | 1830 | 115 | 6.24 | 0.376 | 0.019 | 94.95% | -1.609% |  | 10.8986 | 10.5519 | 1.15 | 0.624 |  | 55 | 90.32% | 0.36582 | 0.035636 | 0.36733 | 0.032581 | 91.15%
2015-01-21 | 1930 | 115 | 6.25 | 0.378 | 0.047 | 87.57% | -8.429% |  | 10.9565 | 10.496 | 1.15 | 0.625 |  | 51 | 88.53%
2015-01-21 | 2125 | 115 | 6.286 | 0.355 | 0.019 | 94.65% | 7.482% |  | 10.2899 | 11.1761 | 1.15 | 0.6286 |  | 55 | 85.11%
2015-01-21 | 2310 | 115 | 6.21 | 0.307 | 0.066 | 78.5% | -20.57% |  | 8.8986 | 12.9235 | 1.15 | 0.621 |  | 50 | 96.8%
2015-01-21 | 25 | 115 | 3.134 | 0.38 | 0.012 | 96.84% | 18.94% |  | 11.0145 | 10.4408 | 1.15 | 0.3134 |  | 53 | 88.48%
2015-01-22 | 300 | 115 | 6.181 | 0.376 | 0.064 | 82.98% | -16.71% |  | 10.8986 | 10.5519 | 1.15 | 0.6181 |  | 54 | 93.49%
2015-01-22 | 445 | 115 | 6.225 | 0.369 | 0.043 | 88.35% | 6.076% |  | 10.6957 | 10.752 | 1.15 | 0.6225
2015-01-22 | 610 | 115 | 6.274 | 0.36 | 0.027 | 92.5% | 4.49% |  | 10.4348 | 11.0208 | 1.15 | 0.6274
2015-01-22 | 710 | 115 | 6.26 | 0.352 | 0.028 | 92.05% | -0.4938% |  | 10.2029 | 11.2713 | 1.15 | 0.626
2015-01-22 | 800 | 115 | 6.286 | 0.364 | 0.049 | 86.54% | -6.364% |  | 10.5507 | 10.8997 | 1.15 | 0.6286
2015-01-22 | 910 | 115 | 6.42 | 0.36 | 0.054 | 85% | -1.81% |  | 10.4348 | 11.0208 | 1.15 | 0.642
2015-01-22 | 1000 | 105 | 6.42 | 0.365 | 0.04 | 89.04% | 4.538% |  | 10.5797 | 9.9247 | 1.05 | 0.642
2015-01-22 | 1055 | 105 | 6.316 | 0.312 | 0.025 | 91.99% | 3.203% |  | 9.0435 | 11.6106 | 1.05 | 0.6316
2015-01-22 | 1150 | 105 | 6.24 | 0.372 | 0.038 | 89.78% | -2.453% |  | 10.7826 | 9.7379 | 1.05 | 0.624
2015-01-22 | 1246 | 105 | 6.294 | 0.361 | 0.035 | 90.3% | 0.5756% |  | 10.4638 | 10.0346 | 1.05 | 0.6294
2015-01-22 | 1350 | 95 | 6.39 | 0.369 | 0.036 | 90.24% | -0.06738% |  | 10.6957 | 8.8821 | 0.95 | 0.639
2015-01-22 | 1510 | 95 | 6.024 | 0.383 | 0.019 | 95.04% | 5.046% |  | 11.1014 | 8.5574 | 0.95 | 0.6024
2015-01-22 | 1540 | 95 | 5.978 | 0.338 | 0.021 | 93.79% | -1.335% |  | 9.7971 | 9.6967 | 0.95 | 0.5978
2015-01-22 | 1708 | 95 | 6.1 | 0.356 | 0.04 | 88.76% | -5.659% |  | 10.3188 | 9.2065 | 0.95 | 0.61
2015-01-22 | 1800 | 95 | 6.195 | 0.358 | 0.039 | 89.11% | 0.3839% |  | 10.3768 | 9.155 | 0.95 | 0.6195
2015-01-22 | 1930 | 95 | 6.013 | 0.382 | 0.034 | 91.1% | 2.188% |  | 11.0725 | 8.5798 | 0.95 | 0.6013
2015-01-22 | 2130 | 95 | 5.822 | 0.41 | 0.042 | 89.76% | -1.497% |  | 11.8841 | 7.9939 | 0.95 | 0.5822
2015-01-22 | 2300 | 95 | 5.662 | 0.382 | 0.025 | 93.46% | 3.958% |  | 11.0725 | 8.5798 | 0.95 | 0.5662
2015-01-23 | 125 | 95 | 5.848 | 0.392 | 0.03 | 92.35% | -1.2% |  | 11.3623 | 8.361 | 0.95 | 0.5848
2015-01-23 | 315 | 95 | 6.056 | 0.395 | 0.058 | 85.32% | -8.24% |  | 11.4493 | 8.2975 | 0.95 | 0.6056
2015-01-23 | 445 | 95 | 5.705 | 0.371 | 0.025 | 93.26% | 8.519% |  | 10.7536 | 8.8342 | 0.95 | 0.5705
2015-01-23 | 610 | 95 | 6.11 | 0.374 | 0.029 | 92.25% | -1.101% |  | 10.8406 | 8.7634 | 0.95 | 0.611
2015-01-23 | 800 | 95 | 6.172 | 0.386 | 0.015 | 96.11% | 4.024% |  | 11.1884 | 8.4909 | 0.95 | 0.6172
2015-01-23 | 848 | 95 | 5.963 | 0.342 | 0.025 | 92.69% | -3.694% | 0.423 | 9.913 | 9.5833 | 0.95 | 0.5963
2015-01-23 | 1000 | 95 | 5.785 | 0.371 | 0.032 | 91.37% | -1.44% | 0.431 | 10.7536 | 8.8342 | 0.95 | 0.5785
2015-01-23 | 1100 | 95 | 5.995 | 0.384 | 0.03 | 92.19% | 0.8817% | 0.436 | 11.1304 | 8.5352 | 0.95 | 0.5995
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
2015-01-23 | 1200 | 95 | 5.858 | 0.388 | 0.058 | 85.05% | -8.39% |  | 11.2464 | 8.4472 | 0.95 | 0.5858
2015-01-23 | 1400 | 95 | 5.87 | 0.355 | 0.045 | 87.32% | 2.602% |  | 10.2899 | 9.2324 | 0.95 | 0.587
2015-01-23 | 1600 | 95 | 5.975 | 0.36 | 0.012 | 96.67% | 9.665% |  | 10.4348 | 9.1042 | 0.95 | 0.5975
2015-01-23 | 1645 | 95 | 5.72 | 0.372 | 0.063 | 83.06% | -16.38% |  | 10.7826 | 8.8105 | 0.95 | 0.572
2015-01-23 | 1815 | 95 | 5.984 | 0.37 | 0.039 | 89.46% | 7.148% |  | 10.7246 | 8.8581 | 0.95 | 0.5984
2015-01-23 | 2045 | 95 | 6.32 | 0.393 | 0.033 | 91.6% | 2.34% |  | 11.3913 | 8.3397 | 0.95 | 0.632
2015-01-23 | 2125 | 95 | 6.08 | 0.392 | 0.039 | 90.05% | -1.724% |  | 11.3623 | 8.361 | 0.95 | 0.608
2015-01-23 | 2200 | 95 | 6.161 | 0.411 | 0.043 | 89.54% | -0.5733% |  | 11.913 | 7.9745 | 0.95 | 0.6161
2015-01-23 | 2330 | 95 | 6.099 | 0.397 | 0.04 | 89.92% | 0.4301% |  | 11.5072 | 8.2557 | 0.95 | 0.6099
2015-01-24 | 115 | 95 | 5.778 | 0.373 | 0.04 | 89.28% | -0.7262% |  | 10.8116 | 8.7869 | 0.95 | 0.5778
2015-01-24 | 330 | 95 | 5.997 | 0.408 | 0.051 | 87.5% | -2.03% |  | 11.8261 | 8.0331 | 0.95 | 0.5997
2015-01-24 | 455 | 95 | 5.697 | 0.365 | 0.019 | 94.79% | 7.695% |  | 10.5797 | 8.9795 | 0.95 | 0.5697
2015-01-24 | 635 | 95 | 6.081 | 0.393 | 0.043 | 89.06% | -6.441% |  | 11.3913 | 8.3397 | 0.95 | 0.6081
2015-01-24 | 740 | 95 | 6.006 | 0.368 | 0.016 | 95.65% | 6.893% |  | 10.6667 | 8.9062 | 0.95 | 0.6006
2015-01-24 | 945 | 95 | 6.08 | 0.364 | 0.019 | 94.78% | -0.92% | 0.423 | 10.5507 | 9.0041 | 0.95 | 0.608
2015-01-24 | 1130 | 95 | 5.723 | 0.359 | 0.016 | 95.54% | 0.7985% | 0.435 | 10.4058 | 9.1295 | 0.95 | 0.5723
2015-01-24 | 1248 | 95 | 6.14 | 0.392 | 0.058 | 85.2% | -12.13% | 0.458 | 11.3623 | 8.361 | 0.95 | 0.614
2015-01-24 | 1525 | 95 | 5.989 | 0.393 | -0.039 | 109.9% | 22.49% | 0.454 | 11.3913 | 8.3397 | 0.95 | 0.5989
2015-01-24 | 1648 | 95 | 5.957 | 0.4 | 0.043 | 89.25% | -23.16% | 0.464 | 11.5942 | 8.1937 | 0.95 | 0.5957
2015-01-24 | 1815 | 95 | 5.846 | 0.391 | 0.035 | 91.05% | 1.975% |  | 11.3333 | 8.3824 | 0.95 | 0.5846
2015-01-24 | 1915 | 95 | 5.844 | 0.392 | 0.033 | 91.58% | 0.582% |  | 11.3623 | 8.361 | 0.95 | 0.5844
2015-01-24 | 2120 | 95 | 5.922 | 0.421 | 0.056 | 86.7% | -5.633% |  | 12.2029 | 7.785 | 0.95 | 0.5922
2015-01-24 | 2235 | 95 | 5.81 | 0.426 | 0.052 | 87.79% | 1.247% |  | 12.3478 | 7.6937 | 0.95 | 0.581
2015-01-25 | 125 | 95 | 5.536 | 0.436 | 0.039 | 91.06% | 3.582% |  | 12.6377 | 7.5172 | 0.95 | 0.5536
2015-01-25 | 315 | 95 | 5.615 | 0.42 | 0.063 | 85% | -7.124% |  | 12.1739 | 7.8036 | 0.95 | 0.5615
2015-01-25 | 445 | 95 | 6.153 | 0.396 | 0.052 | 86.87% | 2.151% |  | 11.4783 | 8.2765 | 0.95 | 0.6153
2015-01-25 | 735 | 95 | 6.101 | 0.411 | 0.062 | 84.91% | -2.301% | 0.471 | 11.913 | 7.9745 | 0.95 | 0.6101
2015-01-25 | 840 | 95 | 5.889 | 0.407 | 0.057 | 86% | 1.256% | 0.457 | 11.7971 | 8.0528 | 0.95 | 0.5889
2015-01-25 | 1002 | 95 | 5.927 | 0.403 | 0.048 | 88.09% | 2.377% | 0.471 | 11.6812 | 8.1328 | 0.95 | 0.5927
2015-01-25 | 1100 | 95 | 6.006 | 0.413 | 0.045 | 89.1% | 1.139% | 0.468 | 11.971 | 7.9358 | 0.95 | 0.6006
2015-01-25 | 1250 | 95 | 5.88 | 0.383 | 0.03 | 92.17% | 3.323% | 0.447 | 11.1014 | 8.5574 | 0.95 | 0.588
2015-01-25 | 1340 | 95 | 5.696 | 0.393 | 0.024 | 93.89% | 1.838% | 0.437 | 11.3913 | 8.3397 | 0.95 | 0.5696
2015-01-25 | 1500 | 95 | 5.851 | 0.394 | 0.004 | 98.98% | 5.144% | 0.435 | 11.4203 | 8.3185 | 0.95 | 0.5851
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
2015-01-25 | 1640 | 95 | 5.939 | 0.373 | 0.02 | 94.64% | -4.593% | 0.43 | 10.8116 | 8.7869 | 0.95 | 0.5939
2015-01-25 | 1815 | 95 | 6.074 | 0.414 | 0.035 | 90.48% | -4.6% |  | 12 | 7.9167 | 0.95 | 0.6074
2015-01-25 | 1920 | 95 | 5.847 | 0.42 | 0.04 | 89% | -1.659% |  | 12.1739 | 7.8036 | 0.95 | 0.5847
2015-01-25 | 2130 | 95 | 5.781 | 0.428 | 0.041 | 90.42% | 1.571% |  | 12.4058 | 7.6577 | 0.95 | 0.5781
2015-01-25 | 2310 | 95 | 5.647 | 0.42 | 0.029 | 93.1% | 2.873% |  | 12.1739 | 7.8036 | 0.95 | 0.5647
2015-01-26 | 130 | 95 | 5.418 | 0.403 | 0.025 | 93.8% | 0.7477% |  | 11.6812 | 8.1328 | 0.95 | 0.5418
2015-01-26 | 315 | 95 | 5.717 | 0.431 | 0.045 | 89.56% | -4.731% |  | 12.4928 | 7.6044 | 0.95 | 0.5717
2015-01-26 | 440 | 95 | 5.569 | 0.423 | 0.037 | 91.25% | 1.856% |  | 12.2609 | 7.7482 | 0.95 | 0.5569
2015-01-26 | 650 | 95 | 5.789 | 0.387 | 0.044 | 88.63% | -2.959% | 0.476 | 11.2174 | 8.469 | 0.95 | 0.5789
2015-01-26 | 845 | 95 | 5.754 | 0.392 | 0.033 | 91.58% | 3.222% | 0.445 | 11.3623 | 8.361 | 0.95 | 0.5754
2015-01-26 | 1000 | 95 | 6.181 | 0.404 | 0.046 | 88.61% | -3.349% | 0.436 | 11.7101 | 8.1126 | 0.95 | 0.6181
2015-01-26 | 1200 | 95 | 5.84 | 0.444 | 0.034 | 92.34% | 4.038% | 0.485 | 12.8696 | 7.3818 | 0.95 | 0.584
2015-01-26 | 1300 | 95 | 5.904 | 0.394 | 0.039 | 90.1% | -2.487% | 0.452 | 11.4203 | 8.3185 | 0.95 | 0.5904
2015-01-26 | 1340 | 95 | 5.858 | 0.39 | 0.017 | 95.64% | 5.792% | 0.43 | 11.3043 | 8.4038 | 0.95 | 0.5858
2015-01-26 | 1517 | 85 | 5.52 | 0.395 | 0.035 | 91.14% | -4.939% | 0.453 | 11.4493 | 7.4241 | 0.85 | 0.552
2015-01-26 | 1600 | 85 | 5.686 | 0.377 | 0.024 | 93.63% | 2.664% | 0.463 | 10.9275 | 7.7785 | 0.85 | 0.5686
2015-01-26 | 1730 | 85 | 5.756 | 0.392 | 0.036 | 90.82% | -3.103% | 0.444 | 11.3623 | 7.4809 | 0.85 | 0.5756
2015-01-26 | 1830 | 80 | 5.598 | 0.385 | 0.047 | 87.79% | -3.445% |  | 11.1594 | 7.1688 | 0.8 | 0.5598
2015-01-26 | 1940 | 80 | 5.644 | 0.376 | 0.021 | 94.41% | 7.014% |  | 10.8986 | 7.3404 | 0.8 | 0.5644
2015-01-26 | 2130 | 80 | 5.547 | 0.391 | 0.044 | 88.75% | -6.387% |  | 11.3333 | 7.0588 | 0.8 | 0.5547
2015-01-26 | 2240 | 80 | 5.568 | 0.428 | 0.037 | 91.36% | 2.855% |  | 12.4058 | 6.4486 | 0.8 | 0.5568
2015-01-27 | 130 | 80 | 5.58 | 0.429 | 0.019 | 95.57% | 4.411% |  | 12.4348 | 6.4336 | 0.8 | 0.558
2015-01-27 | 315 | 80 | 5.601 | 0.418 | 0.029 | 93.06% | -2.696% |  | 12.1159 | 6.6029 | 0.8 | 0.5601
2015-01-27 | 500 | 80 | 5.826 | 0.393 | 0.019 | 95.17% | 2.21% |  | 11.3913 | 7.0229 | 0.8 | 0.5826
2015-01-27 | 610 | 80 | 5.833 | 0.405 | 0.038 | 90.62% | -5.019% | 0.462 | 11.7391 | 6.8148 | 0.8 | 0.5833
2015-01-27 | 1010 | 80 | 5.786 | 0.383 | 0.024 | 93.73% | 3.325% | 0.417 | 11.1014 | 7.2063 | 0.8 | 0.5786
2015-01-27 | 1430 | 80 | 5.85 | 0.366 | 0.018 | 95.08% | 1.418% | 0.424 | 10.6087 | 7.541 | 0.8 | 0.585
2015-01-27 | 1515 | 80 | 5.937 | 0.348 | 0.028 | 91.95% | -3.402% |  | 10.087 | 7.931 | 0.8 | 0.5937
2015-01-27 | 1748 | 80 | 5.99 | 0.387 | 0.025 | 93.54% | 1.696% |  | 11.2174 | 7.1318 | 0.8 | 0.599
2015-01-27 | 1920 | 70 | 5.882 | 0.399 | 0.021 | 94.74% | 2.937% |  | 11.5652 | 6.0526 | 0.7 | 0.5882
2015-01-27 | 2135 | 70 | 5.718 | 0.37 | 0.026 | 92.97% | -1.897% |  | 10.7246 | 6.527 | 0.7 | 0.5718
2015-01-27 | 2315 | 70 | 5.746 | 0.394 | 0.024 | 93.91% | 0.9963% |  | 11.4203 | 6.1294 | 0.7 | 0.5746
2015-01-28 | 130 | 70 | 5.781 | 0.375 | 0.039 | 89.6% | -4.809% |  | 10.8696 | 6.44 | 0.7 | 0.5781
2015-01-28 | 315 | 70 | 5.739 | 0.41 | 0.017 | 95.85% | 6.524% |  | 11.8841 | 5.8902 | 0.7 | 0.5739
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
2015-01-28 | 450 | 70 | 5.79 | 0.376 | 0.015 | 96.01% | 0.1635% |  | 10.8986 | 6.4229 | 0.7 | 0.579
2015-01-28 | 830 | 70 | 5.794 | 0.375 | 0.029 | 92.27% | -4.058% |  | 10.8696 | 6.44 | 0.7 | 0.5794
2015-01-28 | 1100 | 70 | 5.7 | 0.37 | 0.027 | 92.7% | 0.4704% |  | 10.7246 | 6.527 | 0.7 | 0.57
2015-01-28 | 1520 | 60 | 5.763 | 0.342 | 0.013 | 96.2% | 3.634% | 0.403 | 9.913 | 6.0526 | 0.6 | 0.5763
2015-01-28 | 2100 | 60 | 5.893 | 0.365 | 0.053 | 85.48% | -12.54% |  | 10.5797 | 5.6712 | 0.6 | 0.5893
2015-01-28 | 2300 | 60 | 5.804 | 0.366 | 0.041 | 88.8% | 3.737% |  | 10.6087 | 5.6557 | 0.6 | 0.5804
2015-01-29 | 110 | 60 | 6.055 | 0.38 | 0.058 | 84.74% | -4.792% |  | 11.0145 | 5.4474 | 0.6 | 0.6055
2015-01-29 | 330 | 60 | 6.058 | 0.377 | 0.038 | 89.92% | 5.765% |  | 10.9275 | 5.4907 | 0.6 | 0.6058
2015-01-29 | 515 | 60 | 5.83 | 0.373 | 0.041 | 89.01% | -1.025% |  | 10.8116 | 5.5496 | 0.6 | 0.583
2015-01-29 | 715 | 60 | 5.834 | 0.355 | 0.031 | 91.27% | 2.476% |  | 10.2899 | 5.831 | 0.6 | 0.5834
2015-01-29 | 940 | 60 | 5.796 | 0.379 | 0.065 | 82.85% | -10.16% |  | 10.9855 | 5.4617 | 0.6 | 0.5796
2015-01-29 | 1100 | 60 | 6.08 | 0.351 | 0.032 | 90.88% | 8.839% |  | 10.1739 | 5.8974 | 0.6 | 0.608
2015-01-29 | 1425 | 60 | 5.852 | 0.34 | 0.011 | 96.76% | 6.078% |  | 9.8551 | 6.0882 | 0.6 | 0.5852
2015-01-29 | 1630 | 60 | 6.03 | 0.365 | 0.035 | 90.41% | -7.028% |  | 10.5797 | 5.6712 | 0.6 | 0.603
2015-01-29 | 1830 | 60 | 6.04 | 0.339 | 0.04 | 88.2% | -2.506% |  | 9.8261 | 6.1062 | 0.6 | 0.604
2015-01-29 | 2030 | 60 | 6.02 | 0.379 | 0.036 | 90.5% | 2.542% |  | 10.9855 | 5.4617 | 0.6 | 0.602
2015-01-29 | 2234 | 60 | 5.899 | 0.357 | 0.049 | 86.27% | -4.899% |  | 10.3478 | 5.7983 | 0.6 | 0.5899
2015-01-30 | 1248 | 60 | 5.958 | 0.341 | 0.025 | 92.67% | 6.9% |  | 9.8841 | 6.0704 | 0.6 | 0.5958
2015-01-30 | 300 | 60 | 5.865 | 0.436 | 0.078 | 82.11% | -12.86% |  | 12.6377 | 4.7477 | 0.6 | 0.5865
2015-01-30 | 445 | 60 | 5.777 | 0.344 | 0.041 | 88.08% | 6.779% |  | 9.971 | 6.0174 | 0.6 | 0.5777
2015-01-30 | 800 | 60 | 6.057 | 0.307 | -0.016 | 105.2% | 16.28% |  | 8.8986 | 6.7427 | 0.6 | 0.6057
2015-01-30 | 1030 | 60 | 5.859 | 0.334 | 0.015 | 95.51% | -10.16% |  | 9.6812 | 6.1976 | 0.6 | 0.5859
2015-01-30 | 1235 | 60 | 5.717 | 0.328 | 0.018 | 94.51% | -1.055% |  | 9.5072 | 6.311 | 0.6 | 0.5717
2015-01-30 | 1600 | 60 | 5.902 | 0.346 | 0.021 | 93.93% | -0.6191% |  | 10.029 | 5.9827 | 0.6 | 0.5902
2015-01-30 | 1800 | 60 | 5.876 | 0.352 | 0.024 | 93.18% | -0.8036% |  | 10.2029 | 5.8807 | 0.6 | 0.5876
2015-01-30 | 2010 | 60 | 5.884 | 0.387 | 0.029 | 92.51% | -0.7301% |  | 11.2174 | 5.3488 | 0.6 | 0.5884
2015-01-30 | 2247 | 63 | 5.84 | 0.323 | 0.01 | 96.9% | 4.538% |  | 9.3623 | 6.7291 | 0.63 | 0.584
2015-01-31 | 0056 | 63 | 5.932 | 0.373 | 0.039 | 89.54% | -8.219% |  | 10.8116 | 5.8271 | 0.63 | 0.5932
2015-01-31 | 300 | 63 | 5.71 | 0.392 | 0.074 | 81.12% | -10.38% |  | 11.3623 | 5.5446 | 0.63 | 0.571
2015-01-31 | 500 | 63 | 5.789 | 0.358 | 0.036 | 89.94% | 9.808% |  | 10.3768 | 6.0712 | 0.63 | 0.5789
2015-01-31 | 830 | 63 | 5.83 | 0.343 | 0.001 | 99.71% | 9.793% |  | 9.942 | 6.3367 | 0.63 | 0.583
2015-01-31 | 1000 | 63 | 5.74 | 0.345 | 0.026 | 92.46% | -7.835% |  | 10 | 6.3 | 0.63 | 0.574
2015-01-31 | 1200 | 63 | 6.029 | 0.333 | 0.016 | 95.2% | 2.869% |  | 9.6522 | 6.527 | 0.63 | 0.6029
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
2015-01-31 | 1400 | 63 | 5.711 | 0.337 | 0.018 | 94.66% | -0.5667% |  | 9.7681 | 6.4496 | 0.63 | 0.5711
2015-01-31 | 1600 | 63 | 5.753 | 0.346 | 0.023 | 93.35% | -1.399% |  | 10.029 | 6.2818 | 0.63 | 0.5753
2015-01-31 | 1800 | 63 | 5.595 | 0.361 | 0.026 | 92.8% | -0.5979% |  | 10.4638 | 6.0208 | 0.63 | 0.5595
2015-01-31 | 2000 | 63 | 5.79 | 0.355 | 0.032 | 90.99% | -1.991% |  | 10.2899 | 6.1225 | 0.63 | 0.579
2015-01-31 | 2250 | 63 | 5.731 | 0.347 | 0.024 | 93.08% | 2.254% |  | 10.058 | 6.2637 | 0.63 | 0.5731
2015-02-01 | 0100 | 63 | 5.839 | 0.373 | 0.038 | 89.81% | -3.642% |  | 10.8116 | 5.8271 | 0.63 | 0.5839
2015-02-01 | 300 | 63 | 5.619 | 0.361 | 0.035 | 90.3% | 0.5452% |  | 10.4638 | 6.0208 | 0.63 | 0.5619
2015-02-01 | 500 | 63 | 5.756 | 0.36 | 0.041 | 88.61% | -1.911% |  | 10.4348 | 6.0375 | 0.63 | 0.5756
2015-02-01 | 800 | 60 | 5.883 | 0.367 | 0.029 | 92.1% | 3.786% |  | 10.6377 | 5.6403 | 0.6 | 0.5883
2015-02-01 | 1015 | 60 | 6.093 | 0.354 | 0.028 | 92.09% | -0.008358% |  | 10.2609 | 5.8475 | 0.6 | 0.6093
2015-02-01 | 1150 | 55 | 6.14 | 0.366 | 0.039 | 89.34% | -3.074% |  | 10.6087 | 5.1844 | 0.55 | 0.614
2015-02-01 | 1415 | 55 | 5.82 | 0.331 | 0.022 | 93.35% | 4.295% |  | 9.5942 | 5.7326 | 0.55 | 0.582
2015-02-01 | 1600 | 55 | 6.132 | 0.3 | 0.042 | 86% | -8.551% |  | 8.6957 | 6.325 | 0.55 | 0.6132
2015-02-01 | 1800 | 55 | 6.061 | 0.361 | 0.04 | 88.92% | 3.283% |  | 10.4638 | 5.2562 | 0.55 | 0.6061
2015-02-01 | 2000 | 55 | 5.907 | 0.398 | 0.038 | 90.45% | 1.694% |  | 11.5362 | 4.7676 | 0.55 | 0.5907
2015-02-01 | 2234 | 55 | 5.89 | 0.373 | 0.034 | 90.88% | 0.4758% |  | 10.8116 | 5.0871 | 0.55 | 0.589
2015-02-02 | 47 | 55 | 6.059 | 0.367 | 0.029 | 92.1% | 1.317% |  | 10.6377 | 5.1703 | 0.55 | 0.6059
2015-02-02 | 300 | 55 | 5.836 | 0.428 | 0.048 | 88.79% | -3.732% |  | 12.4058 | 4.4334 | 0.55 | 0.5836
2015-02-02 | 500 | 55 | 5.921 | 0.381 | 0.057 | 85.04% | -4.405% |  | 11.0435 | 4.9803 | 0.55 | 0.5921
2015-02-02 | 800 | 55 | 5.825 | 0.367 | 0.02 | 94.55% | 10.06% |  | 10.6377 | 5.1703 | 0.55 | 0.5825
2015-02-02 | 1015 | 55 | 6.117 | 0.352 | 0.023 | 93.47% | -1.16% |  | 10.2029 | 5.3906 | 0.55 | 0.6117
2015-02-02 | 1420 | 55 | 6.171 | 0.344 | 0.031 | 90.99% | -2.723% |  | 9.971 | 5.516 | 0.55 | 0.6171
2015-02-02 | 1625 | 55 | 6.134 | 0.358 | 0.034 | 90.5% | -0.5365% |  | 10.3768 | 5.3003 | 0.55 | 0.6134
2015-02-02 | 1815 | 55 | 6.021 | 0.364 | 0.036 | 90.11% | -0.436% |  | 10.5507 | 5.2129 | 0.55 | 0.6021
2015-02-02 | 2020 | 51 | 5.868 | 0.378 | 0.038 | 89.95% | -0.181% |  | 10.9565 | 4.6548 | 0.51 | 0.5868
2015-02-02 | 2247 | 51 | 6.1 | 0.387 | 0.054 | 86.05% | -4.533% |  | 11.2174 | 4.5465 | 0.51 | 0.61
2015-02-03 | 100 | 51 | 6.01 | 0.376 | 0.043 | 88.56% | 2.842% |  | 10.8986 | 4.6795 | 0.51 | 0.601
2015-02-03 | 300 | 51 | 5.82 | 0.374 | 0.039 | 89.57% | 1.126% |  | 10.8406 | 4.7045 | 0.51 | 0.582
2015-02-03 | 500 | 55 | 5.78 | 0.376 | 0.056 | 85.11% | -5.247% |  | 10.8986 | 5.0465 | 0.55 | 0.578
2015-02-03 | 800 | 50 | 5.752 | 0.326 | -0.024 | 107.4% | 20.73% |  | 9.4493 | 5.2914 | 0.5 | 0.5752
2015-02-03 | 1400 | 50 | 5.864 | 0.336 | 0.022 | 93.45% | -14.88% |  | 9.7391 | 5.1339 | 0.5 | 0.5864
2015-02-03 | 1600 | 50 | 5.864 | 0.346 | 0.036 | 89.6% | -4.305% |  | 10.029 | 4.9855 | 0.5 | 0.5864
2015-02-04 | 1900 | 53 | 5.724 | 0.359 | 0.034 | 90.53% | 1.032% |  | 10.4058 | 5.0933 | 0.53 | 0.5724
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
2015-02-03 | 2100 | 53 | 5.788 | 0.363 | 0.038 | 89.53% | -1.114% |  | 10.5217 | 5.0372 | 0.53 | 0.5788
2015-02-03 | 2245 | 53 | 5.864 | 0.353 | 0.047 | 86.69% | -3.283% |  | 10.2319 | 5.1799 | 0.53 | 0.5864
2015-02-04 | 100 | 53 | 5.886 | 0.372 | 0.04 | 89.25% | 2.87% |  | 10.7826 | 4.9153 | 0.53 | 0.5886
2015-02-04 | 300 | 53 | 5.731 | 0.43 | 0.064 | 85.12% | -4.853% | 0.403 | 12.4638 | 4.2523 | 0.53 | 0.5731
2015-02-04 | 505 | 53 | 5.728 | 0.351 | 0.036 | 89.74% | 5.156% |  | 10.1739 | 5.2094 | 0.53 | 0.5728
2015-02-04 | 600 | 54 | 5.811 | 0.356 | 0.034 | 90.45% | 0.7804% |  | 10.3188 | 5.2331 | 0.54 | 0.5811
2015-02-04 | 900 | 54 | 5.916 | 0.347 | 0.031 | 91.07% | 0.6774% |  | 10.058 | 5.3689 | 0.54 | 0.5916
2015-02-04 | 1100 | 54 | 5.976 | 0.337 | 0.03 | 91.1% | 0.03473% |  | 9.7681 | 5.5282 | 0.54 | 0.5976
2015-02-04 | 1330 | 54 | 5.725 | 0.333 | 0.014 | 95.8% | 4.904% |  | 9.6522 | 5.5946 | 0.54 | 0.5725
2015-02-04 | 1530 | 54 | 5.847 | 0.396 | 0.019 | 95.2% | -0.6237% |  | 11.4783 | 4.7045 | 0.54 | 0.5847
2015-02-04 | 1730 | 54 | 5.758 | 0.397 | 0.019 | 95.21% | 0.01269% |  | 11.5072 | 4.6927 | 0.54 | 0.5758
2015-02-04 | 1800 | 54 | 5.576 | 0.357 | 0.02 | 94.4% | -0.8648% |  | 10.3478 | 5.2185 | 0.54 | 0.5576
2015-02-04 | 2140 | 54 | 5.765 | 0.352 | 0.034 | 90.34% | -4.491% | 0.376 | 10.2029 | 5.2926 | 0.54 | 0.5765
2015-02-04 | 2340 | 54 | 5.797 | 0.362 | 0.013 | 96.41% | 6.294% | 0.377 | 10.4928 | 5.1464 | 0.54 | 0.5797
2015-02-05 | 140 | 54 | 5.608 | 0.314 | 0.016 | 94.9% | -1.585% | 0.355 | 9.1014 | 5.9331 | 0.54 | 0.5608
2015-02-05 | 319 | 54 | 5.767 | 0.308 | 0.02 | 93.51% | -1.495% | 0.345 | 8.9275 | 6.0487 | 0.54 | 0.5767
2015-02-05 | 450 | 54 | 5.844 | 0.279 | 0.031 | 88.89% | -5.195% | 0.3 | 8.087 | 6.6774 | 0.54 | 0.5844
2015-02-05 | 730 | 54 | 5.875 | 0.36 | 0.039 | 89.17% | 0.3115% |  | 10.4348 | 5.175 | 0.54 | 0.5875
2015-02-05 | 930 | 54 | 5.804 | 0.37 | 0.037 | 90% | 0.9259% |  | 10.7246 | 5.0351 | 0.54 | 0.5804
2015-02-05 | 1130 | 54 | 5.918 | 0.368 | 0.046 | 87.5% | -2.857% |  | 10.6667 | 5.0625 | 0.54 | 0.5918
2015-02-05 | 1330 | 54 | 5.723 | 0.353 | 0.015 | 95.75% | 8.617% |  | 10.2319 | 5.2776 | 0.54 | 0.5723
2015-02-05 | 1530 | 54 | 5.719 | 0.351 | 0.023 | 93.45% | -2.465% |  | 10.1739 | 5.3077 | 0.54 | 0.5719
2015-02-05 | 1730 | 54 | 5.863 | 0.333 | 0.016 | 95.2% | 1.836% |  | 9.6522 | 5.5946 | 0.54 | 0.5863
2015-02-05 | 1940 | 54 | 5.96 | 0.288 | 0.02 | 93.06% | -2.299% | 0.321 | 8.3478 | 6.4688 | 0.54 | 0.596
2015-02-05 | 2150 | 54 | 5.796 | 0.301 | 0.017 | 94.35% | 1.374% | 0.323 | 8.7246 | 6.1894 | 0.54 | 0.5796
2015-02-06 | 140 | 54 | 5.587 | 0.263 | 0.036 | 86.31% | -9.315% | 0.304 | 7.6232 | 7.0837 | 0.54 | 0.5587
2015-02-06 | 340 | 54 | 5.69 | 0.294 | 0.01 | 96.6% | 10.65% | 0.338 | 8.5217 | 6.3367 | 0.54 | 0.569
2015-02-06 | 450 | 54 | 5.794 | 0.33 | 0.015 | 95.45% | -1.199% |  | 9.5652 | 5.6455 | 0.54 | 0.5794
2015-02-06 | 630 | 50 | 5.583 | 0.3 | 0.021 | 93% | -2.639% |  | 8.6957 | 5.75 | 0.5 | 0.5583
2015-02-06 | 830 | 50 | 5.901 | 0.309 | 0.016 | 94.82% | 1.922% |  | 8.9565 | 5.5825 | 0.5 | 0.5901
2015-02-06 | 1100 | 50 | 5.873 | 0.315 | 0.012 | 96.19% | 1.423% |  | 9.1304 | 5.4762 | 0.5 | 0.5873
2015-02-06 | 1300 | 50 | 5.596 | 0.335 | 0.009 | 97.31% | 1.154% |  | 9.7101 | 5.1493 | 0.5 | 0.5596
2015-02-06 | 1500 | 50 | 5.794 | 0.303 | 0.02 | 93.4% | -4.191% |  | 8.7826 | 5.6931 | 0.5 | 0.5794
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change | Raw temp | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
Friday,February 06,2015 | 1700 | 50 | 5.624 | 0.272 | 0.005 | 98.16% | 4.852% |  | 7.8841 | 6.3419 | 0.5 | 0.5624
2015-02-11 | 707 | 46 | 5.82 | 0.309 | 0.044 | 85.76% | -14.46% |  | 8.9565 | 5.1359 | 0.46 | 0.582
2015-02-11 | 910 | 46 | 5.741 | 0.293 | 0.037 | 87.37% | 1.844% |  | 8.4928 | 5.4164 | 0.46 | 0.5741
wed, feb 11,2015 | 1130 | 46 | 5.809 | 0.264 | 0.03 | 88.64% | 1.426% |  | 7.6522 | 6.0114 | 0.46 | 0.5809
wed, feb 11,2015 | 1339 | 47 | 5.768 | 0.28 | 0.035 | 87.5% | -1.299% |  | 8.1159 | 5.7911 | 0.47 | 0.5768
wed, feb 11,2015 | 1540 | 47 | 5.626 | 0.274 | 0.018 | 93.43% | 6.348% |  | 7.942 | 5.9179 | 0.47 | 0.5626
wed, feb 11,2015 | 1710 | 47 | 5.721 | 0.267 | 0.025 | 90.64% | -3.083% |  | 7.7391 | 6.073 | 0.47 | 0.5721
wed, feb 11,2015 | 2010 | 55 | 5.8 | 0.302 | 0.02 | 93.38% | 2.935% |  | 8.7536 | 6.2831 | 0.55 | 0.58
wed, feb 11,2015 | 2210 | 55 | 5.759 | 0.292 | 0.024 | 91.78% | -1.74% |  | 8.4638 | 6.4983 | 0.55 | 0.5759
Thursday,Feb 12,2015 | 115 | 55 | 5.799 | 0.296 | 0.027 | 90.88% | -0.993% |  | 8.5797 | 6.4105 | 0.55 | 0.5799
Thursday,Feb 12,2015 | 300 | 55 | 5.869 | 0.306 | 0.02 | 93.46% | 2.766% |  | 8.8696 | 6.201 | 0.55 | 0.5869
Thursday,Feb 12,2015 | 500 | 55 | 5.785 | 0.301 | 0.027 | 91.03% | -2.674% |  | 8.7246 | 6.304 | 0.55 | 0.5785
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! | TEMP | 0 | #DIV/0! | 0 | 0
Thursday 10/15/15 | 900 | 110 | 5.368 | 0.771 | 0.104 | 86.51% | #DIV/0! | 21.8 | 20.2895 | 5.4215 | 1.1 | 0.5368
Thursday 10/15/15 | 1200 | 110 | 5.349 | 0.786 | 0.085 | 89.19% | 2.999% | 22 | 20.6842 | 5.3181 | 1.1 | 0.5349
Thursday 10/15/15 | 1500 | 115 | 5.401 | 0.804 | 0.095 | 88.18% | -1.136% | 22 | 21.1579 | 5.4353 | 1.15 | 0.5401
Thursday 10/15/15 | 1800 | 115 | 5.177 | 0.795 | 0.124 | 84.4% | -4.48% | 20.5 | 20.9211 | 5.4969 | 1.15 | 0.5177
Thursday 10/15/15 | 2100 | 115 | 4.932 | 0.818 | 0.126 | 84.6% | 0.2294% | 20.4 | 21.5263 | 5.3423 | 1.15 | 0.4932
Thursday 10/15/15 | 2315 | 115 | 5.032 | 0.809 | 0.125 | 84.55% | -0.05648% | 20.4 | 21.2895 | 5.4017 | 1.15 | 0.5032
Friday10/16/15 | 320 | 115 | 5.3 | 0.779 | 0.139 | 82.16% | -2.912% | 20.5 | 20.5 | 5.6098 | 1.15 | 0.53
Friday10/16/15 | 600 | 115 | 5.192 | 0.792 | 0.114 | 85.61% | 4.029% | 21.8 | 20.8421 | 5.5177 | 1.15 | 0.5192
Friday10/16/15 | 1000 | 115 | 5.349 | 0.809 | 0.112 | 86.16% | 0.638% | 20 | 21.2895 | 5.4017 | 1.15 | 0.5349
Friday10/16/15 | 1200 | 115 | 5.306 | 0.816 | 0.081 | 90.07% | 4.35% | 20.8 | 21.4737 | 5.3554 | 1.15 | 0.5306
Friday10/16/15 | 1400 | 115 | 5.206 | 0.809 | 0.104 | 87.14% | -3.361% | 21.2 | 21.2895 | 5.4017 | 1.15 | 0.5206
Friday10/16/15 | 1600 | 115 | 5.218 | 0.794 | 0.1 | 87.41% | 0.2985% | 21.2 | 20.8947 | 5.5038 | 1.15 | 0.5218
Friday10/16/15 | 1800 | 115/130 | 5.281 | 0.784 | 0.12 | 84.69% | -3.202% | 21.2 | 20.6316 | #VALUE! | #VALUE! | 0.5281
Friday10/16/15 | 2000 | 115/130 | 5.31 | 0.807 | 0.12 | 85.13% | 0.5124% | 21.1 | 21.2368 | #VALUE! | #VALUE! | 0.531
Friday10/16/15 | 2200 | 115/130 | 5.206 | 0.826 | 0.135 | 83.66% | -1.762% | 21.1 | 21.7368 | #VALUE! | #VALUE! | 0.5206
Saturday10/17/15 | 2400 | 115/130 | 5.474 | 0.822 | 0.2 | 75.67% | -10.56% | 21.1 | 21.6316 | #VALUE! | #VALUE! | 0.5474
Saturday10/17/15 | 200 | 115/130 | 5.463 | 0.769 | 0.182 | 76.33% | 0.8696% | 21.1 | 20.2368 | #VALUE! | #VALUE! | 0.5463
Saturday10/17/15 | 400 | 115/130 | 5.444 | 0.822 | 0.133 | 83.82% | 8.932% | 21 | 21.6316 | #VALUE! | #VALUE! | 0.5444
Saturday10/17/15 | 600 | 115/130 | 5.194 | 0.694 | 0.099 | 85.73% | 2.234% | 21.4 | 18.2632 | #VALUE! | #VALUE! | 0.5194
DATE | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change | TEMP | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
Saturday10/17/15 | 800 | 115 | 5.647 | 0.813 | 0.154 | 81.06% | -5.77% | 20.9 | 21.3947 | 5.3752 | 1.15 | 0.5647
Saturday10/17/15 | 1000 | 115 | 5.63 | 0.83 | 0.1 | 87.95% | 7.838% | 20.9 | 21.8421 | 5.2651 | 1.15 | 0.563
Saturday10/17/15 | 1200 | 115 | 5.359 | 0.803 | 0.108 | 86.55% | -1.619% | 21.6 | 21.1316 | 5.4421 | 1.15 | 0.5359
Saturday10/17/15 | 1400 | 115 | 5.375 | 0.839 | 0.116 | 86.17% | -0.4368% | 20.9 | 22.0789 | 5.2086 | 1.15 | 0.5375
Saturday10/17/15 | 1600 | 115 | 5.275 | 0.823 | 0.11 | 86.63% | 0.5313% | 21 | 21.6579 | 5.3098 | 1.15 | 0.5275
Saturday10/17/15 | 1800 | 115 | 5.162 | 0.847 | 0.126 | 85.12% | -1.774% | 21.2 | 22.2895 | 5.1594 | 1.15 | 0.5162
Saturday10/17/15 | 2000 | 135 | 5.1 | 0.83 | 0.148 | 82.17% | -3.597% | 21 | 21.8421 | 6.1807 | 1.35 | 0.51
Saturday10/17/15 | 2200 | 135 | 5.194 | 0.847 | 0.132 | 84.42% | 2.662% | 20.8 | 22.2895 | 6.0567 | 1.35 | 0.5194
Saturday10/17/15 | 2400 | 135 | 5.327 | 0.842 | 0.123 | 85.39% | 1.143% | 20.5 | 22.1579 | 6.0926 | 1.35 | 0.5327
Sunday10/18/15 | 200 | 135 | 5.472 | 0.849 | 0.132 | 84.45% | 0.04347% | 20.4 | 22.3421 | 6.0424 | 1.35 | 0.5472
Sunday10/18/15 | 400 | 135 | 5.425 | 0.814 | 0.181 | 77.76% | -8.601% | 20.4 | 21.4211 | 6.3022 | 1.35 | 0.5425
Sunday10/18/15 | 600 | 135 | 5.301 | 0.82 | 0.147 | 82.07% | 5.25% | 21.2 | 21.5789 | 6.2561 | 1.35 | 0.5301
Sunday10/18/15 | 800 | 120 | 5.525 | 0.851 | 0.111 | 86.96% | 5.616% | 21.1 | 22.3947 | 5.3584 | 1.2 | 0.5525
Sunday10/18/15 | 1000 | 120 | 5.056 | 0.843 | 0.114 | 86.48% | -0.5547% | 20 | 22.1842 | 5.4093 | 1.2 | 0.5056
Sunday10/18/15 | 1200 | 120 | 5.263 | 0.828 | 0.095 | 88.53% | 2.315% | 20.6 | 21.7895 | 5.5072 | 1.2 | 0.5263
Sunday10/18/15 | 1400 | 120 | 5.35 | 0.832 | 0.105 | 87.38% | -1.312% | 20.7 | 21.8947 | 5.4808 | 1.2 | 0.535
Sunday10/18/15 | 1600 | 120 | 5.485 | 0.824 | 0.104 | 87.38% | -0.001335% | 20.8 | 21.6842 | 5.534 | 1.2 | 0.5485
Sunday10/18/15 | 1800 | 120 | 5.184 | 0.837 | 0.114 | 86.38% | -1.156% | 20 | 22.0263 | 5.448 | 1.2 | 0.5184
Sunday10/18/15 | 2000 | 120 | 5.086 | 0.881 | 0.137 | 84.45% | -2.286% | 19.8 | 23.1842 | 5.1759 | 1.2 | 0.5086
Sunday10/18/15 | 2200 | 120 | 5.486 | 0.895 | 0.121 | 86.48% | 2.348% | 19.6 | 23.5526 | 5.095 | 1.2 | 0.5486
Sunday10/18/15 | 2400 | 120 | 5.586 | 0.874 | 0.151 | 82.72% | -4.542% | 19.5 | 23 | 5.2174 | 1.2 | 0.5586
Monday10/19/15 | 200 | 120 | 5.555 | 0.873 | 0.122 | 86.03% | 3.839% | 19.5 | 22.9737 | 5.2234 | 1.2 | 0.5555
Monday10/19/15 | 400 | 120 | 5.594 | 0.884 | 0.129 | 85.41% | -0.7235% | 19.3 | 23.2632 | 5.1584 | 1.2 | 0.5594
Monday10/19/15 | 600 | 120 | 5.619 | 0.834 | 0.117 | 85.97% | 0.656% | 20 | 21.9474 | 5.4676 | 1.2 | 0.5619
Monday10/19/15 | 800 | 120 | 5.409 | 0.848 | 0.098 | 88.44% | 2.795% | 20 | 22.3158 | 5.3774 | 1.2 | 0.5409
Monday10/19/15 | 1000 | 120 | 5.58 | 0.854 | 0.132 | 84.54% | -4.613% | 18.9 | 22.4737 | 5.3396 | 1.2 | 0.558
Monday10/19/15 | 1200 | 120 | 5.349 | 0.885 | 0.113 | 87.23% | 3.082% | 19 | 23.2895 | 5.1525 | 1.2 | 0.5349
Monday10/19/15 | 1400 | 125 | 5.263 | 0.891 | 0.118 | 86.76% | -0.5477% | 19 | 23.4474 | 5.3311 | 1.25 | 0.5263
Monday10/19/15 | 1600 | 125 | 5.28 | 0.874 | 0.11 | 87.41% | 0.7524% | 19.5 | 23 | 5.4348 | 1.25 | 0.528
Monday10/19/15 | 1800 | 125 | 4.966 | 0.879 | 0.118 | 86.58% | -0.9686% | 18.9 | 23.1316 | 5.4039 | 1.25 | 0.4966
Monday10/19/15 | 2200 | 140 | 5.336 | 0.915 | 0.151 | 83.5% | -3.687% | 18.9 | 24.0789 | 5.8142 | 1.4 | 0.5336
Tuesday10/20/15 | 2400 | 140 | 5.417 | 0.912 | 0.121 | 86.73% | 3.73% | 18.6 | 24 | 5.8333 | 1.4 | 0.5417
Tuesday10/20/15 | 200 | 140 | 5.186 | 0.929 | 0.126 | 86.44% | -0.3418% | 21.4 | 24.4474 | 5.7266 | 1.4 | 0.5186
Tuesday10/20/15 | 400 | 140 | 5.429 | 0.929 | 0.138 | 85.15% | -1.517% | 21.8 | 24.4474 | 5.7266 | 1.4 | 0.5429
Date | Time | Alum Dose | Treated pH | Raw UV 254 | Treated UV 254 | Percent Removal | Percent Change |  | Calculated Raw TOC, mg/L | Alum Dose:TOC Ratio | Alum Dose Divided By 100 | Treated pH Divided By 10
Tuesday10/20/15 | 600 | 140 | 5.185 | 0.889 | 0.139 | 84.36% | -0.9256% | 22.1 | 23.3947 | 5.9843 | 1.4 | 0.5185
Tuesday10/20/15 | 800 | 130 | 5.205 | 0.824 | 0.129 | 84.34% | -0.02347% | 22 | 21.6842 | 5.9951 | 1.3 | 0.5205
Tuesday10/20/15 | 1000 | 130 | 5.439 | 0.864 | 0.117 | 86.46% | 2.445% | 22.1 | 22.7368 | 5.7176 | 1.3 | 0.5439
Tuesday10/20/15 | 1200 | 130 | 5.487 | 0.848 | 0.114 | 86.56% | 0.1135% |  | 22.3158 | 5.8255 | 1.3 | 0.5487
Tuesday10/20/15 | 1400 | 130 | 5.395 | 0.828 | 0.11 | 86.71% | 0.1826% |  | 21.7895 | 5.9662 | 1.3 | 0.5395
Tuesday10/20/15 | 1600 | 130 | 5.654 | 0.848 | 0.091 | 89.27% | 2.861% |  | 22.3158 | 5.8255 | 1.3 | 0.5654
Tuesday10/20/15 | 1800 | 130 |  |  |  | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 1.3 | 0
Wednesday 10/21/15 | 2000 | 145 | 5.5 | 0.962 | 0.17 | 82.33% | #DIV/0! |  | 25.3158 | 5.7277 | 1.45 | 0.55
Wednesday 10/21/15 | 2100 | 150 | 5.54 | 0.95 | 0.11 | 88.42% | 6.89% |  | 25 | 6 | 1.5 | 0.554
Wednesday 10/21/15 | 2300 | 150 | 5.728 | 0.88 | 0.1 | 88.64% | 0.2429% |  | 23.1579 | 6.4773 | 1.5 | 0.5728
Thursday 10/22/15 | 100 | 155 | 5.44 | 0.986 | 0.12 | 87.83% | -0.9185% |  | 25.9474 | 5.9736 | 1.55 | 0.544
Thursday 10/22/15 | 300 | 160 | 5.51 | 0.951 | 0.12 | 87.38% | -0.5126% |  | 25.0263 | 6.3933 | 1.6 | 0.551
Thursday 10/22/15 | 500 | 160 | 5.6 | 0.954 | 0.11 | 88.47% | 1.23% |  | 25.1053 | 6.3732 | 1.6 | 0.56
Thursday 10/22/15 | 700 | 160 | 5.6 | 0.953 | 0.11 | 88.46% | -0.01368% |  | 25.0789 | 6.3799 | 1.6 | 0.56
Thursday 10/22/15 | 900 | 160 | 5.55 | 0.957 | 0.12 | 87.46% | -1.14% |  | 25.1842 | 6.3532 | 1.6 | 0.555
Thursday 10/22/15 | 1100 | 160 | 5.62 | 0.944 | 0.14 | 85.17% | -2.69% |  | 24.8421 | 6.4407 | 1.6 | 0.562
Thursday 10/22/15 | 1300 | 160 | 5.57 | 0.933 | 0.12 | 87.14% | 2.259% |  | 24.5526 | 6.5166 | 1.6 | 0.557
Thursday 10/22/15 | 1500 | 160 | 5.6 | 0.948 | 0.14 | 85.23% | -2.236% |  | 24.9474 | 6.4135 | 1.6 | 0.56
Thursday 10/22/15 | 1700 | 160 | 5.61 | 0.944 | 0.14 | 85.17% | -0.07347% |  | 24.8421 | 6.4407 | 1.6 | 0.561
Thursday 10/22/15 | 1900 | 160 | 5.58 | 0.915 | 0.109 | 88.09% | 3.313% |  | 24.0789 | 6.6448 | 1.6 | 0.558
Thursday 10/22/15 | 2100 | 160 | 5.571 | 0.933 | 0.11 | 88.21% | 0.139% |  | 24.5526 | 6.5166 | 1.6 | 0.5571
Thursday 10/22/15 | 2300 | 160 | 5.685 | 0.875 | 0.106 | 87.89% | -0.3691% |  | 23.0263 | 6.9486 | 1.6 | 0.5685
Friday 10/23/15 | 100 | 160 | 5.583 | 0.881 | 0.114 | 87.06% | -0.9483% |  | 23.1842 | 6.9012 | 1.6 | 0.5583
Friday 10/23/15 | 300 | 160 | 5.658 | 0.931 | 0.113 | 87.86% | 0.9132% |  | 24.5 | 6.5306 | 1.6 | 0.5658
Friday 10/23/15 | 500 | 160 | 5.712 | 0.943 | 0.113 | 88.02% | 0.1755% |  | 24.8158 | 6.4475 | 1.6 | 0.5712
Friday 10/23/15 | 700 | 157 | 5.709 | 0.942 | 0.174 | 81.53% | -7.958% |  | 24.7895 | 6.3333 | 1.57 | 0.5709
Friday 10/23/15 | 900 | 157 | 5.69 | 0.93 | 0.155 | 83.33% | 2.166% |  | 24.4737 | 6.4151 | 1.57 | 0.569
Friday 10/23/15 | 1100 | 157 | 5.62 | 0.934 | 0.119 | 87.26% | 4.499% |  | 24.5789 | 6.3876 | 1.57 | 0.562
Saturday 10/24/15 | 100 | 160 | 5.582 | 0.866 | 0.1 | 88.45% | 1.349% |  | 22.7895 | 7.0208 | 1.6 | 0.5582
Saturday 10/24/15 | 300 | 160 | 5.79 | 0.916 | 0.117 | 87.23% | -1.405% |  | 24.1053 | 6.6376 | 1.6 | 0.579
Saturday 10/24/15 | 500 | 160 | 5.701 | 0.922 | 0.113 | 87.74% | 0.5892% |  | 24.2632 | 6.5944 | 1.6 | 0.5701
Saturday 10/24/15 | 700 | 160 | 5.707 | 0.917 | 0.121 | 86.8% | -1.082% |  | 24.1316 | 6.6303 | 1.6 | 0.5707
Saturday 10/24/15 | 900 | 160 | 5.725 | 0.895 | 0.138 | 84.58% | -2.629% |  | 23.5526 | 6.7933 | 1.6 | 0.5725
Saturday 10/24/15 | 1100 | 160 | 5.646 | 0.906 | 0.128 | 85.87% | 1.503% |  | 23.8421 | 6.7108 | 1.6 | 0.5646
Saturday 10/24/15 | 1500 | 160 | 5.568 | 0.913 | 0.115 | 87.4% | 1.753% |  | 24.0263 | 6.6594 | 1.6 | 0.5568
Saturday 10/24/15 | 1700 | 160 | 5.454 | 0.851 | 0.125 | 85.31% | -2.453% |  | 22.3947 | 7.1445 | 1.6 | 0.5454
Saturday10/24/15 | 1900 | 160 | 5.78 | 0.919 | 0.118 | 87.16% | 2.121% |  | 24.1842 | 6.6159 | 1.6 | 0.578
Saturday10/24/15 | 2100 | 160 | 5.88 | 0.896 | 0.107 | 88.06% | 1.02% |  | 23.5789 | 6.7857 | 1.6 | 0.588
Saturday10/24/15 | 2300 | 160 | 5.97 | 0.833 | 0.111 | 86.67% | -1.596% |  | 21.9211 | 7.2989 | 1.6 | 0.597
Sunday 10/25/15 | 100 | 160 | 5.85 | 0.841 | 0.11 | 86.92% | 0.2826% |  | 22.1316 | 7.2295 | 1.6 | 0.585
Sunday 10/25/15 | 300 | 160 | 5.96 | 0.871 | 0.115 | 86.8% | -0.1423% |  | 22.9211 | 6.9805 | 1.6 | 0.596
Sunday 10/25/15 | 500 | 160 | 5.86 | 0.886 | 0.114 | 87.13% | 0.3861% |  | 23.3158 | 6.8623 | 1.6 | 0.586
Sunday 10/25/15 | 700 | 145 | 5.937 | 0.865 | 0.131 | 84.86% | -2.684% |  | 22.7632 | 6.3699 | 1.45 | 0.5937
Sunday 10/25/15 | 900 | 145 | 6.044 | 0.874 | 0.158 | 81.92% | -3.581% |  | 23 | 6.3043 | 1.45 | 0.6044
Sunday 10/25/15 | 1100 | 145 | 5.95 | 0.876 | 0.15 | 82.88% | 1.152% |  | 23.0526 | 6.29 | 1.45 | 0.595
Sunday 10/25/15 | 1300 | 145 | 5.828 | 0.877 | 0.123 | 85.97% | 3.604% |  | 23.0789 | 6.2828 | 1.45 | 0.5828
Sunday 10/25/15 | 1500 | 145 | 5.926 | 0.851 | 0.122 | 85.66% | -0.363% |  | 22.3947 | 6.4747 | 1.45 | 0.5926
Sunday 10/25/15 | 1700 | 145 | 6.08 | 0.866 | 0.138 | 84.06% | -1.902% |  | 22.7895 | 6.3626 | 1.45 | 0.608
Sunday10/25/15 | 1900 | 145 | 5.92 | 0.844 | 0.113 | 86.61% | 2.94% |  | 22.2105 | 6.5284 | 1.45 | 0.592
Sunday10/25/15 | 2100 | 145 | 5.86 | 0.876 | 0.11 | 87.44% | 0.951% |  | 23.0526 | 6.29 | 1.45 | 0.586
Sunday10/25/15 | 2300 | 145 | 5.95 | 0.819 | 0.11 | 86.57% | -1.01% |  | 21.5526 | 6.7277 | 1.45 | 0.595
Monday10/26/15 | 100 | 145 | 5.98 | 0.843 | 0.117 | 86.12% | -0.5202% |  | 22.1842 | 6.5362 | 1.45 | 0.598
Monday10/26/15 | 300 | 145 | 5.88 | 0.887 | 0.115 | 87.03% | 1.05% |  | 23.3421 | 6.212 | 1.45 | 0.588
Monday10/26/15 | 500 | 145 | 5.851 | 0.89 | 0.119 | 86.63% | -0.4684% |  | 23.4211 | 6.191 | 1.45 | 0.5851
Monday 10/26/15 | 700 | 145 | 5.91 | 0.874 | 0.147 | 83.18% | -4.146% |  | 23 | 6.3043 | 1.45 | 0.591
Monday 10/26/15 | 900 | 145 | 5.955 | 0.865 | 0.16 | 81.5% | -2.059% |  | 22.7632 | 6.3699 | 1.45 | 0.5955
Monday 10/26/15 | 1100 | 145 | 5.933 | 0.877 | 0.157 | 82.1% | 0.725% |  | 23.0789 | 6.2828 | 1.45 | 0.5933
Monday10/26/15 | 1300 | 145 | 5.6 | 0.878 | 0.17 | 80.64% | -1.811% |  | 23.1053 | 6.2756 | 1.45 | 0.56
Monday 10/26/15 | 1500 | 145 | 5.81 | 0.87 | 0.152 | 82.53% | 2.291% |  | 22.8947 | 6.3333 | 1.45 | 0.581
Monday 10/26/15 | 1700 | 145 | 5.82 | 0.88 | 0.159 | 81.93% | -0.7286% |  | 23.1579 | 6.2614 | 1.45 | 0.582
Monday10/26/15 | 1900 | 150 | 5.78 | 0.878 | 0.11 | 87.47% | 6.333% |  | 23.1053 | 6.492 | 1.5 | 0.578
Monday10/26/15 | 2100 | 150 | 5.72 | 0.876 | 0.109 | 87.56% | 0.09771% |  | 23.0526 | 6.5068 | 1.5 | 0.572
Monday10/26/15 | 2300 | 150 | 5.932 | 0.802 | 0.106 | 86.78% | -0.8919% |  | 21.1053 | 7.1072 | 1.5 | 0.5932
Tuesday10/26/15 | 100 | 150 | 5.996 | 0.807 | 0.109 | 86.49% | -0.3351% |  | 21.2368 | 7.0632 | 1.5 | 0.5996
Tuesday10/26/15 | 300 | 150 | 5.85 | 0.869 | 0.113 | 87% | 0.5786% |  | 22.8684 | 6.5593 | 1.5 | 0.585
Tuesday10/26/15 | 500 | 150 | 5.79 | 0.877 | 0.107 | 87.8% | 0.9143% |  | 23.0789 | 6.4994 | 1.5 | 0.579
Tuesday10/26/15 | 700 | 150 | 5.775 | 0.857 | 0.121 | 85.88% | -2.234% |  | 22.5526 | 6.6511 | 1.5 | 0.5775
Tuesday10/26/15 | 900 | 150 | 5.802 | 0.859 | 0.141 | 83.59% | -2.746% |  | 22.6053 | 6.6356 | 1.5 | 0.5802
Tuesday10/26/15 | 1100 | 150 | 5.811 | 0.855 | 0.146 | 82.92% | -0.7978% |  | 22.5 | 6.6667 | 1.5 | 0.5811
Tuesday10/26/15 | 1300 | 150 | 5.97 | 0.817 | 0.119 | 85.43% | 2.939% |  | 21.5 | 6.9767 | 1.5 | 0.597
Tuesday10/26/15 | 1500 | 150 | 5.86 | 0.821 | 0.141 | 82.83% | -3.15% |  | 21.6053 | 6.9428 | 1.5 | 0.586
Tuesday10/26/15 | 1700 | 150 | 5.92 | 0.821 | 0.127 | 84.53% | 2.017% |  | 21.6053 | 6.9428 | 1.5 | 0.592
Tuesday10/26/15 | 1900 | 150 | 5.88 | 0.849 | 0.115 | 86.45% | 2.225% |  | 22.3421 | 6.7138 | 1.5 | 0.588
Tuesday10/26/15 | 2100 | 150 | 5.91 | 0.859 | 0.113 | 86.85% | 0.4497% |  | 22.6053 | 6.6356 | 1.5 | 0.591
Tuesday10/26/15 | 2300 | 150 | 5.936 | 0.781 | 0.102 | 86.94% | 0.1089% |  | 20.5526 | 7.2983 | 1.5 | 0.5936
Wednesday10/27/15 | 100 | 145 | 5.939 | 0.799 | 0.104 | 86.98% | 0.05048% |  | 21.0263 | 6.8961 | 1.45 | 0.5939
Wednesday10/27/15 | 300 | 140 | 5.96 | 0.75 | 0.104 | 86.13% | -0.9873% |  | 19.7368 | 7.0933 | 1.4 | 0.596
Wednesday10/27/15 | 500 | 130 | 5.72 | 0.747 | 0.096 | 87.15% | 1.165% |  | 19.6579 | 6.6131 | 1.3 | 0.572
Monday11/02/2015 | 1800 | 85 | 6.249 | 0.533 | 0.09 | 83.11% | -4.854% |  | 14.0263 | 6.06 | 0.85 | 0.6249
Monday11/02/2015 | 2000 | 85 | 6.235 | 0.555 | 0.096 | 82.7% | -0.4979% |  | 14.6053 | 5.8198 | 0.85 | 0.6235
Monday11/02/2015 | 2200 | 85 | 6.23 | 0.564 | 0.102 | 81.91% | -0.9617% |  | 14.8421 | 5.727 | 0.85 | 0.623
Tuesday11/03/2015 | 0 | 85 | 6.203 | 0.526 | 0.07 | 86.69% | 5.51% |  | 13.8421 | 6.1407 | 0.85 | 0.6203
Tuesday11/03/2015 | 200 | 85 | 6.03 | 0.491 | 0.074 | 84.93% | -2.076% |  | 12.9211 | 6.5784 | 0.85 | 0.603
Tuesday11/03/2015 | 400 | 85 | 5.968 | 0.494 | 0.076 | 84.62% | -0.3703% |  | 13 | 6.5385 | 0.85 | 0.5968
Tuesday11/03/2015 | 600 | 85 |  |  |  | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0.85 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
[6 empty] | #DIV/0! | #DIV/0! |  | 0 | #DIV/0! | 0 | 0
0
0
0
0

## REMOVAL
PLT1
2019-08-12 09:03 |  | DAILY AVG | RAW | RAW | RAW | RAW | RAW | RAW | RAW | RAW | avg last 12 | RAW | TREATED | TREATED | TREATED | Percent | Calculated Raw | Alum Dose: | Alum Dose | Treated pH | Settled UV | FILTER UV
Date | Time | ALUM DOSE | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | raw uv | MN | PH | ALKALINITY | Treated UV | Removal | TOC, mg/L | TOC Ratio | Divided By 100 | Divided By 10
2018-02-01 | 0:00 | 40.1196
| 1:00 | 40.1196 | [8 empty] | #DIV/0!
| 2:00 | 40.1196 | [8 empty] | #DIV/0!
| 3:00 | 40.1196 | 6.92 | 24 | 19 | 8.29 | 48 | 87 | 11.1 | 0.197 | 0.197 |  | 6.06 | 10 | 0.054 | 72.59% | 5.1842 | 7.7388 | 0.4012 | 0.606 | 0.036 | 0.037
| 4:00 | 40.1196 | [8 empty] | 0.197
| 5:00 | 40.1196 | [8 empty] | 0.197
| 6:00 | 40.1196 | [8 empty] | 0.197
| 7:00 | 40.1196 | 6.99 | 26 | 19 | 12.1 | 39 | 105 | 10.4 | 0.207 | 0.202 |  | 6 | 10 | 0.047 | 77.29% | 5.4474 | 7.3649 | 0.4012 | 0.6 | 0.04 | 0.039
| 8:00 | 40.1196 | [8 empty] | 0.202
| 9:00 | 40.1196 | [8 empty] | 0.202 | 0.054
| 10:00 | 40.1196 | [8 empty] | 0.202
| 11:00 | 40.1196 | 6.99 | 25 | 19 | 10.5 | 41 | 103 | 10.6 | 0.199 | 0.201 |  | 5.98 | 10 | 0.042 | 78.89% | 5.2368 | 7.661 | 0.4012 | 0.598 | 0.039 | 0.037
| 12:00 | 40.1196 | [8 empty] | 0.201
| 13:00 | 40.1196 | [8 empty] | 0.201
| 14:00 | 40.1196 | [8 empty] | 0.201
| 15:00 | 40.1196 | 6.88 | 24 | 18 | 9.07 | 44 | 106 | 11.1 | 0.226 | 0.20725 |  | 5.91 | 10 | 0.048 | 78.76% | 5.9474 | 6.7458 | 0.4012 | 0.591 | 0.044 | 0.041
| 16:00 | 40.1196 | [8 empty] | 0.21067
| 17:00 | 40.1196 | [8 empty] | 0.21067
| 18:00 | 40.1196 | [8 empty] | 0.21067
| 19:00 | 40.1196 | 6.94 | 24 | 18 | 9.13 | 42 | 114 | 11.3 | 0.235 | 0.21675 |  | 5.92 | 10 | 0.045 | 80.85% | 6.1842 | 6.4874 | 0.4012 | 0.592 | 0.036 | 0.036
| 20:00 | 40.1196 | [8 empty] | 0.21675
| 21:00 | 40.1196 | [8 empty] | 0.22 | 0.061
| 22:00 | 40.1196 | [8 empty] | 0.22
| 23:00 | 40.1196 | 6.98 | 24 | 20 | 9.54 | 40 | 148 | 11.2 | 0.19 | 0.2125 |  | 5.96 | 10 | 0.063 | 66.84% | 5 | 8.0239 | 0.4012 | 0.596 | 0.041 | 0.041
2018-02-02 | 0:00 | 40.4065 | [8 empty] | 0.2125
| 1:00 | 40.4065 | [8 empty] | 0.217
| 2:00 | 40.4065 | [8 empty] | 0.217
| 3:00 | 40.4065 | 6.93 | 24 | 20 | 10.3 | 44 | 123 | 11.1 | 0.22 | 0.21775 |  | 6.09 | 10 | 0.066 | 70% | 5.7895 | 6.9793 | 0.40407 | 0.609 | 0.042 | 0.042
| 4:00 | 40.4065 | [8 empty] | 0.21775
| 5:00 | 40.4065 | [8 empty] | 0.215
| 6:00 | 40.4065 | [8 empty] | 0.215
| 7:00 | 40.4065 | 6.87 | 25 | 20 | 32.3 | 33 | 252 | 11.1 | 0.228 | 0.21825 |  | 5.96 | 10 | 0.037 | 83.77% | 6 | 6.7344 | 0.40407 | 0.596 | 0.032 | 0.035
| 8:00 | 40.4065 | [8 empty] | 0.21825
| 9:00 | 40.4065 | [8 empty] | 0.21267 | 0.012
| 10:00 | 40.4065 | [8 empty] | 0.21267
| 11:00 | 40.4065 | 6.87 | 25 | 20 | 33.2 | 36 | 253 | 10.9 | 0.194 | 0.208 |  | 6.02 | 11 | 0.041 | 78.87% | 5.1053 | 7.9147 | 0.40407 | 0.602 | 0.031 | 0.032
| 12:00 | 40.4065 | [8 empty] | 0.208
| 13:00 | 40.4065 | [8 empty] | 0.214
| 14:00 | 40.4065 | [8 empty] | 0.214
| 15:00 | 40.4065 | 6.9 | 25 | 19 | 27 | 40 | 219 | 11.1 | 0.207 | 0.21225 |  | 5.75 | 9 | 0.036 | 82.61% | 5.4474 | 7.4176 | 0.40407 | 0.575 | 0.033 | 0.035
| 16:00 | 40.4065 | [8 empty] | 0.21225
| 17:00 | 40.4065 | [8 empty] | 0.20967
| 18:00 | 40.4065 | [8 empty] | 0.20967
| 19:00 | 40.4065 | 6.93 | 23 | 19 | 34 | 47 | 276 | 11.1 | 0.225 | 0.2135 |  | 6.02 | 9 | 0.025 | 88.89% | 5.9211 | 6.8242 | 0.40407 | 0.602 | 0.026 | 0.017
| 20:00 | 40.4065 | [8 empty] | 0.2135
| 21:00 | 40.4065 | [8 empty] | 0.20867 | 0.154
| 22:00 | 40.4065 | [8 empty] | 0.20867
| 23:00 | 40.4065 | 6.82 | 23 | 19 | 42.3 | 45 | 322 | 10.6 | 0.227 | 0.21325 |  | 6.03 | 8 | 0.058 | 74.45% | 5.9737 | 6.7641 | 0.40407 | 0.603 | 0.05 | 0.051
2018-02-03 | 24:00 | 40.6179 | [8 empty] | 0.21325
| 25:00 | 40.6179 | [8 empty] | 0.21967
| 26:00 | 40.6179 | [8 empty] | 0.21967
| 27:00 | 40.6179 | 6.85 | 23 | 19 | 34.4 | 50 | 270 | 10.7 | 0.249 | 0.227 |  | 6 | 8 | 0.047 | 81.12% | 6.5526 | 6.1987 | 0.40618 | 0.6 | 0.036 | 0.036
| 28:00 | 40.6179 | [8 empty] | 0.227
| 29:00 | 40.6179 | [8 empty] | 0.23367
| 30:00 | 40.6179 | [8 empty] | 0.23367
| 31:00 | 40.6179 | 6.92 | 23 | 22 | 38.7 | 46 | 274 | 10.2 | 0.236 | 0.23425 |  | 5.75 | 10 | 0.047 | 80.08% | 6.2105 | 6.5402 | 0.40618 | 0.575 | 0.038 | 0.033
| 32:00 | 40.6179 | [8 empty] | 0.23425
| 33:00 | 40.6179 | [8 empty] | 0.23733 | 0.179
| 34:00 | 40.6179 | [8 empty] | 0.23733
| 35:00 | 40.6179 | 6.46 | 24 | 22 | 41.5 | 41 | 304 | 10.2 | 0.208 | 0.23 |  | 5.78 | 10 | 0.038 | 81.73% | 5.4737 | 7.4206 | 0.40618 | 0.578 | 0.036 | 0.033
| 36:00 | 40.6179 | [8 empty] | 0.23
| 37:00 | 40.6179 | [8 empty] | 0.231
| 38:00 | 40.6179 | [8 empty] | 0.231
| 39:00 | 40.6179 | 6.9 | 23 | 21 | 29.1 | 40 | 230 | 10.3 | 0.241 | 0.2335 |  | 5.76 | 9 | 0.046 | 80.91% | 6.3421 | 6.4045 | 0.40618 | 0.576 | 0.038 | 0.035
| 40:00 | 40.6179 | [8 empty] | 0.2335
| 41:00 | 40.6179 | [8 empty] | 0.22833
| 42:00 | 40.6179 | [8 empty] | 0.22833
| 43:00 | 40.6179 | 6.89 | 23 | 21 | 28.7 | 50 | 228 | 10.2 | 0.257 | 0.2355 |  | 6.3 | 9 | 0.061 | 76.26% | 6.7632 | 6.0058 | 0.40618 | 0.63 | 0.037 | 0.039
| 44:00 | 40.6179 | [8 empty] | 0.2355
| 45:00 | 40.6179 | [8 empty] | 0.23533 | 0.131
| 46:00 | 40.6179 | [8 empty] | 0.23533
| 47:00 | 40.6179 | 6.94 | 23 | 22 | 34.4 | 41 | 258 | 10.3 | 0.219 | 0.23125 |  | 6.22 | 9 | 0.069 | 68.49% | 5.7632 | 7.0479 | 0.40618 | 0.622 | 0.047 | 0.049
2018-02-04 | 48:00 | 43.5291 | [8 empty] | 0.23125
| 49:00 | 43.5291 | [8 empty] | 0.239
| 50:00 | 43.5291 | [8 empty] | 0.239
| 51:00 | 43.5291 | 6.87 | 24 | 21 | 29.6 | 40 | 240 | 10 | 0.249 | 0.2415 |  | 6.06 | 10 | 0.069 | 72.29% | 6.5526 | 6.643 | 0.43529 | 0.606 | 0.045 | 0.046
| 52:00 | 43.5291 | [8 empty] | 0.2415
| 53:00 | 43.5291 | [8 empty] | 0.24167
| 54:00 | 43.5291 | [8 empty] | 0.24167
| 55:00 | 43.5291 | 6.64 | 22 | 22 | 28 | 45 | 225 | 9.7 | 0.288 | 0.25325 |  | 5.68 | 10 | 0.051 | 82.29% | 7.5789 | 5.7434 | 0.43529 | 0.568 | 0.037 | 0.036
| 56:00 | 43.5291 | [8 empty] | 0.25325
| 57:00 | 43.5291 | [8 empty] | 0.252 | 0.123
| 58:00 | 43.5291 | [8 empty] | 0.252
| 59:00 | 43.5291 | 6.84 | 22 | 22 | 30.1 | 46 | 247 | 9.8 | 0.262 | 0.2545 |  | 5.75 | 10 | 0.055 | 79.01% | 6.8947 | 6.3134 | 0.43529 | 0.575 | 0.031 | 0.035
| 60:00 | 43.5291 | [8 empty] | 0.2545
| 61:00 | 43.5291 | [8 empty] | 0.26633
| 62:00 | 43.5291 | [8 empty] | 0.26633
| 63:00 | 43.5291 | 6.78 | 21 | 22 | 25 | 55 | 215 | 9.8 | 0.284 | 0.27075 |  | 5.7 | 9 | 0.06 | 78.87% | 7.4737 | 5.8243 | 0.43529 | 0.57 | 0.034 | 0.042
| 64:00 | 43.5291 | [8 empty] | 0.27075
| 65:00 | 43.5291 | [8 empty] | 0.278
| 66:00 | 43.5291 | [8 empty] | 0.278
| 67:00 | 43.5291 | 6.86 | 22 | 22 | 22.5 | 58 | 198 | 10 | 0.32 | 0.2885 |  | 5.7 | 9 | 0.079 | 75.31% | 8.4211 | 5.1691 | 0.43529 | 0.57 | 0.06 | 0.065
| 68:00 | 43.5291 | [8 empty] | 0.2885
| 69:00 | 43.5291 | [8 empty] | 0.28867 | 0.101
| 70:00 | 43.5291 | [8 empty] | 0.28867
| 71:00 | 43.5291 | 6.86 | 22 | 22 | 24.3 | 57 | 223 | 10.3 | 0.299 | 0.29125 |  | 6.05 | 9 | 0.063 | 78.93% | 7.8684 | 5.5321 | 0.43529 | 0.605 | 0.056 | 0.053
2018-02-05 | 72:00 | 53.8947 | [8 empty] | 0.29125
| 73:00 | 53.8947 | [8 empty] | 0.301
| 74:00 | 53.8947 | [8 empty] | 0.301
| 75:00 | 53.8947 | 6.9 | 22 | 21 | 25.9 | 63 | 218 | 10.5 | 0.321 | 0.306 |  | 5.9 | 9 | 0.058 | 81.93% | 8.4474 | 6.3801 | 0.53895 | 0.59 | 0.046 | 0.046
| 76:00 | 53.8947 | [8 empty] | 0.306
| 77:00 | 53.8947 | [8 empty] | 0.31333
| 78:00 | 53.8947 | [8 empty] | 0.31333
| 79:00 | 53.8947 | 6.82 | 23 | 21 | 24.2 | 64 | 214 | 10.4 | 0.333 | 0.31825 |  | 5.71 | 8 | 0.061 | 81.68% | 8.7632 | 6.1502 | 0.53895 | 0.571 | 0.054 | 0.05
| 80:00 | 53.8947 | [8 empty] | 0.31825
| 81:00 | 53.8947 | [8 empty] | 0.31767 | 0.98
| 82:00 | 53.8947 | [8 empty] | 0.31767
| 83:00 | 53.8947 | 6.71 | 22 | 22 | 23 | 63 | 209 | 10.4 | 0.345 | 0.3245 |  | 5.76 | 8 | 0.068 | 80.29% | 9.0789 | 5.9362 | 0.53895 | 0.576 | 0.056 | 0.054
| 84:00 | 53.8947 | [8 empty] | 0.3245
| 85:00 | 53.8947 | [8 empty] | 0.333
| 86:00 | 53.8947 | [8 empty] | 0.333
| 87:00 | 53.8947 | 6.72 | 23 | 21 | 19.7 | 61 | 200 | 10.7 | 0.351 | 0.3375 |  | 5.91 | 10 | 0.071 | 79.77% | 9.2368 | 5.8348 | 0.53895 | 0.591 | 0.054 | 0.056
| 88:00 | 53.8947 | [8 empty] | 0.3375
| 89:00 | 53.8947 | [8 empty] | 0.343
| 90:00 | 53.8947 | [8 empty] | 0.343
| 91:00 | 53.8947 | 6.81 | 23 | 21 | 18 | 65 | 179 | 11.4 | 0.347 | 0.344 |  | 5.8 | 9 | 0.056 | 83.86% | 9.1316 | 5.902 | 0.53895 | 0.58 | 0.051 | 0.043
| 92:00 | 53.8947 | [8 empty] | 0.344
| 93:00 | 53.8947 | [8 empty] | 0.34767 | 0.071
| 94:00 | 53.8947 | [8 empty] | 0.34767
| 95:00 | 53.8947 | 6.76 | 23 | 21 | 22 | 63 | 200 | 11.3 | 0.313 | 0.339 |  | 5.95 | 9 | 0.059 | 81.15% | 8.2368 | 6.5431 | 0.53895 | 0.595 | 0.052 | 0.052
2018-02-06 | 96:00 | 53.8947 | [8 empty] | 0.339
| 97:00 | 53.8947 | [8 empty] | 0.337
| 98:00 | 53.8947 | [8 empty] | 0.337
| 99:00 | 53.8947 | 6.89 | 23 | 22 | 20.1 | 69 | 193 | 10.5 | 0.354 | 0.34125 |  | 5.94 | 9 | 0.079 | 77.68% | 9.3158 | 5.7853 | 0.53895 | 0.594 | 0.051 | 0.051
| 100:00 | 53.8947 | [8 empty] | 0.34125
| 101:00 | 53.8947 | [8 empty] | 0.338
| 102:00 | 53.8947 | [8 empty] | 0.338
| 103:00 | 53.8947 | 6.69 | 21 | 20 | 18.2 | 61 | 178 | 10.7 | 0.362 | 0.344 |  | 5.65 | 8 | 0.052 | 85.64% | 9.5263 | 5.6575 | 0.53895 | 0.565 | 0.048 | 0.047
| 104:00 | 53.8947 | [8 empty] | 0.344
| 105:00 | 53.8947 | [8 empty] | 0.343 | 0.088
| 106:00 | 53.8947 | [8 empty] | 0.343
| 107:00 | 53.8947 | 6.85 | 21 | 20 | 21 | 58 | 205 | 11 | 0.344 | 0.34325 |  | 5.74 | 9 | 0.059 | 82.85% | 9.0526 | 5.9535 | 0.53895 | 0.574 | 0.052 | 0.054
| 108:00 | 53.8947 | [8 empty] | 0.34325
| 109:00 | 53.8947 | [8 empty] | 0.35333
| 110:00 | 53.8947 | [8 empty] | 0.35333
| 111:00 | 53.8947 | 6.75 | 20 | 20 | 20.1 | 66 | 188 | 11 | 0.363 | 0.35575 |  | 6.02 | 9 | 0.074 | 79.61% | 9.5526 | 5.6419 | 0.53895 | 0.602 | 0.055 | 0.057
| 112:00 | 53.8947 | [8 empty] | 0.35575
| 113:00 | 53.8947 | [8 empty] | 0.35633
| 114:00 | 53.8947 | [8 empty] | 0.35633
| 115:00 | 53.8947 | 6.81 | 20 | 20 | 17.3 | 72 | 174 | 11.4 | 0.365 | 0.3585 |  | 6.1 | 9 | 0.061 | 83.29% | 9.6053 | 5.611 | 0.53895 | 0.61 | 0.065 | 0.068
| 116:00 | 53.8947 | [8 empty] | 0.3585
| 117:00 | 53.8947 | [8 empty] | 0.35733 | 0.066
| 118:00 | 53.8947 | [8 empty] | 0.35733
| 119:00 | 53.8947 | 6.8 | 21 | 21 | 21.8 | 66 | 200 | 11.2 | 0.35 | 0.3555 |  | 6.06 | 9 | 0.07 | 80% | 9.2105 | 5.8514 | 0.53895 | 0.606 | 0.06 | 0.059
2018-02-07 | 120:00 | 66.8964 | [8 empty] | 0.3555
| 121:00 | 66.8964 | [8 empty] | 0.35933
| 122:00 | 66.8964 | [8 empty] | 0.35933
| 123:00 | 66.8964 | 6.8 | 21 | 20 | 23.2 | 69 | 210 | 11 | 0.347 | 0.35625 |  | 6.2 | 10 | 0.081 | 76.66% | 9.1316 | 7.3258 | 0.66896 | 0.62 | 0.068 | 0.067
| 124:00 | 66.8964 | [8 empty] | 0.35625
| 125:00 | 66.8964 | [8 empty] | 0.354
| 126:00 | 66.8964 | [8 empty] | 0.354
| 127:00 | 66.8964 | 6.73 | 22 | 20 | 20.1 | 62 | 186 | 11.8 | 0.333 | 0.34875 |  | 5.99 | 10 | 0.068 | 79.58% | 8.7632 | 7.6338 | 0.66896 | 0.599 | 0.05 | 0.051
| 128:00 | 66.8964 | [8 empty] | 0.34875
| 129:00 | 66.8964 | [8 empty] | 0.34333 | 0.077
| 130:00 | 66.8964 | [8 empty] | 0.34333
| 131:00 | 66.8964 | 6.75 | 23 | 19 | 23.5 | 63 | 208 | 11.6 | 0.33 | 0.34 |  | 5.97 | 10 | 0.07 | 78.79% | 8.6842 | 7.7032 | 0.66896 | 0.597 | 0.05 | 0.051
| 132:00 | 66.8964 | [8 empty] | 0.34
| 133:00 | 66.8964 | [8 empty] | 0.33667
| 134:00 | 66.8964 | [8 empty] | 0.33667
| 135:00 | 66.8964 | 6.78 | 24 | 20 | 26.4 | 62 | 228 | 12.4 | 0.335 | 0.33625 |  | 5.98 | 12 | 0.07 | 79.1% | 8.8158 | 7.5882 | 0.66896 | 0.598 | 0.054 | 0.053
| 136:00 | 66.8964 | [8 empty] | 0.33625
| 137:00 | 66.8964 | [8 empty] | 0.33267
| 138:00 | 66.8964 | [8 empty] | 0.33267
| 139:00 | 66.8964 | 6.73 | 20 | 19 | 24.5 | 72 | 218 | 12.3 | 0.351 | 0.33725 |  | 5.7 | 9 | 0.06 | 82.91% | 9.2368 | 7.2423 | 0.66896 | 0.57 | 0.051 | 0.056
| 140:00 | 66.8964 | [8 empty] | 0.33725
| 141:00 | 66.8964 | [8 empty] | 0.33867 | 0.084
| 142:00 | 66.8964 | [8 empty] | 0.33867
| 143:00 | 66.8964 | 6.71 | 24 | 20 | 28.2 | 67 | 243 | 12.2 | 0.347 | 0.34075 |  | 5.96 | 10 | 0.062 | 82.13% | 9.1316 | 7.3258 | 0.66896 | 0.596 | 0.051 | 0.055
2018-02-08 | 144:00 | 61.7008 | [8 empty] | 0.34075
| 145:00 | 61.7008 | [8 empty] | 0.34433
| 146:00 | 61.7008 | [8 empty] | 0.34433
| 147:00 | 61.7008 | 6.66 | 19 | 15 | 29.6 | 70 | 246 | 13.4 | 0.347 | 0.345 |  | 6 | 8 | 0.064 | 81.56% | 9.1316 | 6.7569 | 0.61701 | 0.6 | 0.055 | 0.057
| 148:00 | 61.7008 | [8 empty] | 0.345
| 149:00 | 61.7008 | [8 empty] | 0.34833
| 150:00 | 61.7008 | [8 empty] | 0.34833
| 151:00 | 61.7008 | 6.72 | 18 | 20 | 26 | 69 | 223 | 12.6 | 0.317 | 0.3405 |  | 6.02 | 11 | 0.051 | 83.91% | 8.3421 | 7.3963 | 0.61701 | 0.602 | 0.041 | 0.051
| 152:00 | 61.7008 | [8 empty] | 0.3405
| 153:00 | 61.7008 | [8 empty] | 0.337 | 0.099
| 154:00 | 61.7008 | [8 empty] | 0.337
| 155:00 | 61.7008 | 6.89 | 20 | 19 | 28.3 | 61 | 239 | 12.6 | 0.308 | 0.32975 |  | 6.09 | 10 | 0.068 | 77.92% | 8.1053 | 7.6124 | 0.61701 | 0.609 | 0.049 | 0.049
| 156:00 | 61.7008 | [8 empty] | 0.32975
| 157:00 | 61.7008 | [8 empty] | 0.324
| 158:00 | 61.7008 | [8 empty] | 0.324
| 159:00 | 61.7008 | 6.85 | 22 | 20 | 32.3 | 56 | 263 | 13 | 0.287 | 0.31475 |  | 6.03 | 11 | 0.067 | 76.66% | 7.5526 | 8.1694 | 0.61701 | 0.603 | 0.053 | 0.046
| 160:00 | 61.7008 | [8 empty] | 0.31475
| 161:00 | 61.7008 | [8 empty] | 0.304
| 162:00 | 61.7008 | [8 empty] | 0.304
| 163:00 | 61.7008 | 6.68 | 18 | 22 | 30 | 68 | 250 | 12.5 | 0.311 | 0.30575 |  | 5.88 | 7.058 | 0.058 | 81.35% | 8.1842 | 7.539 | 0.61701 | 0.588 | 0.05 | 0.052
| 164:00 | 61.7008 | [8 empty] | 0.30575
| 165:00 | 61.7008 | [8 empty] | 0.302 | 0.114
| 166:00 | 61.7008 | [8 empty] | 0.302
| 167:00 | 61.7008 | 6.8 | 20 | 20 | 33.6 | 71 | 251 | 12.5 | 0.305 | 0.30275 |  | 6 | 8 | 0.056 | 81.64% | 8.0263 | 7.6873 | 0.61701 | 0.6 | 0.05 | 0.05
2018-02-09 | 168:00 | 56.3216 | [8 empty] | 0.30275
| 169:00 | 56.3216 | [8 empty] | 0.301
| 170:00 | 56.3216 | [8 empty] | 0.301
| 171:00 | 56.3216 | 6.77 | 19 | 16 | 40.8 | 64 | 316 | 12.5 | 0.298 | 0.30025 |  | 6.07 | 8 | 0.061 | 79.53% | 7.8421 | 7.182 | 0.56322 | 0.607 | 0.051 | 0.049
| 172:00 | 56.3216 | [8 empty] | 0.30025
| 173:00 | 56.3216 | [8 empty] | 0.30467
| 174:00 | 56.3216 | [8 empty] | 0.30467
| 175:00 | 56.3216 | 6.72 | 21 | 18 | 38.6 | 53 | 305 | 13.5 | 0.289 | 0.30075 |  | 5.96 | 10 | 0.054 | 81.31% | 7.6053 | 7.4056 | 0.56322 | 0.596 | 0.045 | 0.044
| 176:00 | 56.3216 | [8 empty] | 0.30075
| 177:00 | 56.3216 | [8 empty] | 0.29733 | 0.133
| 178:00 | 56.3216 | [8 empty] | 0.29733
| 179:00 | 56.3216 | 6.73 | 20 | 17 | 38.2 | 60 | 296 | 12.5 | 0.302 | 0.2985 |  | 5.94 | 10 | 0.062 | 79.47% | 7.9474 | 7.0868 | 0.56322 | 0.594 | 0.044 | 0.041
| 180:00 | 56.3216 | [8 empty] | 0.2985
| 181:00 | 56.3216 | [8 empty] | 0.29633
| 182:00 | 56.3216 | [8 empty] | 0.29633
| 183:00 | 56.3216 | 6.86 | 22 | 17 | 40.7 | 46 | 275 | 12.8 | 0.243 | 0.283 |  | 5.92 | 10 | 0.051 | 79.01% | 6.3947 | 8.8075 | 0.56322 | 0.592 | 0.043 | 0.041
| 184:00 | 56.3216 | [8 empty] | 0.283
| 185:00 | 56.3216 | [8 empty] | 0.278
| 186:00 | 56.3216 | [8 empty] | 0.278
| 187:00 | 56.3216 | 6.84 | 20 | 18 | 36.8 | 57 | 276 | 12 | 0.27 | 0.276 |  | 5.96 | 10 | 0.049 | 81.85% | 7.1053 | 7.9267 | 0.56322 | 0.596 | 0.043 | 0.043
| 188:00 | 56.3216 | [8 empty] | 0.276
| 189:00 | 56.3216 | [8 empty] | 0.27167 | 0.111
| 190:00 | 56.3216 | [8 empty] | 0.27167
| 191:00 | 56.3216 | 6.78 | 22 | 20 | 29.3 | 52 | 224 | 11.8 | 0.267 | 0.2705 |  | 5.93 | 10 | 0.051 | 80.9% | 7.0263 | 8.0158 | 0.56322 | 0.593 | 0.044 | 0.043
2018-02-10 | 192:00 | 49.211 | [8 empty] | 0.2705
| 193:00 | 49.211 | [8 empty] | 0.26
| 194:00 | 49.211 | [8 empty] | 0.26
| 195:00 | 49.211 | 6.79 | 20 | 15 | 29.4 | 48 | 238 | 12.5 | 0.252 | 0.258 |  | 6.05 | 8 | 0.05 | 80.16% | 6.6316 | 7.4207 | 0.49211 | 0.605 | 0.043 | 0.043
| 196:00 | 49.211 | [8 empty] | 0.258
| 197:00 | 49.211 | [8 empty] | 0.263
| 198:00 | 49.211 | [8 empty] | 0.263
| 199:00 | 49.211 | 6.78 | 22 | 17 | 26.5 | 45 | 219 | 12.5 | 0.252 | 0.26025 |  | 5.97 | 10 | 0.051 | 79.76% | 6.6316 | 7.4207 | 0.49211 | 0.597 | 0.041 | 0.039
| 200:00 | 49.211 | [8 empty] | 0.26025
| 201:00 | 49.211 | [8 empty] | 0.257 | 0.109
| 202:00 | 49.211 | [8 empty] | 0.257
| 203:00 | 49.211 | 6.73 | 21 | 16 | 27 | 58 | 256 | 12.6 | 0.277 | 0.262 |  | 5.88 | 11 | 0.052 | 81.23% | 7.2895 | 6.751 | 0.49211 | 0.588 | 0.034 | 0.033
| 204:00 | 49.211 | [8 empty] | 0.262
| 205:00 | 49.211 | [8 empty] | 0.26033
| 206:00 | 49.211 | [8 empty] | 0.26033
| 207:00 | 49.211 | 6.76 | 22 | 16 | 31.6 | 48 | 238 | 12.6 | 0.246 | 0.25675 |  | 5.98 | 11 | 0.047 | 80.89% | 6.4737 | 7.6017 | 0.49211 | 0.598 | 0.034 | 0.034
| 208:00 | 49.211 | [8 empty] | 0.25675
| 209:00 | 49.211 | [8 empty] | 0.25833
| 210:00 | 49.211 | [8 empty] | 0.25833
| 211:00 | 49.211 | 6.75 | 20 | 21 | 35 | 52 | 270 | 12.5 | 0.289 | 0.266 |  | 5.77 | 8 | 0.051 | 82.35% | 7.6053 | 6.4707 | 0.49211 | 0.577 | 0.042 | 0.051
| 212:00 | 49.211 | [8 empty] | 0.266
| 213:00 | 49.211 | [8 empty] | 0.27067 | 0.117
| 214:00 | 49.211 | [8 empty] | 0.27067
| 215:00 | 49.211 | 6.68 | 20 | 20 | 33.7 | 62 | 277 | 12.6 | 0.32 | 0.283 |  | 5.9 | 8 | 0.058 | 81.88% | 8.4211 | 5.8438 | 0.49211 | 0.59 | 0.04 | 0.05
2018-02-11 | 216:00 | 55.1251 | [8 empty] | 0.283
| 217:00 | 55.1251 | [8 empty] | 0.285
| 218:00 | 55.1251 | [8 empty] | 0.285
| 219:00 | 55.1251 | 6.84 | 18 | 16 | 39 | 67 | 314 | 12.7 | 0.324 | 0.29475 |  | 6.06 | 7 | 0.058 | 82.1% | 8.5263 | 6.4653 | 0.55125 | 0.606 | 0.052 | 0.046
| 220:00 | 55.1251 | [8 empty] | 0.29475
| 221:00 | 55.1251 | [8 empty] | 0.311
| 222:00 | 55.1251 | [8 empty] | 0.311
| 223:00 | 55.1251 | 6.7 | 20 | 16 | 38.9 | 58 | 308 | 13 | 0.308 | 0.31025 |  | 5.99 | 8 | 0.066 | 78.57% | 8.1053 | 6.8012 | 0.55125 | 0.599 | 0.05 | 0.048
| 224:00 | 55.1251 | [8 empty] | 0.31025
| 225:00 | 55.1251 | [8 empty] | 0.31733 | 0.143
| 226:00 | 55.1251 | [8 empty] | 0.31733
| 227:00 | 55.1251 | 6.62 | 19 | 17 | 40.9 | 63 | 319 | 13.1 | 0.31 | 0.3155 |  | 5.92 | 8 | 0.061 | 80.32% | 8.1579 | 6.7573 | 0.55125 | 0.592 | 0.047 | 0.044
| 228:00 | 55.1251 | [8 empty] | 0.3155
| 229:00 | 55.1251 | [8 empty] | 0.314
| 230:00 | 55.1251 | [8 empty] | 0.314
| 231:00 | 55.1251 | 6.64 | 20 | 18 | 36.6 | 58 | 340 | 13.4 | 0.292 | 0.3085 |  | 5.96 | 10 | 0.058 | 80.14% | 7.6842 | 7.1738 | 0.55125 | 0.596 | 0.046 | 0.045
| 232:00 | 55.1251 | [8 empty] | 0.3085
| 233:00 | 55.1251 | [8 empty] | 0.30333
| 234:00 | 55.1251 | [8 empty] | 0.30333
| 235:00 | 55.1251 | 6.63 | 20 | 19 | 44.9 | 64 | 291 | 13.5 | 0.32 | 0.3075 |  | 5.99 | 8 | 0.062 | 80.62% | 8.4211 | 6.5461 | 0.55125 | 0.599 | 0.044 | 0.048
| 236:00 | 55.1251 | [8 empty] | 0.3075
| 237:00 | 55.1251 | [8 empty] | 0.30733 | 0.161
| 238:00 | 55.1251 | [8 empty] | 0.30733
| 239:00 | 55.1251 | 6.67 | 20 | 17 | 42 | 60 | 323 | 13.4 | 0.311 | 0.30825 |  | 5.86 | 9 | 0.066 | 78.78% | 8.1842 | 6.7355 | 0.55125 | 0.586 | 0.047 | 0.05
2018-02-12 | 240:00 | 53.4174 | [8 empty] | 0.30825
| 241:00 | 53.4174 | [8 empty] | 0.30767
| 242:00 | 53.4174 | [8 empty] | 0.30767
| 243:00 | 53.4174 | 6.78 | 16 | 15 | 44.2 | 66 | 342 | 14.1 | 0.311 | 0.3085 |  | 6.02 | 7 | 0.062 | 80.06% | 8.1842 | 6.5269 | 0.53417 | 0.602 | 0.054 | 0.051
| 244:00 | 53.4174 | [8 empty] | 0.3085
| 245:00 | 53.4174 | [8 empty] | 0.314
| 246:00 | 53.4174 | [8 empty] | 0.314
| 247:00 | 53.4174 | 6.68 | 18 | 16 | 44 | 52 | 332 | 14 | 0.27 | 0.303 |  | 5.96 | 9 | 0.057 | 78.89% | 7.1053 | 7.518 | 0.53417 | 0.596 | 0.048 | 0.045
| 248:00 | 53.4174 | [8 empty] | 0.303
| 249:00 | 53.4174 | [8 empty] | 0.29733 | 0.176
| 250:00 | 53.4174 | [8 empty] | 0.29733
| 251:00 | 53.4174 | 6.7 | 19 | 16 | 39 | 61 | 295 | 13.8 | 0.267 | 0.28975 |  | 6.06 | 9 | 0.072 | 73.03% | 7.0263 | 7.6025 | 0.53417 | 0.606 | 0.041 | 0.044
| 252:00 | 53.4174 | [8 empty] | 0.28975
| 253:00 | 53.4174 | [8 empty] | 0.28267
| 254:00 | 53.4174 | [8 empty] | 0.28267
| 255:00 | 53.4174 | 6.72 | 20 | 16 | 39.4 | 54 | 298 | 14 | 0.251 | 0.27475 |  | 6 | 10 | 0.047 | 81.27% | 6.6053 | 8.0871 | 0.53417 | 0.6 | 0.04 | 0.035
| 256:00 | 53.4174 | [8 empty] | 0.27475
| 257:00 | 53.4174 | [8 empty] | 0.26267
| 258:00 | 53.4174 | [8 empty] | 0.26267
| 259:00 | 53.4174 | 6.76 | 23 | 18 | 37.6 | 55 | 285 | 13.8 | 0.259 | 0.26175 |  | 5.99 | 9 | 0.046 | 82.24% | 6.8158 | 7.8373 | 0.53417 | 0.599 | 0.04 | 0.045
| 260:00 | 53.4174 | [8 empty] | 0.26175
| 261:00 | 53.4174 | [8 empty] | 0.259 | 0.168
| 262:00 | 53.4174 | [8 empty] | 0.259
| 263:00 | 53.4174 | 6.71 | 22 | 18 | 32.6 | 52 | 253 | 13.8 | 0.283 | 0.265 |  | 5.92 | 9 | 0.05 | 82.33% | 7.4474 | 7.1726 | 0.53417 | 0.592 | 0.04 | 0.044
2018-02-13 | 264:00 | 60.1344 | [8 empty] | 0.265
| 265:00 | 60.1344 | [8 empty] | 0.26433
| 266:00 | 60.1344 | [8 empty] | 0.26433
| 267:00 | 60.1344 | 6.78 | 19 | 15 | 33 | 58 | 249 | 14.1 | 0.266 | 0.26475 |  | 5.98 | 6 | 0.053 | 80.08% | 7 | 8.5906 | 0.60134 | 0.598 | 0.043 | 0.044
| 268:00 | 60.1344 | [8 empty] | 0.26475
| 269:00 | 60.1344 | [8 empty] | 0.26933
| 270:00 | 60.1344 | [8 empty] | 0.26933
| 271:00 | 60.1344 | 6.78 | 20 | 14 | 32.1 | 52 | 254 | 14.4 | 0.256 | 0.266 |  | 5.94 | 8 | 0.051 | 80.08% | 6.7368 | 8.9262 | 0.60134 | 0.594 | 0.041 | 0.04
| 272:00 | 60.1344 | [8 empty] | 0.266
| 273:00 | 60.1344 | [8 empty] | 0.26833 | 0.125
| 274:00 | 60.1344 | [8 empty] | 0.26833
| 275:00 | 60.1344 | 6.69 | 19 | 14 | 29.3 | 48 | 230 | 14.2 | 0.259 | 0.266 |  | 5.93 | 8 | 0.047 | 81.85% | 6.8158 | 8.8228 | 0.60134 | 0.593 | 0.037 | 0.038
| 276:00 | 60.1344 | [8 empty] | 0.266
| 277:00 | 60.1344 | [8 empty] | 0.26033
| 278:00 | 60.1344 | [8 empty] | 0.26033
| 279:00 | 60.1344 | 6.73 | 20 | 14 | 28.2 | 42 | 238 | 14.4 | 0.246 | 0.25675 |  | 5.97 | 8 | 0.051 | 79.27% | 6.4737 | 9.2891 | 0.60134 | 0.597 | 0.041 | 0.04
| 280:00 | 60.1344 | [8 empty] | 0.25675
| 281:00 | 60.1344 | [8 empty] | 0.25367
| 282:00 | 60.1344 | [8 empty] | 0.25367
| 283:00 | 60.1344 | 6.73 | 20 | 16 | 31.3 | 49 | 249 | 13.4 | 0.256 | 0.25425 |  | 5.91 | 6 | 0.047 | 81.64% | 6.7368 | 8.9262 | 0.60134 | 0.591 | 0.038 | 0.044
| 284:00 | 60.1344 | [8 empty] | 0.25425
| 285:00 | 60.1344 | [8 empty] | 0.25367 | 0.14
| 286:00 | 60.1344 | [8 empty] | 0.25367
| 287:00 | 60.1344 | 6.69 | 19 | 17 | 27.3 | 51 | 225 | 13.4 | 0.279 | 0.26 |  | 5.92 | 8 | 0.05 | 82.08% | 7.3421 | 8.1903 | 0.60134 | 0.592 | 0.04 | 0.045
2018-02-14 | 288:00 | 59.9559 | [8 empty] | 0.26
| 289:00 | 59.9559 | [8 empty] | 0.26033
| 290:00 | 59.9559 | [8 empty] | 0.26033
| 291:00 | 59.9559 | 6.68 | 16 | 18 | 28.1 | 56 | 221 | 13.7 | 0.269 | 0.2625 |  | 5.99 | 7 | 0.049 | 81.78% | 7.0789 | 8.4696 | 0.59956 | 0.599 | 0.042 | 0.038
| 292:00 | 59.9559 | [8 empty] | 0.2625
| 293:00 | 59.9559 | [8 empty] | 0.268
| 294:00 | 59.9559 | [8 empty] | 0.268
| 295:00 | 59.9559 | 6.67 | 22 | 20 | 29.2 | 55 | 227 | 12.9 | 0.282 | 0.2715 |  | 6.01 | 9 | 0.048 | 82.98% | 7.4211 | 8.0792 | 0.59956 | 0.601 | 0.049 | 0.045
| 296:00 | 59.9559 | [8 empty] | 0.2715
| 297:00 | 59.9559 | [8 empty] | 0.27667 | 0.11
| 298:00 | 59.9559 | [8 empty] | 0.27667
| 299:00 | 59.9559 | 6.68 | 22 | 19 | 26.8 | 58 | 220 | 13 | 0.285 | 0.27875 |  | 6 | 9 | 0.051 | 82.11% | 7.5 | 7.9941 | 0.59956 | 0.6 | 0.048 | 0.044
| 300:00 | 59.9559 | [8 empty] | 0.27875
| 301:00 | 59.9559 | [8 empty] | 0.27867
| 302:00 | 59.9559 | [8 empty] | 0.27867
| 303:00 | 59.9559 | 6.68 | 22 | 19 | 27.3 | 56 | 215 | 13.2 | 0.276 | 0.278 |  | 6 | 9 | 0.065 | 76.45% | 7.2632 | 8.2548 | 0.59956 | 0.6 | 0.035 | 0.035
| 304:00 | 59.9559 | [8 empty] | 0.278
| 305:00 | 59.9559 | [8 empty] | 0.281
| 306:00 | 59.9559 | [8 empty] | 0.281
| 307:00 | 59.9559 | 6.25 | 22 | 18 | 26.6 | 48 | 207 | 13.4 | 0.285 | 0.282 |  | 5.77 | 11 | 0.056 | 80.35% | 7.5 | 7.9941 | 0.59956 | 0.577 | ..047 | 0.044
| 308:00 | 59.9559 | [8 empty] | 0.282
| 309:00 | 59.9559 | [8 empty] | 0.282 | 0.119
| 310:00 | 59.9559 | [8 empty] | 0.282
| 311:00 | 59.9559 | 6.7 | 23 | 19 | 25.5 | 54 | 203 | 13.4 | 0.292 | 0.2845 |  | 6.12 | 11 | 0.067 | 77.05% | 7.6842 | 7.8025 | 0.59956 | 0.612 | 0.047 | 0.037
2018-02-15 | 312:00 | 60.6115 | [8 empty] | 0.2845
| 313:00 | 60.6115 | [8 empty] | 0.28433
| 314:00 | 60.6115 | [8 empty] | 0.28433
| 315:00 | 60.6115 | 6.72 | 22 | 18 | 26.5 | 51 | 212 | 13.3 | 0.26 | 0.27825 |  | 6.03 | 10 | 0.054 | 79.23% | 6.8421 | 8.8586 | 0.60612 | 0.603 | 0.042 | 0.035
| 316:00 | 60.6115 | [8 empty] | 0.27825
| 317:00 | 60.6115 | [8 empty] | 0.279
| 318:00 | 60.6115 | [8 empty] | 0.279
| 319:00 | 60.6115 | 6.69 | 22 | 18 | 26.6 | 60 | 222 | 13.4 | 0.296 | 0.28325 |  | 5.89 | 10 | 0.056 | 81.08% | 7.7895 | 7.7812 | 0.60612 | 0.589 | 0.047 | 0.046
| 320:00 | 60.6115 | [8 empty] | 0.28325
| 321:00 | 60.6115 | [8 empty] | 0.28267 | 0.103
| 322:00 | 60.6115 | [8 empty] | 0.28267
| 323:00 | 60.6115 | 6.64 | 22 | 19 | 26.8 | 55 | 220 | 13.7 | 0.288 | 0.284 |  | 6 | 10 | 0.059 | 79.51% | 7.5789 | 7.9974 | 0.60612 | 0.6 | 0.044 | 0.045
| 324:00 | 60.6115 | [8 empty] | 0.284
| 325:00 | 60.6115 | [8 empty] | 0.28133
| 326:00 | 60.6115 | [8 empty] | 0.28133
| 327:00 | 60.6115 | 6.73 | 22 | 20 | 27 | 63 | 218 | 13.9 | 0.286 | 0.2825 |  | 6.02 | 10 | 0.04 | 86.01% | 7.5263 | 8.0533 | 0.60612 | 0.602 | 0.033 | 0.033
| 328:00 | 60.6115 | [8 empty] | 0.2825
| 329:00 | 60.6115 | [8 empty] | 0.29
| 330:00 | 60.6115 | [8 empty] | 0.29
| 331:00 | 60.6115 | 6.72 | 21 | 19 | 28.7 | 57 | 225 | 14.2 | 0.293 | 0.29075 |  | 5.95 | 10 | 0.053 | 81.91% | 7.7105 | 7.8609 | 0.60612 | 0.595 | 0.047 | 0.049
| 332:00 | 60.6115 | [8 empty] | 0.29075
| 333:00 | 60.6115 | [8 empty] | 0.289 | 0.111
| 334:00 | 60.6115 | [8 empty] | 0.289
| 335:00 | 60.6115 | 6.72 | 22 | 20 | 26.8 | 60 | 214 | 14.4 | 0.3 | 0.29175 |  | 5.94 | 11 | 0.054 | 82% | 7.8947 | 7.6775 | 0.60612 | 0.594 | 0.045 | 0.045
2018-02-16 | 336:00 | 60.521 | [8 empty] | 0.29175
| 337:00 | 60.521 | [8 empty] | 0.293
| 338:00 | 60.521 | [8 empty] | 0.293
| 339:00 | 60.521 | 6.72 | 22 | 20 | 25.9 | 58 | 218 | 14.3 | 0.296 | 0.29375 |  | 6.01 | 11 | 0.046 | 84.46% | 7.7895 | 7.7696 | 0.60521 | 0.601 | 0.04 | 0.042
| 340:00 | 60.521 | [8 empty] | 0.29375
| 341:00 | 60.521 | [8 empty] | 0.29633
| 342:00 | 60.521 | [8 empty] | 0.29633
| 343:00 | 60.521 | 6.68 | 22 | 20 | 25.4 | 63 | 222 | 14.3 | 0.288 | 0.29425 |  | 6.12 | 10 | 0.057 | 80.21% | 7.5789 | 7.9854 | 0.60521 | 0.612 | 0.046 | 0.044
| 344:00 | 60.521 | [8 empty] | 0.29425
| 345:00 | 60.521 | [8 empty] | 0.29467 | 0.1
| 346:00 | 60.521 | [8 empty] | 0.29467
| 347:00 | 60.521 | 6.65 | 22 | 20 | 25.7 | 59 | 213 | 14.4 | 0.289 | 0.29325 |  | 5.9 | 9 | 0.071 | 75.43% | 7.6053 | 7.9578 | 0.60521 | 0.59 | 0.051 | 0.048
| 348:00 | 60.521 | [8 empty] | 0.29325
| 349:00 | 60.521 | [8 empty] | 0.291
| 350:00 | 60.521 | [8 empty] | 0.291
| 351:00 | 60.521 | 6.68 | 22 | 20 | 24.3 | 57 | 218 | 14.5 | 0.278 | 0.28775 |  | 6.14 | 9 | 0.052 | 81.29% | 7.3158 | 8.2727 | 0.60521 | 0.614 | 0.037 | 0.041
| 352:00 | 60.521 | [8 empty] | 0.28775
| 353:00 | 60.521 | [8 empty] | 0.285
| 354:00 | 60.521 | [8 empty] | 0.285
| 355:00 | 60.521 | 6.73 | 21 | 20 | 24.6 | 53 | 200 | 14.6 | 0.266 | 0.28025 |  | 5.94 | 10 | 0.045 | 83.08% | 7 | 8.6459 | 0.60521 | 0.594 | 0.034 | 0.037
| 356:00 | 60.521 | [8 empty] | 0.28025
| 357:00 | 60.521 | [8 empty] | 0.27767 | 0.106
| 358:00 | 60.521 | [8 empty] | 0.27767
| 359:00 | 60.521 | 6.7 | 21 | 21 | 23.1 | 49 | 195 | 14.7 | 0.252 | 0.27125 |  | 6 | 10 | 0.049 | 80.56% | 6.6316 | 9.1262 | 0.60521 | 0.6 | 0.042 | 0.045
2018-02-17 | 360:00 | 60.4908 | [8 empty] | 0.27125
| 361:00 | 60.4908 | [8 empty] | 0.26533
| 362:00 | 60.4908 | [8 empty] | 0.26533
| 363:00 | 60.4908 | 6.73 | 22 | 20 | 21.2 | 51 | 183 | 14.6 | 0.25 | 0.2615 |  | 6.11 | 12 | 0.045 | 82% | 6.5789 | 9.1946 | 0.60491 | 0.611 | 0.039 | 0.046
| 364:00 | 60.4908 | [8 empty] | 0.2615
| 365:00 | 60.4908 | [8 empty] | 0.256
| 366:00 | 60.4908 | [8 empty] | 0.256
| 367:00 | 60.4908 | 6.77 | 22 | 20 | 21.1 | 43 | 180 | 14.7 | 0.231 | 0.24975 |  | 6.2 | 10 | 0.034 | 85.28% | 6.0789 | 9.9509 | 0.60491 | 0.62 | 0.03 | 0.039
| 368:00 | 60.4908 | [8 empty] | 0.24975
| 369:00 | 60.4908 | [8 empty] | 0.24433 | 0.084
| 370:00 | 60.4908 | [8 empty] | 0.24433
| 371:00 | 60.4908 | 6.74 | 22 | 20 | 20 | 54 | 170 | 14.8 | 0.278 | 0.25275 |  | 6.21 | 10 | 0.062 | 77.7% | 7.3158 | 8.2685 | 0.60491 | 0.621 | 0.052 | 0.053
| 372:00 | 60.4908 | [8 empty] | 0.25275
| 373:00 | 60.4908 | [8 empty] | 0.253
| 374:00 | 60.4908 | [8 empty] | 0.253
| 375:00 | 60.4908 | 6.72 | 22 | 20 | 21.3 | 56 | 175 | 14.7 | 0.268 | 0.25675 |  | 6.27 | 10 | 0.055 | 79.48% | 7.0526 | 8.5771 | 0.60491 | 0.627 | 0.05 | 0.05
| 376:00 | 60.4908 | [8 empty] | 0.25675
| 377:00 | 60.4908 | [8 empty] | 0.259
| 378:00 | 60.4908 | [8 empty] | 0.259
| 379:00 | 60.4908 | 6.72 | 21 | 19 | 20 | 52 | 170 | 14.5 | 0.241 | 0.2545 |  | 6.08 | 12 | 0.047 | 80.5% | 6.3421 | 9.538 | 0.60491 | 0.608 | 0.045 | 0.05
| 380:00 | 60.4908 | [8 empty] | 0.2545
| 381:00 | 60.4908 | [8 empty] | 0.26233 | 0.082
| 382:00 | 60.4908 | [8 empty] | 0.26233
| 383:00 | 60.4908 | 6.75 | 23 | 20 | 18.9 | 54 | 161 | 14.7 | 0.266 | 0.26325 |  | 6.06 | 11 | 0.05 | 81.2% | 7 | 8.6415 | 0.60491 | 0.606 | 0.044 | 0.046
2018-02-18 | 384:00 | 60.4908 | [8 empty] | 0.26325
| 385:00 | 60.4908 | [8 empty] | 0.25833
| 386:00 | 60.4908 | [8 empty] | 0.25833
| 387:00 | 60.4908 | 6.73 | 22 | 20 | 17.5 | 50 | 158 | 14.7 | 0.241 | 0.254 |  | 6.1 | 11 | 0.045 | 81.33% | 6.3421 | 9.538 | 0.60491 | 0.61 | 0.036 | 0.046
| 388:00 | 60.4908 | [8 empty] | 0.254
| 389:00 | 60.4908 | [8 empty] | 0.24933
| 390:00 | 60.4908 | [8 empty] | 0.24933
| 391:00 | 60.4908 | 6.72 | 22 | 20 | 17.3 | 49 | 150 | 14.7 | 0.274 | 0.2555 |  | 6.09 | 10 | 0.05 | 81.75% | 7.2105 | 8.3892 | 0.60491 | 0.609 | 0.043 | 0.046
| 392:00 | 60.4908 | [8 empty] | 0.2555
| 393:00 | 60.4908 | [8 empty] | 0.26033 | 0.075
| 394:00 | 60.4908 | [8 empty] | 0.26033
| 395:00 | 60.4908 | 6.69 | 21 | 20 | 18.6 | 55 | 160 | 14.9 | 0.289 | 0.2675 |  | 6.01 | 10 | 0.052 | 82.01% | 7.6053 | 7.9538 | 0.60491 | 0.601 | 0.042 | 0.042
| 396:00 | 60.4908 | [8 empty] | 0.2675
| 397:00 | 60.4908 | [8 empty] | 0.268
| 398:00 | 60.4908 | [8 empty] | 0.268
| 399:00 | 60.4908 | 6.67 | 21 | 20 | 18.8 | 54 | 158 | 14.9 | 0.279 | 0.27075 |  | 6.16 | 10 | 0.052 | 81.36% | 7.3421 | 8.2389 | 0.60491 | 0.616 | 0.04 | 0.04
| 400:00 | 60.4908 | [8 empty] | 0.27075
| 401:00 | 60.4908 | [8 empty] | 0.28067
| 402:00 | 60.4908 | [8 empty] | 0.28067
| 403:00 | 60.4908 | 6.62 | 21 | 18 | 16.6 | 55 | 145 | 15 | 0.268 | 0.2775 |  | 6.01 | 11 | 0.052 | 80.6% | 7.0526 | 8.5771 | 0.60491 | 0.601 | 0.041 | 0.043
| 404:00 | 60.4908 | [8 empty] | 0.2775
| 405:00 | 60.4908 | [8 empty] | 0.27867 | 0.071
| 406:00 | 60.4908 | [8 empty] | 0.27867
| 407:00 | 60.4908 | 6.64 | 21 | 19 | 15.9 | 51 | 152 | 15.1 | 0.268 | 0.276 |  | 5.86 | 10 | 0.054 | 79.85% | 7.0526 | 8.5771 | 0.60491 | 0.586 | 0.043 | 0.042
2018-02-19 | 408:00 | 57.6536 | [8 empty] | 0.276
| 409:00 | 57.6536 | [8 empty] | 0.27167
| 410:00 | 57.6536 | [8 empty] | 0.27167
| 411:00 | 57.6536 | 6.68 | 21 | 20 | 15.4 | 48 | 150 | 15.1 | 0.254 | 0.26725 |  | 6.03 | 11 | 0.048 | 81.1% | 6.6842 | 8.6253 | 0.57654 | 0.603 | 0.04 | 0.037
| 412:00 | 57.6536 | [8 empty] | 0.26725
| 413:00 | 57.6536 | [8 empty] | 0.26333
| 414:00 | 57.6536 | [8 empty] | 0.26333
| 415:00 | 57.6536 | 6.65 | 21 | 20 | 15 | 55 | 150 | 15 | 0.275 | 0.26625 |  | 5.95 | 10 | 0.05 | 81.82% | 7.2368 | 7.9667 | 0.57654 | 0.595 | 0.045 | 0.048
| 416:00 | 57.6536 | [8 empty] | 0.26625
| 417:00 | 57.6536 | [8 empty] | 0.26567 | 0.069
| 418:00 | 57.6536 | [8 empty] | 0.26567
| 419:00 | 57.6536 | 6.66 | 21 | 20 | 15.6 | 53 | 149 | 15.3 | 0.284 | 0.27025 |  | 6 | 10 | 0.055 | 80.63% | 7.4737 | 7.7142 | 0.57654 | 0.6 | 0.043 | 0.043
| 420:00 | 57.6536 | [8 empty] | 0.27025
| 421:00 | 57.6536 | [8 empty] | 0.271
| 422:00 | 57.6536 | [8 empty] | 0.271
| 423:00 | 57.6536 | 6.69 | 22 | 20 | 15.9 | 55 | 149 | 15.2 | 0.264 | 0.26925 |  | 6.14 | 10 | 0.048 | 81.82% | 6.9474 | 8.2986 | 0.57654 | 0.614 | 0.042 | 0.042
| 424:00 | 57.6536 | [8 empty] | 0.26925
| 425:00 | 57.6536 | [8 empty] | 0.27433
| 426:00 | 57.6536 | [8 empty] | 0.27433
| 427:00 | 57.6536 | 6.62 | 22 | 20 | 13.8 | 53 | 142 | 15.4 | 0.291 | 0.2785 |  | 6.14 | 11 | 0.051 | 82.47% | 7.6579 | 7.5287 | 0.57654 | 0.614 | 0.044 | 0.045
| 428:00 | 57.6536 | [8 empty] | 0.2785
| 429:00 | 57.6536 | [8 empty] | 0.27967 | 0.064
| 430:00 | 57.6536 | [8 empty] | 0.27967
| 431:00 | 57.6536 | 6.64 | 21 | 20 | 14.2 | 56 | 144 | 15.5 | 0.288 | 0.28175 |  | 6.02 | 11 | 0.051 | 82.29% | 7.5789 | 7.6071 | 0.57654 | 0.602 | 0.048 | 0.049
2018-02-20 | 432:00 | 49.9557 | [8 empty] | 0.28175
| 433:00 | 49.9557 | [8 empty] | 0.281
| 434:00 | 49.9557 | [8 empty] | 0.281
| 435:00 | 49.9557 | 6.68 | 21 | 20 | 14 | 54 | 140 | 15.5 | 0.267 | 0.2775 |  | 5.88 | 10 | 0.046 | 82.77% | 7.0263 | 7.1098 | 0.49956 | 0.588 | 0.045 | 0.044
| 436:00 | 49.9557 | [8 empty] | 0.2775
| 437:00 | 49.9557 | [8 empty] | 0.282
| 438:00 | 49.9557 | [8 empty] | 0.282
| 439:00 | 49.9557 | 6.64 | 21 | 20 | 13.4 | 56 | 137 | 15.4 | 0.286 | 0.283 |  | 6.02 | 10 | 0.046 | 83.92% | 7.5263 | 6.6375 | 0.49956 | 0.602 | 0.041 | 0.042
| 440:00 | 49.9557 | [8 empty] | 0.283
| 441:00 | 49.9557 | [8 empty] | 0.28033 | 0.058
| 442:00 | 49.9557 | [8 empty] | 0.28033
| 443:00 | 49.9557 | 6.58 | 25 | 20 | 13.4 | 55 | 139 | 15.7 | 0.261 | 0.2755 |  | 6.13 | 10 | 0.026 | 90.04% | 6.8684 | 7.2732 | 0.49956 | 0.613 | 0.014 | 0.016
| 444:00 | 49.9557 | [8 empty] | 0.2755
| 445:00 | 49.9557 | [8 empty] | 0.27133
| 446:00 | 49.9557 | [8 empty] | 0.27133
| 447:00 | 49.9557 | 6.71 | 26 | 20 | 12.3 | 57 | 131 | 16 | 0.297 | 0.27775 |  | 6.2 | 10 | 0.058 | 80.47% | 7.8158 | 6.3916 | 0.49956 | 0.62 | 0.045 | 0.042
| 448:00 | 49.9557 | [8 empty] | 0.27775
| 449:00 | 49.9557 | [8 empty] | 0.28133
| 450:00 | 49.9557 | [8 empty] | 0.28133
| 451:00 | 49.9557 | 6.65 | 24 | 19 | 12.2 | 55 | 125 | 16.2 | 0.293 | 0.28425 |  | 5.9 | 9 | 0.048 | 83.62% | 7.7105 | 6.4789 | 0.49956 | 0.59 | 0.048 | 0.048
| 452:00 | 49.9557 | [8 empty] | 0.28425
| 453:00 | 49.9557 | [8 empty] | 0.28367 | 0.052
| 454:00 | 49.9557 | [8 empty] | 0.28367
| 455:00 | 49.9557 | 6.63 | 23 | 19 | 12.3 | 52 | 120 | 16.3 | 0.292 | 0.28575 |  | 5.94 | 11 | 0.051 | 82.53% | 7.6842 | 6.5011 | 0.49956 | 0.594 | 0.042 | 0.043
2018-02-21 | 456:00 | 53.6463 | [8 empty] | 0.28575
| 457:00 | 53.6463 | [8 empty] | 0.294
| 458:00 | 53.6463 | [8 empty] | 0.294
| 459:00 | 53.6463 | 6.64 | 23 | 20 | 12 | 58 | 128 | 16.4 | 0.256 | 0.2845 |  | 5.95 | 11 | 0.044 | 82.81% | 6.7368 | 7.9631 | 0.53646 | 0.595 | 0.037 | 0.041
| 460:00 | 53.6463 | [8 empty] | 0.2845
| 461:00 | 53.6463 | [8 empty] | 0.28033
| 462:00 | 53.6463 | [8 empty] | 0.28033
| 463:00 | 53.6463 | 6.61 | 25 | 20 | 12.8 | 52 | 132 | 16.5 | 0.277 | 0.2795 |  | 5.91 | 14 | 0.046 | 83.39% | 7.2895 | 7.3594 | 0.53646 | 0.591 | 0.041 | 0.05
| 464:00 | 53.6463 | [8 empty] | 0.2795
| 465:00 | 53.6463 | [8 empty] | 0.275 | 0.057
| 466:00 | 53.6463 | [8 empty] | 0.275
| 467:00 | 53.6463 | 6.61 | 24 | 20 | 12.2 | 54 | 130 | 16.5 | 0.292 | 0.27925 |  | 6.02 | 11 | 0.046 | 84.25% | 7.6842 | 6.9814 | 0.53646 | 0.602 | 0.041 | 0.047
| 468:00 | 53.6463 | [8 empty] | 0.27925
| 469:00 | 53.6463 | [8 empty] | 0.275
| 470:00 | 53.6463 | [8 empty] | 0.275
| 471:00 | 53.6463 | 6.68 | 20 | 21 | 12.1 | 54 | 135 | 16.8 | 0.287 | 0.278 |  | 6.01 | 11 | 0.045 | 84.32% | 7.5526 | 7.103 | 0.53646 | 0.601 | 0.044 | 0.047
| 472:00 | 53.6463 | [8 empty] | 0.278
| 473:00 | 53.6463 | [8 empty] | 0.28533
| 474:00 | 53.6463 | [8 empty] | 0.28533
| 475:00 | 53.6463 | 5.67 | 20 | 20 | 10.8 | 55 | 112 | 17.4 | 0.281 | 0.28425 |  | 6.06 | 10 | 0.055 | 80.43% | 7.3947 | 7.2547 | 0.53646 | 0.606 | 0.043 | 0.045
| 476:00 | 53.6463 | [8 empty] | 0.28425
| 477:00 | 53.6463 | [8 empty] | 0.28667 | 0.046
| 478:00 | 53.6463 | [8 empty] | 0.28667
| 479:00 | 53.6463 | 6.65 | 23 | 19 | 8.45 | 57 | 109 | 17.5 | 0.281 | 0.28525 |  | 5.94 | 9 | 0.064 | 77.22% | 7.3947 | 7.2547 | 0.53646 | 0.594 | 0.043 | 0.041
2018-02-22 | 480:00 | 55.0704 | [8 empty] | 0.28525
| 481:00 | 55.0704 | [8 empty] | 0.283
| 482:00 | 55.0704 | [8 empty] | 0.283
| 483:00 | 55.0704 | 6.61 | 22 | 18 | 9.01 | 56 | 112 | 17.5 | 0.281 | 0.2825 |  | 5.95 | 10 | 0.06 | 78.65% | 7.3947 | 7.4472 | 0.5507 | 0.595 | 0.047 | 0.045
| 484:00 | 55.0704 | [8 empty] | 0.2825
| 485:00 | 55.0704 | [8 empty] | 0.281
| 486:00 | 55.0704 | [8 empty] | 0.281
| 487:00 | 55.0704 | 6.6 | 20 | 17 | 8.45 | 60 | 113 | 16.8 | 0.293 | 0.284 |  | 5.92 | 10 | 0.055 | 81.23% | 7.7105 | 7.1422 | 0.5507 | 0.592 | 0.046 | 0.043
| 488:00 | 55.0704 | [8 empty] | 0.284
| 489:00 | 55.0704 | [8 empty] | 0.285 | 0.041
| 490:00 | 55.0704 | [8 empty] | 0.285
| 491:00 | 55.0704 | 6.67 | 24 | 20 | 8.64 | 70 | 115 | 16.8 | 0.307 | 0.2905 |  | 5.91 | 10 | 0.053 | 82.74% | 8.0789 | 6.8165 | 0.5507 | 0.591 | 0.044 | 0.046
| 492:00 | 55.0704 | [8 empty] | 0.2905
| 493:00 | 55.0704 | [8 empty] | 0.29367
| 494:00 | 55.0704 | [8 empty] | 0.29367
| 495:00 | 55.0704 | 6.61 | 24 | 20 | 8.08 | 58 | 111 | 17.1 | 0.308 | 0.29725 |  | 5.96 | 10 | 0.052 | 83.12% | 8.1053 | 6.7944 | 0.5507 | 0.596 | 0.041 | 0.041
| 496:00 | 55.0704 | [8 empty] | 0.29725
| 497:00 | 55.0704 | [8 empty] | 0.30267
| 498:00 | 55.0704 | [8 empty] | 0.30267
| 499:00 | 55.0704 | 6.62 | 25 | 20 | 7.79 | 55 | 106 | 18 | 0.278 | 0.2965 |  | 5.98 | 10 | 0.055 | 80.22% | 7.3158 | 7.5276 | 0.5507 | 0.598 | 0.042 | 0.042
| 500:00 | 55.0704 | [8 empty] | 0.2965
| 501:00 | 55.0704 | [8 empty] | 0.29767 | 0.042
| 502:00 | 55.0704 | [8 empty] | 0.29767
| 503:00 | 55.0704 | 6.61 | 23 | 19 | 8.75 | 57 | 112 | 17.9 | 0.273 | 0.2915 |  | 5.96 | 11 | 0.062 | 77.29% | 7.1842 | 7.6655 | 0.5507 | 0.596 | 0.044 | 0.041
2018-02-23 | 504:00 | 55.7469 | [8 empty] | 0.2915
| 505:00 | 55.7469 | [8 empty] | 0.28633
| 506:00 | 55.7469 | [8 empty] | 0.28633
| 507:00 | 55.7469 | 6.62 | 25 | 18 | 8.91 | 58 | 115 | 18 | 0.286 | 0.28625 |  | 5.98 | 12 | 0.057 | 80.07% | 7.5263 | 7.4069 | 0.55747 | 0.598 | 0.042 | 0.043
| 508:00 | 55.7469 | [8 empty] | 0.28625
| 509:00 | 55.7469 | [8 empty] | 0.279
| 510:00 | 55.7469 | [8 empty] | 0.279
| 511:00 | 55.7469 | 6.58 | 23 | 18 | 8.76 | 55 | 116 | 17.1 | 0.312 | 0.28725 |  | 5.81 | 10 | 0.048 | 84.62% | 8.2105 | 6.7897 | 0.55747 | 0.581 | 0.044 | 0.047
| 512:00 | 55.7469 | [8 empty] | 0.28725
| 513:00 | 55.7469 | [8 empty] | 0.29033 | 0.044
| 514:00 | 55.7469 | [8 empty] | 0.29033
| 515:00 | 55.7469 | 6.63 | 23 | 18 | 8.54 | 55 | 114 | 17.2 | 0.295 | 0.2915 |  | 6.01 | 11 | 0.049 | 83.39% | 7.7632 | 7.181 | 0.55747 | 0.601 | 0.046 | 0.046
| 516:00 | 55.7469 | [8 empty] | 0.2915
| 517:00 | 55.7469 | [8 empty] | 0.29767
| 518:00 | 55.7469 | [8 empty] | 0.29767
| 519:00 | 55.7469 | 6.58 | 23 | 19 | 8.81 | 57 | 114 | 17.5 | 0.299 | 0.298 |  | 5.99 | 11 | 0.047 | 84.28% | 7.8684 | 7.0849 | 0.55747 | 0.599 | 0.04 | 0.045
| 520:00 | 55.7469 | [8 empty] | 0.298
| 521:00 | 55.7469 | [8 empty] | 0.302
| 522:00 | 55.7469 | [8 empty] | 0.302
| 523:00 | 55.7469 | 6.62 | 24 | 20 | 8.5 | 56 | 112 | 18 | 0.291 | 0.29925 |  | 5.96 | 12 | 0.061 | 79.04% | 7.6579 | 7.2797 | 0.55747 | 0.596 | 0.045 | 0.049
| 524:00 | 55.7469 | [8 empty] | 0.29925
| 525:00 | 55.7469 | [8 empty] | 0.295 | 0.045
| 526:00 | 55.7469 | [8 empty] | 0.295
| 527:00 | 55.7469 | 6.67 | 22 | 21 | 8.3 | 57 | 113 | 18.2 | 0.283 | 0.292 |  | 5.98 | 13 | 0.056 | 80.21% | 7.4474 | 7.4854 | 0.55747 | 0.598 | 0.046 | 0.045
2018-02-24 | 528:00 | 55.7469 | [8 empty] | 0.292
| 529:00 | 55.7469 | [8 empty] | 0.291
| 530:00 | 55.7469 | [8 empty] | 0.291
| 531:00 | 55.7469 | 6.63 | 24 | 20 | 8.24 | 60 | 115 | 18.2 | 0.3 | 0.29325 |  | 5.99 | 12 | 0.06 | 80% | 7.8947 | 7.0613 | 0.55747 | 0.599 | 0.045 | 0.044
| 532:00 | 55.7469 | [8 empty] | 0.29325
| 533:00 | 55.7469 | [8 empty] | 0.29133
| 534:00 | 55.7469 | [8 empty] | 0.29133
| 535:00 | 55.7469 | 6.64 | 20 | 19 | 7.77 | 57 | 113 | 17.6 | 0.297 | 0.29275 |  | 5.92 | 10 | 0.054 | 81.82% | 7.8158 | 7.1326 | 0.55747 | 0.592 | 0.044 | 0.047
| 536:00 | 55.7469 | [8 empty] | 0.29275
| 537:00 | 55.7469 | [8 empty] | 0.29333 | 0.048
| 538:00 | 55.7469 | [8 empty] | 0.29333
| 539:00 | 55.7469 | 6.64 | 21 | 19 | 7.51 | 55 | 108 | 17.9 | 0.291 | 0.29275 |  | 5.98 | 8 | 0.051 | 82.47% | 7.6579 | 7.2797 | 0.55747 | 0.598 | 0.044 | 0.046
| 540:00 | 55.7469 | [8 empty] | 0.29275
| 541:00 | 55.7469 | [8 empty] | 0.296
| 542:00 | 55.7469 | [8 empty] | 0.296
| 543:00 | 55.7469 | 6.61 | 18 | 17 | 7.62 | 58 | 112 | 18.4 | 0.307 | 0.29875 |  | 6 | 9 | 0.069 | 77.52% | 8.0789 | 6.9003 | 0.55747 | 0.6 | 0.052 | 0.038
| 544:00 | 55.7469 | [8 empty] | 0.29875
| 545:00 | 55.7469 | [8 empty] | 0.29833
| 546:00 | 55.7469 | [8 empty] | 0.29833
| 547:00 | 55.7469 | 6.62 | 22 | 18 | 7.54 | 58 | 108 | 18.8 | 0.317 | 0.303 |  | 5.99 | 10 | 0.064 | 79.81% | 8.3421 | 6.6826 | 0.55747 | 0.599 | 0.046 | 0.046
| 548:00 | 55.7469 | [8 empty] | 0.303
| 549:00 | 55.7469 | [8 empty] | 0.305 | 0.04
| 550:00 | 55.7469 | [8 empty] | 0.305
| 551:00 | 55.7469 | 6.6 | 21 | 18 | 7.46 | 60 | 109 | 18.7 | 0.302 | 0.30425 |  | 6.01 | 11 | 0.065 | 78.48% | 7.9474 | 7.0145 | 0.55747 | 0.601 | 0.05 | 0.048
2018-02-25 | 552:00 | 55.1632 | [8 empty] | 0.30425
| 553:00 | 55.1632 | [8 empty] | 0.30867
| 554:00 | 55.1632 | [8 empty] | 0.30867
| 555:00 | 55.1632 | 6.67 | 24 | 18 | 7.55 | 64 | 114 | 18.5 | 0.268 | 0.2985 |  | 6.04 | 12 | 0.057 | 78.73% | 7.0526 | 7.8216 | 0.55163 | 0.604 | 0.041 | 0.041
| 556:00 | 55.1632 | [8 empty] | 0.2985
| 557:00 | 55.1632 | [8 empty] | 0.29567
| 558:00 | 55.1632 | [8 empty] | 0.29567
| 559:00 | 55.1632 | 6.63 | 21 | 17 | 7.54 | 65 | 114 | 18.3 | 0.328 | 0.30375 |  | 6.03 | 8 | 0.059 | 82.01% | 8.6316 | 6.3909 | 0.55163 | 0.603 | 0.045 | 0.047
| 560:00 | 55.1632 | [8 empty] | 0.30375
| 561:00 | 55.1632 | [8 empty] | 0.29933 | 0.034
| 562:00 | 55.1632 | [8 empty] | 0.29933
| 563:00 | 55.1632 | 6.61 | 20 | 15 | 6.22 | 65 | 107 | 18.5 | 0.335 | 0.30825 |  | 5.99 | 9 | 0.061 | 81.79% | 8.8158 | 6.2573 | 0.55163 | 0.599 | 0.055 | 0.052
| 564:00 | 55.1632 | [8 empty] | 0.30825
| 565:00 | 55.1632 | [8 empty] | 0.31033
| 566:00 | 55.1632 | [8 empty] | 0.31033
| 567:00 | 55.1632 | 6.63 | 21 | 15 | 7.2 | 65 | 114 | 18.6 | 0.331 | 0.3155 |  | 6.09 | 9 | 0.061 | 81.57% | 8.7105 | 6.3329 | 0.55163 | 0.609 | 0.049 | 0.05
| 568:00 | 55.1632 | [8 empty] | 0.3155
| 569:00 | 55.1632 | [8 empty] | 0.33133
| 570:00 | 55.1632 | [8 empty] | 0.33133
| 571:00 | 55.1632 | 6.68 | 22 | 16 | 7.27 | 65 | 117 | 19.5 | 0.283 | 0.31925 |  | 5.9 | 10 | 0.066 | 76.68% | 7.4474 | 7.4071 | 0.55163 | 0.59 | 0.052 | 0.05
| 572:00 | 55.1632 | [8 empty] | 0.31925
| 573:00 | 55.1632 | [8 empty] | 0.31633 | 0.043
| 574:00 | 55.1632 | [8 empty] | 0.31633
| 575:00 | 55.1632 | 6.57 | 20 | 16 | 7.05 | 71 | 119 | 19.5 | 0.353 | 0.3255 |  | 5.91 | 11 | 0.069 | 80.45% | 9.2895 | 5.9382 | 0.55163 | 0.591 | 0.05 | 0.048
2018-02-26 | 576:00 | 63.9681 | [8 empty] | 0.3255
| 577:00 | 63.9681 | [8 empty] | 0.32233
| 578:00 | 63.9681 | [8 empty] | 0.32233
| 579:00 | 63.9681 | 6.57 | 22 | 16 | 7.39 | 72 | 123 | 19.8 | 0.313 | 0.32 |  | 6.02 | 11 | 0.06 | 80.83% | 8.2368 | 7.7661 | 0.63968 | 0.602 | 0.055 | 0.054
| 580:00 | 63.9681 | [8 empty] | 0.32
| 581:00 | 63.9681 | [8 empty] | 0.31633
| 582:00 | 63.9681 | [8 empty] | 0.31633
| 583:00 | 63.9681 | 6.55 | 20 | 17 | 7.41 | 71 | 123 | 18.7 | 0.367 | 0.329 |  | 5.71 | 8 | 0.061 | 83.38% | 9.6579 | 6.6234 | 0.63968 | 0.571 | 0.051 | 0.057
| 584:00 | 63.9681 | [8 empty] | 0.329
| 585:00 | 63.9681 | [8 empty] | 0.34433 | 0.049
| 586:00 | 63.9681 | [8 empty] | 0.34433
| 587:00 | 63.9681 | 6.56 | 25 | 18 | 7.01 | 74 | 122 | 18.7 | 0.371 | 0.351 |  | 5.96 | 10 | 0.06 | 83.83% | 9.7632 | 6.552 | 0.63968 | 0.596 | 0.05 | 0.055
| 588:00 | 63.9681 | [8 empty] | 0.351
| 589:00 | 63.9681 | [8 empty] | 0.35033
| 590:00 | 63.9681 | [8 empty] | 0.35033
| 591:00 | 63.9681 | 6.61 | 21 | 17 | 7.71 | 68 | 120 | 18.8 | 0.353 | 0.351 |  | 6.09 | 9 | 0.062 | 82.44% | 9.2895 | 6.8861 | 0.63968 | 0.609 | 0.055 | 0.052
| 592:00 | 63.9681 | [8 empty] | 0.351
| 593:00 | 63.9681 | [8 empty] | 0.36367
| 594:00 | 63.9681 | [8 empty] | 0.36367
| 595:00 | 63.9681 | 6.59 | 22 | 18 | 8.3 | 70 | 125 | 19.6 | 0.348 | 0.35975 |  | 5.95 | 10 | 0.065 | 81.32% | 9.1579 | 6.985 | 0.63968 | 0.595 | 0.05 | 0.048
| 596:00 | 63.9681 | [8 empty] | 0.35975
| 597:00 | 63.9681 | [8 empty] | 0.35733 | 0.048
| 598:00 | 63.9681 | [8 empty] | 0.35733
| 599:00 | 63.9681 | 6.57 | 22 | 17 | 8.18 | 77 | 130 | 19.5 | 0.355 | 0.35675 |  | 5.94 | 11 | 0.061 | 82.82% | 9.3421 | 6.8473 | 0.63968 | 0.594 | 0.046 | 0.043
2018-02-27 | 600:00 | 69.9903 | [8 empty] | 0.35675
| 601:00 | 69.9903 | [8 empty] | 0.352
| 602:00 | 69.9903 | [8 empty] | 0.352
| 603:00 | 69.9903 | 6.59 | 22 | 18 | 9.9 | 72 | 140 | 19.4 | 0.358 | 0.3535 |  | 5.97 | 12 | 0.068 | 81.01% | 9.4211 | 7.4291 | 0.6999 | 0.597 | 0.054 | 0.051
| 604:00 | 69.9903 | [8 empty] | 0.3535
| 605:00 | 69.9903 | [8 empty] | 0.35367
| 606:00 | 69.9903 | [8 empty] | 0.35367
| 607:00 | 69.9903 | 6.57 | 27 | 20 | 9.02 | 74 | 133 | 18.1 | 0.371 | 0.358 |  | 5.89 | 12 | 0.064 | 82.75% | 9.7632 | 7.1688 | 0.6999 | 0.589 | 0.046 | 0.045
| 608:00 | 69.9903 | [8 empty] | 0.358
| 609:00 | 69.9903 | [8 empty] | 0.36133 | 0.049
| 610:00 | 69.9903 | [8 empty] | 0.36133
| 611:00 | 69.9903 | 6.58 | 22 | 20 | 7.52 | 79 | 130 | 18.1 | 0.409 | 0.37325 |  | 5.92 | 11 | 0.062 | 84.84% | 10.7632 | 6.5028 | 0.6999 | 0.592 | 0.045 | 0.045
| 612:00 | 69.9903 | [8 empty] | 0.37325
| 613:00 | 69.9903 | [8 empty] | 0.37933
| 614:00 | 69.9903 | [8 empty] | 0.37933
| 615:00 | 69.9903 | 6.52 | 22 | 16 | 8.18 | 77 | 130 | 18.2 | 0.389 | 0.38175 |  | 5.92 | 10 | 0.062 | 84.06% | 10.2368 | 6.8371 | 0.6999 | 0.592 | 0.05 | 0.047
| 616:00 | 69.9903 | [8 empty] | 0.38175
| 617:00 | 69.9903 | [8 empty] | 0.38967
| 618:00 | 69.9903 | [8 empty] | 0.38967
| 619:00 | 69.9903 | 6.62 | 22 | 20 | 9.29 | 65 | 127 | 19 | 0.323 | 0.373 |  | 5.95 | 10 | 0.064 | 80.19% | 8.5 | 8.2342 | 0.6999 | 0.595 | 0.051 | 0.049
| 620:00 | 69.9903 | [8 empty] | 0.373
| 621:00 | 69.9903 | [8 empty] | 0.37367 | 0.056
| 622:00 | 69.9903 | [8 empty] | 0.37367
| 623:00 | 69.9903 | 6.63 | 23 | 19 | 7.71 | 75 | 122 | 18.5 | 0.357 | 0.3695 |  | 5.99 | 11 | 0.07 | 80.39% | 9.3947 | 7.4499 | 0.6999 | 0.599 | 0.042 | 0.041
2018-02-28 | 624:00 | 71.8824 | [8 empty] | 0.3695
| 625:00 | 71.8824 | [8 empty] | 0.35633
| 626:00 | 71.8824 | [8 empty] | 0.35633
| 627:00 | 71.8824 | 6.56 | 24 | 18 | 7.79 | 72 | 133 | 18.5 | 0.323 | 0.348 |  | 5.99 | 12 | 0.07 | 78.33% | 8.5 | 8.4568 | 0.71882 | 0.599 | 0.054 | 0.049
| 628:00 | 71.8824 | [8 empty] | 0.348
| 629:00 | 71.8824 | [8 empty] | 0.33433
| 630:00 | 71.8824 | [8 empty] | 0.33433
| 631:00 | 71.8824 | 6.61 | 24 | 19 | 7.43 | 71 | 123 | 17.4 | 0.369 | 0.343 |  | 5.88 | 10 | 0.056 | 84.82% | 9.7105 | 7.4025 | 0.71882 | 0.588 | 0.041 | 0.042
| 632:00 | 71.8824 | [8 empty] | 0.343
| 633:00 | 71.8824 | [8 empty] | 0.34967 | 0.053
| 634:00 | 71.8824 | [8 empty] | 0.34967
| 635:00 | 71.8824 | 6.62 | 23 | 20 | 7.73 | 67 | 120 | 17.4 | 0.387 | 0.359 |  | 6.02 | 12 | 0.052 | 86.56% | 10.1842 | 7.0582 | 0.71882 | 0.602 | 0.04 | 0.042
| 636:00 | 71.8824 | [8 empty] | 0.359
| 637:00 | 71.8824 | [8 empty] | 0.35967
| 638:00 | 71.8824 | [8 empty] | 0.35967
| 639:00 | 71.8824 | 6.57 | 24 | 20 | 7.08 | 84 | 129 | 17.4 | 0.425 | 0.376 |  | 5.95 | 12 | 0.097 | 77.18% | 11.1842 | 6.4271 | 0.71882 | 0.595 | 0.055 | 0.056
| 640:00 | 71.8824 | [8 empty] | 0.376
| 641:00 | 71.8824 | [8 empty] | 0.39367
| 642:00 | 71.8824 | [8 empty] | 0.39367
| 643:00 | 71.8824 | 6.6 | 24 | 20 | 8.4 | 78 | 130 | 17.4 | 0.384 | 0.39125 |  | 6.1 | 12 | 0.064 | 83.33% | 10.1053 | 7.1134 | 0.71882 | 0.61 | 0.053 | 0.048
| 644:00 | 71.8824 | [8 empty] | 0.39125
| 645:00 | 71.8824 | [8 empty] | 0.39867 | 0.054
| 646:00 | 71.8824 | [8 empty] | 0.39867
| 647:00 | 71.8824 | 6.65 | 24 | 20 | 7.8 | 76 | 129 | 17.2 | 0.365 | 0.39025 |  | 6 | 12 | 0.07 | 80.82% | 9.6053 | 7.4836 | 0.71882 | 0.6 | 0.058 | 0.056
2018-03-01 | 648:00 | 0 | [8 empty] | 0.39025
| 649:00 | 0 | [8 empty] | 0.39133
| 650:00 | 0 | [8 empty] | 0.39133
| 651:00 | 0 | [8 empty] | 0.39133
| 652:00 | 0 | [8 empty] | 0.39133
| 653:00 | 0 | [8 empty] | 0.3745
| 654:00 | 0 | [8 empty] | 0.3745
| 655:00 | 0 | [8 empty] | 0.3745
| 656:00 | 0 | [8 empty] | 0.3745
| 657:00 | 0 | [8 empty] | 0.365
| 658:00 | 0 | [8 empty] | 0.365
| 659:00 | 0 | [8 empty] | 0.365
| 660:00 | 0 | [8 empty] | 0.365
| 661:00 | 0 | [8 empty] | #DIV/0!
| 662:00 | 0 | [8 empty] | #DIV/0!
| 663:00 | 0 | [8 empty] | #DIV/0!
| 664:00 | 0 | [8 empty] | #DIV/0!
| 665:00 | 0 | [8 empty] | #DIV/0!
| 666:00 | 0 | [8 empty] | #DIV/0!
| 667:00 | 0 | [8 empty] | #DIV/0!
| 668:00 | 0 | [8 empty] | #DIV/0!
| 669:00 | 0 | [8 empty] | #DIV/0!
| 670:00 | 0 | [8 empty] | #DIV/0!
| 671:00 | 0 | [8 empty] | #DIV/0!
2018-03-02 | 672:00 | 0 | [8 empty] | #DIV/0!
| 673:00 | 0 | [8 empty] | #DIV/0!
| 674:00 | 0 | [8 empty] | #DIV/0!
| 675:00 | 0 | [8 empty] | #DIV/0!
| 676:00 | 0 | [8 empty] | #DIV/0!
| 677:00 | 0 | [8 empty] | #DIV/0!
| 678:00 | 0 | [8 empty] | #DIV/0!
| 679:00 | 0 | [8 empty] | #DIV/0!
| 680:00 | 0 | [8 empty] | #DIV/0!
| 681:00 | 0 | [8 empty] | #DIV/0!
| 682:00 | 0 | [8 empty] | #DIV/0!
| 683:00 | 0 | [8 empty] | #DIV/0!
| 684:00 | 0 | [8 empty] | #DIV/0!
| 685:00 | 0 | [8 empty] | #DIV/0!
| 686:00 | 0 | [8 empty] | #DIV/0!
| 687:00 | 0 | [8 empty] | #DIV/0!
| 688:00 | 0 | [8 empty] | #DIV/0!
| 689:00 | 0 | [8 empty] | #DIV/0!
| 690:00 | 0 | [8 empty] | #DIV/0!
| 691:00 | 0 | [8 empty] | #DIV/0!
| 692:00 | 0 | [8 empty] | #DIV/0!
| 693:00 | 0 | [8 empty] | #DIV/0!
| 694:00 | 0 | [8 empty] | #DIV/0!
| 695:00 | 0 | [8 empty] | #DIV/0!
2018-03-03 | 696:00 | 0 | [8 empty] | #DIV/0!
. | 697:00 | 0 | [8 empty] | #DIV/0!
| 698:00 | 0 | [8 empty] | #DIV/0!
| 699:00 | 0 | [8 empty] | #DIV/0!
| 700:00 | 0 | [8 empty] | #DIV/0!
| 701:00 | 0 | [8 empty] | #DIV/0!
| 702:00 | 0 | [8 empty] | #DIV/0!
| 703:00 | 0 | [8 empty] | #DIV/0!
| 704:00 | 0 | [8 empty] | #DIV/0!
| 705:00 | 0 | [8 empty] | #DIV/0!
| 706:00 | 0 | [8 empty] | #DIV/0!
| 707:00 | 0 | [8 empty] | #DIV/0!
| 708:00 | 0 | [8 empty] | #DIV/0!
| 709:00 | 0 | [8 empty] | #DIV/0!
| 710:00 | 0 | [8 empty] | #DIV/0!
| 711:00 | 0 | [8 empty] | #DIV/0!
| 712:00 | 0 | [8 empty] | #DIV/0!
| 713:00 | 0 | [8 empty] | #DIV/0!
| 714:00 | 0 | [8 empty] | #DIV/0!
| 715:00 | 0 | [8 empty] | #DIV/0!
| 716:00 | 0 | [8 empty] | #DIV/0!
| 717:00 | 0 | [8 empty] | #DIV/0!
| 718:00 | 0 | [8 empty] | #DIV/0!
| 719:00 | 0 | [8 empty] | #DIV/0!
TOTAL |  | 37587.9153 | 1126.23 | 3674 | 3186 | 3522.24 | 9658 | 31724 | 2407 | 49.151 |  | 5.73 | 1003.26 | 1648.058 | 9.438 | 135.5035 | 1293.4474 | 1230.766 | 93.9698 | 100.326 | 7.48 | 7.563
AVERAGE |  | 50.5354 | 6.7037 | 21.869 | 18.9643 | 20.9657 | 57.4881 | 188.8333 | 14.3274 | 0.29257 |  | 0.10232 | 5.9718 | 9.8099 | 0.056179 | 0.80657 | 7.6991 | 7.326 | 0.55934 | 0.59718 | 0.04479 | 0.045018
MINIMUM |  | 0 | 5.67 | 16 | 14 | 6.22 | 33 | 87 | 9.7 | 0.19 |  | 0.012 | 5.65 | 6 | 0.025 | 0.66842 | 5 | 5.1691 | 0.4012 | 0.565 | 0.014 | 0.016
MAXIMUM |  | 71.8824 | 6.99 | 27 | 22 | 44.9 | 84 | 342 | 19.8 | 0.425 |  | 0.98 | 6.3 | 14 | 0.097 | 0.90038 | 11.1842 | 9.9509 | 0.71882 | 0.63 | 0.068 | 0.068
09:03 |  | 09:03 | [13 empty] | HIGHLIGHT BETWEEN LIME |  | 5
08/12/19 |  | 08/13/19 | [12 empty] | TOTAL # IN THIS RANGE |  | 1 | 5.5
| 09:03 |  | TRUE | [11 empty] | TOTAL SAMPLES |  | 168
FALSE
WHAT
2019-08-12 09:03
1901-12-21
Formulas:
Date = MATCH([Date, row above],A4:A747,1)

## BW 1
|  | Surface Water System Monthly Operation Report | [10 empty] | DATE | TIME
|  | Operation of Filters | [9 empty] | LAST WASH | 1900-01-13 | 14:00 | 1900-01-13 14:00
|  | Bureau of Water | [9 empty] | THIS WASH | 1900-01-17 | 13:00 | 1900-01-17 13:00
TOTAL HOURS
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 1 |  |  |  |  | 2018-02-01 | [8 empty] | 95
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED
2018-02-01
2018-02-02
2018-02-03
2018-02-04
2018-02-05 | 5:30 | 20 | 30 | 93.5 | 117200 | 55729.1667 | 10.7 | 22791.3705 | SN | TIME | 172929.1667
2018-02-06
2018-02-07
2018-02-08
2018-02-09
2018-02-10 | 8:30 | 20 | 30 | 123 | 117200 | 44270.8333 | 8.5 | 23817.6599 | GE | TIME | 161470.8333
2018-02-11
2018-02-12
2018-02-13
2018-02-14 | 14:00 | 20 | 30 | 101.5 | 117200 | 44791.6667 | 8.6 | 19885.6388 | JMM |  | 161991.6667
2018-02-15
2018-02-16
2018-02-17
2018-02-18 | 13:00 | 20 | 30 | 95 | 117200 | 46875 | 9 | 19477.8568 | JMM |  | 164075
2018-02-19
2018-02-20
2018-02-21
2018-02-22
2018-02-23 | 9:00 | 20 | 30 | 114 | 117200 | 46875 | 9 | 23373.4281 | DH |  | 164075
2018-02-24
2018-02-25
2018-02-26
2018-02-27
2018-02-28 | 9:00 | 20 | 30 | 119 | 117200 | 53645.8333 | 10.3 | 27922.8176 |  |  | 170845.8333
2018-03-01
2018-03-02
2018-03-03
Total |  | 120 | 180 | 646 | 703200
Average |  | 20 | 30 | 107.6667 | 117200
Maximum |  | 20 | 30 | 123 | 117200
Minimum |  | 20 | 30 | 93.5 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Formulas:
Day = [Day, row above]+1
Note on F8: BCOperator: 5860 = water wash / min

## BW 2
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 2 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-12 | 15:00 | 1900-01-12 15:00
2 | [11 empty] | THIS WASH | 1900-01-17 | 10:00 | 1900-01-17 10:00
3 | [12 empty] | TOTAL HOURS
4 | 9:00 | 20 | 30 | 57 | 117200 | 41666.6667 | 8 | 8679.7624 | SN | TIME | 158866.6667
5 | [13 empty] | 115
6
7
8 | 19:00 | 20 | 30 | 106 | 117200 | 44270.8333 | 8.5 | 17150.1447 | DH |  | 161470.8333
9
10
11
12
13 | 15:00 | 20 | 30 | 116 | 117200 | 43750 | 8.4 | 18547.2819 | ghe | time | 160950
14
15
16
17
18 | 10:00 | 20 | 30 | 115 | 117200 | 46875 | 9 | 19700.7766 | JMM |  | 164075
19
20
21
22
23 | 7:00 | 20 | 30 | 117 | 117200 | 52083.3333 | 10 | 22270.4431 | DH |  | 169283.3333
24
25
26
27
28 | 7:30 | 20 | 30 | 120.5 | 117200 | 53645.8333 | 10.3 | 23624.7526 | SN | TIME | 170845.8333
29
30
31
Total |  | 120 | 180 | 631.5 | 703200
Average |  | 20 | 30 | 105.25 | 117200
Maximum |  | 20 | 30 | 120.5 | 117200
Minimum |  | 20 | 30 | 57 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash /min

## BW 3
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 3 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-16 | 9:00 | 1900-01-16 09:00
2 | [11 empty] | THIS WASH | 1900-01-21 | 9:00 | 1900-01-21 09:00
3 | 8:00 | 20 | 30 | 44 | 117200 | 28645.8333 | 5.5 | 5513.0308 | SN | HEAD | 145845.8333 |  | TOTAL HOURS
4
5 | [13 empty] | 120
6
7 | 21:00 | 20 | 30 | 108 | 117200 | 49479.1667 | 9.5 | 23373.4281 | DB |  | 166679.1667
8
9
10
11
12 | 16:00 | 20 | 30 | 115 | 117200 | 41666.6667 | 8 | 20958.6295 | GE | TIME | 158866.6667
13
14
15
16
17 | 9:00 | 20 | 30 | 113 | 117200 | 46875 | 9 | 23168.398 | CBW |  | 164075
18
19
20
21
22 | 13:00 | 20 | 30 | 123 | 117200 | 57291.6667 | 11 | 30822.854 | SN | TIME | 174491.6667
23
24
25
26
27 | 7:00 | 20 | 30 | 114 | 117200 | 50520.8333 | 9.7 | 25191.3614 | DH |  | 167720.8333
28
29
30
31
Total |  | 120 | 180 | 617 | 703200
Average |  | 20 | 30 | 102.8333 | 117200
Maximum |  | 20 | 30 | 123 | 117200
Minimum |  | 20 | 30 | 44 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 4
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 4 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-16 | 3:30 | 1900-01-16 03:30
2 | 6:00 | 20 | 30 | 30 | 117200 | 31250 | 6 | 4100.6014 | SN | HEAD | 148450 | THIS WASH | 1900-01-21 | 7:00 | 1900-01-21 07:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 123.5
6
7 | 14:00 | 20 | 30 | 128 | 117200 | 49479.1667 | 9.5 | 27701.8407 | MN | TIME/HEAD | 166679.1667
8
9
10
11
12 | 1414:00 | 20 | 30 | 120 | 117200 | 46875 | 9 | 24603.6085 | MN | TIME | 164075
13
14
15
16
17 | 3:30 | 20 | 30 | 109.5 | 117200 | 46875 | 9 | 22450.7928 | R.H. | TURB. | 164075
18
19
20
21
22 | 7:00 | 20 | 30 | 123.5 | 117200 | 57291.6667 | 11 | 30948.1502 | JMM |  | 174491.6667
23
24
25
26 | 14:00 | 20 | 30 | 103 | 117200 | 54687.5 | 10.5 | 24637.7802 | dh |  | 171887.5
27
28
29
30
31
Total |  | 120 | 180 | 614 | 703200
Average |  | 20 | 30 | 102.3333 | 117200
Maximum |  | 20 | 30 | 128 | 117200
Minimum |  | 20 | 30 | 30 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 5
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 5 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-16 | 8:00 | 1900-01-16 08:00
2 | [11 empty] | THIS WASH | 1900-01-21 | 8:00 | 1900-01-21 08:00
3 | 10:00 | 20 | 30 | 46 | 117200 | 50000 | 9.6 | 10060.1422 | SN | TIME | 167200 |  | TOTAL HOURS
4
5 | [13 empty] | 120
6
7
8 | 9:00 | 20 | 30 | 119 | 117200 | 48958.3333 | 9.4 | 25482.9597 | GHE | TIME | 166158.3333
9
10
11
12
13 | 9:00 | 20 | 30 | 120 | 117200 | 41666.6667 | 8 | 21869.8742 | GE | TIME | 158866.6667
14
15
16
17 | 8:00 | 20 | 30 | 95 | 117200 | 46875 | 9 | 19477.8568 | JMM |  | 164075
18
19
20
21
22 | 8:30 | 20 | 30 | 120.5 | 117200 | 57291.6667 | 11 | 30196.3732 | JMM |  | 174491.6667
23
24
25
26 | 7:00 | 20 | 30 | 95 | 117200 | 54687.5 | 10.5 | 22724.1662 | DH |  | 171887.5
27
28
29
30
31
Total |  | 120 | 180 | 595.5 | 703200
Average |  | 20 | 30 | 99.25 | 117200
Maximum |  | 20 | 30 | 120.5 | 117200
Minimum |  | 20 | 30 | 46 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 6
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 6 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-14 | 16:00 | 1900-01-14 16:00
2 | [11 empty] | THIS WASH | 1900-01-19 | 6:30 | 1900-01-19 06:30
3 | [12 empty] | TOTAL HOURS
4
5 | 8:00 | 20 | 30 | 95 | 117200 | 52083.3333 | 10 | 21642.0631 | SN | TIME | 169283.3333 |  |  | 110.5
6
7
8
9
10
11 | 8:00 | 20 | 30 | 120 | 117200 | 45312.5 | 8.7 | 23783.4882 | MN | TIME | 162512.5
12
13
14
15 | 16:00 | 20 | 30 | 104 | 117200 | 46875 | 9 | 21323.1274 | CBW |  | 164075
16
17
18
19
20 | 6:30 | 20 | 30 | 110.5 | 117200 | 53125 | 10.2 | 25676.5992 | JMM |  | 170325
21
22
23
24 | 12:30 | 20 | 30 | 102 | 117200 | 46875 | 9 | 20913.0672 | DH |  | 164075
25
26
27
28
29
30
31
Total |  | 100 | 150 | 531.5 | 586000
Average |  | 20 | 30 | 106.3 | 117200
Maximum |  | 20 | 30 | 120 | 117200
Minimum |  | 20 | 30 | 95 | 117200
|  | 5 | 5 | 5 | 5
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 7
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 7 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 1:00 | 20 | 30 | 1 | 117200 | 50520.8333 | 9.7 | 220.9769 | JMM |  | 167720.8333 | LAST WASH | 1900-01-14 | 15:00 | 1900-01-14 15:00
2 | [11 empty] | THIS WASH | 1900-01-18 | 17:00 | 1900-01-18 17:00
3 | [12 empty] | TOTAL HOURS
4
5 | 15:00 | 20 | 45 | 110 | 117200 | 78125 | 10 | 25059.2309 | SN | HEAD | 195325 |  |  | 98
6
7
8
9
10 | 15:00 | 20 | 30 | 120 | 117200 | 46875 | 9 | 24603.6085 | GHE | TIME | 164075
11
12
13
14
15 | 12:00 | 20 | 30 | 117 | 117200 | 46875 | 9 | 23988.5183 | CBW | TIME | 164075
16
17
18
19 | 17:00 | 20 | 30 | 99 | 117200 | 47916.6667 | 9.2 | 20749.0432 | CBW |  | 165116.6667
20
21
22
23
24 | 7:00 | 20 | 30 | 110 | 117200 | 46875 | 9 | 22553.3078 | DH |  | 164075
25
26
27
28
29
30
31
Total |  | 120 | 195 | 557 | 703200
Average |  | 20 | 32.5 | 92.8333 | 117200
Maximum |  | 20 | 45 | 120 | 117200
Minimum |  | 20 | 30 | 1 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 8
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 8 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 9:00 | 20 | 30 | 120 | 117200 | 54687.5 | 10.5 | 28704.21 | SN | TIME | 171887.5 | LAST WASH | 1900-01-15 | 10:30 | 1900-01-15 10:30
2 | [11 empty] | THIS WASH | 1900-01-20 | 10:30 | 1900-01-20 10:30
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 120
6 | 19:15 | 20 | 30 | 130 | 117200 | 52083.3333 | 10 | 29615.4547 | JMM |  | 169283.3333
7
8
9
10
11 | 16:00 | 20 | 30 | 117 | 117200 | 44791.6667 | 8.6 | 22922.3619 | GHE | TIME | 161991.6667
12
13
14
15
16 | 10:30 | 20 | 30 | 114.5 | 117200 | 46875 | 9 | 23475.9431 | CBW | TIME | 164075
17
18
19
20
21 | 14:30 | 20 | 30 | 124 | 117200 | 52083.3333 | 10 | 28248.5876 | DH |  | 169283.3333
22
23
24
25 | 13:30 | 20 | 30 | 95 | 117200 | 46875 | 9 | 19477.8568 | DH |  | 164075
26
27
28
29
30
31
Total |  | 120 | 180 | 700.5 | 703200
Average |  | 20 | 30 | 116.75 | 117200
Maximum |  | 20 | 30 | 130 | 117200
Minimum |  | 20 | 30 | 95 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 9
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 9 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-13 | 10:00 | 1900-01-13 10:00
2 | [11 empty] | THIS WASH | 1900-01-18 | 10:00 | 1900-01-18 10:00
3 | 13:00 | 20 | 30 | 48 | 125000 | 50000 | 9.6 | 9108.1594 | SN | TIME | 175000 |  | TOTAL HOURS
4
5 | [13 empty] | 120
6
7
8 | 13:00 | 20 | 30 | 120 | 125000 | 49479.1667 | 9.5 | 22533.2068 | GE | TIME/HEAD | 174479.1667
9
10
11
12
13
14 | 10:00 | 20 | 30 | 141 | 125000 | 44791.6667 | 8.6 | 23968.2163 | JMM |  | 169791.6667
15
16
17
18
19 | 10:00 | 20 | 30 | 120 | 125000 | 45312.5 | 8.7 | 20635.6736 | JMM |  | 170312.5
20
21
22
23
24 | 15:00 | 20 | 30 | 125 | 125000 | 46875 | 9 | 22236.7173 | DH |  | 171875
25
26
27
28 | 16:00 | 20 | 30 | 97 | 125000 | 32812.5 | 6.3 | 12078.9848 | sn |  | 157812.5
29
30
31
Total |  | 120 | 180 | 651 | 750000
Average |  | 20 | 30 | 108.5 | 125000
Maximum |  | 20 | 30 | 141 | 125000
Minimum |  | 20 | 30 | 48 | 125000
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 10
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 10 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-22 | 14:00 | 1900-01-22 14:00
2 | 8:30 | 20 | 30 | 31.5 | 125000 | 50520.8333 | 9.7 | 6039.4924 | SN | HEAD | 175520.8333 | THIS WASH | 1900-01-27 | 11:00 | 1900-01-27 11:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 117
6
7 | 20:30 | 20 | 30 | 132 | 125000 | 49479.1667 | 9.5 | 24786.5275 | DH |  | 174479.1667
8
9
10
11
12
13 | 7:30 | 20 | 30 | 131 | 125000 | 41666.6667 | 8 | 20714.7375 | GE | TIME | 166666.6667
14
15
16
17
18 | 8:00 | 20 | 30 | 120.5 | 125000 | 46875 | 9 | 21436.1954 | JMM |  | 171875
19
20
21
22
23 | 14:00 | 20 | 30 | 126 | 125000 | 46875 | 9 | 22414.611 | sn |  | 171875
24
25
26
27
28 | 11:00 | 20 | 30 | 117 | 125000 | 53645.8333 | 10.3 | 23819.9715 | SN | HEAD\TIME | 178645.8333
29
30
31
Total |  | 120 | 180 | 658 | 750000
Average |  | 20 | 30 | 109.6667 | 125000
Maximum |  | 20 | 30 | 132 | 125000
Minimum |  | 20 | 30 | 31.5 | 125000
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 11
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 11 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-13 | 7:00 | 1900-01-13 07:00
2 | 12:30 | 20 | 30 | 36.5 | 125000 | 51041.6667 | 9.8 | 7070.2878 | SN | TIME | 176041.6667 | THIS WASH | 1900-01-18 | 7:30 | 1900-01-18 07:30
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 120.5
6
7
8 | 7:30 | 20 | 30 | 139 | 125000 | 47916.6667 | 9.2 | 25276.7236 | GHE | TIME/HEAD | 172916.6667
9
10
11
12
13
14 | 7:00 | 20 | 30 | 143.5 | 125000 | 44791.6667 | 8.6 | 24393.1847 | CBW |  | 169791.6667
15
16
17
18
19 | 7:30 | 20 | 30 | 120.5 | 125000 | 45312.5 | 8.7 | 20721.6556 | CBW |  | 170312.5
20
21
22
23
24 | 9:30 | 20 | 30 | 122 | 125000 | 46875 | 9 | 21703.0361 | dh |  | 171875
25
26
27
28
29
30
31
Total |  | 100 | 150 | 561.5 | 625000
Average |  | 20 | 30 | 112.3 | 125000
Maximum |  | 20 | 30 | 143.5 | 125000
Minimum |  | 20 | 30 | 36.5 | 125000
|  | 5 | 5 | 5 | 5
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 12
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 12 |  |  |  |  | 2018-02-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 20:00 | 20 | 30 | 20 | 125000 | 54687.5 | 10.5 | 4150.8539 | JMM |  | 179687.5 | LAST WASH | 1900-01-16 | 13:00 | 1900-01-16 13:00
2 | [11 empty] | THIS WASH | 1900-01-21 | 13:00 | 1900-01-21 13:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 120
6
7 | 13:00 | 20 | 30 | 137 | 125000 | 49479.1667 | 9.5 | 25725.4111 | GE | TIME/HEAD | 174479.1667
8
9
10
11
12 | 13:00 | 20 | 30 | 120 | 125000 | 46875 | 9 | 21347.2486 | GE | TIME | 171875
13
14
15
16
17 | 13:00 | 20 | 30 | 120 | 125000 | 46875 | 9 | 21347.2486 | CBW |  | 171875
18
19
20
21
22 | 9:00 | 20 | 60 | 115 | 125000 | 62500 | 6 | 13638.5199 | SN | HEAD | 187500
23
24
25
26
27 | 9:00 | 20 | 30 | 120 | 125000 | 28645.8333 | 5.5 | 13045.5408 | DH |  | 153645.8333
28
29
30
31
Total |  | 120 | 210 | 632 | 750000
Average |  | 20 | 35 | 105.3333 | 125000
Maximum |  | 20 | 60 | 137 | 125000
Minimum |  | 20 | 30 | 20 | 125000
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## FILTER PERFORMANCE (hidden)
Filter Performance Test
[18 empty] | Filter 1 |  | Filter 2 |  | Filter 3 |  | Filter 4 |  | Filter 5 |  | Filter 6 |  | Filter 7 |  | Filter 8 |  | Filter 9 |  | Filter 10 |  | Filter 11 |  | Filter 12
Date | OPER | Time | Filter # washed | Flow to Filter Cluster, MGD | Raw Uv 254 | Calculated Alum Dose, mg/L | Alum Dose, mg/L | Filter Washed headloss, ft | Filter washed Time in service, hrs | Filter # Affected with turbidity spike | Filter affected by turbidity spike Headloss, ft | Filter affected by turbidity spike time in service, hrs | Reason for filter washed (time or Headloss) | Settled water turbidity avg. for plant that filter was washed on. 24 hr avg., ntu | Filter affected max turbidity, ntu | Filtration rate, gpm'sq.ft | Solids Loading onto Filters, lbs/day/filter | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs |  | DATE | TIME
[42 empty] | LAST WASH | 2015-05-29 | 1:00
2015-05-28 | CBW | 1800 | 9 | 11.4 | 0.294 | 38.6842 | 40 | 4.25 | 92 | 10 | 3.91 | 82 | TIME | 0.5 | 0.19 | 5.492 | 35.6535 | [18 empty] | 1.59 | 82 | 2.3 | 5 | 5.29 | 73.5 | THIS WASH | 2015-05-31 | 0:00
2015-05-28 | JM | 2100 | 7 | 10.6 | 0.357 | 46.9737 | 40 | 3.91 | 65 | NONE |  |  | HEAD | 0.47 |  | 5.1066 | 31.1624 | [8 empty] | 5.87 | 106 | 3.61 | 11 |  |  | 3.33 | 25 | [9 empty] | TOTAL HOURS
2015-05-29 | CBW | 100 | 10 | 11.3 | 0.292 | 38.4211 | 40 | 1.9 | 89 | 12 | 6.35 | 101.5 | TURB | 0.5 | 0.11 | 5.4438 | 35.3407 | [16 empty] | 2.45 | 7 |  |  | 2.8 | 12 | 6.35 | 102.5 |  | 2015-05-29 | 48
2015-05-29 | GE | 600 | 3 | 10.4 | 0.276 | 36.3158 | 40 | 4.11 | 87 | NONE |  |  | HEAD | 0.45 |  | 5.0102 | 29.2734 | 5.21 | 86 | 4.23 | 22 |  |  | 4.22 | 89 | [17 empty] | 2015-05-31
2015-05-29 | MN | 700 | 5 | 10.5 | 0.276 | 36.3158 | 40 | 4.74 | 116 | NONE |  |  | TIME/HEAD | 0.29 |  | 5.0584 | 19.0465 | [10 empty] | 3.47 | 21 | 2.29 | 10 | 2.66 | 35
[16 empty] | 0 | 0
2015-05-29 | CBW | 2300 | 12 | 11.2 | 0.312 | 41.0526 | 44 | 5.28 | 123.5 | NONE |  |  | NTU/TIME | 0.591 |  | 5.3956 | 41.4031 | [16 empty] | 1.91 | 29 | 2.4 | 22 | 2.76 | 34 | 5.28 | 132.5
2015-05-30 | GE | 600 | 4 | 10.4 | 0.229 | 30.1316 | 40 | 3.66 | 120 | NONE |  |  | TIME/HEAD | 0.46 |  | 5.0102 | 29.9239 | 4.1 | 110.5 | 3.69 | 75 | 1.98 | 24
2015-05-30 | GE | 1030 | 1 | 10.4 | 0.235 | 30.9211 | 40 | 3.54 | 115 | NONE |  |  | TIME/HEAD | 0.52 |  | 5.0102 | 33.827 |  |  | 3.13 | 79.5 | 1.86 | 29 | 1.01 | 4.5
2015-05-31 | MN | 1000 | 2 | 11.2 | 0.226 | 29.7368 | 40 | 3.25 | 103 | NONE |  |  | TIME/HEAD | 0.41 |  | 5.3956 | 28.723 | 0.083 | 23.5 |  |  | 1.25 | 52.5 | 0.47 | 28
NEW MONTH | [15 empty] | 0 | 0
2015-06-02 | CBW | 4:30 | 8 | 34.1 | 0.241 | 31.7105 | 35 | 4.57 | 127.5/28.5 | NONE |  |  | HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 4.93 | 66/28.5 | 5.78 | 28.5 | 4.24 | 105/28.5
2015-06-02 | MN | 600 | 6 | 34.1 | 0.176 | 23.1579 | 35 | 3.71 | 115 / 30 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.33 | 94 / 30 |  |  | 2.43 | 104 / 30 | 1.03 | 129/30
2015-06-02 | GE | 1000 | 7 | 34.1 | 0.195 | 25.6579 | 32 | 2.42 | 104/34 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.86 | 99/34 | 0.09 | 4 |  |  | 0.45 | 5.5
2015-06-02 | GE | 1330 | 11 | 34.1 | 0.217 | 28.5526 | 32 | 5.37 | 120.5/37.5 | NONE |  |  | TIME/HEAD | 0.272 |  | 4.4803 | 58.0164 | [16 empty] | 5.45 | 115.5 | 1.9 | 67.5 |  |  | 3.83 | 86.5
2015-06-02 | CBW | 1930 | 3 | 34.1 | 0.181 | 23.8158 | 35 | 2.57 | 65.5/43.5 | NONE |  |  | TIME/HEAD | 0.281 |  | 4.4803 | 59.936 | 1.07 | 43.5 | 1.23 | 43.5 | 1.55 | 43.5 | 0.77 | 43.5
2015-06-03 | HE | 700 | 10 | 26.1 | 0.247 | 32.5 | 35 | 1.4 | 55 | NONE |  |  | TIME/HEAD | 0.25 |  | 3.4292 | 40.8139 | [16 empty] | 4.9 | 55 | 1.4 | 55 | 1.49 | 17 | 3.82 | 55
2015-06-10 | CBW | 1130 | 2 | 33.2 | 0.251 | 33.0263 | 35 | 0.19 | 116.5 | NONE |  |  | TIME/HEAD | 0.3 |  | 4.362 | 62.2998 | 0.01 | 29.5 | 0.91 | 116.5 | 0.48 | 26 | 0.27 | 92.5
2015-06-10 | CBW | 1330 | 5 | 33.2 | 0.251 | 33.0263 | 35 | 1.77 | 117.5 | NONE |  |  | TIME/HEAD | 0.21 |  | 4.362 | 43.6099 | [8 empty] | 1.77 | 117.5 | 0.49 | 69 | 0.06 | 45 | 0.05 | 48
2015-06-10 | GHE | 1900 | 12 | 33.2 | 0.239 | 31.4474 | 35 | 4.72 | 156 | NONE |  |  | TIME/HEAD | 0.2 |  | 4.362 | 41.5332 | [16 empty] | 0.05 | 32.5 | 0.06 | 35 | 0.05 | 36
2015-06-11 | GHE | 2:00 | 4 | 33.1 | 0.239 | 31.4474 | 35 | 3.81 | 107 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.3489 | 64.1826 | 3.54 | 44 | 3.48 | 14.5 | 3.51 | 40.5
2015-06-11 | CBW | 6:00 | 7 | 33.1 | 0.283 | 37.2368 | 35 | 3.75 | 67 | NONE |  |  | HEAD/CLEAR | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 3.99 | 16.5 | 5.53 | 85.5 | 3.75 | 61.5 | 0.05 | 64.5
2015-06-11 | CBW | 8:00 | 6 | 33.1 | 0.283 | 37.2368 | 35 | 3.41 | 87.5 | NONE |  |  | TIME/HEAD | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 2.92 | 18.5 |  |  | 1.56 | 62.5 | 2.1 | 66.5
2015-06-12 | CBW | 9:00 | 11 | 35.7 | 0.291 | 38.2895 | 35 | 3.91 | 98 | NONE |  |  | TIME/HEAD | 0.228 |  | 4.6905 | 50.9132
2015-06-12 | CBW | 14:00 | 8 | 35.7 | 0.232 | 30.5263 | 35 | 1.53 | 96.5 | NONE |  |  | TIME/HEAD | 0.278 |  | 4.6905 | 62.0784 | [8 empty] | 2.67 | 48.5 | 2.35 | 30 | 2.66 | 32 | 1.53 | 96.5 | 2.98 | 70.5 | 2.21 | 75 | 3.91 | 98 | 2.28 | 38
2015-06-13 | CBW | 600 | 1 | 38.6 | 0.224 | 29.4737 | 35 | 3.91 | 96 | NONE |  |  | TIME/HEAD | 0.3 |  | 5.0715 | 72.4329 |  |  | 3.82 | 75.5 | 3.62 | 69.5 | 2.49 | 52
2015-06-13 | CBW | 800 | 10 | 38.6 | 0.224 | 29.4737 | 35 | 3.02 | 98 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [16 empty] | 4.78 | 94.5 |  |  | 2.36 | 23 | 3.36 | 61
2015-06-13 | CBW | 900 | 3 | 38.6 | 0.224 | 29.4737 | 35 | 3.54 | 95.5 | NONE |  |  | TIME/HEAD | 0.35 |  | 5.0715 | 84.505 | 1.91 | 3 | 3.66 | 78.5 |  |  | 2.4 | 55
2015-06-13 | CBW | 1100 | 9 | 38.6 | 0.224 | 29.4737 | 35 | 4.78 | 96.5 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [18 empty] | 2.49 | 3 | 2.36 | 26 | 3.36 | 64
2015-06-14 | CBW | 600 | 7 | 42 | 0.26 | 34.2105 | 35 | 3.27 | 72 | NONE |  |  | HEAD/CLEAR WELL | 0.208 |  | 5.5182 | 54.6437 | [8 empty] | 5.21 | 88.5 | 4.31 | 70 |  |  | 2.97 | 40
2015-06-14 | CBW | 800 | 2 | 42 | 0.26 | 34.2105 | 35 | 3.59 | 92.5 | NONE |  |  | TIME | 0.257 |  | 5.5182 | 67.5165 | 3.37 | 26 |  |  | 2.96 | 23 | 3.74 | 78
2015-06-14 | CBW | 900 | 5 | 42 | 0.26 | 34.2105 | 35 | 5.09 | 91.5 | NONE |  |  | TIME | 0.208 |  | 5.5182 | 54.6437 | [10 empty] | 3.86 | 73 | 2.16 | 3 | 2.4 | 43
2015-06-14 | CBW | 1430 | 4 | 42 | 0.24 | 31.5789 | 35 | 4.68 | 84.5 | NONE |  |  | HEAD/CLEAR WELL | 0.257 |  | 5.5182 | 67.5165 | 4.04 | 32.5 | 3.96 | 6.5 | 3.54 | 29.5 | [10 empty] | 2.47 |  | 2.49 |  | 3.36 |  | 4.67
2015-06-14 | GE | 1800 | 8 | 42 | 0.218 | 28.6842 | 35 | 3.61 | 22 | NONE |  |  | HEAD | 0.31 |  | 5.5182 | 81.4401 | [8 empty] | 4.08 | 9 | 5.65 | 82 | 3.52 | 12
2015-06-15 | GE | 500 | 6 | 41.4 | 0.22 | 28.9474 | 35 | 3.88 | 23 | NONE |  |  | HEAD | 0.32 |  | 5.4394 | 82.8662 | [8 empty] | 4.52 | 20 |  |  | 3.88 | 23 | 3.15 | 11
2015-06-15 | CBW | 10:00 | 12 | 41.4 | 0.254 | 33.4211 | 35 | 5.15 | 111 | NONE |  |  | TIME | 0.202 |  | 5.4394 | 52.3093
2015-06-16 | CBW | 13:30 | 11 | 40.4 | 0.229 | 30.1316 | 35 | 5.36 | 100.5 | NONE |  |  | TIME | 0.216 |  | 5.308 | 54.5836
2015-06-17 | DMH | 1500 | 10 | 40.2 | 0.251 | 33.0263 | 40 | 1.49 | 103 | None |  |  | TIME | 0.225 |  | 5.2817 | 56.5765 | [16 empty] | 5.1 | 100 |  |  | 2.8 | 25.5 | 3.6 | 53
2015-06-18 | WL | 6:00 | 1 | 36.8 | 0.262 | 34.4737 | 40 | 2.2 | 120 | None |  |  | Time | 0.316 |  | 4.835 | 72.7381 |  |  | 1.54 | 93.4 | 2.23 | 84 | 0.79 | 81.5
2015-06-18 | WL | 9:00 | 3 | 36.8 | 0.262 | 34.4737 | 40 | 1.55 | 120 | NONE |  |  | Time | 0.316 |  | 4.835 | 72.7381 | 0.23 | 0.75 | 1.55 | 95.4 |  |  | 1.31 | 83.5
2015-06-18 | DMH | 1300 | 4 | 36.8 | 0.262 | 34.4737 | 40 | 1.31 | 94.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 5.79 | 1.56 | 100.45 | 0 | 3.78
2015-06-18 | DMH | 1530 | 2 | 36.8 | 0.262 | 34.4737 | 40 | 1.57 | 103.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 8.17 |  |  | 0 | 6.16 | 0.31 | 0.64
2015-06-19 | WL | 9:00 | 7 | 33.7 | 0.274 | 36.0526 | 40 | 3.5 | 123 | NONE |  |  | Time/HEAD | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 3.7 | 118.54 | 2.4 | 98.21 |  |  | 2.7 | 109.62
2015-06-19 | DMH | 11:00 | 5 | 33.7 | 0.274 | 36.0526 | 40 | 3.88 | 122 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [10 empty] | 2.33 | 100.25 | 0.33 | 0.072 | 2.73 | 111.65
2015-06-19 | DMH | 13:00 | 6 | 33.7 | 0.274 | 36.0526 | 40 | 2.32 | 104 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 0.36 | 1.03 |  |  | 0.33 | 3.01 | 2.72 | 113.94
2015-06-20 | WL | 8:30 | 8 | 31.4 | 0.289 | 38.0263 | 45 | 2.72 | 134.5 | NONE |  |  | TIME | 0.243 |  | 4.1255 | 47.7269 | [8 empty] | 0.36 | 20.71 | 0.02 | 18.65 | 0.33 | 22.68
2015-06-20 | WL | 12:00 | 12 | 31.4 | 0.31 | 40.7895 | 45 | 5.32 | 122 | NONE | 9,11 |  | TIME | 0.374 | 0.06 | 4.1255 | 73.4562 | [16 empty] | 2.23 |  | 2.25 |  | 4.41
2015-06-22 | DMH | 13:30 | 11 | 33.5 | 0.327 | 43.0263 | 50 | 6.42 | 144 | 9,10 | 9 |  | TIME/HEAD | 0.466 | .09,.5 | 4.4015 | 97.6468 | [16 empty] | 4.28 | 114.5 | 1.75 | 118.5 |  |  | 2.4 | 49.5
2015-06-23 | WL | 6:00 | 10 | 42.1 | 0.305 | 40.1316 | 50 | 1.25 | 135 | 9 |  |  | TIME | 0.419 | 0.13 | 5.5314 | 110.3376 | [16 empty] | 5.28 |  |  |  | 2.21 |  | 3.47
2015-06-23 | WL | 9:00 | 9 | 42.1 | 0.305 | 40.1316 | 50 | 5.28 | 134 | None | 11,12 |  | TIME | 0.419 |  | 5.5314 | 110.3376 | [18 empty] | 2.26 |  | 2.72 |  | 3.98
2015-06-24 | MN | 1200 | 3 | 42.1 | 0.294 | 38.6842 | 40 | 3.54 | 147 | NONE |  |  | TIME/HEAD | 0.335 |  | 5.5314 | 88.2174 | 2.75 | 150 | 2.2 | 139 |  |  | 2.34 | 142
2015-06-24 | MN | 1600 | 7 | 37.1 | 0.297 | 39.0789 | 40 | 3.87 | 127 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.8744 | 71.9388 | [8 empty] | 3.89 | 125 | 3.05 | 119 |  |  | 2.9 | 104.5
2015-06-25 | GHE | 2:00 | 4 | 37.1 | 0.372 | 48.9474 | 50 | 3.83 | 157 | None |  |  | Time | 0.4 |  | 4.8744 | 92.8242 | 4.76 | 164 | 4.26 | 154.5 | 0.46 | 161
2015-06-25 | MN | 830 | 8 | 37.1 | 0.306 | 40.2632 | 40 | 3.96 | 120 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 | [8 empty] | 5.83 | 141.5 | 4.63 | 138.5 | 0.44 | 18.5
2015-06-25 | MN | 1000 | 1 | 37.1 | 0.306 | 40.2632 | 40 | 4.78 | 172 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 |  |  | 4.21 | 162.5 | 0.46 | 22 | 0.26 | 3 |  |  | 4.61 | 142.5 | 0.97 | 23 | 0.47 | 4.5
2015-06-25 | MN | 1300 | 5 | 37.1 | 0.306 | 40.2632 | 40 | 5.73 | 148 |  |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906
2015-06-25 | CBW | 1900 | 12 | 37.1 | 0.304 | 40 | 40 | 6.62 | 127 | NONE |  |  | TIME | 0.46 |  | 4.8744 | 106.7478 | [16 empty] | 4.39 | 58 | 1.26 | 61 | 5.75 | 77.5
2015-06-25 | CBW | 2300 | 11 | 37.1 | 0.304 | 40 | 40 | 5.75 | 81.5 | NONE |  |  | TIME | 0.68 |  | 4.8744 | 157.8011 | [16 empty] | 4.39 | 62 | 1.25 | 65 |  |  | 0.76 | 6
2015-06-26 | CBW | 1300 | 2 | 37.1 | 0.304 | 40 | 40 | 4.17 | 178.5 | NONE |  |  | TIME | 0.58 |  | 4.8744 | 134.5951 | 0.27 | 15 |  |  | 0.97 | 37 | 0.05 | 18 | 0.44 | 18 |  |  | 0.97 | 41 | 0.47 | 24.5
2015-06-26 | MN | 900 | 6 | 37.1 | 0.304 | 40 | 40 | 4.55 | 164 | NONE |  |  | TIME/HEAD | 0.52 |  | 4.8744 | 120.6715
2015-06-27 | CBW | 4:30 | 10 | 37.1 | 0.311 | 40.9211 | 40 | 2.81 | 94.5 | 9 | 6.4 | 91.5 | Turb. | 0.48 |  | 4.8744 | 111.389 | [16 empty] | 6.4 | 91.5 |  |  | 2.32 | 29.5 | 2.97 | 33.5
2015-06-27 | CBW | 19:00 | 9 | 37.1 | 0.338 | 44.4737 | 40 | 5.89 | 106 | NONE |  |  | TIME | 0.54 |  | 4.8744 | 125.3127 | [18 empty] | 2.89 | 14.5 | 3.4 | 44 | 3.37 | 48
2015-06-28 | GHE | 19:00 | 7 | 38.3 | 0.226 | 29.7368 | 35 | 2.94 | 101 | NONE |  |  | TIME/AUTO | 0.38 |  | 5.0321 | 91.0353 | [8 empty] | 2.46 | 78 | 1.4 | 58 |  |  | 1.81 | 82.5
2015-06-29 | CBW | 600 | 3 | 38.3 | 0.226 | 29.7368 | 35 | 4 | 114 | NONE |  |  | HEAD | 0.62 |  | 5.0321 | 148.5312 | 2.29 | 102 | 1.01 | 76 |  |  | 2.03 | 100
2015-06-29 | MN | 1030 | 8 | 42 | 0.226 | 29.7368 | 35 | 3.01 | 98 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [8 empty] | 3.47 | 93 | 2.42 | 73.5 | 0.18 | 15.5
2015-06-29 | MN | 1400 | 4 | 42 | 0.232 | 30.5263 | 35 | 2.03 | 103 | NONE |  |  | TIME | 0.31 |  | 5.5182 | 81.4401 | 3.31 | 100 | 2.06 | 61 | 0.11 | 8
2015-06-29 | CBW | 2000 | 12 | 42 | 0.251 | 33.0263 | 35 | 5.39 | 97 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [16 empty] | 3.31 | 49 | 2.31 | 63.5 | 5.42 | 93
2015-06-29 | CBW | 2200 | 1 | 42 | 0.251 | 33.0263 | 35 | 4.37 | 118 | NONE |  |  | TIME | 0.51 |  | 5.5182 | 133.9821 |  |  | 3.06 | 92 | 0.11 | 16 | 0.11 | 8
2015-06-30 | MN | 700 | 5 | 42 | 0.244 | 32.1053 | 35 | 4.47 | 114 | NONE |  |  | TIME | 0.45 |  | 5.5182 | 118.2195 | [10 empty] | 3.95 | 94 | 1.98 | 36 | 0.85 | 21.5
2015-07-01 | CBW | 1:30 | 6 | 40 | 0.252 | 33.1579 | 35 | 4.97 | 111 | NONE |  |  | TIME | 0.4 |  | 5.2555 | 100.08 | [8 empty] | 0.11 | 18.5 |  |  | 2.74 | 54.5 | 1.87 | 27
2015-07-02 | wl | 1:30 | 8 | 13.3 | 0.226 | 29.7368 | 45 | 3.3 | 63 | none |  |  | head | 0.327 |  | 1.7474 | 27.2036 | [8 empty] | 1.8 | 41.5 | 0.6 | 22.5 | 0 | 15.5
2015-07-02 | wl | 4:00 | 3 | 13.6 | 0.239 | 31.4474 | 45 | 2.8 | 70 | none |  |  | head | 0.306 |  | 1.7869 | 26.0308 | 1.7 | 54 | 0.7 | 38 |  |  | 2 | 61
2015-07-07 | wl | 18:00 | 1 | 11.6 | 0.217 | 28.5526 | 45 | 1.2 | 103 | none |  |  | time | 0.262 |  | 1.5241 | 19.0102 |  |  | 0.2 | 54 | 0 | 30.5 | 1.7 | 128
2015-07-07 | DMH | 20:00 | 4 | 11.6 | 0.217 | 28.5526 | 45 | 1.51 | 131 |  |  |  | time | 0.275 |  | 1.5241 | 19.9535 | 0.35 | 0.79 | 0.25 | 56.12 | 0.03 | 0.06
2015-07-09 | JM | 900 | 12 | 13.7 | 0.253 | 33.2895 | 40 | 6.27 | 147 | NONE |  |  | TIME | 0.372 |  | 1.8 | 31.878 | [16 empty] | 4.09 | 93 | 2.18 | 74 | 5.95 | 123
2015-07-09 | MN | 1100 | 5 | 13.2 | 0.253 | 33.2895 | 40 | 2.86 | 98 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | [10 empty] | 2.27 | 93.5 | 1.61 | 69.5 | 0.54 | 49
2015-07-09 | MN | 1530 | 2 | 13.2 | 0.253 | 33.2895 | 40 | 1.78 | 96 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | 0.3 | 44.5 |  |  | 1.05 | 67 | 0 | 43.5
2015-07-10 | JM | 800 | 11 | 13.8 | 0.252 | 33.1579 | 40 | 6.96 | 146 | NONE |  |  | TIME/TURB | 0.39 |  | 1.8131 | 33.6644 | [16 empty] | 5.09 | 116 | 1.68 | 97 |  |  | 2.17 | 23
2015-07-10 | MN | 1030 | 3 | 13.2 | 0.252 | 33.1579 | 40 | 2.05 | 96 | NONE |  |  | TIME | 0.42 |  | 1.7343 | 34.6777 | 0.86 | 66 | 0.07 | 19 |  |  | 1.01 | 62
2015-07-10 | MN | 1330 | 6 | 13.2 | 0.252 | 33.1579 | 40 | 3.29 | 120 | NONE |  |  | TIME | 0.38 |  | 1.7343 | 31.3751 | [8 empty] | 0.7 | 26.5 |  |  | 3.12 | 102 | 2.07 | 76
2015-07-10 | CBW | 2230 | 9 | 14.4 | 0.272 | 35.7895 | 40 | 6.1 | 130.5 | NONE |  |  | TIME/TURB | 0.52 |  | 1.892 | 46.8374 | [18 empty] | 1.68 | 111.5 | 2.18 | 14.5 | 3.26 | 37.5
2015-07-11 | CBW | 3:30 | 10 | 14.7 | 0.272 | 35.7895 | 40 | 3.01 | 116 | NONE |  |  | TIME/TURB | 0.56 |  | 1.9314 | 51.4912 | [16 empty] | 1.67 | 5 |  |  | 2.68 | 19.5 | 3.26 | 42.5
2015-07-11 | MN | 630 | 7 | 14.5 | 0.281 | 36.9737 | 40 | 4.61 | 118 | NONE |  |  | TIME/HEAD | 0.42 |  | 1.9051 | 38.093 | [8 empty] | 2.21 | 19.5 | 0.15 | 17 |  |  | 3.59 | 92.5
2015-07-11 | MN | 1100 | 4 | 14.4 | 0.281 | 36.9737 | 45 | 2.53 | 86 | NONE |  |  | TIME | 0.28 |  | 1.892 | 25.2202 | 2.4 | 89 | 1.07 | 44 | 0.5 | 24.5
2015-07-11 | MN | 1400 | 8 | 14.5 | 0.281 | 36.9737 | 45 | 4.12 | 100 | NONE |  |  | HEAD | 0.35 |  | 1.9051 | 31.7441 | [8 empty] | 2.71 | 27 | 0.7 | 24.5 | 0.06 | 7.5
2015-07-12 | MN | 900 | 1 | 13.4 | 0.305 | 40.1316 | 45 | 3.4 | 111 | NONE |  |  | TIME | 0.34 |  | 1.7606 | 28.4978 |  |  | 2.08 | 66.5 | 1.5 | 22.5 | 0.46 | 22
2015-07-13 | CBW | 4:00 | 12 | 12.7 | 0.319 | 41.9737 | 45 | 5.75 | 91 | NONE |  |  | TIME | 0.355 |  | 1.6686 | 28.2007 | [16 empty] | 3.68 | 53.5 | 2 | 48.5 | 5.19 | 67.5
2015-07-14 | MN | 600 | 5 | 12 | 0.345 | 45.3947 | 50 | 5.82 | 115 | NONE |  |  | TIME/HEAD | 0.25 |  | 1.5766 | 18.765 | [10 empty] | 3.25 | 91.5 | 2.6 | 71.5 | 2.51 | 62
2015-07-14 | MN | 830 | 2 | 12 | 0.345 | 45.3947 | 50 | 3.55 | 113 | NONE |  |  | TIME | 0.29 |  | 1.5766 | 21.7674 | 0.41 | 23.5 |  |  | 3.3 | 97 | 1 | 69.5
2015-07-15 | DMH | 830 | 3 | 12.1 | 0.388 | 51.0526 | 50 | 4 | 118 | NONE |  |  | TIME/HEAD | 0.23 |  | 1.5898 | 17.4077 | 0.91 | 70.02 | 0.26 | 0.079 |  |  | 1.5 | 91.16
2015-07-15 | DMH | 1130 | 11 | 13.7 | 0.388 | 51.0526 | 50 | 7.25 | 123.5 | 9,10 | 6.03,1.29 | 109104 | TIME/HEAD | 0.369 | 0.215 | 1.8 | 31.6209 | [16 empty] | 6.03 | 109 | 1.29 | 104 |  |  | 3.02 | 55.5
2015-07-15 | DMH | 1300 | 7 | 13.4 | 0.388 | 51.0526 | 50 | 4.14 | 102.5 | NONE |  |  | HEAD | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.26 | 29.63 | 4.25 | 118.24 |  |  | 3.52 | 93.34
2015-07-15 | DMH | 1430 | 6 | 13.4 | 0.388 | 51.0526 | 50 | 4.26 | 121 | NONE |  |  | TIME | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.77 | 30.97 |  |  | 0.49 | 0.27 | 3.52 | 94.69
2015-07-15 | DMH | 1630 | 9 | 13.7 | 0.346 | 45.5263 | 50 | 6.03 | 114 | NONE |  |  | TIME | 0.417 |  | 1.8 | 35.7342 | [18 empty] | 1.29 | 109 | 1.98 | 5 | 3.04 | 60.5
2015-07-16 | DMH | 1000 | 4 | 13 | 0.381 | 50.1316 | 55 | 3.02 | 119 | NONE |  |  | TIME/HEAD | 0.239 |  | 1.708 | 19.4343 | 2.47 | 95.77 | 0.76 | 48.68 | 0.49 | 24.61
2015-07-16 | DMH | 1130 | 1 | 10.8 | 0.381 | 50.1316 | 55 | 1.96 | 107.5 | NONE |  |  | TIME | 0.419 |  | 1.419 | 28.3051 |  |  | 0.76 | 50.32 | 0.49 | 26.25 | 0.47 | 0.86
2015-07-18 | DMH | 1300 | 12 | 10.3 | 0.391 | 51.4474 | 60 | 4.98 | 129 | NONE |  |  | TIME | 0.359 |  | 1.3533 | 23.1291 | [16 empty] | 3.24 | 69 | 1.99 | 65.5 | 4.01 | 74
2015-07-19 | R.H. | 400 | 8 | 10.8 | 0.365 | 48.0263 | 60 | 2.31 | 82 | NONE |  |  | TIME/HEAD | 0.22 |  | 1.419 | 14.8619 | [14 empty] | 2.33 | 82
2015-07-19 | DMH | 900 | 2 | 11.1 | 0.378 | 49.7368 | 60 | 1.77 | 120.5 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 67.03 |  |  | 2.02 | 95.23 | 0.47 | 69.84
2015-07-19 | DMH | 1030 | 7 | 11.2 | 0.378 | 49.7368 | 60 | 3.06 | 93.5 | NONE |  |  | TIME/HEAD | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 12.43 | 2.41 | 91.16 |  |  | 1.62 | 92.45
2015-07-19 | DMH | 1430 | 3 | 11.1 | 0.378 | 49.7368 | 60 | 2.02 | 102 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 72.28 | 0 | 4 |  |  | 0.47 | 75.1
2015-07-19 | DMH | 1600 | 6 | 11.2 | 0.331 | 43.5526 | 60 | 2.39 | 97.5 | NONE |  |  | TIME | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 18.01 |  |  | 0.48 | 4.33 | 0.01 | 10.56
2015-07-20 | DMH | 1300 | 10 | 13 | 0.341 | 44.8684 | 55 | 3.24 | 113 | NONE |  |  | TIME | 0.398 |  | 1.708 | 32.3634 | [16 empty] | 2.12 | 43 |  |  | 6.05 | 98 | 2.76 | 48
2015-07-21 | DMH | 1130 | 4 | 11 | 0.358 | 47.1053 | 55 | 1.47 | 121.5 | NONE |  |  | TIME | 0.204 |  | 1.4453 | 14.0362 | 1.02 | 117.42 | 0 | 49.14 | 0.33 | 43.89
2015-07-21 | DMH | 1400 | 1 | 10.7 | 0.358 | 47.1053 | 55 | 1.02 | 122.5 |  |  |  | TIME | 0.204 |  | 1.4058 | 13.6534 |  |  | 0 | 51.75 | 0.33 | 46.5 | 0.46 | 1.31
2015-07-23 | GE | 900 | 2 | 10.9 | 0.267 | 35.1316 | 45 | 0.53 | 96 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | 0.11 | 19 |  |  | 0.85 | 92.5 | 0.46 | 21.5
2015-07-23 | MN | 1200 | 5 | 10.9 | 0.267 | 35.1316 | 40 | 3.07 | 111 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | [10 empty] | 1.52 | 92 | 1.48 | 97.5 | 2.03 | 102
2015-07-24 | GE | 900 | 12 | 10.1 | 0.214 | 28.1579 | 40 | 4.78 | 140 | NONE |  |  | TIME | 0.35 |  | 1.327 | 22.1114 | [16 empty] | 4.16 | 110.5 | 2.21 | 86 | 3.37 | 92
2015-07-24 | MN | 1230 | 4 | 9.6 | 0.214 | 28.1579 | 35 | 0.46 | 73 | NONE |  |  | TIME | 0.3 |  | 1.2613 | 18.0144 | 0.12 | 68.5 | 0.24 | 51.5 | 0.84 | 118
2015-07-25 | GHE | 730 | 7 | 9.1 | 0.188 | 24.7368 | 35 | 2.01 | 141 | NONE |  |  | TIME | 0.24 |  | 1.1956 | 13.6609 | [8 empty] | 0.44 | 19.5 | 2.03 | 111.5 |  |  | 2.52 | 123.5
2015-07-25 | GE | 930 | 9 | 9.4 | 0.181 | 23.8158 | 35 | 4.64 | 160 | NONE |  |  | TIME | 0.31 |  | 1.235 | 18.2271 | [18 empty] | 2.21 | 116.5 | 3.36 | 110.5 | 1.3 | 11.5
2015-07-26 | CBW | 5:00 | 8 | 9.1 | 0.181 | 23.8158 | 35 | 3.75 | 169 | NONE |  |  | HEAD | 0.27 |  | 1.1956 | 15.3685 | [8 empty] | 1.45 | 65 | 3.57 | 157 | 0.02 | 21.5
2015-07-26 | MN | 730 | 3 | 9.1 | 0.163 | 21.4474 | 32 | 2.37 | 157 | NONE |  |  | TIME | 0.28 |  | 1.1956 | 15.9377 | 1.29 | 113 | 0.24 | 69.5 |  |  | 0.46 | 43
2015-07-26 | MN | 900 | 6 | 9.1 | 0.163 | 21.4474 | 32 | 3.05 | 161 | NONE |  |  | TIME | 0.26 |  | 1.1956 | 14.7993 | [8 empty] | 1.45 | 69 |  |  | 0.02 | 25.5 | 0.46 | 4
2015-07-27 | GE | 800 | 10 | 10.9 | 0.169 | 22.2368 | 30 | 1.71 | 163 | NONE |  |  | TIME | 0.29 |  | 1.4321 | 19.7721 | [16 empty] | 4.68 | 23.5 |  |  | 4.93 | 157 | 2.67 | 71
2015-07-27 | MN | 1500 | 1 | 11 | 0.172 | 22.6316 | 30 | 2.82 | 145 | NONE |  |  | TIME | 0.28 |  | 1.4453 | 19.2654 |  |  | 1.79 | 102 | 0 | 31.5 | 0.96 | 74.5
2015-07-28 | GE | 800 | 11 | 9.9 | 0.19 | 25 | 30 | 5.48 | 161 | NONE |  |  | TIME | 0.29 |  | 1.3007 | 17.9581 | [16 empty] | 3.2 | 47 | 2.14 | 24 |  |  | 4.39 | 95
2015-07-28 | MN | 1400 | 5 | 9.9 | 0.19 | 25 | 30 | 4.47 | 122 | NONE |  |  | TIME | 0.25 |  | 1.3007 | 15.4811 | [10 empty] | 0.72 | 52 | 2.06 | 78.5 | 1.47 | 57
2015-08-02 | dh | 2000 | 8 | 10.4 | 0.186 | 24.4737 | 38 | 1.84 | 44 | none |  |  | head | 0.228 |  | 1.3664 | 14.8319 | [8 empty] | 0.26 | 11.21 | 0.01 | 36.7 | 3.06 | 106.11
2015-08-04 | wl | 1800 | 2 | 7.2 | 0.156 | 20.5263 | 38 | 2.07 | 140 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 59 |  |  | 0.04 | 106 | 0 | 31.5
2015-08-04 | dh | 2000 | 3 | 7.2 | 0.156 | 20.5263 | 38 | 1.48 | 92 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 60.89 | 0 | 0.76 |  |  | 0 | 33.23
2015-08-05 | CBW | 13:30 | 9 | 9.1 | 0.151 | 19.8684 | 30 | 4.84 | 109.5 | NONE |  |  | TIME | 0.19 |  | 1.1956 | 10.8149 | [16 empty] | 4.84 | 109.5 | 109.5 | 1.65 | 4.14 | 102 | 2.18 | 53.5
2015-08-06 | CBW | 7:00 | 10 | 9.6 | 0.163 | 21.4474 | 30 | 2.83 | 127 | NONE |  |  | TIME | 0.391 |  | 1.2613 | 23.4788 | [16 empty] | 1.29 | 17.5 | 2.83 | 127 | 5.68 | 119 | 3.24 | 71
2015-08-06 | CBW | 1400 | 6 | 9.2 | 0.171 | 22.5 | 30 | 1.52 | 134 | NONE |  |  | TIME | 0.39 |  | 1.2088 | 22.4429 | [8 empty] | 1.27 | 102.5 | 1.52 | 134 | 0 | 78.5 | 0.81 | 90
2015-08-06 | CBW | 1600 | 11 | 9.6 | 0.174 | 22.8947 | 30 | 5.69 | 128.5 | NONE |  |  | TIME | 0.31 |  | 1.2613 | 18.6149 | [16 empty] | 1.29 | 26.5 | 2.32 | 9 |  |  | 3.24 | 80
2015-08-07 | CBW | 8:00 | 1 | 8.6 | 0.178 | 23.4211 | 37 | 1.02 | 128 | NONE |  |  | TIME | 0.5 |  | 1.1299 | 26.8965 | 1.02 | 128 | 0.39 | 62 | 0 | 60 | 0.5 | 95.5
2015-08-07 | CBW | 13:00 | 5 | 8.6 | 0.178 | 23.4211 | 37 | 2.27 | 125.5 | NONE |  |  | TIME | 0.32 |  | 1.1299 | 17.2138 | [8 empty] | 2.27 | 125.5 | 0 | 23 | 1.01 | 101.5 | 1.81 | 113
2015-08-08 | CBW | 6:00 | 8 | 8.5 | 0.235 | 30.9211 | 35 | 2.8 | 130 | NONE |  |  | TIME | 0.47 |  | 1.1168 | 24.9887 | [8 empty] | 0 | 17 | 0.5 | 40 | 2.52 | 118.5 | 2.8 | 130
2015-08-08 | CBW | 8:00 | 7 | 8.5 | 0.165 | 21.7105 | 35 | 2.52 | 120 | NONE |  |  | TIME | 0.46 |  | 1.1168 | 24.4571 | [8 empty] | 0 | 19 | 0.5 | 42 | 2.52 | 120 | 0 | 2
2015-08-09 | CBW | 6:30 | 12 | 9.2 | 0.169 | 22.2368 | 35 | 6.05 | 142.5 | NONE |  |  | TIME | 0.58 |  | 1.2088 | 33.3767 | [16 empty] | 3.81 | 89 | 2.34 | 71.5 | 3.42 | 62.5 | 6.05 | 142.5
2015-08-09 | CBW | 9:00 | 4 | 8.9 | 0.169 | 22.2368 | 35 | 2.18 | 144.5 | NONE |  |  | TIME | 0.43 |  | 1.1693 | 23.9379 | 0.46 | 49 | 0.78 | 111 | 2 | 109 | 2.18 | 144.5
2015-08-10 | CBW | 6:00 | 2 | 9.3 | 0.181 | 23.8158 | 35 | 2.37 | 132 | NONE |  |  | TIME | 0.66 |  | 1.2219 | 38.3932 | 0.46 | 70 | 2.37 | 132 | 3.52 | 130 | 0 | 21
2015-08-10 | CBW | 10:00 | 3 | 10 | 0.181 | 23.8158 | 35 | 3.52 | 134 | NONE |  |  | TIME | 0.33 |  | 1.3139 | 20.6415 | 0.96 | 74 | 0.06 | 136 | 3.52 | 134 | 0 | 25
2015-08-11 | CBW | 6:30 | 9 | 9.8 | 0.177 | 23.2895 | 34 | 6.84 | 137 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [18 empty] | 1.32 | 119.5 | 6.97 | 110.5 | 3.74 | 48
2015-08-11 | CBW | 8:00 | 10 | 9.8 | 0.177 | 23.2895 | 34 | 0.8 | 121 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 1.5 |  |  | 6.97 | 112 | 3.76 | 49.5
2015-08-11 | CBW | 13:30 | 11 | 9.8 | 0.177 | 23.2895 | 34 | 6.47 | 117.5 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 7 | 2.58 | 5.5 |  |  | 3.74 | 55
2015-08-11 | CBW | 1500 | 6 | 9.4 | 0.177 | 23.2895 | 34 | 5.01 | 121 | NONE |  |  | TIME | 0.27 |  | 1.235 | 15.8752 | [8 empty] | 4.56 | 98 | 5.01 | 121 | 0 | 79 | 3.53 | 81
2015-08-11 | GHE | 18:00 | 1 | 7.4 | 0.138 | 18.1579 | 35 | 1.45 | 106 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 |  |  | 0.06 | 37 | 0 | 32 | 0.51 | 57
2015-08-11 | GHE | 20:00 | 5 | 7.4 | 0.138 | 18.1579 | 35 | 2.5 | 103 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 | [10 empty] | 0 | 5 | 0 | 84 | 3.03 | 86
2015-08-12 | MN | 600 | 8 | 7.5 | 0.152 | 20 | 35 | 2.54 | 96 | NONE |  |  | TIME | 0.42 |  | 0.9854 | 19.7032 | [8 empty] | 0.12 | 9 | 0 | 14 | 0.2 | 93
2015-08-12 | DMH | 11:30 | 7 | 7.8 | 0.133 | 17.5 | 35 | 0.02 | 99.5 | NONE |  |  | TIME | 0.282 |  | 1.0248 | 13.7585 | [8 empty] | 0.09 | 14.45 | 0.06 | 19.07 |  |  | 0 | 4.64
2015-08-13 | wl | 10:00 | 12 | 9.3 | 0.149 | 19.6053 | 40 | 4.94 | 99.5 | none |  |  | time | 0.39 |  | 1.2219 | 22.6869 | [16 empty] | 1.37 | 51.5 | 2.57 | 50 | 2.05 | 44.5
2015-08-13 | wl | 16:00 | 4 | 8.8 | 0.15 | 19.7368 | 40 | 1.1 | 103 | none |  |  | time | 0.267 |  | 1.1562 | 14.6967 | 0 | 44.6 | 0.2 | 80.6 | 0.2 | 76
2015-08-14 | dmh | 11:00 | 2 | 10.4 | 0.15 | 19.7368 | 40 | 0.51 | 101 | none |  |  | time | 0.289 |  | 1.3664 | 18.8 | 0 | 63.34 |  |  | 1 | 95.12 | 0 | 17.27
2015-08-14 | dmh | 15:30 | 3 | 10.6 | 0.15 | 19.7368 | 40 | 0.1 | 99.5 | none |  |  | time | 0.289 |  | 1.3927 | 19.1616 | 0 | 3.56 | 0.45 | 68.11 |  |  | 0.06 | 22.04
2015-08-15 | wl | 9:30 | 1 | 9.9 | 0.149 | 19.6053 | 40 | 0 | 84 | none |  |  | time | 0.399 |  | 1.3007 | 24.7079 |  |  | 0 | 22 | 0 | 17 | 0 | 40.5
2015-08-15 | CBW | 11:30 | 9 | 10.4 | 0.149 | 19.6053 | 40 | 3.2 | 101 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [18 empty] | 2 | 99.5 | 3.5 | 94.5 | 2.6 | 49.5
2015-08-15 | CBW | 1400 | 10 | 10.4 | 0.149 | 19.6053 | 40 | 2.9 | 102 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [16 empty] | 1.1 |  |  |  | 3.6 |  | 2.8
2015-08-15 | wl | 1600 | 6 | 9.2 | 0.149 | 19.6053 | 40 | 0.5 | 96 | none |  |  | time | 0.448 |  | 1.2088 | 25.7806 | [8 empty] | 0.5 | 91 |  |  | 0.4 | 75 | 0.2 | 80
2015-08-15 | he | 1800 | 11 |  |  | 0 | 45 | 3.62 | 99.5 | none |  |  | time | 0.487 |  | 0 | 0
2015-08-16 | wl | 8:30 | 5 | 9.4 | 0.147 | 19.3421 | 45 | 1 | 110.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [10 empty] | 0 | 15.5 | 0.8 | 92 | 0.7 | 97
2015-08-16 | wl | 10:30 | 8 | 9.4 | 0.147 | 19.3421 | 45 | 0.7 | 100.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 1 | 0 | 17.5 | 0.8 | 94
2015-08-16 | wl | 13:30 | 7 | 9.4 | 0.147 | 19.3421 | 45 | 0.8 | 98 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 4 | 0 | 20.5 |  |  | 0 | 2
2015-08-17 | wl | 11:00 | 12 | 10.3 | 0.149 | 19.6053 | 45 | 3.63 | 97 | none |  |  | time | 0.348 |  | 1.3533 | 22.4204 | [16 empty] | 1.7 | 47.5 | 2.82 | 45 | 1.89 | 41
2015-08-17 | wl | 1600 | 4 | 9.7 | 0.149 | 19.6053 | 45 | 0.1 | 96 | none |  |  | time | 0.367 |  | 1.2745 | 22.2672 | 0 | 52.5 | 0 | 76 | 0 | 71.5
2015-08-18 | wl | 7:30 | 2 | 9.6 | 0.149 | 19.6053 | 45 | 0.3 | 91.6 | none |  |  | time | 0.354 |  | 1.2613 | 21.257 | 0 | 68.3 |  |  | 0.2 | 86.8 | 0 | 14.1
2015-08-18 | dh | 10:00 | 3 | 9.6 | 0.149 | 19.6053 | 45 | 0.04 | 89 | none |  |  | time | 0.403 |  | 1.2613 | 24.1993 | 0 | 70.53 | 0 | 1.01 |  |  | 0 | 16.39
2015-08-19 | GE | 9:30 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0.45 | 10 | 0.05 | 11.5 | 0 | 17.5
2015-08-19 | GE | 13:30 | 9 | 8.9 |  | 0 | 40 | 2.21 | 98 | NONE |  |  | TIME | 0.32 |  | 1.1693 | 17.8142 | [18 empty] | 2.32 | 93.5 | 2.43 | 91.5 | 1.59 | 51.5
2015-08-19 | GE | 16:00 | 6 | 8.3 |  | 0 | 40 | 0.22 | 96 | NONE |  |  | TIME | 0.3 |  | 1.0905 | 15.575 | [8 empty] | 0.31 | 79.5 |  |  | 0.34 | 74.5 | 0.23 | 77.5
2015-08-19 | CBW | 19:00 | 10 | 8.8 |  | 0 | 39 | 2.91 | 101 | NONE |  |  | TIME | 0.231 |  | 1.1562 | 12.7152 | [16 empty] | 1.26 | 5.5 |  |  | 2.43 | 99 | 1.6 | 56
2015-08-19 | CBW | 23:00 | 11 | 8.8 |  | 0 | 39 | 2.43 | 100.5 | NONE |  |  | TIME | 0.227 |  | 1.1562 | 12.495 | [16 empty] | 1.26 | 9.5 | 2.91 | 4 |  |  | 2.1 | 60
2015-08-20 | MN | 830 | 5 | 8.3 |  | 0 | 38 | 0.81 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [10 empty] | 0.21 | 16 | 0.34 | 91 | 0.23 | 94
2015-08-20 | MN | 1030 | 8 | 8.3 |  | 0 | 38 | 0.21 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [8 empty] | 0 | 2 | 0.21 | 18 | 0.34 | 93
2015-08-20 | MN | 1330 | 7 | 8.3 |  | 0 | 38 | 0.34 | 96 | NONE |  |  | TIME | 0.2 |  | 1.0905 | 10.3833 | [8 empty] | 0 | 5 | 0.21 | 21 |  |  | 0.13 | 3 | 1.29 | 45.5 | 2.51 | 28 | 1.36 | 38
2015-08-21 | MN | 1100 | 12 | 8.8 |  | 0 | 35 | 2.1 | 96 | NONE |  |  | TIME | 0.22 |  | 1.1562 | 12.1097
2015-08-21 | MN | 1600 | 4 | 8.3 | 0.176 | 23.1579 | 35 | 0 | 96 | NONE |  |  | TIME | 0.22 |  | 1.0905 | 11.4216 | 0 | 54.5 | 0 | 80.5 | 0 | 78
2015-08-22 | CBW | 4:00 | 2 | 8.3 | 0.176 | 23.1579 | 35 | N/A | 92.5 | NONE |  |  | TIME | 0.34 |  | 1.0905 | 17.6516 | N/A | 66.5 |  |  | N/A | 90 | N/A | 12
2015-08-22 | MN | 1000 | 3 | 8.3 |  | 0 | 35 | 0 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | 0 | 72.5 | 0 | 6 |  |  | 0 | 18
2015-08-23 | MN | 930 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0 | 29.5 | 0.44 | 23.5 | 0 | 42.5
2015-08-23 | MN | 1600 | 6 | 8.3 |  | 0 | 45 | 0 | 96 | NONE |  |  | TIME | 0.28 |  | 1.0905 | 14.5366 | [8 empty] | 0 | 78 |  |  | 0 | 73 | 0 | 76 |  |  | 2.51 | 110.5 | 1.86 | 105.5 | 1.47 | 69.5
2015-08-24 | MN | 830 | 9 | 9.5 |  | 0 | 45 | 2.3 | 115 | NONE |  |  | TIME | 0.25 |  | 1.2482 | 14.8556
2015-08-24 | MN | 1030 | 5 | 9 |  | 0 | 45 | 1.02 | 98 | NONE |  |  | TIME | 0.23 |  | 1.1825 | 12.9478 | [10 empty] | 0 | 16 | 0 | 92 | 0.52 | 95
2015-08-24 | CBW | 21:00 | 10 | 10.3 | 0.14 | 18.4211 | 35 | 3.03 | 124 | NONE |  |  | TIME | 0.25 |  | 1.3533 | 16.1066 | [16 empty] | 1.19 | 12.5 |  |  | 2.87 | 118 | 2.5 | 82
2015-08-25 | CBW | 2:00 | 11 | 10.2 | 0.14 | 18.4211 | 35 | 2.36 | 123 | NONE |  |  | TIME | 0.2 |  | 1.3401 | 12.7602 | [16 empty] | 1.19 | 17.5 | 2.5 | 5 |  |  | 1.99 | 87
2015-09-02 | CBW | 13:00 | 3 | 7.3 | 0.263 | 34.6053 | 45 | N/A | 37 | NONE |  |  | TIME | 0.26 |  | 0.95912 | 11.872 | N/A | 28 | N/A | 29 |  |  | N/A | 37
2015-09-02 | CBW | 15:00 | 1 | 7.7 | 0.263 | 34.6053 | 45 | N/A | 39 | NONE |  |  | TIME | 0.21 |  | 1.0117 | 10.1143 |  |  | N/A | 31 | N/A | 2 | N/A | 39
2015-09-03 | CBW | 6:00 | 6 | 8.5 | 0.256 | 33.6842 | 45 | 1 | 54 | NONE |  |  | TIME | 0.3 |  | 1.1168 | 15.9503 | [8 empty] | 0.5 | 54 | 1.01 | 54 | 0 | 54 | 0.01 | 54
2015-09-03 | CBW | 9:00 | 9 | 9.2 | 0.256 | 33.6842 | 45 | 2.24 | 57 | NONE |  |  | TIME | 0.276 |  | 1.2088 | 15.8827 | [18 empty] | 2.58 | 57 | 1.92 | 57 | 1.67 | 48
2015-09-03 | CBW | 12:00 | 5 | 7.3 | 0.256 | 33.6842 | 45 | 1 | 60 | NONE |  |  | TIME | 0.22 |  | 0.95912 | 10.0455 | [10 empty] | 0.29 | 6 | 0 | 60 | 0.01 | 60
2015-09-04 | CBW | 7:00 | 10 | 7 | 0.256 | 33.6842 | 45 | 2.08 | 79 | NONE |  |  | TIME | 0.58 |  | 0.91971 | 25.3953 | [16 empty] | 0.67 | 22 |  |  | 1.91 | 79 | 0.67 | 79
2015-09-04 | CBW | 9:30 | 11 | 8.5 | 0.256 | 33.6842 | 45 | 1.92 | 81.5 | NONE |  |  | TIME | 0.4 |  | 1.1168 | 21.267 | [16 empty] | 0.67 | 24.5 | 2.71 | 2.5 |  |  | 1.68 | 81.5
2015-09-04 | CBW | 13:00 | 8 | 8.5 | 0.256 | 33.6842 | 45 | N/A | 85 | NONE |  |  | TIME | 0.32 |  | 1.1168 | 17.0136 | [8 empty] | 4.7 | 25 | 0.29 | 31 | 0 | 85
2015-09-05 | CBW | 7:00 | 12 | 9.1 | 0.256 | 33.6842 | 45 | 1.38 | 103 | NONE |  |  | TIME | 0.6 |  | 1.1956 | 34.1523 | [16 empty] | 1.22 | 46 | 2.62 | 24 | 1.16 | 21.5
2015-09-05 | CBW | 9:00 | 7 | 8.3 | 0.304 | 40 | 45 | 0.31 | 105 | NONE |  |  | TIME | 0.27 |  | 1.0905 | 14.0175 | [8 empty] | N/A | 45 | N/A | 51 |  |  | N/A | 20
2015-09-05 | CBW | 1500 | 4 | 7.1 | 0.304 | 40 | 45 | N/A | 111 | NONE |  |  | TIME | 0.25 |  | 0.93285 | 11.1026 | N/A | 72 | N/A | 103 | N/A | 74
2015-09-06 | CBW | 7:00 | 2 | 7.1 | 0.295 | 38.8158 | 40 | N/A | 119 | NONE |  |  | TIME | 0.56 |  | 0.93285 | 24.8699 | N/A | 88 |  |  | N/A | 90 | N/A | 16
2015-09-07 | CBW | 9:00 | 3 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 116 | NONE |  |  | TIME | 0.49 |  | 1.0117 | 23.6001 | N/A | 114 | N/A | 26 |  |  | N/A | 4
2015-09-07 | CBW | 14:00 | 1 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 119 | NONE |  |  | TIME | 0.38 |  | 1.0117 | 18.3021 |  |  | N/A | 31 | N/A | 5 | N/A | 47
2015-09-08 | CBW | 6:00 | 6 | 8.1 | 0.233 | 30.6579 | 45 | 2.51 | 120 | NONE |  |  | TIME | 0.4 |  | 1.0642 | 20.2662 | [8 empty] | 2.02 | 114 |  |  | 1.72 | 69 | 2.53 | 89
2015-09-08 | CBW | 8:00 | 9 | 8.9 | 0.233 | 30.6579 | 45 | 3.74 | 119 | NONE |  |  | TIME | 0.5 |  | 1.1693 | 27.8347 | [18 empty] | 2.11 | 97 | 3.24 | 94 | 2.43 | 73
2015-09-08 | CBW | 12:00 | 5 | 0.31 | 0.233 | 30.6579 | 45 | 2.56 | 120 | NONE |  |  | TIME | 0.32 |  | 0.04073 | 0.6205 | [10 empty] | 0 | 6 | 2.24 | 7.5 | 3.05 | 95
2015-09-09 | wl | 8:00 | 8 | 7.2 | 0.335 | 44.0789 | 45 | 3.8 | 115 | NONE |  |  | time | 0.367 |  | 0.94598 | 16.5282 | [8 empty] | 0 | 18 | 0 | 25.5 | 2.9 | 93.5
2015-09-10 | wl | 8:30 | 4 | 6.6 | 0.345 | 45.3947 | 50 | 1.3 | 113.5 | NONE |  |  | time | 0.317 |  | 0.86715 | 13.0867 | 0 | 66 | 0.4 | 96 | 0 | 71
2015-09-10 | dh | 10:30 | 12 | 7.5 | 0.345 | 45.3947 | 50 | 3.05 | 123.5 | NONE |  |  | time | 0.381 |  | 0.9854 | 17.8737 | [16 empty] | 1.04 |  | 0.06 |  | 1.06
2015-09-11 | wl | 14:30 | 2 | 7.2 | 0.309 | 40.6579 | 50 | 0.8 | 127.5 | NONE |  |  | time | 0.301 |  | 0.94598 | 13.5558 | 0 | 95.5 |  |  | 0.3 | 101 | 7.4 | 28.5
2015-09-12 | DH | 10:00 | 1 | 7.2 | 0.31 | 40.7895 | 50 | 0.035 | 116 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 |  |  | 0.059 | 18.02 | 0.04 | 120.31 | 0.06 | 47.81
2015-09-12 | DH | 14:00 | 3 | 7.2 | 0.31 | 40.7895 | 50 | 0.04 | 125 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 | 0.069 | 2.97 | 0.063 | 22.42 |  |  | 0.06 | 52.21
2015-09-13 | wl | 10:00 | 6 | 6.6 | 0.31 | 40.7895 | 50 | 0.9 | 124 | none |  |  | Time | 0.285 |  | 0.86715 | 11.7657 | [8 empty] | 0.8 | 115.5 |  |  | 0 | 96 | 0 | 98
2015-09-13 | DH | 12:00 | 5 | 6.5 | 0.31 | 40.7895 | 50 | 0.06 | 120 | NONE |  |  | TIME | 0.285 |  | 0.85401 | 11.5874 | [10 empty] | 0.08 | 0.71 | 0.06 | 97.48 | 0.04 | 99.49
2015-09-14 | DH | 9:00 | 10 | 8.5 | 0.306 | 40.2632 | 60 | 2 | 115 | NONE |  |  | TIME | 0.438 |  | 1.1168 | 23.2874 | [16 empty] | 1 | 18 |  |  | 2.3 | 114.5 | 2 | 90.5
2015-09-15 | wl | 8:00 | 7 | 7.3 | 0.31 | 40.7895 | 60 | 1.4 | 142 | none |  |  | time | 0.461 |  | 0.95912 | 21.05 | [8 empty] | 0.2 | 43 | 0.1 | 45 |  |  | 0 | 16
2015-09-15 | wl | 10:00 | 4 | 7.3 | 0.31 | 40.7895 | 60 | 0 | 121.5 | none |  |  | time | 0.422 |  | 0.95912 | 19.2692 | 0 | 70.5 | 0 | 90 | 0 | 66.5
2015-09-15 | DH | 13:00 | 12 | 7.8 | 0.312 | 41.0526 | 60 | 2.4 | 122.5 | NONE |  |  | TIME | 0.426 |  | 1.0248 | 20.7841 | [16 empty] | 1.4 | 46 | 2.5 | 28 | 1.2 | 26.5
2015-09-18 | CBW | 22:00 | 9 | 7.9 | 0.283 | 37.2368 | 45 | 4.58 | 127 | NONE |  |  | TIME | 0.423 |  | 1.038 | 20.9023 | [18 empty] | 1.71 | 109 | 3.78 | 107.5 | 3.01 | 81

## FILTER STUDY
Hour
| DATE | 2018-02-01 | 2018-02-02 | 2018-02-03 | 2018-02-04 | 2018-02-05 | 2018-02-06 | 2018-02-07 | 2018-02-08 | 2018-02-09 | 2018-02-10 | 2018-02-11 | 2018-02-12 | 2018-02-13 | 2018-02-14 | 2018-02-15 | 2018-02-16 | 2018-02-17 | 2018-02-18 | 2018-02-19 | 2018-02-20 | 2018-02-21 | 2018-02-22 | 2018-02-23 | 2018-02-24 | 2018-02-25 | 2018-02-26 | 2018-02-27 | 2018-02-28 | 2018-03-01 | 2018-03-02 | 2018-03-03
| DOSE | 4361 | 4264 | 4237.3333 | 4978.4 | 5766.6667 | 7241 | 7653.3333 | 6946.6667 | 5705 | 5190 | 5990 | 5626.6667 | 6050 | 6326.6667 | 6693.3333 | 6683.3333 | 6680 | 6680 | 6205 | 4720 | 5566.6667 | 6231.6667 | 6238.3333 | 6238.3333 | 6091.6667 | 7064 | 7366.6667 | 7746.6667 |  |  |  |  | NUMBER OF WASHS
| Alum Dose:TOC Ratio | 792.9091 | 747.2652 | 685.1858 | 666.9067 | 654.1294 | 772.1927 | 854.1165 | 844.7147 | 779.3529 | 723.3007 | 732.2895 | 781.7672 | 883.0986 | 854.0438 | 885.711 | 913.0018 | 992.8553 | 940.7288 | 854.3116 | 634.5283 | 758.184 | 816.5632 | 805.402 | 784.0904 | 731.7703 | 764.4006 | 761.0331 | 783.9503 | #VALUE! | #VALUE! | #VALUE!
| UV 254 | 0.209 | 0.21683 | 0.235 | 0.28367 | 0.335 | 0.35633 | 0.3405 | 0.3125 | 0.27817 | 0.27267 | 0.31083 | 0.2735 | 0.26033 | 0.2815 | 0.28717 | 0.27817 | 0.25567 | 0.26983 | 0.276 | 0.28267 | 0.279 | 0.29 | 0.29433 | 0.30233 | 0.31633 | 0.35117 | 0.36783 | 0.3755
RAW | FLOWS | 25.755 | 26.148 | 28.135 | 27.554 | 25.357 | 25.517 | 27.954 | 27.561 | 24.431 | 26.106 | 26.755 | 26.213 | 25.197 | 26.105 | 26.558 | 27.109 | 26.743 | 26.522 | 26.638 | 23.989 | 24.843 | 28.185 | 27.575 | 26.96 | 26.315 | 27.465 | 25.18 | 22.15 | 0 | 0 | 0
FILTERS | [34 empty] | Days | GAL USED
| FILT 1 |  |  |  |  | 93.5 |  |  |  |  | 123 |  |  |  | 101.5 |  |  |  | 95 |  |  |  |  | 114 |  |  |  |  | 119 |  |  |  |  | 6 | 1 | [6 empty] | 167720.8333 | 171887.5 |  |  |  | 179687.5 | 519295.8333
| FILT 2 |  |  |  | 57 |  |  |  | 106 |  |  |  |  | 116 |  |  |  |  | 115 |  |  |  |  | 117 |  |  |  |  | 120.5 |  |  |  |  | 6 | 2 |  |  |  | 148450 | [5 empty] | 175520.8333 | 176041.6667 |  | 500012.5
| FILT 3 |  |  | 44 |  |  |  | 108 |  |  |  |  | 115 |  |  |  |  | 113 |  |  |  |  | 123 |  |  |  |  | 114 | [5 empty] | 6 | 3 |  |  | 145845.8333 |  | 167200 |  |  |  | 175000 |  |  |  | 488045.8333
| FILT 4 |  | 30 |  |  |  |  | 128 |  |  |  |  | 120 |  |  |  |  | 109.5 |  |  |  |  | 123.5 |  |  |  | 103 | [6 empty] | 6 | 4 |  | 158866.6667 | [10 empty] | 158866.6667
| FILT 5 |  |  | 46 |  |  |  |  | 119 |  |  |  |  | 120 |  |  |  | 95 |  |  |  |  | 120.5 |  |  |  | 95 | [6 empty] | 6 | 5 | 172929.1667 |  |  |  |  | 169283.3333 | 195325 | [5 empty] | 537537.5
| FILT 6 |  |  |  |  | 95 | [5 empty] | 120 |  |  |  | 104 |  |  |  |  | 110.5 |  |  |  | 102 | [8 empty] | 5 | 6 | [7 empty] | 169283.3333 |  |  |  |  | 169283.3333
| FILT 7 | 1 |  |  |  | 110 |  |  |  |  | 120 |  |  |  |  | 117 |  |  |  | 99 |  |  |  |  | 110 | [8 empty] | 6 | 7 |  |  | 166679.1667 | 166679.1667 | [5 empty] | 174479.1667 |  | 174479.1667 | 682316.6667
| FILT 8 | 120 |  |  |  |  | 130 |  |  |  |  | 117 |  |  |  |  | 114.5 |  |  |  |  | 124 |  |  |  | 95 | [7 empty] | 6 | 8 |  | 161470.8333 |  |  | 166158.3333 |  |  |  | 174479.1667 |  | 172916.6667 |  | 675025
| FILT 9 |  |  | 48 |  |  |  |  | 120 | [5 empty] | 141 |  |  |  |  | 120 |  |  |  |  | 125 |  |  |  | 97 |  |  |  |  | 6 | 9 | [12 empty] | 0
| FILT 10 |  | 31.5 |  |  |  |  | 132 | [5 empty] | 131 |  |  |  |  | 120.5 |  |  |  |  | 126 |  |  |  |  | 117 |  |  |  |  | 6 | 10 | 161470.8333 | [5 empty] | 164075 | [5 empty] | 325545.8333
| FILT 11 |  | 36.5 | [5 empty] | 139 | [5 empty] | 143.5 |  |  |  |  | 120.5 |  |  |  |  | 122 | [8 empty] | 5 | 11 | [5 empty] | 162512.5 |  | 161991.6667 |  |  |  |  | 324504.1667
| FILT 12 | 20 | [5 empty] | 137 |  |  |  |  | 120 |  |  |  |  | 120 |  |  |  |  | 115 |  |  |  |  | 120 | [5 empty] | 6 | 12 |  |  | 158866.6667 | 164075 | [7 empty] | 171875 | 494816.6667
NUMBER WASHED |  | 3 | 3 | 3 | 1 | 3 | 1 | 4 | 4 | 0 | 2 | 2 | 3 | 3 | 3 | 2 | 1 | 4 | 3 | 3 | 1 | 1 | 4 | 3 | 4 | 1 | 2 | 2 | 4 | 0 | 0 | 0 | 0 |  | 13 |  | 160950 |  |  | 158866.6667 |  |  |  |  | 166666.6667 |  |  | 486483.3333
GAL USED |  | 519295.8333 | 500012.5 | 488045.8333 | 158866.6667 | 537537.5 | 169283.3333 | 682316.6667 | 675025 | 0 | 325545.8333 | 324504.1667 | 494816.6667 | 486483.3333 | 501575 | 328150 | 164075 | 664100 | 500025 | 505741.6667 | 170325 | 169283.3333 | 710975 | 505233.3333 | 671900 | 164075 | 343775 | 321366.6667 | 678150 | 0 | 0 | 0 | 11760483.3333 |  | 14 | 161991.6667 | [7 empty] | 169791.6667 |  | 169791.6667 |  | 501575
| UV TIMES 100 | 20.9 | 21.6833 | 23.5 | 28.3667 | 33.5 | 35.6333 | 34.05 | 31.25 | 27.8167 | 27.2667 | 31.0833 | 27.35 | 26.0333 | 28.15 | 28.7167 | 27.8167 | 25.5667 | 26.9833 | 27.6 | 28.2667 | 27.9 | 29 | 29.4333 | 30.2333 | 31.6333 | 35.1167 | 36.7833 | 37.55 | [5 empty] | 15 | [5 empty] | 164075 | 164075 | [5 empty] | 328150
[35 empty] | 16 | [7 empty] | 164075 |  |  |  |  | 164075
[35 empty] | 17 |  |  | 164075 | 164075 | 164075 | [6 empty] | 171875 | 664100
[35 empty] | 18 | 164075 | 164075 | [7 empty] | 171875 |  |  | 500025
[35 empty] | 19 | [6 empty] | 165116.6667 |  | 170312.5 |  | 170312.5 |  | 505741.6667
[35 empty] | 20 | [5 empty] | 170325 | [6 empty] | 170325
[35 empty] | 21 | [7 empty] | 169283.3333 |  |  |  |  | 169283.3333
[35 empty] | 22 |  |  | 174491.6667 | 174491.6667 | 174491.6667 | [6 empty] | 187500 | 710975
[35 empty] | 23 | 164075 | 169283.3333 | [7 empty] | 171875 |  |  | 505233.3333
[35 empty] | 24 | [5 empty] | 164075 | 164075 |  | 171875 |  | 171875 |  | 671900
[35 empty] | 25 | [7 empty] | 164075 |  |  |  |  | 164075
[35 empty] | 26 |  |  |  | 171887.5 | 171887.5 | [7 empty] | 343775
[35 empty] | 27 |  |  | 167720.8333 | [8 empty] | 153645.8333 | 321366.6667
[35 empty] | 28 | 170845.8333 | 170845.8333 | [6 empty] | 157812.5 | 178645.8333 |  |  | 678150
[35 empty] | 29 | [12 empty] | 0
[35 empty] | 30 | [12 empty] | 0
[35 empty] | 31 | [12 empty] | 0

## Total Flows
Water Production and Waste (MGD) | [7 empty] | 2018-02-01
Day | Raw Flow | Finished 1 Flow | Finished 2 Flow | Combined Finished | Finished South Meter 1 | Finished South Meter 2 | Finished Conway #66 | Finished Perry #67 | Blowdown | Backwash | Decant Flow | Decant Actual Flow | Plant 1 Raw Flow, MGD | Plant 2 Raw Flow, MGD | Plant 3 Raw Flow, MGD | Plant 1 Polymer Dose, mg/L | Plant 2 Polymer Dose, mg/L | Plant 3 Polymer Dose, mg/L | Plant 1 Settled Turb. | Plant 2 Settled Turb. | Plant 3 Settled Turb.
1 | 25.755 | 9.928 | 14.638 | 24.566 | 4.743 | 5.185 | 4.703 | 9.935 | 0.60328 | 0.5193 | 1.263 | 1.0066 | 6 | 10.275 | 10.3 | 211.25 | 255.625 | 226.25 | 0.4065 | 0.43575 | 0.51275
2 | 26.148 | 9.306 | 13.016 | 22.322 | 4.105 | 5.201 | 4.243 | 8.773 | 0.54751 | 0.50001 | 1.376 | 0.93168 | 5.7333 | 9.9667 | 10.1 | 154.1667 | 218.3333 | 195 | 0.3515 | 0.4085 | 0.4725
3 | 28.135 | 10.358 | 14.14 | 24.498 | 4.527 | 5.831 | 4.245 | 9.895 | 0.49872 | 0.48805 | 1.241 | 1.4011 | 5.7 | 9.8667 | 9.9333 | 138.3333 | 231.6667 | 203.3333 | 0.33075 | 0.4135 | 0.43325
4 | 27.554 | 11.23 | 14.577 | 25.807 | 5.355 | 5.875 | 4.279 | 10.298 | 0.52325 | 0.15887 | 1.051 | 1.4904 | 6.88 | 10.54 | 10.54 | 155 | 224.5 | 207.5 | 0.41475 | 0.48525 | 0.471
5 | 25.357 | 10.061 | 13.183 | 23.244 | 4.335 | 5.726 | 4.149 | 9.034 | 0.97678 | 0.53754 | 1.306 | 0.87552 | 5.8 | 10.2333 | 10.2333 | 153.3333 | 250 | 230.8333 | 0.62975 | 0.5515 | 0.62525
6 | 25.517 | 9.875 | 13.733 | 23.608 | 4.328 | 5.547 | 4.065 | 9.668 | 0.60438 | 0.16928 | 1.097 | 1.5466 | 5 | 10.25 | 10.25 | 197.5 | 280 | 268.75 | 0.5545 | 0.4995 | 0.52575
7 | 27.954 | 12.019 | 18.518 | 30.537 | 5.726 | 6.293 | 5.424 | 13.094 | 0.75889 | 0.68232 | 1.3 | 0.93744 | 8 | 10 | 10 | 268.3333 | 283.3333 | 276.6667 | 0.5535 | 0.49025 | 0.628
8 | 27.561 | 10.379 | 15.218 | 25.597 | 5.114 | 5.265 | 4.564 | 10.654 | 0.96053 | 0.67502 | 2.063 | 1.8029 | 9.1667 | 9.1667 | 9.1667 | 310 | 336.6667 | 256.6667 | 0.497 | 0.35325 | 0.4955
9 | 24.431 | 9.519 | 13.35 | 22.869 | 4.044 | 5.475 | 3.92 | 9.43 | 0.83823 | 0 | 1.258 | 2.2867 | 8.25 | 8.25 | 8.25 | 262.5 | 270 | 213.75 | 0.46175 | 0.3455 | 0.435
10 | 26.106 | 9.714 | 14.522 | 24.236 | 4.672 | 5.042 | 4.014 | 10.508 | 0.92958 | 0.32555 | 1.447 | 1.2384 | 8.625 | 8.625 | 8.625 | 248.75 | 253.75 | 216.25 | 0.515 | 0.32625 | 0.441
11 | 26.755 | 10.121 | 14.84 | 24.961 | 4.153 | 5.968 | 4.291 | 10.549 | 1.0625 | 0.3245 | 1.528 | 1.5264 | 8.9 | 8.8667 | 8.9 | 286.6667 | 266.6667 | 210 | 0.5955 | 0.5035 | 0.52775
12 | 26.213 | 9.416 | 14.404 | 23.82 | 3.995 | 5.421 | 3.953 | 10.451 | 0.94134 | 0.49482 | 1.319 | 1.525 | 8.5667 | 8.5667 | 8.5667 | 261.6667 | 248.3333 | 210 | 0.5645 | 0.4945 | 0.50475
13 | 25.197 | 8.403 | 15.165 | 23.568 | 3.029 | 5.374 | 3.979 | 11.186 | 0.7636 | 0.48648 | 1.61 | 2.1456 | 8.2 | 8.2 | 8.2 | 228.3333 | 241.6667 | 186.6667 | 0.42 | 0.3375 | 0.44325
14 | 26.105 | 9.525 | 14.557 | 24.082 | 3.74 | 5.785 | 3.662 | 10.895 | 0.63359 | 0.50158 | 1.488 | 1.1779 | 8.6 | 8.6 | 8.6 | 241.6667 | 237.5 | 171.6667 | 0.4545 | 0.48975 | 0.388
15 | 26.558 | 10.307 | 14.535 | 24.842 | 4.807 | 5.5 | 4.02 | 10.515 | 0.53924 | 0.32815 | 1.058 | 0.81216 | 9 | 9 | 9 | 256.6667 | 250 | 185.8333 | 0.3395 | 0.39375 | 0.39525
16 | 27.109 | 10.995 | 14.323 | 25.318 | 5.261 | 5.734 | 4.251 | 10.072 | 0.55233 | 0.16407 | 0.936 | 1.0135 | 9 | 9 | 9 | 255 | 243.3333 | 171.6667 | 0.3695 | 0.41175 | 0.4035
17 | 26.743 | 11.093 | 14.258 | 25.351 | 5.231 | 5.862 | 4.521 | 9.737 | 0.54314 | 0.6641 | 1.413 | 0.85274 | 9 | 9 | 9 | 253.3333 | 243.3333 | 158.3333 | 0.34975 | 0.43125 | 0.40425
18 | 26.522 | 10.975 | 13.286 | 24.261 | 4.979 | 5.996 | 4.111 | 9.175 | 0.53351 | 0.50003 | 1.501 | 0.95111 | 9 | 9 | 9 | 258.3333 | 250 | 160 | 0.32275 | 0.3905 | 0.41325
19 | 26.638 | 10.753 | 13.374 | 24.127 | 4.816 | 5.937 | 4.444 | 8.93 | 0.54931 | 0.50574 | 1.332 | 1.3652 | 9.55 | 9.425 | 7.325 | 250 | 248.75 | 131.25 | 0.38225 | 0.394 | 0.3695
20 | 23.989 | 11.101 | 12.039 | 23.14 | 5.105 | 5.996 | 4.199 | 7.84 | 0.63307 | 0.17033 | 1.732 | 0.20016 | 9.15 | 9.15 | 4.8 | 262.5 | 257.5 | 125 | 0.45475 | 0.46725 | 0.4575
21 | 24.843 | 10.399 | 13.187 | 23.586 | 4.879 | 5.52 | 4.11 | 9.077 | 0.73948 | 0.16928 | 1.299 | 1.2467 | 10 | 10 | 5.3 | 350 | 326.6667 | 150 | 0.334 | 0.38225 | 0.3975
22 | 28.185 | 11.76 | 14.16 | 25.92 | 5.73 | 6.03 | 4.48 | 9.68 | 0.99554 | 0.71098 | 1.793 | 1.2931 | 10.3333 | 10.3333 | 7 | 348.3333 | 325 | 245 | 0.4215 | 0.4055 | 0.4645
23 | 27.575 | 11.31 | 13.55 | 24.86 | 5.44 | 5.87 | 4.2 | 9.35 | 0.85647 | 0.50523 | 1.501 | 1.2787 | 9.1333 | 9.1 | 9.1333 | 303.3333 | 296.6667 | 288.3333 | 0.246 | 0.238 | 0.3245
24 | 26.96 | 10.7 | 14.11 | 24.81 | 5.165 | 5.535 | 3.99 | 10.12 | 0.8739 | 0.6719 | 1.783 | 1.1693 | 9.1333 | 9.1 | 9.1333 | 310 | 310 | 293.3333 | 0.23425 | 0.2025 | 0.36425
25 | 26.315 | 11.09 | 13.74 | 24.83 | 5.48 | 5.61 | 4.4 | 9.34 | 0.88021 | 0.16407 | 1.287 | 1.3824 | 9 | 9 | 9 | 315 | 310 | 291.6667 | 0.303 | 0.24225 | 0.32775
26 | 27.465 | 10.495 | 14.315 | 24.81 | 5 | 5.495 | 4.085 | 10.23 | 0.75495 | 0.34377 | 1.738 | 1.0627 | 10.5 | 10.5 | 6 | 388 | 390 | 388 | 0.41075 | 0.326 | 0.31325
27 | 25.18 | 10.095 | 13.935 | 24.03 | 4.805 | 5.29 | 4.885 | 9.05 | 0.80996 | 0.32137 | 1.793 | 1.6877 | 9.9333 | 9.9333 | 5.8667 | 376.6667 | 363.3333 | 220 | 0.35575 | 0.30075 | 0.38575
28 | 22.15 | 8.197 | 10.278 | 18.475 | 3.957 | 4.24 | 2.669 | 7.609 | 1.0227 | 0.67815 | 1.37 | 1.5782 | 10.0667 | 10.0667 | 6.2 | 361.6667 | 358.3333 | 259.1667 | 0.35575 | 0.288 | 0.388
29 | [11 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
30 | [11 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
31 | [11 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Total | 735.02 | 289.124 | 392.951 | 682.075 | 132.521 | 156.603 | 117.856 | 275.095 | 20.926 | 11.7605 | 39.883 |  | 236.2217 | 264.015 | 237.4233 | #DIV/0! | #DIV/0! | #DIV/0! | 11.629 | 11.0083 | 12.3125
Average | 26.2507 | 10.3259 | 14.034 | 24.3598 | 4.7329 | 5.593 | 4.2091 | 9.8248 | 0.74736 | 0.42002 | 1.4244 |  | 8.4365 | 9.4291 | 8.4794 | #DIV/0! | #DIV/0! | #DIV/0! | 0.41532 | 0.39315 | 0.43973
Maximum | 28.185 | 12.019 | 18.518 | 30.537 | 5.73 | 6.293 | 5.424 | 13.094 | 1.0625 | 0.71098 | 2.063 |  | 10.5 | 10.54 | 10.54 | #DIV/0! | #DIV/0! | #DIV/0! | 0.62975 | 0.5515 | 0.628
Minimum | 22.15 | 8.197 | 10.278 | 18.475 | 3.029 | 4.24 | 2.669 | 7.609 | 0.49872 | 0 | 0.936 |  | 5 | 8.2 | 4.8 | #DIV/0! | #DIV/0! | #DIV/0! | 0.23425 | 0.2025 | 0.31325
Finished Water Pumped (from South + Conway+ Perry Meters) | [7 empty] | 682.075
Finished Water Pumped (Raw Flow - Blowdown + Backwash) | [7 empty] | 702.3335
Finished Water Pumped (Raw Flow -Decant + Sludge) | [7 empty] | 691.137
Total Decant Flow |  |  | 39.883 |  |  | MG
Total Sudge Pumped (est) |  |  | 4
Total Blowdown Flow |  |  | 20.926
Total Backwash Flow |  |  | 11.7605
Total Waste Flow from Decant and Sludge | [7 empty] | 43.883
Total Waste Flow from Blowdown and Backwash | [7 empty] | 32.6865

## Flows
Surface Water System Monthly Operation Report
Water Production Log
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  | 2018-02-01
Plant Name: Bull Creek SWTP |  |  | Plant Id #: | A26001 |  | Capacity (MGD): 45
| Number and Grade of Operator in Charge |  | Hours in Operation | Water Pumped (MG) |  |  |  | Peak Hourly Flow Rate (MGD)
Day | 1st Shift | 2nd Shift |  | Raw | Finished1 | Finished2 | Combined
1 | 17 | 18 | 24 | 25.755 | 9.928 | 14.638 | 24.566 | 27.1
2 | 17 | 18 | 24 | 26.148 | 9.306 | 13.016 | 22.322 | 27
3 | 17 | 18 | 24 | 28.135 | 10.358 | 14.14 | 24.498 | 28.5
4 | 17 | 18 | 24 | 27.554 | 11.23 | 14.577 | 25.807 | 29
5 | 17 | 18 | 24 | 25.357 | 10.061 | 13.183 | 23.244 | 27.6
6 | 17 | 18 | 24 | 25.517 | 9.875 | 13.733 | 23.608 | 27
7 | 5 | 4 | 24 | 27.954 | 12.019 | 18.518 | 30.537 | 28.5
8 | 5 | 4 | 24 | 27.561 | 10.379 | 15.218 | 25.597 | 28.5
9 | 5 | 4 | 24 | 24.431 | 9.519 | 13.35 | 22.869 | 25.5
10 | 5 | 4 | 24 | 26.106 | 9.714 | 14.522 | 24.236 | 27
11 | 5 | 4 | 24 | 26.755 | 10.121 | 14.84 | 24.961 | 27.9
12 | 5 | 4 | 24 | 26.213 | 9.416 | 14.404 | 23.82 | 27
13 | 5 | 4 | 24 | 25.197 | 8.403 | 15.165 | 23.568 | 25.8
14 | 18 | 17 | 24 | 26.105 | 9.525 | 14.557 | 24.082 | 26.3
15 | 18 | 17 | 24 | 26.558 | 10.307 | 14.535 | 24.842 | 27
16 | 18 | 17 | 24 | 27.109 | 10.995 | 14.323 | 25.318 | 27.5
17 | 18 | 17 | 24 | 26.743 | 11.093 | 14.258 | 25.351 | 27
18 | 18 | 17 | 24 | 26.522 | 10.975 | 13.286 | 24.261 | 27
19 | 18 | 17 | 24 | 26.638 | 10.753 | 13.374 | 24.127 | 27
20 | 18 | 17 | 24 | 23.989 | 11.101 | 12.039 | 23.14 | 24.4
21 | 4 | 5 | 24 | 24.843 | 10.399 | 13.187 | 23.586 | 28
22 | 18 | 5 | 24 | 28.185 | 11.76 | 14.16 | 25.92 | 28.5
23 | 4 | 5 | 24 | 27.575 | 11.31 | 13.55 | 24.86 | 28.1
24 | 4 | 5 | 24 | 26.96 | 10.7 | 14.11 | 24.81 | 28.1
25 | 4 | 5 | 24 | 26.315 | 11.09 | 13.74 | 24.83 | 27
26 | 4 | 5 | 24 | 27.465 | 10.495 | 14.315 | 24.81 | 27.8
27 | 4 | 5 | 24 | 25.18 | 10.095 | 13.935 | 24.03 | 27
28 | 17 | 5 | 24 | 22.15 | 8.197 | 10.278 | 18.475 | 26.9
29
30
31
Total |  |  | 672 | 735.02 | 289.124 | 392.951 | 682.075 | 764
Average |  |  | 24 | 26.2507 | 10.3259 | 14.034 | 24.3598 | 27.2857
Maximum |  |  | 24 | 28.185 | 12.019 | 18.518 | 30.537 | 29
Minimum |  |  | 24 | 22.15 | 8.197 | 10.278 | 18.475 | 24.4
| #3-Lederman A | #4-Hughes B #5-Nicolosi B | #12-Eaddy A #20 Brookover A | #14-Wall A #16-Eaton A | #17-Holden B #18-Mercer A
Prepared by: ___________________________________________ |  |  |  |  | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## Raw & Coagulated
Surface Water System Monthly Operation Report
Chemical & Physical Analyses of
Raw, Coagulated, & Settled Water
Bureau of Water
System Name: Grand Strand Regional | [6 empty] | System Number: 2620004
Certified Lab ID#: 26102 | [6 empty] | 2018-02-01
| Raw Water | [6 empty] | Coagulated Water |  | Settled Water
Day | pH | Alkalinity (mg/L) | Temp (oC) | Hardness (mg/L) | Turbidity (NTU) | True Color (CU) | Apparent Color (CU) | pH | Alkalinity (mg/L) | Turbidity (NTU) | Disinfectant Residual (mg/L)
1 | 6.95 | 24.5 | 10.95 | 18.8333 | 12.1 | 42.3333 | 110.5 | 5.9822 | 10.1111 | 0.563 | 0.56
2 | 6.8867 | 24.1667 | 10.9833 | 19.5 | 42.3 | 40.8333 | 240.8333 | 5.9056 | 9.3889 | 0.504 | 0.5
3 | 6.8267 | 23.1667 | 10.3167 | 21.1667 | 41.5 | 44.6667 | 260.6667 | 5.9689 | 9 | 0.471 | 0.48
4 | 6.8083 | 22.1667 | 9.9333 | 21.8333 | 30.1 | 50.1667 | 224.6667 | 5.8167 | 9.4444 | 0.593 | 0.59
5 | 6.7867 | 22.6667 | 10.7833 | 21.1667 | 25.9 | 63.1667 | 203.3333 | 5.8222 | 8.7778 | 0.899 | 0.37
6 | 6.7983 | 21 | 10.9667 | 20.5 | 21.8 | 65.3333 | 189.6667 | 5.9228 | 8.8889 | 0.589 | 0.55
7 | 6.75 | 22.3333 | 11.8833 | 19.6667 | 28.2 | 65.8333 | 215.5 | 5.9617 | 10.2222 | 0.722 | 0.54
8 | 6.7667 | 19.5 | 12.7667 | 19.3333 | 33.6 | 65.8333 | 245.3333 | 5.9833 | 9.1143 | 0.571 | 0.54
9 | 6.7833 | 20.6667 | 12.5167 | 17.6667 | 40.8 | 55.3333 | 282 | 5.9556 | 9.7222 | 0.505 | 0.54
10 | 6.7483 | 20.8333 | 12.55 | 17.5 | 35 | 52.1667 | 249.6667 | 5.8978 | 9.2222 | 0.737 | 0.57
11 | 6.6833 | 19.5 | 13.1833 | 17.1667 | 44.9 | 61.6667 | 315.8333 | 5.9272 | 8.2778 | 0.661 | 0.47
12 | 6.725 | 19.6667 | 13.9167 | 16.5 | 44.2 | 56.6667 | 300.8333 | 5.9658 | 8.8889 | 0.664 | 0.52
13 | 6.7333 | 19.5 | 13.9833 | 15 | 33 | 50 | 240.8333 | 5.9272 | 7.5 | 0.495 | 0.5
14 | 6.61 | 21.1667 | 13.2667 | 18.8333 | 29.2 | 54.5 | 215.5 | 5.9633 | 9.2222 | 0.599 | 0.47
15 | 6.7033 | 21.8333 | 13.8167 | 19 | 28.7 | 57.6667 | 218.5 | 5.98 | 10.3333 | 0.479 | 0.59
16 | 6.6933 | 21.6667 | 14.4667 | 20.1667 | 25.9 | 56.5 | 211 | 6.0817 | 9.9444 | 0.505 | 0.62
17 | 6.7383 | 22 | 14.6667 | 19.8333 | 21.3 | 51.6667 | 173.1667 | 6.1428 | 10.8333 | 0.475 | 0.6
18 | 6.6783 | 21.3333 | 14.8833 | 19.5 | 18.8 | 52.3333 | 153.8333 | 6.0317 | 10.2778 | 0.476 | 0.58
19 | 6.6567 | 21.3333 | 15.25 | 20 | 15.9 | 53.3333 | 147.3333 | 6.0456 | 10.6111 | 0.471 | 0.47
20 | 6.6483 | 23.3333 | 15.85 | 19.6667 | 14 | 54.8333 | 132 | 6.01 | 10.1111 | 0.583 | 0.3
21 | 6.4767 | 22.5 | 16.85 | 20 | 12.8 | 55 | 124.3333 | 5.9656 | 10.8889 | 0.465 | 0.33
22 | 6.62 | 23 | 17.35 | 19 | 9.01 | 59.3333 | 111.5 | 5.96 | 10.1111 | 0.592 | 0.46
23 | 6.6167 | 23.3333 | 17.6667 | 19 | 8.91 | 56.3333 | 114 | 5.9561 | 11.3889 | 0.41 | 0.47
24 | 6.6233 | 21 | 18.2667 | 18.5 | 8.24 | 58 | 110.8333 | 5.9767 | 9.9444 | 0.436 | 0.46
25 | 6.6317 | 21.3333 | 18.8167 | 16.1667 | 7.55 | 65.8333 | 114.1667 | 5.9889 | 9.8333 | 0.369 | 0.41
26 | 6.575 | 22 | 19.1833 | 17.1667 | 8.3 | 72 | 123.8333 | 5.9444 | 9.8889 | 0.501 | 0.36
27 | 6.585 | 23 | 18.55 | 18.8333 | 9.9 | 73.6667 | 130.3333 | 5.9283 | 10.8889 | 0.561 | 0.34
28 | 6.6017 | 23.8333 | 17.55 | 19.5 | 8.4 | 74.6667 | 127.3333 | 5.9872 | 11.8333 | 0.476 | 0.4
29
30
31
Avg. | 6.7037 | 21.869 | 14.3274 | 18.9643 | 23.5825 | 57.4881 | 188.8333 | 5.9643 | 9.8096 | 0.549 | 0.48536
Max. | 6.95 | 24.5 | 19.1833 | 21.8333 | 44.9 | 74.6667 | 315.8333 | 6.1428 | 11.8333 | 0.899 | 0.62
Min. | 6.4767 | 19.5 | 9.9333 | 15 | 7.55 | 40.8333 | 110.5 | 5.8167 | 7.5 | 0.369 | 0.3
Prepared by: ____________________________________________ | [7 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## Finished
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2018-02-01
Finished Water 1
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.3067 | 27.5 | 10.25 | 3.8 |  |  | 29.5 | 0.062 | 1 | 0.5262
2 | 7.3233 | 26 | 10.1167 | 3.5 |  |  | 21 | 0.063 | 1 | N/A
3 | 7.3317 | 21.5 | 9.6667 | 3.8 |  |  | 20 | 0.067 | 1 | 0.4807
4 | 7.5317 | 22.5 | 9.3167 | 4.2 |  |  | 22.5 | 0.063 | 1 | 0.4979
5 | 7.675 | 25.5 | 9.9833 | 3.9 |  |  | 37 | 0.07 | 1 | 0.5343
6 | 7.69 | 26 | 10.35 | 4.1 | 0.32 | 0.006 | 47 | 0.062 | 1.3333 | 0.4845
7 | 7.7283 | 24.5 | 10.8 | 3.8 |  |  | 39.5 | 0.064 | 1 | 0.4761
8 | 7.6967 | 25 | 11.55 | 3.6 |  |  | 44 | 0.084 | 1.1667 | 0.5768
9 | 7.6717 | 24 | 11.4 | 3.7 |  |  | 41 | 0.055 | 1 | 0.5061
10 | 7.4567 | 22 | 11.5333 | 3 |  |  | 33 | 0.089 | 1.1667 | 0.4356
11 | 7.9517 | 22 | 12.4833 | 3.8 |  |  | 29 | 0.074 | 1 | 0.5693
12 | 7.6383 | 21.5 | 13.1333 | 3.8 |  |  | 37.5 | 0.067 | 1.1667 | 0.5351
13 | 7.56 | 22.5 | 13.3167 | 3.5 |  |  | 36 | 0.063 | 1.6667 | 0.4325
14 | 7.4567 | 22.5 | 12.8833 | 3.4 |  |  | 39.5 | 0.059 | 1.1667 | 0.5533
15 | 7.6667 | 24 | 13.3833 | 3.3 |  |  | 43 | 0.069 | 1.1667 | 0.5495
16 | 7.445 | 22 | 13.8167 | 4.1 |  |  | 43 | 0.063 | 1 | 0.5021
17 | 7.7667 | 23.5 | 14.15 | 4.4 |  |  | 38 | 0.074 | 1 | 0.5777
18 | 7.455 | 22.5 | 14.25 | 4.2 |  |  | 33.5 | 0.063 | 1 | 0.5205
19 | 7.3233 | 24 | 14.5333 | 4 | 0.36 | 0.012 | 36 | 0.067 | 1 | 0.543
20 | 7.43 | 26 | 15.0667 | 3.9 |  |  | 32 | 0.069 | 1 | 0.568
21 | 7.1567 | 26 | 15.9167 | 3.8 |  |  | 32.5 | 0.062 | 1.1667 | 0.4817
22 | 7.0533 | 23.5 | 16.4167 | 3.4 |  |  | 31.5 | 0.065 | 1 | 0.5872
23 | 7.5717 | 26 | 16.85 | 3.4 |  |  | 32.5 | 0.064 | 1 | 0.6262
24 | 7.5633 | 22 | 17.1667 | 3.7 |  |  | 29.5 | 0.063 | 1.3333 | 0.536
25 | 7.4783 | 20 | 17.7167 | 3.9 |  |  | 29 | 0.059 | 1 | 0.5392
26 | 7.285 | 26 | 18.2667 | 3.7 |  |  | 39 | 0.07 | 1.8333 | 0.5403
27 | 7.4483 | 25.5 | 18 | 4.1 |  |  | 38 | 0.06 | 1.3333 | 0.5447
28 | 7.3083 | 28 | 17.1833 | 4.2 |  |  | 49 | 0.075 | 1 | 0.6128
29
30
31
Avg. | 7.4989 | 24 | 13.5536 | 3.7857 | 0.34 | 0.009 | 35.1071 | 0.066607 | 1.125 | 0.53101
Max. | 7.9517 | 28 | 18.2667 | 4.4 | 0.36 | 0.012 | 49 | 0.089 | 1.8333 | 0.6262
Min. | 7.0533 | 20 | 9.3167 | 3 | 0.32 | 0.006 | 20 | 0.055 | 1 | 0.4325
Notes: | Phosphate reported as P
Lab Quality Control
Prepared by: ____________________________________________ | [6 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## Finished2
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2018-02-01
Finished Water 2
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.5917 | 28.5 | 10.8833 | 3.9 |  |  | 31 | 0.063 | 1 | 0.7274
2 | 7.8233 | 25.5 | 11.0667 | 3.7 |  |  | 20.5 | 0.066 | 1 | N/A
3 | 7.615 | 22.5 | 10.4 | 3.5 |  |  | 19.5 | 0.056 | 1 | 0.5952
4 | 7.69 | 21.5 | 10.3833 | 3.7 |  |  | 23.5 | 0.067 | 1 | 0.6308
5 | 7.915 | 26 | 10.7833 | 3.9 |  |  | 38.5 | 0.073 | 1 | 0.7167
6 | 7.8517 | 26 | 11.2833 | 4 | 0.42 | 0.007 | 46.5 | 0.068 | 1.3333 | 0.7037
7 | 7.6283 | 21.5 | 11.4167 | 3.5 |  |  | 40.5 | 0.069 | 1 | 0.6108
8 | 7.5317 | 22.5 | 12.45 | 3.7 |  |  | 42.5 | 0.068 | 1.1667 | 0.6654
9 | 7.5533 | 21.5 | 12.4167 | 3.6 |  |  | 38 | 0.062 | 1 | 0.603
10 | 7.4267 | 22.5 | 12.3 | 3.2 |  |  | 32.5 | 0.066 | 1 | 0.502
11 | 7.5383 | 20 | 13.1333 | 3 |  |  | 30 | 0.071 | 1 | 0.5466
12 | 7.5 | 23 | 13.75 | 3.5 |  |  | 37 | 0.067 | 1.1667 | 0.5511
13 | 7.4633 | 21 | 13.8833 | 3.4 |  |  | 33.5 | 0.065 | 1.3333 | 0.4979
14 | 7.4433 | 22 | 12.95 | 3.2 |  |  | 40 | 0.063 | 1.1667 | 0.6278
15 | 7.7333 | 24 | 13.25 | 3.4 |  |  | 42 | 0.074 | 1.1667 | 0.5941
16 | 7.535 | 21.5 | 14.0667 | 3.5 |  |  | 44.5 | 0.063 | 1 | 0.5475
17 | 7.81 | 23 | 14.0667 | 2.8 |  |  | 38.5 | 0.07 | 1 | 0.5498
18 | 7.4267 | 23 | 14.1667 | 3.1 |  |  | 34 | 0.061 | 1 | 0.5977
19 | 7.3667 | 24.5 | 14.3833 | 3.5 | 0.37 | 0.009 | 36 | 0.059 | 1 | 0.607
20 | 7.6867 | 25.5 | 15.0333 | 3.5 |  |  | 33.5 | 0.074 | 1 | 0.6192
21 | 7.3133 | 25 | 15.6 | 3.3 |  |  | 36.5 | 0.069 | 1.1667 | 0.578
22 | 7.2517 | 24.5 | 16.3667 | 3.4 |  |  | 32.5 | 0.064 | 1.1667 | 0.6062
23 | 7.2517 | 25.5 | 16.6667 | 3.4 |  |  | 31.5 | 0.064 | 1.1667 | 0.6497
24 | 7.7783 | 23 | 16.9 | 3.4 |  |  | 30 | 0.058 | 1.3333 | 0.6385
25 | 7.47 | 23 | 17.3 | 3.6 |  |  | 28 | 0.059 | 1.3333 | 0.5945
26 | 7.3533 | 25.5 | 17.4333 | 3.4 |  |  | 39 | 0.065 | 1.8333 | 0.6041
27 | 7.62 | 29.5 | 17.1833 | 3.9 |  |  | 38 | 0.06 | 1.3333 | 0.6986
28 | 7.425 | 27.5 | 16.5167 | 4.3 |  |  | 49 | 0.072 | 1 | 0.7037
29
30
31
Avg. | 7.5569 | 23.8929 | 13.7869 | 3.5107 | 0.395 | 0.008 | 35.2321 | 0.065571 | 1.131 | 0.61359
Max. | 7.915 | 29.5 | 17.4333 | 4.3 | 0.42 | 0.009 | 49 | 0.074 | 1.8333 | 0.7274
Min. | 7.2517 | 20 | 10.3833 | 2.8 | 0.37 | 0.007 | 19.5 | 0.056 | 1 | 0.4979
Notes: | Phosphate reported as P
Lab Quality Control
Prepared by: ____________________________________________ | [6 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## Chems lbs
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2018-02-01
Pounds or Gallons of Chemicals Used
Day | Pre Disinf (gal) | Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | Post Disenfectant (gal) (gal) |  | Post-pH (gal) | Fluoride (gal) | Phosphate (gal) | Zinc (gal) | Filter Aid (gal) | Polymer (gal) | Pre-pH (gal) | PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 255.8153 | 1606.8875 |  |  | 601.5709 | 90.7782 | 248.7328 | 48.9773 | 44.4335 | 6.3177 | 2.6452 | 3.5253 |  | 650
2 | 255.2298 | 1643.0766 |  |  | 565.2732 | 86.1729 | 234.2354 | 43.9822 | 42.1516 | 5.8814 | 2.612 | 2.8319 |  | 650
3 | 283.6711 | 1777.1829 |  | 84.2 | 616.787 | 90.3072 | 263.247 | 47.9075 | 46.3365 | 6.6653 | 2.5237 | 3.1127 |  | 650
4 | 274.102 | 1865.2262 |  | 362.06 | 644.7178 | 97.8507 | 261.4276 | 46.8197 | 48.573 | 6.7346 | 2.7237 | 3.065 |  | 650
5 | 279.5029 | 2125.2589 |  | 1060.92 | 586.0235 | 90.1666 | 231.9568 | 47.5952 | 43.8113 | 6.4218 | 2.6594 | 2.9895 |  | 650
6 | 308.0613 | 2755.2296 |  | 1852.4 | 588.1131 | 94.8694 | 217.5463 | 46.6144 | 44.493 | 6.2976 | 2.6073 | 3.7899 |  | 650
7 | 334.2009 | 2908.1326 |  | 1692.42 | 764.9894 | 118.1032 | 257.0625 | 63.4595 | 58.2222 | 8.2773 | 2.7729 | 5.2623 |  | 715
8 | 365.8859 | 2644.5605 |  | 1338.78 | 650.4527 | 96.3676 | 209.2192 | 50.7427 | 48.1265 | 6.8785 | 2.7319 | 4.7072 |  | 640
9 | 319.7848 | 2139.8527 |  | 1060.92 | 578.9845 | 84.1119 | 188.6493 | 44.3842 | 43.6039 | 6.2981 | 2.4606 | 3.8466 |  | 600
10 | 309.4801 | 1997.8847 |  | 766.22 | 620.4178 | 89.1276 | 202.7897 | 49.0035 | 45.4262 | 6.4439 | 2.5363 | 3.7646 |  | 675
11 | 298.8621 | 2293.6234 |  | 799.9 | 622.8401 | 93.6568 | 213.8877 | 50.7442 | 45.6243 | 6.5075 | 2.7004 | 3.9957 |  | 650
12 | 312.893 | 2177.5429 |  | 1060.92 | 608.3587 | 88.3501 | 208.093 | 64.5718 | 44.8699 | 4.4691 | 2.5521 | 3.7296 |  | 575
13 | 295.0727 | 2356.3469 |  | 993.56 | 595.8971 | 88.5641 | 194.0611 | 59.9581 | 38.0128 | 4.4985 | 2.4543 | 3.5183 |  | 650
14 | 281.584 | 2434.0147 |  | 1490.34 | 608.6377 | 89.2441 | 214.9497 | 62.2138 | 39.13 | 4.7715 | 2.6278 | 3.3963 |  | 650
15 | 299.351 | 2503.3312 |  | 1305.1 | 644.3595 | 89.6314 | 247.6481 | 64.0693 | 46.4072 | 4.6905 | 2.7319 | 3.5621 |  | 650
16 | 308.5515 | 2551.4503 |  | 2542.84 | 637.3645 | 81.9637 | 247.2197 | 65.297 | 46.8088 | 4.7804 | 2.7288 | 3.5124 |  | 650
17 | 303.3239 | 2515.7476 |  | 1566.12 | 662.087 | 85.203 | 242.855 | 65.3821 | 47.2604 | 4.7866 | 2.7256 | 3.4383 |  | 600
18 | 304.9124 | 2494.9579 |  | 1397.72 | 617.5413 | 77.6425 | 221.7323 | 62.5709 | 45.789 | 4.5808 | 2.7256 | 3.3574 |  | 600
19 | 288.6005 | 2388.3385 |  | 1330.36 | 622.1229 | 82.4848 | 233.3491 | 64.205 | 48.1435 | 4.9014 | 2.6901 | 3.1924 |  | 600
20 | 237.6768 | 1863.6506 |  | 2323.92 | 589.6654 | 83.831 | 212.9006 | 60.728 | 41.9874 | 4.7009 | 2.3612 | 3.6301 |  | 600
21 | 281.6338 | 2072.5806 |  | 1027.24 | 591.957 | 88.3165 | 212.9302 | 60.0365 | 44.808 | 4.6082 | 2.3975 | 4.1835 |  | 700
22 | 347.3517 | 2413.8159 |  | 2323.92 | 641.6696 | 93.2715 | 248.2847 | 69.6459 | 48.7119 | 4.8367 | 2.6657 | 4.8686 |  | 700
23 | 324.8039 | 2390.5816 |  | 2323.92 | 626.5663 | 90.1879 | 260.873 | 69.7016 | 46.345 | 4.6939 | 2.7414 | 4.5124 |  | 700
24 | 321.1279 | 2337.2649 |  | 2323.92 | 634.7994 | 94.4823 | 253.2088 | 69.6826 | 46.0607 | 4.6845 | 2.7572 | 4.6317 |  | 700
25 | 313.4451 | 2257.4596 |  | 2323.92 | 634.1467 | 96.2766 | 238.124 | 67.3131 | 46.2891 | 4.6882 | 2.7666 | 4.7129 |  | 700
26 | 335.5034 | 2732.1893 |  | 2323.92 | 634.1543 | 96.898 | 237.2041 | 66.459 | 45.8696 | 4.6845 | 2.7578 | 5.9049 |  | 700
27 | 310.2509 | 2740.6976 |  | 2323.92 | 615.5519 | 94.8617 | 227.8246 | 68.2443 | 45.0683 | 4.4653 | 2.5837 | 5.0224 |  | 650
28 | 285.8961 | 2476.0747 |  | 2323.92 | 475.4226 | 69.2812 | 168.011 | 48.4837 | 36.3377 | 3.4871 | 2.612 | 3.8995 |  | 675
Tot | 8436.5747 | 64462.9605 |  | 40323.38 | 17280.4716 | 2522.0025 | 6398.0237 | 1628.7927 | 1268.7012 | 151.0518 | 73.8528 | 109.9637 |  | 18280
Avg | 301.3062 | 2302.2486 |  | 1550.8992 | 617.1597 | 90.0715 | 228.5008 | 58.1712 | 45.3108 | 5.3947 | 2.6376 | 3.9273 |  | 652.8571
Max | 365.8859 | 2908.1326 |  | 2542.84 | 764.9894 | 118.1032 | 263.247 | 69.7016 | 58.2222 | 8.2773 | 2.7729 | 5.9049 |  | 715
Min | 237.6768 | 1606.8875 |  | 84.2 | 475.4226 | 69.2812 | 168.011 | 43.9822 | 36.3377 | 3.4871 | 2.3612 | 2.8319 |  | 575
* Please specify the chemical compound(s) and units used. Include product name if applicable
Pre-ph=Liquid Lime |  |  |  | Pre & Post Disinfectant= Sodium Hypochlorite | [5 empty] | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC | [5 empty] | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Brennfloc CP9895P | [5 empty] | Coagulant= Aluminum Sulfate
PAC= Calgon Carbon |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## Chem Dose
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2018-02-01
Chemical dosage mg/l
Day | Pre Disinf (gal) | * Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | * Post Disenfectant (gal) (gal) |  | * Post-pH (gal) | * Fluoride (gal) | * Phosphate (gal) | * Zinc (gal) | Filter Aid | * Polymer (gal) | Pre-pH | * PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 1.3101 | 40.1196 |  |  | 3.5822 | 0.66874 | 7.9714 | 0.44974 | 1.0584 | 0.096766 | 0.059592 | 0.14643 |  | 3.0261
2 | 1.2874 | 40.4065 |  |  | 3.7044 | 0.69863 | 8.1876 | 0.44447 | 1.1049 | 0.099139 | 0.061346 | 0.12945 |  | 2.9806
3 | 1.3298 | 40.6179 |  | 0.8971 | 3.683 | 0.66712 | 8.3396 | 0.44114 | 1.1067 | 0.10237 | 0.060295 | 0.12965 |  | 2.7701
4 | 1.3121 | 43.5291 |  | 3.9389 | 3.6545 | 0.68618 | 7.8606 | 0.40925 | 1.1013 | 0.098192 | 0.060641 | 0.12119 |  | 2.8285
5 | 1.4538 | 53.8947 |  | 12.5418 | 3.6881 | 0.70201 | 7.7724 | 0.4619 | 1.1029 | 0.10395 | 0.060671 | 0.13124 |  | 3.0736
6 | 1.5923 | 69.4322 |  | 21.761 | 3.6441 | 0.72724 | 7.29 | 0.44541 | 1.1028 | 0.10037 | 0.062068 | 0.16381 |  | 3.0543
7 | 1.5768 | 66.8964 |  | 18.1484 | 3.6646 | 0.69991 | 6.7739 | 0.46878 | 1.1156 | 0.10199 | 0.062068 | 0.17584 |  | 3.0669
8 | 1.751 | 61.7008 |  | 14.5609 | 3.7172 | 0.68132 | 6.4587 | 0.44718 | 1.1001 | 0.10111 | 0.060378 | 0.18764 |  | 2.7843
9 | 1.7264 | 56.3216 |  | 13.0171 | 3.7035 | 0.66561 | 6.423 | 0.43781 | 1.1157 | 0.10362 | 0.060613 | 0.17163 |  | 2.9447
10 | 1.5636 | 49.211 |  | 8.7981 | 3.7447 | 0.66552 | 6.5245 | 0.45611 | 1.0967 | 0.10004 | 0.060303 | 0.1585 |  | 3.1003
11 | 1.4733 | 55.1251 |  | 8.962 | 3.6501 | 0.67903 | 6.6444 | 0.45859 | 1.0695 | 0.098095 | 0.060206 | 0.16334 |  | 2.913
12 | 1.5744 | 53.4174 |  | 12.1322 | 3.736 | 0.67124 | 6.8009 | 0.47131 | 1.1022 | 0.10135 | 0.061336 | 0.15977 |  | 2.6302
13 | 1.5446 | 60.1344 |  | 11.82 | 3.6986 | 0.68006 | 6.484 | 0.44231 | 0.94376 | 0.1031 | 0.060305 | 0.15233 |  | 3.0931
14 | 1.4227 | 59.9559 |  | 17.1134 | 3.6971 | 0.67065 | 6.8293 | 0.44915 | 0.95076 | 0.10703 | 0.061225 | 0.14391 |  | 2.9855
15 | 1.4867 | 60.6115 |  | 14.7307 | 3.7943 | 0.65295 | 7.4833 | 0.4484 | 1.0931 | 0.10199 | 0.060827 | 0.14631 |  | 2.9346
16 | 1.5012 | 60.521 |  | 28.1177 | 3.6826 | 0.58587 | 7.3632 | 0.4484 | 1.0818 | 0.10199 | 0.06062 | 0.14156 |  | 2.875
17 | 1.496 | 60.4908 |  | 17.5545 | 3.8204 | 0.60823 | 7.2402 | 0.4484 | 1.0908 | 0.10199 | 0.06062 | 0.13839 |  | 2.6901
18 | 1.5163 | 60.4908 |  | 15.7975 | 3.7235 | 0.57916 | 6.9312 | 0.4484 | 1.1043 | 0.10199 | 0.06062 | 0.14121 |  | 2.7126
19 | 1.429 | 57.6536 |  | 14.9707 | 3.772 | 0.6187 | 7.2734 | 0.46267 | 1.1676 | 0.10973 | 0.071192 | 0.13501 |  | 2.7007
20 | 1.3068 | 49.9557 |  | 29.0391 | 3.7277 | 0.65562 | 6.9837 | 0.45628 | 1.0617 | 0.10973 | 0.063309 | 0.16007 |  | 2.999
21 | 1.4952 | 53.6463 |  | 12.3949 | 3.6714 | 0.67764 | 6.864 | 0.44255 | 1.1116 | 0.10554 | 0.060874 | 0.18099 |  | 3.3785
22 | 1.6255 | 55.0704 |  | 24.7159 | 3.6213 | 0.65121 | 7.2503 | 0.46716 | 1.0996 | 0.1008 | 0.061566 | 0.19166 |  | 2.9779
23 | 1.5536 | 55.7469 |  | 25.2627 | 3.6869 | 0.65653 | 8.0097 | 0.48747 | 1.0908 | 0.10199 | 0.06124 | 0.18521 |  | 3.0438
24 | 1.571 | 55.7469 |  | 25.839 | 3.7429 | 0.68918 | 7.8238 | 0.48831 | 1.0863 | 0.10199 | 0.060827 | 0.19049 |  | 3.1132
25 | 1.571 | 55.1632 |  | 26.4723 | 3.736 | 0.7017 | 7.3375 | 0.47133 | 1.0908 | 0.10199 | 0.061137 | 0.19368 |  | 3.1895
26 | 1.6112 | 63.9681 |  | 25.3639 | 3.7391 | 0.7068 | 7.3375 | 0.46572 | 1.0818 | 0.10199 | 0.060827 | 0.24286 |  | 3.056
27 | 1.6251 | 69.9903 |  | 27.6656 | 3.7472 | 0.71441 | 7.3088 | 0.49376 | 1.0974 | 0.10037 | 0.060827 | 0.21327 |  | 3.0952
28 | 1.7024 | 71.8824 |  | 31.4501 | 3.7643 | 0.67864 | 6.9978 | 0.45626 | 1.1509 | 0.10195 | 0.060201 | 0.21537 |  | 3.654
29
30
31
Tot | 42.4092 | 1581.7005 |  | 463.0652 | 103.7977 | 18.7399 | 202.5649 | 12.7683 | 30.4801 | 2.8612 | 1.7157 | 4.6108 |  | 83.6716
Avg | 1.5146 | 56.4893 |  | 17.8102 | 3.7071 | 0.66928 | 7.2345 | 0.45601 | 1.0886 | 0.10219 | 0.061276 | 0.16467 |  | 2.9883
Max | 1.751 | 71.8824 |  | 31.4501 | 3.8204 | 0.72724 | 8.3396 | 0.49376 | 1.1676 | 0.10973 | 0.071192 | 0.24286 |  | 3.654
Min | 1.2874 | 40.1196 |  | 0.8971 | 3.5822 | 0.57916 | 6.423 | 0.40925 | 0.94376 | 0.096766 | 0.059592 | 0.12119 |  | 2.6302
* Please specify the chemical compound(s) and units used. Include product name if applicable | 28 | 28 | 0 | 26 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 0 | 28
Pre-ph = Liquid Lime |  |  |  | Pre and Post Disinfectant= Sodium Hypochlorite |  |  |  |  | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC |  |  |  |  | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Brennfloc CP9895P |  |  |  |  | Coagulant= Aluminum Sulfate
PAC= Calgon Carbon |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Supervisor

## Turbidity
Surface Water System Monthly Operation Report
Compliance with Turbidity Requirements for Filtered Systems &
Bacteriological Analysis for Raw and Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  | 2018-02-01
Lab Cert ID #: 26102 |  |  |  | Total Population: | >10,000
| Combined Filtered Water Turbidity Compliance |  |  |  | Bacteriological Analysis
Day | Maximum Filtered Water Turbidity | (A) Number of Turbidity Measurements | (B) Number of Turbidity Measurements <= 95% Limit | Number of Turbidity Measurements > Max Allowed | Raw Water |  | Finished1 Finished2
[5 empty] | Total Coliform per 100 mls | E.coli per 100 mls | Total Coliform P/A | Total Coliform P/A
1 | 0.05 | 18 | 18 | 0 | 420 | 20 | A | A
2 | 0.042 | 18 | 18 | 0 | 2382 | 10 | A | A
3 | 0.05 | 18 | 18 | 0 | 545 | 41 | A | A
4 | 0.045 | 18 | 18 | 0 | 464 | 10 | A | A
5 | 0.059 | 18 | 18 | 0 | 359 | 10 | A | A
6 | 0.048 | 18 | 18 | 0 | 839 | 31 | A | A
7 | 0.06 | 18 | 18 | 0 | 1223 | <10 | A | A
8 | 0.062 | 18 | 18 | 0 | 1198 | <10 | A | A
9 | 0.053 | 18 | 18 | 0 | 4352 | 63 | A | A
10 | 0.07 | 18 | 18 | 0 | 2143 | 51 | A | A
11 | 0.052 | 18 | 18 | 0 | 1723 | 75 | A | A
12 | 0.089 | 18 | 18 | 0 | 1956 | 31 | A | A
13 | 0.062 | 18 | 18 | 0 | 1086 | <10 | A | A
14 | 0.055 | 18 | 18 | 0 | 548 | <10 | A | A
15 | 0.049 | 18 | 18 | 0 | 602 | <10 | A | A
16 | 0.048 | 18 | 18 | 0 | 504 | <10 | A | A
17 | 0.073 | 18 | 18 | 0 | 473 | <10 | A | A
18 | 0.057 | 18 | 18 | 0 | 504 | <10 | A | A
19 | 0.072 | 18 | 18 | 0 | 576 | <10 | A | A
20 | 0.058 | 18 | 18 | 0 | 480 | 10 | A | A
21 | 0.044 | 18 | 18 | 0 | 441 | 10 | A | A
22 | 0.061 | 18 | 18 | 0 | 364 | 10 | A | A
23 | 0.055 | 18 | 18 | 0 | 364 | 31 | A | A
24 | 0.042 | 18 | 18 | 0 | 189 | 10 | A | A
25 | 0.059 | 18 | 18 | 0 | 246 | <10 | A | A
26 | 0.059 | 18 | 18 | 0 | 213 | <10 | A | A
27 | 0.068 | 18 | 18 | 0 | 318 | 10 | A | A
28 | 0.073 | 18 | 18 | 0 | 373 | <10 | A | A
29
30
31
| Total | 504 | 504 | 0
Max. Allow. Turbidity: |  | 1 NTU |  | Type of Plant: |  | Super Pulsator/Greenleaf Filters
95% Turbidity Limit: |  | 0.3 NTU |  | Max. Approved Filtration Rate: |  | 6 |  | (gpm/ft2)
The percentage of turbidity measurements |  |  |  | 100
meeting the specific limit is equal to: B/A x 100
Prepared by: ____________________________________________ |  |  |  |  | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## Indiv Filter
Surface Water System Monthly Operation Report
Turbidity Requirements for Individual Filters For Complaince With
Long Term 2 Enhanced Surface Water Treatment Rule
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  |  |  | 2018-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lab Cert ID #: 26102 |  |  | Population: >10,000
Turbidity Requirements |  |  |  | Individual Filters
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Was the turbidity recorded every 15 minutes for each
individual filter (while in operation) for the entire
month? | bar: Individual Filters 1 to Individual Filters 12
2 | Were 95% of the Turbidity Measurements less than
the 0.15 NTU Limit (excluding the 15 minute period
after a backwash cycle)? | bar: Individual Filters 1 to Individual Filters 12
3 | Were there any consecutive measurements greater
than 0.30 NTU? | bar: Individual Filters 1 to Individual Filters 12
Prepared by: |  |  |  | Individual Filters 5: Date:; Individual Filters 7: 2018-02-01
(signature) William Lederman Plant Superintendent

## Individual Filters
0 | Surface Water System Monthly Operation Report
Individual Filter Performance Worksheet
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  | 2018-02-01
Lab Cert ID #: 26102 |  | Total Population Served: >10,000
1. Was the turbidity recorded every 15 minutes for each individual filter |  |  |  |  | yes
(while in operation) for the entire month?
2a. Was there a failure of any of the continuous turbidity monitoring equipment during the month? |  |  |  |  | no
2b. If there was a failure, were grab samples taken from the filter effluent every 4 hours? |  |  |  |  | N.A.
2c. If there was failure of any continuous monitoring equipment, was it repaired within
5 working days? |  |  |  |  | N.A.
3a. Did any individual filter(s) have a measured effluent turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart? |  |  |  |  | no
3b. If the answer to 3a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
3c. If the answer to 3a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | N.A.
4a. Did any individual filter(s) have a measured effluent turbidity level of > 0.5 NTU in two consecutive
measurements taken 15 minutes apart, excluding the first four hours of operation after the filter
has been backwashed or otherwise taken out of service? |  |  |  |  | no
4b. If the answer to 4a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
4c. If the answer to 4a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | N.A.
5a. Did any individual filter(s) have a measured turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 3 months? |  |  |  |  | no
5b. If the answer to 5a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
5c. If the answer to 5a was "yes", have arrangements been made for a filter self-assessment to be
conducted within 14 days of the exceedance? |  |  |  |  | N.A.
6a. Did any individual filter(s) have a measured turbidity level of > 2.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 2 months? |  |  |  |  | no
6b. If the answer to 6a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
6c. If the answer to 6a was "yes", have arrangements been made to have a CPE conducted by the
Department or by a third party approved by the Department within 30 days of the exceedance? |  |  |  |  | N.A.
Prepared by: ___________________________________________ |  |  | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## MOR CT
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-02-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.65 | 10.4 | 24.4615 | 15.9 | 6.06 | 10.9 | 15 | 1.06
2 | 0.7 | 10.5 | 24.2286 | 16.96 | 6.07 | 10.8 | 15 | 1.1307
3 | 0.7 | 9.6 | 26.5 | 18.55 | 5.88 | 9.9 | 17 | 1.0912
4 | 0.75 | 10.5 | 24.2286 | 18.1714 | 5.89 | 9.8 | 17 | 1.0689
5 | 0.53 | 10 | 25.44 | 13.4832 | 5.85 | 10.3 | 13 | 1.0372
6 | 0.63 | 10 | 25.44 | 16.0272 | 6.14 | 10.7 | 15 | 1.0685
7 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.12 | 11.2 | 15 | 1.0533
8 | 0.54 | 9.3 | 29.0323 | 15.6774 | 6.13 | 13.7 | 15 | 1.0452
9 | 0.54 | 8.5 | 31.7647 | 17.1529 | 6.01 | 14.4 | 15 | 1.1435
10 | 0.57 | 9 | 28.2667 | 16.112 | 6.03 | 12.7 | 15 | 1.0741
11 | 0.48 | 9 | 28.2667 | 13.568 | 5.96 | 12.4 | 13 | 1.0437
12 | 0.61 | 9 | 28.2667 | 17.2427 | 6.02 | 14 | 15 | 1.1495
13 | 0.56 | 8.6 | 29.5814 | 16.5656 | 6.02 | 13.2 | 15 | 1.1044
14 | 0.47 | 9 | 30 | 14.1 | 5.97 | 14.3 | 13 | 1.0846
15 | 0.6 | 9 | 28.2667 | 16.96 | 6.07 | 13.2 | 15 | 1.1307
16 | 0.67 | 9 | 28.2667 | 18.9387 | 6.05 | 14.5 | 15 | 1.2626
17 | 0.6 | 9 | 28.2667 | 16.96 | 6.06 | 14.9 | 15 | 1.1307
18 | 0.58 | 9 | 28.2667 | 16.3947 | 6.13 | 14.7 | 15 | 1.093
19 | 0.6 | 9.4 | 27.0638 | 16.2383 | 6.03 | 14.9 | 15 | 1.0826
20 | 0.51 | 9.5 | 26.7789 | 13.6573 | 6.1 | 15.3 | 10 | 1.3657
21 | 0.49 | 11 | 23.1273 | 11.3324 | 6.09 | 17.5 | 10 | 1.1332
22 | 0.46 | 11.1 | 22.9189 | 10.5427 | 6.08 | 16.5 | 10 | 1.0543
23 | 0.47 | 9.4 | 27.0638 | 12.72 | 6.07 | 18 | 10 | 1.272
24 | 0.46 | 9 | 28.2667 | 13.0027 | 6.13 | 17.4 | 10 | 1.3003
25 | 0.41 | 9 | 28.2667 | 11.5893 | 6.07 | 18 | 10 | 1.1589
26 | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.02 | 18.9 | 10 | 1.1387
27 | 0.44 | 10.3 | 24.699 | 10.8676 | 5.96 | 19.1 | 8 | 1.3584
28 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.006 | 17.2 | 10 | 1.1115
29
30
31
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## CT AVG (hidden)
|  |  |  | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT
1 | #DIV/0! | 11.025 | 10 | 5.985 | 6 | 13 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 34.4 | 25 | 6.025 | 6.5 | 5 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 11.875 | 10 | 6.03 | 6.5 | 15 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0!
2 | #DIV/0! | 11.1 | 10 | 5.97 | 6 | 13 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 10.6 | 10 | 5.9775 | 6 | 13 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 12.275 | 10 | 5.985 | 6 | 13 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0!
3 | #DIV/0! | 10.5 | 10 | 5.8975 | 6 | 13 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 9.85 | 5 | 5.955 | 6 | 17 | 0 | #DIV/0! | 0.7 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 11.85 | 10 | 5.955 | 6 | 13 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0!
4 | #DIV/0! | 10.375 | 10 | 5.9925 | 6 | 13 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 9.65 | 5 | 5.99 | 6 | 17 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 11.3 | 10 | 6 | 6 | 13 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0!
5 | #DIV/0! | 10.175 | 10 | 5.8375 | 6 | 13 | 0 | #DIV/0! | 0.37 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 10.025 | 10 | 5.8675 | 6 | 13 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 11.625 | 10 | 5.8925 | 6 | 13 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0!
6 | #DIV/0! | 10.2 | 10 | 5.9375 | 6 | 13 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 10.475 | 10 | 5.96 | 6 | 13 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 11.575 | 10 | 5.955 | 6 | 13 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
7 | #DIV/0! | 11.35 | 10 | 6.0925 | 6.5 | 15 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 11.75 | 10 | 6.085 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 13.175 | 10 | 6.09 | 6.5 | 15 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0!
8 | #DIV/0! | 12.25 | 10 | 6.005 | 6.5 | 15 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 12.475 | 10 | 6.0325 | 6.5 | 15 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 13.825 | 10 | 6.0425 | 6.5 | 15 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
9 | #DIV/0! | 12.05 | 10 | 6.06 | 6.5 | 15 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 12.475 | 10 | 6.0475 | 6.5 | 15 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 14.075 | 10 | 6.0325 | 6.5 | 15 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
10 | #DIV/0! | 11.925 | 10 | 6.0125 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 12.2 | 10 | 6.03 | 6.5 | 15 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 13.425 | 10 | 6.03 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
11 | #DIV/0! | 12.85 | 10 | 5.885 | 6 | 13 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 13.1 | 10 | 5.885 | 6 | 13 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 14.375 | 10 | 5.9325 | 6 | 13 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0!
12 | #DIV/0! | 13.55 | 10 | 6.025 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 13.75 | 10 | 6.0375 | 6.5 | 15 | 0 | #DIV/0! | 0.52 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 15.075 | 15 | 6.025 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0!
13 | #DIV/0! | 13.875 | 10 | 5.975 | 6 | 13 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 13.8 | 10 | 5.995 | 6 | 13 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 15.025 | 15 | 6.0125 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0!
14 | #DIV/0! | 12.85 | 10 | 5.94 | 6 | 13 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 12.725 | 10 | 5.98 | 6 | 13 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 14.225 | 10 | 5.9525 | 6 | 13 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0!
15 | #DIV/0! | 13.575 | 10 | 6.1025 | 6.5 | 15 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 13.325 | 10 | 6.1275 | 6.5 | 15 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 14.775 | 10 | 6.125 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
16 | #DIV/0! | 14.625 | 10 | 6.0675 | 6.5 | 15 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 14.35 | 10 | 6.075 | 6.5 | 15 | 0 | #DIV/0! | 0.69 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 15.85 | 15 | 6.1 | 6.5 | 10 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0!
17 | #DIV/0! | 14.6 | 10 | 6.1725 | 6.5 | 15 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 14.35 | 10 | 6.22 | 6.5 | 15 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 16.075 | 15 | 6.255 | 6.5 | 10 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0!
18 | #DIV/0! | 14.9 | 10 | 6.1075 | 6.5 | 15 | 0 | #DIV/0! | 0.58 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 14.7 | 10 | 6.1425 | 6.5 | 15 | 0 | #DIV/0! | 0.66 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 15.65 | 15 | 6.155 | 6.5 | 10 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0!
19 | #DIV/0! | 15.15 | 15 | 6.1025 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 15 | 15 | 6.0825 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 16.15 | 15 | 6.1075 | 6.5 | 10 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
20 | #DIV/0! | 15.8 | 15 | 6.07 | 6.5 | 10 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 15.55 | 15 | 6.0925 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 16.7 | 15 | 6.125 | 6.5 | 10 | 0 | #DIV/0! | 0.3 | #DIV/0! | #DIV/0!
21 | #DIV/0! | 16.875 | 15 | 6.06 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 16.675 | 15 | 6.085 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 17.575 | 15 | 6.0975 | 6.5 | 10 | 0 | #DIV/0! | 0.33 | #DIV/0! | #DIV/0!
22 | #DIV/0! | 17.375 | 15 | 6.0325 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 17.25 | 15 | 6.0575 | 6.5 | 10 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 17.95 | 15 | 6.0775 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
23 | #DIV/0! | 17.675 | 15 | 6.025 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 17.6 | 15 | 6.0325 | 6.5 | 10 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 18.35 | 15 | 6.04 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0!
24 | #DIV/0! | 18.075 | 15 | 6.0525 | 6.5 | 10 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 17.875 | 15 | 6.05 | 6.5 | 10 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 18.675 | 15 | 6.055 | 6.5 | 10 | 0 | #DIV/0! | 0.58 | #DIV/0! | #DIV/0!
25 | #DIV/0! | 18.55 | 15 | 6.005 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 18.5 | 15 | 6.03 | 6.5 | 10 | 0 | #DIV/0! | 0.41 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 19.275 | 15 | 6.0125 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0!
26 | #DIV/0! | 19.1 | 15 | 5.975 | 6 | 8 | 0 | #DIV/0! | 0.4 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 19.025 | 15 | 6.0075 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 19.75 | 15 | 5.9925 | 6 | 8 | 0 | #DIV/0! | 0.36 | #DIV/0! | #DIV/0!
27 | #DIV/0! | 18.475 | 15 | 5.9825 | 6 | 8 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 18.375 | 15 | 6 | 6 | 8 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 19.05 | 15 | 6.0075 | 6.5 | 10 | 0 | #DIV/0! | 0.34 | #DIV/0! | #DIV/0!
28 | #DIV/0! | 17.425 | 15 | 5.9715 | 6 | 8 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 17.3 | 15 | 6.0175 | 6.5 | 10 | 0 | #DIV/0! | 0.4 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 18.275 | 15 | 6.0525 | 6.5 | 10 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0!
29 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 29 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 29 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE!
30 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 30 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 30 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE!
31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE!
ONLY FILL GREEN
|  |  |  | TEST | [8 empty] | DALY CAL SHEET FLOW, DALY AVG TEMP & PH Min CT Calculater
| Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# |  |  |  | Settle temp |  | use temp | Settle PH |  | use ph |  | FLOW CAL SHEET | t10#
| Plt 1 | 18.8 | 15 | Plt 1 PH | 6.09 | 6.5 | plt 1 flow | 12 | 21.2 |  |  |  | Plt 1 | 13.55 | 10 | Plt 1 PH | 6.025 | 6.5 | plt 1 flow | 10.3 | 24.699
| Plt 2 | 18.9 | 15 | Plt 2 PH | 6.13 | 6.5 | plt 2 flow | 12 | 21.2 |  |  |  | Plt 2 | 13.75 | 10 | Plt 2 PH | 6.0375 | 6.5 | plt 2 flow | 10.3 | 24.699
| Plt 3 | 19.5 | 15 | Plt 3 PH | 6.24 | 6.5 | plt 3 flow | 12 | 22.5 |  |  |  | Plt 3 | 15.075 | 15 | Plt 3 PH | 6.025 | 6.5 | plt 3 flow | 6.3 | 42.8571
2019-08-12 09:03
|  | min CT | TARGET CT |  | temp | ph | min ct table | [7 empty] | min CT | TARGET CT |  | temp | ph | min ct table
| ct plt 1 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 1 | 0.60731 | 0.70731 |  | 10 | 6.5 | 15
| ct plt 2 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 2 | 0.60731 | 0.70731 |  | 10 | 6.5 | 15
| ct plt 3 | 0.44444 | 0.54444 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 3 | 0.23333 | 0.33333 |  | 15 | 6.5 | 10
Bill's Cal | flow | temp | ph | t10# | cal ct table | MIN CT | target ct
plt1 | 12 | 18.8 | 6.09 | 21.2 | 7.1064 | 0.33521 | 0.43521
plt2 | 12 | 18.9 | 6.13 | 21.2 | 7.1599 | 0.33773 | 0.43773
plt3 | 12 | 19.5 | 6.24 | 22.5 | 7.1424 | 0.31744 | 0.41744

## CT Calc
Surface Water System Monthly Operation Report
Disinfection Information
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | 2018-02-01
| Min. Disinfect. Resid. | Sample Type for | CT calc/CT table Disinfectant Sequence | [5 empty] | SUM (CT calc/CT table)
Day | at Point-of-Entry to Distribution System (mg/L) | Point-of-Entry (POE) | 1st | 2nd | 3rd | 4th | 5th | 6th
1 | 3.1 | A | 1.06 | 0 | 0 | 0 | 0 | 0 | 1.06
2 | 3.4 | A | 1.1307 | 0 | 0 | 0 | 0 | 0 | 1.1307
3 | 2.9 | A | 1.0912 | 0 | 0 | 0 | 0 | 0 | 1.0912
4 | 3.3 | A | 1.0689 | 0 | 0 | 0 | 0 | 0 | 1.0689
5 | 2.9 | A | 1.0372 | 0 | 0 | 0 | 0 | 0 | 1.0372
6 | 3.5 | A | 1.0685 | 0 | 0 | 0 | 0 | 0 | 1.0685
7 | 3.4 | A | 1.0533 | 0 | 0 | 0 | 0 | 0 | 1.0533
8 | 3.1 | A | 1.0452 | 0 | 0 | 0 | 0 | 0 | 1.0452
9 | 3.3 | A | 1.1435 | 0 | 0 | 0 | 0 | 0 | 1.1435
10 | 2.9 | A | 1.0741 | 0 | 0 | 0 | 0 | 0 | 1.0741
11 | 3 | A | 1.0437 | 0 | 0 | 0 | 0 | 0 | 1.0437
12 | 3.1 | A | 1.1495 | 0 | 0 | 0 | 0 | 0 | 1.1495
13 | 2.7 | A | 1.1044 | 0 | 0 | 0 | 0 | 0 | 1.1044
14 | 2.8 | A | 1.0846 | 0 | 0 | 0 | 0 | 0 | 1.0846
15 | 2.5 | A | 1.1307 | 0 | 0 | 0 | 0 | 0 | 1.1307
16 | 2.9 | A | 1.2626 | 0 | 0 | 0 | 0 | 0 | 1.2626
17 | 2.8 | A | 1.1307 | 0 | 0 | 0 | 0 | 0 | 1.1307
18 | 2.5 | A | 1.093 | 0 | 0 | 0 | 0 | 0 | 1.093
19 | 2.7 | A | 1.0826 | 0 | 0 | 0 | 0 | 0 | 1.0826
20 | 2.4 | A | 1.3657 | 0 | 0 | 0 | 0 | 0 | 1.3657
21 | 2.8 | A | 1.1332 | 0 | 0 | 0 | 0 | 0 | 1.1332
22 | 3.3 | A | 1.0543 | 0 | 0 | 0 | 0 | 0 | 1.0543
23 | 2.6 | A | 1.272 | 0 | 0 | 0 | 0 | 0 | 1.272
24 | 3 | A | 1.3003 | 0 | 0 | 0 | 0 | 0 | 1.3003
25 | 2.9 | A | 1.1589 | 0 | 0 | 0 | 0 | 0 | 1.1589
26 | 3.1 | A | 1.1387 | 0 | 0 | 0 | 0 | 0 | 1.1387
27 | 3.2 | A | 1.3584 | 0 | 0 | 0 | 0 | 0 | 1.3584
28 | 2.7 | A | 1.1115 | 0 | 0 | 0 | 0 | 0 | 1.1115
29
30
31
A. Number of days SUM (CT calc/CT table) <1: |  |  | 0 |  | Days the Distribution Residual was <0.2 mg/L
[5 empty] | Day | Duration (hrs) |  | Date Reported
B. Compliance with disinfection residual criteria |  |  |  |  | None | None |  | None
at Point-of-Entry to distribution system: |  |  | Yes |  | None | None |  | None
Prepared by: _________________________________________________ | [6 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Superintendent

## CT (1)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-02-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.56 | 6 | 42.4 | 23.744 | 5.94 | 10.5 | 13 | 1.8265
2 | 0.5 | 5.5 | 46.2545 | 23.1273 | 6.03 | 10.9 | 15 | 1.5418
3 | 0.48 | 5.5 | 46.2545 | 22.2022 | 5.82 | 10.5 | 13 | 1.7079
4 | 0.64 | 8 | 31.8 | 20.352 | 5.9 | 9.9 | 17 | 1.1972
5 | 0.37 | 5.6 | 45.4286 | 16.8086 | 5.83 | 10.3 | 13 | 1.293
6 | 0.65 | 5 | 50.88 | 33.072 | 5.96 | 9.9 | 17 | 1.9454
7 | 0.61 | 9.5 | 26.7789 | 16.3352 | 6.01 | 12.2 | 15 | 1.089
8 | 0.57 | 9.2 | 27.6522 | 15.7617 | 6.03 | 12.3 | 15 | 1.0508
9 | 0.64 | 8 | 31.8 | 20.352 | 6.2 | 11.6 | 15 | 1.3568
10 | 0.59 | 9 | 28.2667 | 16.6773 | 6.07 | 12.1 | 15 | 1.1118
11 | 0.47 | 8.6 | 29.5814 | 13.9033 | 5.81 | 13.1 | 13 | 1.0695
12 | 0.55 | 8 | 31.8 | 17.49 | 6.09 | 13.9 | 15 | 1.166
13 | 0.56 | 8.6 | 29.5814 | 16.5656 | 6.02 | 13.2 | 15 | 1.1044
14 | 0.51 | 9 | 28.2667 | 14.416 | 5.92 | 12.9 | 13 | 1.1089
15 | 0.6 | 9 | 28.2667 | 16.96 | 6.07 | 13.2 | 15 | 1.1307
16 | 0.67 | 9 | 28.2667 | 18.9387 | 6.05 | 14.5 | 15 | 1.2626
17 | 0.6 | 9 | 28.2667 | 16.96 | 6.06 | 14.9 | 15 | 1.1307
18 | 0.58 | 9 | 28.2667 | 16.3947 | 6.13 | 14.7 | 15 | 1.093
19 | 0.47 | 10.2 | 24.9412 | 11.7224 | 6.08 | 15.5 | 10 | 1.1722
20 | 0.45 | 10.2 | 24.9412 | 11.2235 | 5.99 | 15.5 | 8 | 1.4029
21 | 0.49 | 11 | 23.1273 | 11.3324 | 6.09 | 17.5 | 10 | 1.1332
22 | 0.48 | 11.1 | 22.9189 | 11.0011 | 6.07 | 16.7 | 10 | 1.1001
23 | 0.47 | 9.4 | 27.0638 | 12.72 | 6.07 | 18 | 10 | 1.272
24 | 0.46 | 9 | 28.2667 | 13.0027 | 6.13 | 17.4 | 10 | 1.3003
25 | 0.47 | 9 | 28.2667 | 13.2853 | 6.09 | 18.1 | 10 | 1.3285
26 | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.02 | 18.9 | 10 | 1.1387
27 | 0.44 | 10.3 | 24.699 | 10.8676 | 5.96 | 19.1 | 8 | 1.3584
28 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.006 | 17.2 | 10 | 1.1115
29 | [7 empty] | 0
30 | [7 empty] | 0
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) Randall Johnson Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (2)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-02-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.65 | 10.4 | 24.4615 | 15.9 | 6.06 | 10.9 | 15 | 1.06
2 | 0.7 | 10.5 | 24.2286 | 16.96 | 6.07 | 10.8 | 15 | 1.1307
3 | 0.7 | 9.6 | 26.5 | 18.55 | 5.88 | 9.9 | 17 | 1.0912
4 | 0.75 | 10.5 | 24.2286 | 18.1714 | 5.89 | 9.8 | 17 | 1.0689
5 | 0.53 | 10 | 25.44 | 13.4832 | 5.85 | 10.3 | 13 | 1.0372
6 | 0.63 | 10 | 25.44 | 16.0272 | 6.14 | 10.7 | 15 | 1.0685
7 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.12 | 11.2 | 15 | 1.0533
8 | 0.58 | 9.2 | 27.6522 | 16.0383 | 6.08 | 12.2 | 15 | 1.0692
9 | 0.57 | 8 | 31.8 | 18.126 | 6.14 | 11.6 | 15 | 1.2084
10 | 0.57 | 9 | 28.2667 | 16.112 | 6.03 | 12.7 | 15 | 1.0741
11 | 0.48 | 9 | 28.2667 | 13.568 | 5.96 | 12.4 | 13 | 1.0437
12 | 0.61 | 9 | 28.2667 | 17.2427 | 6.02 | 14 | 15 | 1.1495
13 | 0.59 | 8.6 | 29.5814 | 17.453 | 6.04 | 12.9 | 15 | 1.1635
14 | 0.58 | 8.6 | 29.5814 | 17.1572 | 6.06 | 12.6 | 15 | 1.1438
15 | 0.63 | 9 | 28.2667 | 17.808 | 6.15 | 13 | 15 | 1.1872
16 | 0.76 | 9 | 28.2667 | 21.4827 | 6.14 | 14 | 15 | 1.4322
17 | 0.63 | 9 | 28.2667 | 17.808 | 6.22 | 14.2 | 15 | 1.1872
18 | 0.7 | 9 | 28.2667 | 19.7867 | 6.17 | 14.4 | 15 | 1.3191
19 | 0.6 | 9.4 | 27.0638 | 16.2383 | 6.03 | 14.9 | 15 | 1.0826
20 | 0.51 | 9.5 | 26.7789 | 13.6573 | 6.1 | 15.3 | 10 | 1.3657
21 | 0.54 | 11 | 23.1273 | 12.4887 | 6.1 | 17.5 | 10 | 1.2489
22 | 0.46 | 11.1 | 22.9189 | 10.5427 | 6.08 | 16.5 | 10 | 1.0543
23 | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.03 | 18 | 10 | 1.6139
24 | 0.63 | 9.4 | 27.0638 | 17.0502 | 6.07 | 17.9 | 10 | 1.705
25 | 0.41 | 9 | 28.2667 | 11.5893 | 6.07 | 18 | 10 | 1.1589
26 | 0.47 | 10.5 | 24.2286 | 11.3874 | 6.01 | 18.8 | 10 | 1.1387
27 | 0.55 | 9.2 | 27.6522 | 15.2087 | 6.02 | 18.3 | 10 | 1.5209
28 | 0.4 | 10.3 | 24.699 | 9.8796 | 5.93 | 17.2 | 8 | 1.235
29 | [7 empty] | 0
30 | [7 empty] | 0
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (3)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-02-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.67 | 10.7 | 25.2336 | 16.9065 | 6.08 | 11.9 | 15 | 1.1271
2 | 0.68 | 10.5 | 25.7143 | 17.4857 | 6.06 | 12.6 | 15 | 1.1657
3 | 0.65 | 9.8 | 27.551 | 17.9082 | 5.97 | 11.8 | 13 | 1.3776
4 | 0.7 | 10.6 | 25.4717 | 17.8302 | 6.17 | 11.8 | 15 | 1.1887
5 | 0.5 | 9.8 | 27.551 | 13.7755 | 5.9 | 11.6 | 13 | 1.0597
6 | 0.66 | 10 | 27 | 17.82 | 6.1 | 11.9 | 15 | 1.188
7 | 0.6 | 10.2 | 26.4706 | 15.8824 | 6.07 | 13.7 | 15 | 1.0588
8 | 0.54 | 9.3 | 29.0323 | 15.6774 | 6.13 | 13.7 | 15 | 1.0452
9 | 0.54 | 8.5 | 31.7647 | 17.1529 | 6.01 | 14.4 | 15 | 1.1435
10 | 0.59 | 9 | 30 | 17.7 | 6.06 | 13.8 | 15 | 1.18
11 | 0.47 | 9 | 30 | 14.1 | 5.98 | 13.9 | 13 | 1.0846
12 | 0.61 | 8.6 | 31.3953 | 19.1512 | 5.97 | 14.9 | 13 | 1.4732
13 | 0.53 | 8.6 | 31.3953 | 16.6395 | 6.02 | 14.5 | 15 | 1.1093
14 | 0.47 | 9 | 30 | 14.1 | 5.97 | 14.3 | 13 | 1.0846
15 | 0.59 | 9 | 30 | 17.7 | 6.16 | 14.5 | 15 | 1.18
16 | 0.62 | 9 | 30 | 18.6 | 6.13 | 16.2 | 10 | 1.86
17 | 0.65 | 9 | 30 | 19.5 | 6.24 | 16 | 10 | 1.95
18 | 0.69 | 9 | 30 | 20.7 | 6.08 | 14.8 | 15 | 1.38
19 | 0.59 | 8.7 | 31.0345 | 18.3103 | 6.14 | 16 | 10 | 1.831
20 | 0.3 | 4.6 | 58.6957 | 17.6087 | 6.19 | 17.2 | 10 | 1.7609
21 | 0.33 | 4.9 | 55.102 | 18.1837 | 6.12 | 17.4 | 10 | 1.8184
22 | 0.79 | 9 | 30 | 23.7 | 6.09 | 18 | 10 | 2.37
23 | 0.55 | 9.5 | 28.4211 | 15.6316 | 6.05 | 18.6 | 10 | 1.5632
24 | 0.58 | 9 | 30 | 17.4 | 6.04 | 19 | 10 | 1.74
25 | 0.5 | 9 | 30 | 15 | 6.08 | 18.9 | 10 | 1.5
26 | 0.36 | 6 | 45 | 16.2 | 6 | 19.9 | 8 | 2.025
27 | 0.34 | 6.1 | 44.2623 | 15.0492 | 6.01 | 19.7 | 10 | 1.5049
28 | 0.43 | 6.2 | 43.5484 | 18.7258 | 6.03 | 18.9 | 10 | 1.8726
29 | [7 empty] | 0
30 | [7 empty] | 0
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-02-01
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## ct CAL
ONLY FILL GREEN
TEST
Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# | Flows from Plant Check Sheet
Plt 1 | 17.3 | 15 | Plt 1 PH | 5.82 | 6 | plt 1 flow | 10.3 | 24.699 | Raw PLT 1 | 10.3
Plt 2 | 17.2 | 15 | Plt 2 PH | 5.93 | 6 | plt 2 flow | 10.3 | 24.699 | Raw PLT 2 | 10.3
Plt 3 | 18 | 15 | Plt 3 PH | 6.05 | 6.5 | plt 3 flow | 6.3 | 42.8571 | Raw PLT 3 | 6.3
| min CT | TARGET CT |  | temp | ph | min ct table
ct plt 1 | 0.3239 | 0.4239 |  | 15 | 6 | 8
ct plt 2 | 0.3239 | 0.4239 |  | 15 | 6 | 8
ct plt 3 | 0.23333 | 0.33333 |  | 15 | 6.5 | 10

## Turbidity Analysis
South Carolina Department of Health and Environmental Control
Bureau of Drinking Water Protection
Turbidity Analysis Input Form
System Number .............................................................…………… |  |  | 2620004
Name of Water System ................................................……………. |  |  | GSWSA
Analytical Method ..........................................................…………… |  |  | 001
Contaminant ID ..............................................................…………… |  |  | 0100
Compliance Period Begin (mo/day/yr) ........................………………. |  |  | 2018-02-01
Compliance Period End (mo/day/yr) ..........................……………….. |  |  | 2018-02-28
Number of Samples Required ....................................……………….. |  |  | 168
Number of Samples Taken .........................................………………. |  |  | 504
Highest Turbidity for Compliance Period ..................………………… |  |  | 0.089
Lowest Turbidity for Compliance Period ...................………………… |  |  | 0.042
Average Turbidity for Compliance Period ..................………………… |  |  | 0.057679
Laboratory ID ..................................................................…………… |  |  | 26102
Laboratory Name ...........................................................……………. |  |  | GSWSA /BCSWTP
Comments:
Signature ________________________________ Date |  | 2018-02-01
William Lederman Plant Supervisor
This signature certifies that all samples were collected, analyzed and reported according to the State Primary Drinking
Water Regulations.
DHEC 1975 (Rev. 5/00)

## Distribution
Surface Water System Monthly Operation Report
Distribution System Disinfectant Residual Data
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: |  | 2016-08-01
Lab Cert ID #: 26102 |  |  | Lab # for lab conducting HPC analyses: 26102
Day | No. of Sites Disinfect. Residual was Measured | No. of Sites Disinfect. Residual NOT Measured, but HPC Measured | No. of Sites where Disinfect. Residual NOT Detected & HPC NOT Measured | No. of Sites where Disinfectant Residual was NOT Detected and HPC > 500/ml | No. of Sites Disinfect. Residual NOT Measured and HPC > 500/ml | Average Disinfectant Residual (mg/L)
1 |  | 0 | 0 | 0 | 0
2 |  | 0 | 0 | 0 | 0
3 |  | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 0 | 0
5 |  | 0 | 0 | 0 | 0
6 |  | 0 | 0 | 0 | 0
7 |  | 0 | 0 | 0 | 0
8 |  | 0 | 0 | 0 | 0
9 |  | 0 | 0 | 0 | 0
10 |  | 0 | 0 | 0 | 0
11 |  | 0 | 0 | 0 | 0
12 |  | 0 | 0 | 0 | 0
13 |  | 0 | 0 | 0 | 0
14 |  | 0 | 0 | 0 | 0
15 |  | 0 | 0 | 0 | 0
16 |  | 0 | 0 | 0 | 0
17 |  | 0 | 0 | 0 | 0
18 |  | 0 | 0 | 0 | 0
19 |  | 0 | 0 | 0 | 0
20 |  | 0 | 0 | 0 | 0
21 |  | 0 | 0 | 0 | 0
22 |  | 0 | 0 | 0 | 0
23 |  | 0 | 0 | 0 | 0
24 |  | 0 | 0 | 0 | 0
25 |  | 0 | 0 | 0 | 0
26 |  | 0 | 0 | 0 | 0
27 |  | 0 | 0 | 0 | 0
28 |  | 0 | 0 | 0 | 0
29 |  | 0 | 0 | 0 | 0
30 |  | 0 | 0 | 0 | 0
31 |  | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | Avg. Resid.
| a | b | c | d | e | #DIV/0!
Compliance with Distribution System Disinfectant Residual Criteria |  |  |  |  | #DIV/0!
V = ( c + d + e ) / ( a + b ) x 100 = ( + + ) / ( + ) x 100 =
For Previous Month: V =
Prepared by: __________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## Chloramine
Surface Water System Monthly Operation Report
For Systems Using Chlorine and/or Chloramines
To Maintain A Residual In The Distribution System
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | For (Month/yr): | 2016-08-01
Month/Year | *Average Residual |  | Quarterly Average (mg/L)
| Chlorine (mg/L) | Chloramines (mg/L)
2016-01-02 |  | 3.42 | 3.17
2016-02-03 |  | 2.79 |  | *Average residual values may be obtained from page 10 of 15 of this form
2016-03-03 |  | 3.3
2016-04-02 |  | 3.42 | 3.14
2016-05-03 |  | 3.46
2016-06-02 |  | 2.75
2016-07-02 |  | 3.42
2016-08-02 |  | 2.86
2016-09-02
2015-10-02 |  | 3.11 | 2.99
2015-11-02 |  | 2.78
2015-12-02 |  | 3.08
RAA at the end of the most recent quarter: |  |  | 3.1
Prepared by: _________________________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## TOC
Surface Water System Monthly Operation Report
Compliance With DBP Precursor Removal Requirements
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  |  | For (Month/yr): |  | 2016-08-01
Lab Cert ID #: 26102
Month | Source Water |  | Treated Water TOC (mg/L) | (A) Actual % TOC Removal | (B) Required % TOC Removal | Basis for Required % Removal | Removal Ratio (A) / (B) | Quarterly Average Ratio | RAA1 Ratio (Last 4 Quarters)
| Alkalinity (mg/L) | TOC (mg/L)
2016-01-01 | 14 | 21.88 | 4.05 | 81.4899 | 50 | Step 1 | 1.6298 | 1.51
2016-02-01 | 20 | 9.738 | 2.72 | 72.0682 | 50 | Step 1 | 1.4414
2016-03-01 | 14 | 10.23 | 2.81 | 72.5318 | 50 | Step 1 | 1.4506
2016-04-01 | 21 | 9.776 | 2.82 | 71.1538 | 50 | Step 1 | 1.4231 | 1.3387 | 1.37
2016-05-01 | 23 | 10.09 | 2.97 | 70.5649 | 50 | Step 1 | 1.4113
2016-06-01 | 23 | 8.579 | 3.51 | 59.0861 | 50 | Step 1 | 1.1817
2016-07-01 | 24 | 8.27 | 3.538 | 57.2189 | 50 | Step 1 | 1.1444
2016-08-01 | 22 | 11.4 | 3.69 | 67.6316 | 50 | Step 1 | 1.3526
2016-09-01
2015-10-01 | 21 | 12.04 | 3.49 | 71.0133 | 50 | Step 1 | 1.4203 | 1.5
2015-11-01 | 28 | 17.264 | 4.18 | 75.7878 | 50 | Step 1 | 1.5158
2015-12-01 | 18 | 18.612 | 4.11 | 77.9175 | 50 | Step 1 | 1.5583
1 RAA = Running Annual Average, Computed Quarterly
Alternate Criteria
**Should only be filled out if Alternate Criteria 3 or 4 are being used
Month | Source water |  |  |  | Finished water
| DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m) |  | DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m)
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
Alternate Criteria
Alt. 1 | Source Water TOC < 2.0 mg/L
Alt. 2 | Treated Water TOC < 2.0 mg/L
Alt. 3 | Source Water SUVA < 2.0 L/mg-m
Alt. 4 | Treated Water SUVA < 2.0 L/mg-m
Prepared by: ____________________________________________ | [5 empty] | Date:
(signature) Clint Elliott Lab Supervisor

## Bacteria(new)
Bacteriological Analysis Sample Summary
1. Please fill out page 2 of this form if you have a total coliform posative sample and repeat samples.
2. Submit this form to SCDHEC along with a copy of your labrotories chain of custody no later than ten (10) days after the end of the compliance period.
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
COMPLIANCE PERIOD |  |  | 2016-09-01
CYCLE |  |  | M
(Q)-QUARTERLY (M)-MONTHLY
CHLORINE RESIDUAL |  |  | #DIV/0!
Lab ID measuring chlorine residual |  |  | 26102
# OF INITIAL SAMPLES |  |  | 0
# OF INITIAL TC POSITIVE SAMPLES |  |  | 0
# OF E. COLI POSITIVE SAMPLES |  |  | 0
TOTAL COLIFORM ANALYSIS METHOD CODE |  |  | SM9223B-2004
E. COLI ANALYSIS METHOD |  |  | SM9223B-2004
Lab ID |  |  | 26102
SIGNATURE
Date
Bacteriological Analysis Individual Samples (Part 2)
PART 2 CAN BE USED FOR ALL TOTAL COLIFORM SAMPLES AND ASSOCIATED
REPEATS AND SOURCE WATER SAMPLES
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
LAB ID |  |  | #VALUE!
TYPE | REPEAT | LAB SAMPLE NUMBER | COLLECTION DATE (MM/DD/YYYY) | [7 empty] | SAMPLING LOCATION |  | SOURCE ID | TOTAL A/P | E.COLI A/P | TOTAL/FREE CHLORINE RESIDUAL
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
Explanation: | [11 empty] | Comments
Type (RT, RP or GW ) |  |  |  | RT = Routine; RP=Repeat; GW=Groundwater
Repeat (only if sample type =RP) |  |  |  | DN = Downstream; UP=Upstream;
Lab Sample # |  |  |  | # assigned by lab for that particular sample
Collection Date (mmddyyyy) |  |  |  | Date sample was collected
Sampling Location |  |  |  | Physical address where sample was collected
Source ID(only used for source samples) |  |  |  | 5 digit DHEC Source ID (ie. G_ _ _ _ _)
Total Coliform (A or P) |  |  |  | Indicate with an "A" if absent or a "P" if present
E. Coli = (A or P) |  |  |  | E = Ecoli Positive
Total/Free Chlorine Residual |  |  |  | Chlorine Residual Reading
Within 24 hours of learning of a total coliform-positive (TC+) sample result, REPEAT samples must be collected and analyzed for total coliforms:
One REPEAT sample must be collected from the same tap as the TC+ sample.
One REPEAT sample must be collected within five service connections upstream of the TC+ sample.
One REPEAT sample must be collected within five service connections downstream of the TC+ sample.
If the system is served by Ground water then a Triggered Source sample must be collected prior to treatment from each source in use at the time the total coliform-positive sample was collected. The number of samples taken PER WELL must equal the number of positive TCR samples. If you collected three TC+ samples, then three well samples must be taken at EACH WELL that was in service at the time.
The triggered source water sample must be analyzed for the presence of E.coli.
If any triggered source water sample is E.coli-positive, the Ground Water system (GWS) must either take corrective action, as directed by the state, or the GWS must take 5 additional source water sampleswithin 24 hours.
If the GW system Purchases some or all af there water they must notify the wholesale system (s) within 24 hours.
If any REPEAT sample is TC+:
The system must analyze that total coliform-positive culture for E.coli.
The system must collect another set of REPEAT samples, as before, unless the E.coli MCL has been violated or an assessment has been triggered.
For a system on quarterly monitoring, a TC+ result requires a minimum of three ROUTINE samples be collected the following month.
CALL SCDHEC on the same day you learned of the E. coli-positive (EC+) result, or by the end of the next business day if the result came in after business hours
Please submit a copy of your labrotories chain of custody along with this form.

## Bacteria
Bacteriological Analysis Sample Summary (Part 1)
PART 1 CAN BE USED IN ONE (1) OF TWO (2) WAYS
1. If the system has had no Total Coliform (TC) Positives samples for a compliance cycle or,
2. If the system wants to report those samples that were initial TC Absent and use Part 2 for
the TC Present and all repeats.
DESCRIPTION
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
0 | 4 | 0 | 1 | 2 | 0 | 1 | 6 | 2 |  |  |  |  | First day of month / quarter
1 | 2 | 0 | [10 empty] | # of Initial Total Coliform Negative
0 | 4 | 0 | 2 | 2 | 0 | 1 | 6 | [5 empty] | M=Month; Q=Quarter; Y=Year
| 2 | 6 | 1 | 0 | 2 |  |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
Note: This can be used for any system that does
not have a total coliform positive
DOES SYSTEM ADD DISINFECTION | [8 empty] | YES
AVERAGE DISINFECTION RESIDUAL | [8 empty] | 3 | . | 4 | 2
AND/OR
Bacteriological Analysis Individual Samples (Part 2)
NOTE: This form would only be used for the initial routine (RT) TC or TC/FC Positive and
and the Repeats that are required by regulation.
PART 2 CAN MUST BE USED FOR ALL TOTAL COLIFORM POSITIVES AND ALL ASSOCIATED
REPEATS
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
|  | 2 | 6 | 1 | 0 | 2 |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
[15 empty] | Total | Fecal (F) or | Free/Total
[13 empty] | TYPE | Lab Sample ID | Coliform | E Coli (E) + | Chlorine
SAMPLE ID # AND LOCATION | [8 empty] | COLLECTION DATE (MMDDYYYY) |  |  |  | (RT or RP) | Number | A/P | If Present | Residual*
.
.
.
.
.
.
Explanation:
Collection Date (mmddyyyy)………………..Date sample was collected
Lab Sample #…………………………………# assigned by lab for that particular sample
Type (RT or RP)………………………………RT = Routine; RP=Repeat
Sampling Point ID……………………………..If lab has something that identifies site other than physical location
Sampling Location……………………………Physical address where sample was collected from
Total Coliform (A or P)…………………….Indicate with an "A" if absent or a "P" if present
FC (F = FC+ or E = Ecoli+)…………………..F= Fecal Coliform Positive; E = Ecoli Positive
Total/Free Chlorine Residual…………………………Chlorine Residiual Reading

## TOC Sample ID
TOC SAMPLE ID LOG
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  | 2018-02-01
Lab Cert ID #: 26102
Treated | TOC | Raw | TOC | Alkalinity
D-02011608 |  | D-02011611 |  | 20
D-02011609
D-02011610

## Calculation for TOC
| TOC | [6 empty] | Sample Number | [5 empty] | Raw
| Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled |  | Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled | Alkalinity
Week 1
| 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 |  | D-07061506 | D-07061507 | D-07061511 | D-07061508 | D-07061509 | D-07061510 | 36
2.47
5.88
Week 2
#DIV/0!
#DIV/0!
Week 3
#DIV/0!
#DIV/0!
Week 4 | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786
2.931
7.579
Average | 2.7005 | 2.555 | 6.7295 | 4.2765 | 2.8045 | 2.619 | [5 empty] | Average Alkalinity Raw |  | 36
Max | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786 | 3.726
Min | 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 | 2.7407
Average Treated TOC |  |  | 3.2333
Average % TOC Removal |  |  | 51.9528
Max % TOC Removal |  |  | 59.2738
Min % TOC Removal |  |  | 44.6318
TOC Sample ID Number Submittal
Treated | TOC |  |  | Raw | TOC | Alkalinity

## Chem Cost
2018-02-01
Chemical Usage / Dosage / Cost
Chemical | Usage |  | Dosage (mg/l) |  |  | Cost ($) |  |  | Alternate Units |  |  | density as is |  | Purity
| Unit | Total | Average | Maximum | Minimum | $/Unit | Total $ | $/1000 gal water | Unit | Total | $/unit | g/ml | lb/gal | wt. % | lb/gal
Pre Chlorine | gals | 8436.5747 | 1.5146 | 1.751 | 1.2874 | 0.81 | 6833.6255 | 0.010019 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Aluminum Sulfate | gals | 64462.9605 | 56.4893 | 71.8824 | 40.1196 | 1.69 | 108942.4033 | 0.15972 | lbs | 713862.8249 | 0.15225 | 1.325 | 11.05 | 48.5 | 5.36
Pre Caustic | gals | 0 | 0 | 0 | 0 | 1.86 | 0 | 0 | lbs | 0 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Post Chlorine | gals | 17280.4716 | 3.7071 | 3.8204 | 3.5822 | 0.81 | 13997.182 | 0.020521 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Ammonia | gals | 2522.0025 | 0.66928 | 0.72724 | 0.57916 | 0.68 | 1714.9617 | 0.0025143 |  |  |  | 0.928 | 7.74 | 19.5 | 1.51
Post Caustic | gals | 6398.0237 | 7.2345 | 8.3396 | 6.423 | 1.86 | 11900.3241 | 0.017447 | lbs | 81638.7828 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Lime | gals | 40323.38 | 17.8102 | 31.4501 | 0.8971 | 0.055 | 2217.7859 | 0.0032515
Fluoride | gals | 1628.7927 | 0.45601 | 0.49376 | 0.40925 | 3.2 | 5212.1365 | 0.0076416 | lbs | 16450.806
Activated Carbon | lbs | 18280 | 2.9883 | 3.654 | 2.6302 | 0.89 | 16269.2 | 0.023853
Polymer | gals | 109.9637 | 0.16467 | 0.24286 | 0.12119 | 11.95 | 1314.0666 | 0.0019266 | lbs | 945.6881 | 1.39
Filter Aid | gals | 0 | 0 | 0 | 0 | 5.59 | 0 | 0 | lbs | 0 | 0.65
Zinc Chloride Dosed as Zinc | gals | 151.0518 | 0.10219 | 0.10973 | 0.096766 | 6.89 | 1040.7466 | 0.0015259 | lbs | 1978.778 | 0.526
Corrosion Inhibitor Dosed as Phosphorus | gals | 1268.7012 | 1.0886 | 1.1676 | 0.94376 | 11.72 | 14869.1781 | 0.0218 | lbs | 18396.1674 | 0.808
|  |  | Total Chemical Cost |  |  |  | 184311.6102
|  |  | Cost per 1000 gallons |  |  |  | 0.27022

## Extras
| TOC | [25 empty] | pH |  |  |  | Alkalinity |  |  |  | Hardness |  |  |  | Turbidity |  |  |  | Color |  |  |  | Temp |  |  |  | TRC |  |  | Fluoride |  |  | Flow (MG) |  |  |  | COLIFORM
| Finish1 | Finish2 | Raw |  | Conductivity |  |  | TDS |  |  | Chloride |  |  |  | Sodium |  |  | Sulfate |  |  | Iron |  |  | Manganese |  |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 |  | Finish1 | Finish2 |  | Raw | Finish1 | Finish2 |  | Raw | Finish1 | Finish2
Week 1 |  |  |  |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | 7.3067 | 7.5917 | 6.95 |  | 27.5 | 28.5 | 24.5 |  | 29.5 | 31 | 18.8333 |  | 0.062 | 0.063 | 12.1 |  | 1 | 1 | 42.3333 |  | 10.25 | 10.8833 | 10.95 |  | 3.8 | 3.9 |  | 0.5262 | 0.7274 |  | 25.755 | 9.928 | 14.638 |  | 420 | A | A
|  |  |  | Week 1 | [6 empty] | 11.1 | 11.3 | 7.27 |  |  |  |  | 21.8 | 21.9 | 7.46 | [6 empty] | 7.3233 | 7.8233 | 6.8867 |  | 26 | 25.5 | 24.1667 |  | 21 | 20.5 | 19.5 |  | 0.063 | 0.066 | 42.3 |  | 1 | 1 | 40.8333 |  | 10.1167 | 11.0667 | 10.9833 |  | 3.5 | 3.7 |  | N/A | N/A |  | 9.306 | 9.306 | 13.016 |  | 2382 | A | A
|  |  |  | Week 2 | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  |  |  |  | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.3317 | 7.615 | 6.8267 |  | 21.5 | 22.5 | 23.1667 |  | 20 | 19.5 | 21.1667 |  | 0.067 | 0.056 | 41.5 |  | 1 | 1 | 44.6667 |  | 9.6667 | 10.4 | 10.3167 |  | 3.8 | 3.5 |  | 0.4807 | 0.5952 |  | 10.358 | 10.358 | 14.14 |  | 545 | A | A
|  |  |  | Week 3 | [22 empty] | 7.5317 | 7.69 | 6.8083 |  | 22.5 | 21.5 | 22.1667 |  | 22.5 | 23.5 | 21.8333 |  | 0.063 | 0.067 | 30.1 |  | 1 | 1 | 50.1667 |  | 9.3167 | 10.3833 | 9.9333 |  | 4.2 | 3.7 |  | 0.4979 | 0.6308 |  | 11.23 | 11.23 | 14.577 |  | 464 | A | A
|  |  |  | Week 4 | [10 empty] | 13.3 | 13.5 | 9.1 | [9 empty] | 7.675 | 7.915 | 6.7867 |  | 25.5 | 26 | 22.6667 |  | 37 | 38.5 | 21.1667 |  | 0.07 | 0.073 | 25.9 |  | 1 | 1 | 63.1667 |  | 9.9833 | 10.7833 | 10.7833 |  | 3.9 | 3.9 |  | 0.5343 | 0.7167 |  | 10.061 | 10.061 | 13.183 |  | 359 | A | A
[27 empty] | 7.69 | 7.8517 | 6.7983 |  | 26 | 26 | 21 |  | 47 | 46.5 | 20.5 |  | 0.062 | 0.068 | 21.8 |  | 1.3333 | 1.3333 | 65.3333 |  | 10.35 | 11.2833 | 10.9667 |  | 4.1 | 4 |  | 0.4845 | 0.7037 |  | 9.875 | 9.875 | 13.733 |  | 839 | A | A
#DIV/0! | [26 empty] | 7.7283 | 7.6283 | 6.75 |  | 24.5 | 21.5 | 22.3333 |  | 39.5 | 40.5 | 19.6667 |  | 0.064 | 0.069 | 28.2 |  | 1 | 1 | 65.8333 |  | 10.8 | 11.4167 | 11.8833 |  | 3.8 | 3.5 |  | 0.4761 | 0.6108 |  | 12.019 | 12.019 | 18.518 |  | 1223 | A | A
#DIV/0! |  |  |  | Average | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.8 | 11.95 | 8.535 |  | 13.3 | 13.5 | 9.1 | 23.65 | 23.8 | 8.705 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.6967 | 7.5317 | 6.7667 |  | 25 | 22.5 | 19.5 |  | 44 | 42.5 | 19.3333 |  | 0.084 | 0.068 | 33.6 |  | 1.1667 | 1.1667 | 65.8333 |  | 11.55 | 12.45 | 12.7667 |  | 3.6 | 3.7 |  | 0.5768 | 0.6654 |  | 10.379 | 10.379 | 15.218 |  | 1198 | A | A
Week 2 | 2.74 | 2.51 | 7.02 | Max | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  | 13.3 | 13.5 | 9.1 | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.6717 | 7.5533 | 6.7833 |  | 24 | 21.5 | 20.6667 |  | 41 | 38 | 17.6667 |  | 0.055 | 0.062 | 40.8 |  | 1 | 1 | 55.3333 |  | 11.4 | 12.4167 | 12.5167 |  | 3.7 | 3.6 |  | 0.5061 | 0.603 |  | 9.519 | 9.519 | 13.35 |  | 4352 | A | A
|  |  |  | Min | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.1 | 11.3 | 7.27 |  | 13.3 | 13.5 | 9.1 | 21.8 | 21.9 | 7.46 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.4567 | 7.4267 | 6.7483 |  | 22 | 22.5 | 20.8333 |  | 33 | 32.5 | 17.5 |  | 0.089 | 0.066 | 35 |  | 1.1667 | 1 | 52.1667 |  | 11.5333 | 12.3 | 12.55 |  | 3 | 3.2 |  | 0.4356 | 0.502 |  | 9.714 | 9.714 | 14.522 |  | 2143 | A | A
[27 empty] | 7.9517 | 7.5383 | 6.6833 |  | 22 | 20 | 19.5 |  | 29 | 30 | 17.1667 |  | 0.074 | 0.071 | 44.9 |  | 1 | 1 | 61.6667 |  | 12.4833 | 13.1333 | 13.1833 |  | 3.8 | 3 |  | 0.5693 | 0.5466 |  | 10.121 | 10.121 | 14.84 |  | 1723 | A | A
[15 empty] | Flow (MG) | [11 empty] | 7.6383 | 7.5 | 6.725 |  | 21.5 | 23 | 19.6667 |  | 37.5 | 37 | 16.5 |  | 0.067 | 0.067 | 44.2 |  | 1.1667 | 1.1667 | 56.6667 |  | 13.1333 | 13.75 | 13.9167 |  | 3.8 | 3.5 |  | 0.5351 | 0.5511 |  | 9.416 | 9.416 | 14.404 |  | 1956 | A | A
[15 empty] | Raw | Comb Fin |  |  | Aluminum |  |  | Phosph Fin1 |  | Phosph Fin2 |  |  | 7.56 | 7.4633 | 6.7333 |  | 22.5 | 21 | 19.5 |  | 36 | 33.5 | 15 |  | 0.063 | 0.065 | 33 |  | 1.6667 | 1.3333 | 50 |  | 13.3167 | 13.8833 | 13.9833 |  | 3.5 | 3.4 |  | 0.4325 | 0.4979 |  | 8.403 | 8.403 | 15.165 |  | 1086 | A | A
[14 empty] | 1 | 25.755 | 24.566 |  |  | 1 Filter | 2 Filter | 3 Filter | Total | Ortho | Total | Ortho |  | 7.4567 | 7.4433 | 6.61 |  | 22.5 | 22 | 21.1667 |  | 39.5 | 40 | 18.8333 |  | 0.059 | 0.063 | 29.2 |  | 1.1667 | 1.1667 | 54.5 |  | 12.8833 | 12.95 | 13.2667 |  | 3.4 | 3.2 |  | 0.5533 | 0.6278 |  | 9.525 | 9.525 | 14.557 |  | 548 | A | A
2.74 | [13 empty] | 2 | 26.148 | 22.322 |  | Week 1 |  |  |  | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.6667 | 7.7333 | 6.7033 |  | 24 | 24 | 21.8333 |  | 43 | 42 | 19 |  | 0.069 | 0.074 | 28.7 |  | 1.1667 | 1.1667 | 57.6667 |  | 13.3833 | 13.25 | 13.8167 |  | 3.3 | 3.4 |  | 0.5495 | 0.5941 |  | 10.307 | 10.307 | 14.535 |  | 602 | A | A
7.02 | [13 empty] | 3 | 28.135 | 24.498 |  | Week 2 | 0.036 | 0.036 | 0.029 | [5 empty] | 7.445 | 7.535 | 6.6933 |  | 22 | 21.5 | 21.6667 |  | 43 | 44.5 | 20.1667 |  | 0.063 | 0.063 | 25.9 |  | 1 | 1 | 56.5 |  | 13.8167 | 14.0667 | 14.4667 |  | 4.1 | 3.5 |  | 0.5021 | 0.5475 |  | 10.995 | 10.995 | 14.323 |  | 504 | A | A
Week 3 | [13 empty] | 4 | 27.554 | 25.807 |  | Week 3 |  |  |  | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.7667 | 7.81 | 6.7383 |  | 23.5 | 23 | 22 |  | 38 | 38.5 | 19.8333 |  | 0.074 | 0.07 | 21.3 |  | 1 | 1 | 51.6667 |  | 14.15 | 14.0667 | 14.6667 |  | 4.4 | 2.8 |  | 0.5777 | 0.5498 |  | 11.093 | 11.093 | 14.258 |  | 473 | A | A
[14 empty] | 5 | 25.357 | 23.244 |  | Week 4 | [8 empty] | 7.455 | 7.4267 | 6.6783 |  | 22.5 | 23 | 21.3333 |  | 33.5 | 34 | 19.5 |  | 0.063 | 0.061 | 18.8 |  | 1 | 1 | 52.3333 |  | 14.25 | 14.1667 | 14.8833 |  | 4.2 | 3.1 |  | 0.5205 | 0.5977 |  | 10.975 | 10.975 | 13.286 |  | 504 | A | A
[14 empty] | 6 | 25.517 | 23.608 | [10 empty] | 7.3233 | 7.3667 | 6.6567 |  | 24 | 24.5 | 21.3333 |  | 36 | 36 | 20 |  | 0.067 | 0.059 | 15.9 |  | 1 | 1 | 53.3333 |  | 14.5333 | 14.3833 | 15.25 |  | 4 | 3.5 |  | 0.543 | 0.607 |  | 10.753 | 10.753 | 13.374 |  | 576 | A | A
[14 empty] | 7 | 27.954 | 30.537 | [10 empty] | 7.43 | 7.6867 | 6.6483 |  | 26 | 25.5 | 23.3333 |  | 32 | 33.5 | 19.6667 |  | 0.069 | 0.074 | 14 |  | 1 | 1 | 54.8333 |  | 15.0667 | 15.0333 | 15.85 |  | 3.9 | 3.5 |  | 0.568 | 0.6192 |  | 11.101 | 11.101 | 12.039 |  | 480 | A | A
[14 empty] | 8 | 27.561 | 25.597 |  | Average | 0.036 | 0.036 | 0.029 | 0.681 | 0.048 | 0.6905 | 0.0445 |  | 7.1567 | 7.3133 | 6.4767 |  | 26 | 25 | 22.5 |  | 32.5 | 36.5 | 20 |  | 0.062 | 0.069 | 12.8 |  | 1.1667 | 1.1667 | 55 |  | 15.9167 | 15.6 | 16.85 |  | 3.8 | 3.3 |  | 0.4817 | 0.578 |  | 10.399 | 10.399 | 13.187 |  | 441 | A | A
[14 empty] | 9 | 24.431 | 22.869 |  | Max | 0.036 | 0.036 | 0.029 | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.0533 | 7.2517 | 6.62 |  | 23.5 | 24.5 | 23 |  | 31.5 | 32.5 | 19 |  | 0.065 | 0.064 | 9.01 |  | 1 | 1.1667 | 59.3333 |  | 16.4167 | 16.3667 | 17.35 |  | 3.4 | 3.4 |  | 0.5872 | 0.6062 |  | 11.76 | 11.76 | 14.16 |  | 364 | A | A
#DIV/0! | [13 empty] | 10 | 26.106 | 24.236 |  | Min | 0.036 | 0.036 | 0.029 | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.5717 | 7.2517 | 6.6167 |  | 26 | 25.5 | 23.3333 |  | 32.5 | 31.5 | 19 |  | 0.064 | 0.064 | 8.91 |  | 1 | 1.1667 | 56.3333 |  | 16.85 | 16.6667 | 17.6667 |  | 3.4 | 3.4 |  | 0.6262 | 0.6497 |  | 11.31 | 11.31 | 13.55 |  | 364 | A | A
#DIV/0! | [13 empty] | 11 | 26.755 | 24.961 | [10 empty] | 7.5633 | 7.7783 | 6.6233 |  | 22 | 23 | 21 |  | 29.5 | 30 | 18.5 |  | 0.063 | 0.058 | 8.24 |  | 1.3333 | 1.3333 | 58 |  | 17.1667 | 16.9 | 18.2667 |  | 3.7 | 3.4 |  | 0.536 | 0.6385 |  | 10.7 | 10.7 | 14.11 |  | 189 | A | A
Week 4 | [13 empty] | 12 | 26.213 | 23.82 |  | Average 1,2,3 |  | 0.033667 | [6 empty] | 7.4783 | 7.47 | 6.6317 |  | 20 | 23 | 21.3333 |  | 29 | 28 | 16.1667 |  | 0.059 | 0.059 | 7.55 |  | 1 | 1.3333 | 65.8333 |  | 17.7167 | 17.3 | 18.8167 |  | 3.9 | 3.6 |  | 0.5392 | 0.5945 |  | 11.09 | 11.09 | 13.74 |  | 246 | A | A
[14 empty] | 13 | 25.197 | 23.568 | [10 empty] | 7.285 | 7.3533 | 6.575 |  | 26 | 25.5 | 22 |  | 39 | 39 | 17.1667 |  | 0.07 | 0.065 | 8.3 |  | 1.8333 | 1.8333 | 72 |  | 18.2667 | 17.4333 | 19.1833 |  | 3.7 | 3.4 |  | 0.5403 | 0.6041 |  | 10.495 | 10.495 | 14.315 |  | 213 | A | A
[14 empty] | 14 | 26.105 | 24.082 | [8 empty] | Day |  | 7.4483 | 7.62 | 6.585 |  | 25.5 | 29.5 | 23 |  | 38 | 38 | 18.8333 |  | 0.06 | 0.06 | 9.9 |  | 1.3333 | 1.3333 | 73.6667 |  | 18 | 17.1833 | 18.55 |  | 4.1 | 3.9 |  | 0.5447 | 0.6986 |  | 10.095 | 10.095 | 13.935 |  | 318 | A | A
[14 empty] | 15 | 26.558 | 24.842 | [8 empty] | 28 |  | 7.3083 | 7.425 | 6.6017 |  | 28 | 27.5 | 23.8333 |  | 49 | 49 | 19.5 |  | 0.075 | 0.072 | 8.4 |  | 1 | 1 | 74.6667 |  | 17.1833 | 16.5167 | 17.55 |  | 4.2 | 4.3 |  | 0.6128 | 0.7037 |  | 8.197 | 8.197 | 10.278 |  | 373 | A | A
[14 empty] | 16 | 27.109 | 25.318 | [8 empty] | 29 | [7 empty] | 0 | [23 empty] | 0 | 0 | 0 |  | 0 | 0 | 0
#DIV/0! | [13 empty] | 17 | 26.743 | 25.351 | [8 empty] | 30 | [31 empty] | 0 | 0 | 0 |  | 0 | 0 | 0
#DIV/0! | [13 empty] | 18 | 26.522 | 24.261 | [8 empty] | 31 | [31 empty] | 0 | 0 | 0 |  | 0 | 0 | 0
Average | 2.74 | 2.51 | 7.02 | [10 empty] | 19 | 26.638 | 24.127 | [8 empty] | Avg 1 |  | 7.5354 | 7.7058 | 6.8217 | Avg 1 | 24.8125 | 24.25 | 22.4375 | Avg 1 | 32.5625 | 32.8125 | 20.25 | Avg 1 | 0.066875 | 0.06625 | 29.4375 | Avg 1 | 1.0625 | 1.0625 | 54.7708 | Avg 1 | 10.2542 | 11.0833 | 11.0729 | Avg 1 | 3.8375 | 3.7375 | Avg 1 | 0.51093 | 0.66429 | Avg 1 | 12.3729 | 10.3945 | 14.6279 | Avg 1 | 928.75
Max | 2.74 | 2.51 | 7.02 | [10 empty] | 20 | 23.989 | 23.14 | [8 empty] | Avg 2 |  | 7.6288 | 7.5226 | 6.7124 | Avg 2 | 22.6429 | 22 | 20.4524 | Avg 2 | 37 | 36.1429 | 17.381 | Avg 2 | 0.068 | 0.066857 | 36.5429 | Avg 2 | 1.1905 | 1.119 | 55.4286 | Avg 2 | 12.5905 | 13.0976 | 13.319 | Avg 2 | 3.5 | 3.3286 | Avg 2 | 0.51163 | 0.56036 | Avg 2 | 9.5721 | 9.5721 | 14.4819 | Avg 2 | 1772.8571
Min | 2.74 | 2.51 | 7.02 | [10 empty] | 21 | 24.843 | 23.586 | [8 empty] | Avg 3 |  | 7.4002 | 7.4552 | 6.641 | Avg 3 | 24.1875 | 24.0625 | 22.3125 | Avg 3 | 34.875 | 35.875 | 19.6458 | Avg 3 | 0.065875 | 0.0655 | 15.8275 | Avg 3 | 1.0208 | 1.0625 | 54.9167 | Avg 3 | 15.125 | 15.0438 | 15.8729 | Avg 3 | 3.9 | 3.3125 | Avg 3 | 0.5508 | 0.59439 | Avg 3 | 11.0483 | 11.0483 | 13.5221 | Avg 3 | 463.25
[14 empty] | 22 | 28.185 | 25.92 | [8 empty] | Avg 4 |  | 7.4167 | 7.5293 | 6.6033 | Avg 4 | 24.3 | 25.7 | 18.5278 | Avg 4 | 36.9 | 36.8 | 18.0333 | Avg 4 | 0.0654 | 0.0628 | 8.478 | Avg 4 | 1.3 | 1.3667 | 68.8333 | Avg 4 | 17.6667 | 17.0667 | 18.4733 | Avg 4 | 3.92 | 3.72 | Avg 4 | 0.5546 | 0.64788 | Avg 4 | 6.3221 | 6.3221 | 8.2973 | Avg 4 | 167.375
Fin1 | [13 empty] | 23 | 27.575 | 24.86 | [12 empty] | pH | Alk | Hard |  | Turb | Color | Temp |  | Coliform | TRC | Fluoride
CCR Data | High |  | Low | Avg | [9 empty] | 24 | 26.96 | 24.81 | [8 empty] | Avg 1 |  | Raw |  | 6.8217 | 22.4375 | 20.25 |  | 29.4375 | 54.7708 | 11.0729 |  | 928.75
Turbidity | 0.089 |  | 0.042 | 0.057679 | [9 empty] | 25 | 26.315 | 24.83 | [8 empty] | Avg 2 |  |  |  | 6.7124 | 20.4524 | 17.381 |  | 36.5429 | 55.4286 | 13.319 |  | 1772.8571
Fluoride | 0.6262 |  | 0.4325 | 0.53101 | [9 empty] | 26 | 27.465 | 24.81 | [8 empty] | Avg 3 |  |  |  | 6.641 | 22.3125 | 19.6458 |  | 15.8275 | 54.9167 | 15.8729 |  | 463.25
Sulfate | 25.5 |  | 21.8 | 23.65 | [9 empty] | 27 | 25.18 | 24.03 | [8 empty] | Avg 4 |  |  |  | 6.6033 | 18.5278 | 18.0333 |  | 8.478 | 68.8333 | 18.4733 |  | 167.375
Iron | 0.003 |  | 0.003 | 0.003 | [9 empty] | 28 | 22.15 | 18.475 | [8 empty] | Avg 1 |  | Finished |  | 7.5354 | 24.8125 | 32.5625 |  | 0.066875 | 1.0625 | 10.2542 |  |  | 3.8375 | 0.51093
Manganes | 0.029 |  | 0.029 | 0.029 | [9 empty] | 29 | 0 | 0 | [8 empty] | Avg 2 |  |  |  | 7.6288 | 22.6429 | 37 |  | 0.068 | 1.1905 | 12.5905 |  |  | 3.5 | 0.51163
pH | 7.9517 |  | 7.0533 | 7.4989 | [9 empty] | 30 | 0 | 0 | [8 empty] | Avg 3 |  |  |  | 7.4002 | 24.1875 | 34.875 |  | 0.065875 | 1.0208 | 15.125 |  |  | 3.9 | 0.5508
Color | 1.8333 |  | 1 | 1.125 | [9 empty] | 31 | [10 empty] | Avg 4 |  |  |  | 7.4167 | 24.3 | 36.9 |  | 0.0654 | 1.3 | 17.6667 |  |  | 3.92 | 0.5546
Chloride | 12.5 |  | 11.1 | 11.8
TOC | 2.74 |  | 2.74 | 2.74
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.681
o-phosph |  |  |  | 0.048
Aluminum |  |  |  | 0.033667
Fin2
CCR Data | High |  | Low | Avg
Turbidity | 0.089 |  | 0.042 | 0.058429
Fluoride | 0.7274 |  | 0.4979 | 0.61359
Sulfate | 25.7 |  | 21.9 | 23.8
Iron | 0.006 |  | 0.006 | 0.006
Manganes | 0.033 |  | 0.033 | 0.033
pH | 7.915 |  | 7.2517 | 7.5569
Color | 1.8333 |  | 1 | 1.131
Chloride | 12.6 |  | 11.3 | 11.95
TOC | 2.51 |  | 2.51 | 2.51
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.6905
o-phosph |  |  |  | 0.0445
Aluminum |  |  |  | 0.033667
TOC Ratio |  |  |  | #REF!
TOC % Removal |  |  |  | #REF!

## LAB
DAILY LAB SHEET
2018-02-01
| RAW | [13 empty] | Filtered #1 |  |  |  | Filtered #2 |  |  |  | Filtered #3 |  |  |  | Settled #1 | [11 empty] | Settled #2 | [11 empty] | Settled #3 | [12 empty] | Finished Plant #1 | [16 empty] | Finished Plant #2
| pH | Temp | Alk | DO | TOC | DOC | UV-254 | SUVA | Factor | Low | High | Total Coliform | E. coli | Temp. °C | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Settled Water Average TOC | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T |  | Decant Flow | Back Wash Water | Backwash Waste Sludge flow | Alum sludge | Raw
1 |  |  | 32 |  | 6.203 | 5.656 | 0.194 | 3.43 | 29.1546 | 145.7732 | 291.5464 | 420 | 20 |  |  | 2 | 0.063 | 0.64 |  | 2 | 0.057 | 0.62 |  | 2 | 0.051 | 0.54 |  |  |  | 5.94 | 10.5 | 6 | 0.433 | 2.476 | 2.342 | 0.034 | 60.0838 | 1.4518 |  |  |  | 5.99 | 10.2 | 7 | 0.465 | 2.495 | 2.355 | 0.036 | 59.7775 | 1.5287 |  |  |  | 5.97 | 11.8 | 8 | 0.563 | 2.612 | 2.433 | 0.037 | 57.8913 | 1.5208 | 2.5277 | 7.38 | 10.3 | 2 | 0.051 | 27 | 29 | 4.1 |  |  | 0.5262 |  |  | 2.32 | 2.333 | 0.054 | 2.3146 | A | 7.49 | 10.6 | 2 | 0.053 | 29 | 32 | 4.1 |  |  | 0.7274 |  |  | 2.343 | 2.353 | 0.054 | 2.2949 | A |  | 1.263 | 0 | 0 | 0
2 | [11 empty] | 2382 | 10 | [66 empty] | A | [16 empty] | A |  | 1.376 | 0 | 0 | 0
3 | [11 empty] | 545 | 41 | [59 empty] | 0.4807 | [6 empty] | A | [9 empty] | 0.5952 | [6 empty] | A |  | 1.241 | 0 | 0 | 0
4 | [11 empty] | 464 | 10 | [59 empty] | 0.4979 | [6 empty] | A | [9 empty] | 0.6308 | [6 empty] | A |  | 1.051 | 0 | 0 | 0
5 |  |  | 23 |  | 9.914 | 8.911 | 0.326 | 3.658 | 27.3344 | 136.6718 | 273.3436 | 359 | 10 |  |  | 2 | 0.118 | 0.42 | [5 empty] | 2 | 0.066 | 0.39 |  |  |  | 5.83 | 10.3 | 7 | 0.582 | 3.251 | 3.145 | 0.049 | 67.208 | 1.558 |  |  |  | 5.87 | 9.7 | 7 | 0.58 | 3.284 | 3.155 | 0.051 | 66.8751 | 1.6165 |  |  |  | 5.9 | 11.6 | 7 | 0.596 | 3.386 | 3.202 | 0.051 | 65.8463 | 1.5928 | 3.307 | 7.84 | 10.5 | 2 | 0.063 | 25 | 36 | 4.5 |  |  | 0.5343 |  |  | 3.107 | 3.063 | 0.069 | 2.2527 | A | 8.06 | 10.6 | 2 | 0.065 | 26 | 39 | 4.4 |  |  | 0.7167 |  |  | 3.143 | 3.146 | 0.07 | 2.225 | A |  | 1.306 | 0 | 0 | 0
6 | 6.85 | 11 | [9 empty] | 839 | 31 |  |  | 2 | 0.063 | 0.33 |  | 2 | 0.058 | 0.21 |  | 2 | 0.052 | 0.24 |  |  |  | 5.82 | 10 | 7 | 0.527 | [8 empty] | 5.83 | 10.2 | 6 | 0.476 | [8 empty] | 5.84 | 11.3 | 7 | 0.5 | [6 empty] | 7.52 | 11 | 2 | 0.056 | 26 | 46 | 4.1 |  |  | 0.4845 | [6 empty] | A | 7.9 | 12 | 2 | 0.054 | 26 | 45 | 4.5 |  |  | 0.7037 | [6 empty] | A |  | 1.097 | 0 | 0 | 0
7 | 7.05 | 11.4 | [9 empty] | 1223 | <10 |  |  | 2 | 0.057 | 0.38 |  | 2 | 0.058 | 0.36 |  | 2 | 0.055 | 0.29 |  |  |  | 6.18 | 10.7 | 12 | 0.943 | [8 empty] | 6.17 | 10.9 | 13 | 1.09 | [8 empty] | 6.1 | 11.9 | 13 | 0.999 | [6 empty] | 8.02 | 11.4 | 3 | 0.058 | 27 | 47 | 3.8 |  |  | 0.4761 | [6 empty] | A | 7.9 | 11.4 | 3 | 0.058 | 23 | 49 | 4 |  |  | 0.6108 | [6 empty] | A |  | 1.3 | 0 | 0 | 0
8 | 7.11 | 12.2 | 22 |  | 9.943 | 9.093 | 0.316 | 3.475 | 28.7753 | 143.8766 | 287.7532 | 1198 | <10 |  |  | 3 | 0.068 | 0.53 |  | 2 | 0.056 | 0.48 |  | 2 | 0.06 | 0.54 |  |  |  | 5.93 | 12 | 7 | 0.512 | 3.207 | 3.1 | 0.049 | 67.7462 | 1.5806 |  |  |  | 5.96 | 12.5 | 6 | 0.459 | 3.159 | 3.066 | 0.051 | 68.2289 | 1.6634 |  |  |  | 5.94 | 13.4 | 7 | 0.509 | 3.222 | 3.137 | 0.049 | 67.5953 | 1.562 | 3.196 | 7.76 | 11.8 | 3 | 0.054 | 25 | 48 | 4.6 |  |  | 0.5768 |  |  | 3.107 | 3.109 | 0.074 | 2.3802 | A | 7.55 | 12.2 | 3 | 0.056 | 24 | 43 | 4.3 |  |  | 0.6654 |  |  | 3.103 | 3.109 | 0.072 | 2.316 | A |  | 2.063 | 0 | 0 | 0
9 | 7.07 | 12.2 | [9 empty] | 4352 | 63 |  |  | 2 | 0.056 | 0.51 |  | 2 | 0.058 | 0.53 |  | 2 | 0.059 | 0.55 |  |  |  | 5.9 | 11.7 | 7 | 0.671 | [8 empty] | 5.96 | 12.3 | 5 | 0.495 | [8 empty] | 5.99 | 14.1 | 6 | 0.55 | [6 empty] | 7.67 | 11.7 | 2 | 0.058 | 26 | 47 | 4 |  |  | 0.5061 | [6 empty] | A | 7.69 | 12.2 | 2 | 0.061 | 21 | 43 | 3.9 |  |  | 0.603 | [6 empty] | A |  | 1.258 | 0 | 0 | 0
10 | [11 empty] | 2143 | 51 | [59 empty] | 0.4356 | [6 empty] | A | [9 empty] | 0.502 | [6 empty] | A |  | 1.447 | 0 | 0 | 0
11 | [11 empty] | 1723 | 75 | [59 empty] | 0.5693 | [6 empty] | A | [9 empty] | 0.5466 | [6 empty] | A |  | 1.528 | 0 | 0 | 0
12 | 6.9 | 13.3 | 26 |  | 8.617 | 7.813 | 0.266 | 3.405 | 29.3722 | 146.8609 | 293.7218 | 1956 | 31 |  |  | 3 | 0.11 | 0.47 |  | 3 | 0.086 | 0.46 |  | 2 | 0.06 | 0.5 |  |  |  | 5.99 | 13 | 9 | 0.73 | 3.097 | 2.981 | 0.046 | 64.0594 | 1.5431 |  |  |  | 6.04 | 13.2 | 9 | 0.728 | 3.056 | 3.025 | 0.049 | 64.5352 | 1.6198 |  |  |  | 6.03 | 14.9 | 8 | 0.642 | 3.071 | 2.986 | 0.044 | 64.3611 | 1.4735 | 3.0747 | 7.46 | 13.3 | 3 | 0.064 | 23 | 45 | 4.7 |  |  | 0.5351 |  |  | 3 | 2.995 | 0.07 | 2.3372 | A | 7.33 | 13.5 | 3 | 0.067 | 24 | 41 | 3.8 |  |  | 0.5511 |  |  | 2.979 | 2.961 | 0.065 | 2.1952 | A |  | 1.319 | 0 | 0 | 0
13 | 6.96 | 13.6 | [9 empty] | 1086 | <10 |  |  | 2 | 0.063 | 0.4 |  | 2 | 0.061 | 0.35 |  | 2 | 0.068 | 0.49 |  |  |  | 5.97 | 13 | 9 | 0.54 | [8 empty] | 5.99 | 13.1 | 7 | 0.401 | [8 empty] | 5.98 | 14.8 | 4 | 0.353 | [6 empty] | 7.25 | 13.2 | 2 | 0.054 | 24 | 38 | 3.6 |  |  | 0.4325 | [6 empty] | A | 7.61 | 13.1 | 3 | 0.078 | 22 | 36 | 3.8 |  |  | 0.4979 | [6 empty] | A |  | 1.61 | 0 | 0 | 0
14 | 6.7 | 13 | [9 empty] | 548 | <10 |  |  | 2 | 0.065 | 0.41 |  | 3 | 0.08 | 0.39 |  | 2 | 0.06 | 0.51 |  |  |  | 5.98 | 12.5 | 6 | 0.496 | [8 empty] | 6.02 | 12.5 | 6 | 0.438 | [8 empty] | 6 | 14 | 5 | 0.363 | [6 empty] | 7.6 | 12.9 | 3 | 0.056 | 23 | 40 | 3.7 |  |  | 0.5533 | [6 empty] | A | 7.65 | 12.8 | 3 | 0.053 | 22 | 42 | 3.7 |  |  | 0.6278 | [6 empty] | A |  | 1.488 | 0 | 0 | 0
15 | 6.86 | 13.5 | 24 |  | 8.295 | 7.484 | 0.264 | 3.528 | 28.3485 | 141.7424 | 283.4848 | 602 | <10 |  |  | 2 | 0.074 | 0.46 |  | 2 | 0.065 | 0.49 |  | 2 | 0.063 | 0.5 |  |  |  | 6.07 | 13.2 | 6 | 0.337 | 2.755 | 2.677 | 0.043 | 66.7872 | 1.6063 |  |  |  | 6.15 | 13 | 6 | 0.479 | 2.741 | 2.674 | 0.043 | 66.956 | 1.6081 |  |  |  | 6.14 | 14.5 | 6 | 0.415 | 2.797 | 2.717 | 0.043 | 66.2809 | 1.5826 | 2.7643 | 7.69 | 13.2 | 2 | 0.057 | 25 | 45 | 4.6 |  |  | 0.5495 |  |  | 2.66 | 2.667 | 0.066 | 2.4747 | A | 7.81 | 12.9 | 3 | 0.074 | 25 | 42 | 4.2 |  |  | 0.5941 |  |  | 2.665 | 2.649 | 0.063 | 2.3783 | A |  | 1.058 | 0 | 0 | 0
16 | [11 empty] | 504 | <10 | [59 empty] | 0.5021 | [6 empty] | A | [9 empty] | 0.5475 | [6 empty] | A |  | 0.936 | 0 | 0 | 0
17 | [11 empty] | 473 | <10 | [59 empty] | 0.5777 | [6 empty] | A | [9 empty] | 0.5498 | [6 empty] | A |  | 1.413 | 0 | 0 | 0
18 | [11 empty] | 504 | <10 | [59 empty] | 0.5205 | [6 empty] | A | [9 empty] | 0.5977 | [6 empty] | A |  | 1.501 | 0 | 0 | 0
19 | 6.82 | 15 | 27 |  | 7.781 | 7.233 | 0.257 | 3.553 | 28.144 | 140.7198 | 281.4397 | 576 | <10 |  |  | 2 | 0.071 | 0.59 |  | 2 | 0.062 | 0.65 |  | 3 | 0.088 | 0.63 |  |  |  | 6.07 | 15 | 7 | 0.368 | 2.632 | 2.575 | 0.038 | 66.174 | 1.4757 |  |  |  | 6.14 | 14.8 | 7 | 0.4 | 2.608 | 2.535 | 0.038 | 66.4825 | 1.499 |  |  |  | 6.14 | 16.1 | 7 | 0.365 | 2.655 | 2.582 | 0.038 | 65.8784 | 1.4717 | 2.6317 | 7.42 | 14.8 | 3 | 0.058 | 26 | 40 | 4.4 |  |  | 0.543 |  |  | 2.532 | 2.544 | 0.06 | 2.3585 | A | 7.4 | 14.3 | 3 | 0.055 | 29 | 42 | 3.3 |  |  | 0.607 |  |  | 2.532 | 2.508 | 0.053 | 2.1132 | A |  | 1.332 | 0 | 0 | 0
20 | 6.8 | 15.6 | [9 empty] | 480 | 10 |  |  | 3 | 0.067 | 0.29 |  | 3 | 0.075 | 0.32 |  | 2 | 0.056 | 0.32 |  |  |  | 6.04 | 15.4 | 6 | 0.505 | [8 empty] | 6.05 | 15.2 | 5 | 0.439 | [8 empty] | 6.06 | 16.4 | 5 | 0.404 | [6 empty] | 7.27 | 14.9 | 2 | 0.054 | 29 | 37 | 4.4 |  |  | 0.568 | [6 empty] | A | 7.82 | 14.7 | 2 | 0.05 | 29 | 36 | 3.9 |  |  | 0.6192 | [6 empty] | A |  | 1.732 | 0 | 0 | 0
21 | 6.76 | 16.2 | [9 empty] | 441 | 10 |  |  | 3 | 0.063 | 0.39 |  | 2 | 0.058 | 0.47 |  | 2 | 0.059 | 0.3 |  |  |  | 6.05 | 16.3 | 6 | 0.461 | [8 empty] | 6.07 | 16.1 | 6 | 0.434 | [8 empty] | 6.07 | 17.3 | 5 | 0.331 | [6 empty] | 7.18 | 15.8 | 2 | 0.058 | 28 | 35 | 4.3 |  |  | 0.4817 | [6 empty] | A | 7.26 | 15.2 | 2 | 0.057 | 27 | 40 | 3.8 |  |  | 0.578 | [6 empty] | A |  | 1.299 | 0 | 0 | 0
22 | 6.77 | 16.8 | 26 |  | 8.235 | 7.663 | 0.283 | 3.693 | 27.0777 | 135.3887 | 270.7774 | 364 | 10 |  |  | 3 | 0.069 | 0.38 |  | 3 | 0.073 | 0.38 |  | 3 | 0.065 | 0.44 |  |  |  | 6.07 | 16.7 | 7 | 0.512 | 2.96 | 2.827 | 0.045 | 64.0559 | 1.5918 |  |  |  | 6.08 | 16.5 | 8 | 0.592 | 2.916 | 2.803 | 0.046 | 64.5902 | 1.6411 |  |  |  | 6.08 | 17.7 | 8 | 0.569 | 2.967 | 2.858 | 0.044 | 63.9709 | 1.5395 | 2.9477 | 7.1 | 16 | 3 | 0.064 | 23 | 34 | 4.3 |  |  | 0.5872 |  |  | 2.797 | 2.795 | 0.066 | 2.3614 | A | 7.28 | 15.7 | 2 | 0.057 | 28 | 34 | 3.5 |  |  | 0.6062 |  |  | 2.814 | 2.805 | 0.06 | 2.139 | A |  | 1.793 | 0 | 0 | 0
23 | 6.84 | 17.2 | [9 empty] | 364 | 31 |  |  | 2 | 0.06 | 0.38 |  | 2 | 0.067 | 0.49 |  | 2 | 0.065 | 0.51 |  |  |  | 6 | 17.1 | 7 | 0.468 | [8 empty] | 6.03 | 17 | 6 | 0.343 | [8 empty] | 6.04 | 18.1 | 6 | 0.346 | [6 empty] | 7.76 | 16.8 | 2 | 0.061 | 27 | 37 | 4.6 |  |  | 0.6262 | [6 empty] | A | 7.84 | 16 | 2 | 0.057 | 28 | 34 | 4.1 |  |  | 0.6497 | [6 empty] | A |  | 1.501 | 0 | 0 | 0
24 | [11 empty] | 189 | 10 | [59 empty] | 0.536 | [6 empty] | A | [9 empty] | 0.6385 | [6 empty] | A |  | 1.783 | 0 | 0 | 0
25 | [11 empty] | 246 | <10 | [59 empty] | 0.5392 | [6 empty] | A | [9 empty] | 0.5945 | [6 empty] | A |  | 1.287 | 0 | 0 | 0
26 | 6.73 | 18.8 | 25 |  | 10.37 | 10.04 | 0.39 | 3.884 | 25.7436 | 128.7179 | 257.4359 | 213 | <10 |  |  | 3 | 0.071 | 0.19 |  | 3 | 0.108 | 0.34 |  | 2 | 0.062 | 0.14 |  |  |  | 5.89 | 18.8 | 8 | 0.478 | 3.319 | 3.264 | 0.055 | 67.9942 | 1.685 |  |  |  | 5.96 | 18.7 | 7 | 0.363 | 3.286 | 3.198 | 0.055 | 68.3124 | 1.7198 |  |  |  | 5.97 | 19.5 | 6 | 0.259 | 3.301 | 3.257 | 0.055 | 68.1678 | 1.6887 | 3.302 | 7.22 | 18.1 | 3 | 0.067 | 25 | 45 | 4.2 |  |  | 0.5403 |  |  | 3.177 | 3.207 | 0.073 | 2.2763 | A | 7.368 | 17.2 | 3 | 0.065 | 27 | 43 | 3.9 |  |  | 0.6041 |  |  | 3.176 | 3.204 | 0.072 | 2.2472 | A |  | 1.738 | 0 | 0 | 0
27 | 6.83 | 18.1 | [9 empty] | 318 | 10 |  |  | 2 | 0.057 | 0.39 |  | 3 | 0.089 | 0.44 |  | 2 | 0.052 | 0.21 |  |  |  | 5.97 | 17.9 | 6 | 0.358 | [8 empty] | 5.98 | 17.8 | 6 | 0.381 | [8 empty] | 5.99 | 18.8 | 6 | 0.351 | [6 empty] | 7.49 | 17.7 | 3 | 0.06 | 29 | 44 | 4.7 |  |  | 0.5447 | [6 empty] | A | 8.5 | 16.8 | 3 | 0.06 | 35 | 39 | 5.3 |  |  | 0.6986 | [6 empty] | A |  | 1.793 | 0 | 0 | 0
28 | 6.79 | 17.3 | [9 empty] | 373 | <10 |  |  | 3 | 0.057 | 0.37 |  | 3 | 0.063 | 0.39 |  | 3 | 0.076 | 0.4 |  |  |  | 6.01 | 17.1 | 6 | 0.368 | [8 empty] | 6.04 | 17 | 5 | 0.316 | [8 empty] | 6.05 | 18.1 | 5 | 3.08 | [6 empty] | 7.38 | 17 | 2 | 0.058 | 28 | 49 | 4.7 |  |  | 0.6128 | [6 empty] | A | 7.53 | 16.1 | 2 | 0.058 | 27 | 49 | 4.4 |  |  | 0.7037 | [6 empty] | A |  | 1.37 | 0 | 0 | 0
[99 empty] | 0 | 0 | 0 | 0
[99 empty] | 0 | 0 | 0 | 0
[99 empty] | 0 | 0 | 0 | 0
[5 empty] | 8.6698 |  |  | 3.5783 | 27.9938 | 139.9689 | 279.9378 |  |  |  | #DIV/0! | 2.3889 |  |  | #DIV/0! | 2.4118 |  |  | #DIV/0! | 2.1667 |  |  | #DIV/0! | #DIV/0! | [5 empty] | 2.9621 |  |  | 65.5136 |  | #DIV/0! | #DIV/0! | [5 empty] | 2.9431 |  |  | 65.7197 |  | #DIV/0! | #DIV/0! | [5 empty] | 3.0014 |  |  | 64.999 |  | 2.9689 | [12 empty] | 2.8375 | [16 empty] | 2.8444 |  |  |  |  | Sum | 39.883 | 0 | 0 | 0
[98 empty] | Max | 2.063 | 0 | 0 | 0
[98 empty] | Avg. | 1.2865 | 0 | 0 | 0
Note on DG37: Sum
Note on DG38: Max
Note on DG39: Avg.

## LAB pH
[5 empty] | pH |  |  |  | Meter: | VSTAS40B2
[9 empty] | Probe: | 8102BNUWP
Date | Time | Analyst | Slope | Std. | Lot Number | Sample ID | QC | Temp | PH | Comments
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
SETTLED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | Dup.
# 2
|  |  |  | 10 | 156700
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | D
# 2
SETTLED # 1
# 2
# 3
|  |  |  | 10 | 156700