## PLANT CHECK
BULL CREEK PLANT CHECK
SHEET KEY
DATE/TIME |  | 2019-08-12 09:20 |  |  |  |  | OPERATOR |  | DB / GE |  |  | FILL IN BEFORE GOING ON PLANT CK.
FILL IN AFTER GOING ON PLANT CK.
Raw Water Pumps |  |  | 1,2,3,6 |  |  | Raw UV | 0.544 | mg/l |  |  |  | FOR MIDNIGHT PLANT OK
Caison Level |  | 13.2 | SCADA Raw flow |  | 34 | Raw TOC | 14.3158 | mg/l |  |  |  | THIS IS WHAT YOU TRANSFER TO DAILY
Control Valve% Open Raw |  |  | 44 | Plant 1 | 71 | Plant 2 | 81 | Plant 3 | 52 |  |  | NO NEED TO TYPE IN THESE BLANKS FOR ROUNDS ONLY
MGD
Total Raw Flow |  |  | 34 |  | MGD | Fin North1 Flow |  | 0 | 0 | Master Meter Readings
Plant 1 Raw Flow |  |  | 11 |  | MGD | Fin 1 Pumps |  | 0 |  | South 1 |  | 0
Plant 2 Raw Flow |  |  | 11 |  | MGD | Fin Coastal1 Flow |  | 8842 | 12.7325 | South 2 |  | 0
Plant 3 Raw Flow |  |  | 12 |  | MGD | Fin 1 Pumps |  | 1,2 |  | Conway |  | 0
Total Filter Flow |  |  | 32.5 |  | MGD | Fin Perry 2 Flow |  | 10283 | 14.8075 | Perry |  | 0
Plant 1 Filter Flow |  |  | 10.5 |  | MGD | Fin 2 Pumps |  | 1,3 |  | Raw PLT 1 |  | 0
Plant 2 Filter Flow |  |  | 10.5 |  | MGD | Fin Conway 2 Flow |  | 2828 | 4.0723 | Raw PLT 2 |  | 0
Plant 3 Filter Flow |  |  | 11.5 |  | MGD | Fin 2 Pumps |  | 1,3 |  | Raw PLT 3 |  | 0
[12 empty] | Flow | Totalizer
Chemical |  |  | DOSE |  | Calculated |  | Measured |  |  | Decant Weir flow |  | 1813.2 | 0
|  |  | ppm |  | Feed ml/min |  | Feed ml/min |  |  | Sludge Bl.Dwn meter |  | 1.773 | 0
Alum | DESIRED DOSE |  | 120 |  | 5398.8 |  | 5520 |  |  | Thickener Torque 1 |  | 25 | Sludge Judge | 3 | feet
[5 empty] | 5398.8 |  | 5480 |  |  | Thickener Torque 2 |  |  | Sludge Judge
[5 empty] | 6019.2 |  | 5520 |  |  | BACKWASH WATER USED
Tank Levels
[5 empty] | 16687.2 |  | 16520 |  | 118.7976 |  | BULK
[11 empty] | ALUM 1 | ALUM 2 | ALUM 3 | ALUM 4 | ALUM 5
Polymer | Plant 1 | basin 1 | 0.71 |  | 1368.966 |  | 1200 |  | 0.62233 | Alum | 4949 | 8612 | 8612 | 9161 | 9161
NUMBER OF BASIN | 2 | basin 2 | 0.68 |  | 1311.1223 |  | 1240 |  | 0.64307 | Caustic 1 |  | 6286 |  | 6666 | 6666
Polymer | Plant 2 | basin 3 | 0.74 |  | 1426.8096 |  | 1280 |  | 0.66382 |  |  | CL2 Pre/Post |  | CL2 Post
NUMBER OF BASIN | 2 | basin 4 | 0.74 |  | 1426.8096 |  | 1320 |  | 0.68456 |  | CL2 | 11.5 |  | 33
Polymer | Plant 3 | basin 5 | 0.61 |  | 1283.0769 |  | 960 |  | 0.45637 | Phosphate |  | 1439
NUMBER OF BASIN | 2 | basin 6 | 0.69 |  | 1451.3493 |  | 1280 |  | 0.6085 | Fluoride |  | 1500
Polymer |  | Thickener | 950 |  |  |  | 1100 |  | 2.0925 | CAL~FLO |  | 13.4
Fliter Aid |  | plt1 | 0.05 |  | 995.1136 |  | 1000 |  | 0.050246 | Zinc |  | 1069
Fliter Aid |  | plt2 | 0.05 |  | 995.1136 |  | 1000 |  | 0.050246 | Polymer
Fliter Aid |  | plt3 | 0.05 |  | 1089.8864 |  | 1080 |  | 0.049546 | Ammonia |  | 7.63
Chlorine |  | Pre 1 | 1.5 |  | 353.8328 |  | 360 |  | 1.5261 | Hylime LBS/Day
Chlorine |  | Pre 2 | 1.6 |  | 377.4217 |  | 400 |  | 1.6957 | PAC LBS/Day
Chlorine |  | Pre 3 | 1.4 |  | 361.6958 |  | 400 |  | 1.5483 | BI-SULFITE |  | 1650
[10 empty] | FILTER AIDE |  | 2
Caustic |  | Post 1 | 4.8 |  | 345.4636 |  | 245 |  | 3.4041 | ALUM TOWER
Caustic |  | Post 2 | 4.7 |  | 185.2412 |  | 147 |  | 3.7297
Caustic |  | Pre 1 | 18.7 |  | 704.9789 |  | 540 |  | 14.3238
Caustic |  | Pre 2 | 19.4 |  | 731.3685 |  | 565 |  | 14.987
Caustic |  | Pre 3 | 17.8 |  | 732.0539 |  | 565 |  | 13.7381
Chemical |  |  |  |  | Calculated |  |  |  | Calculated
|  |  | Plant 1&2 | Plt 3 | Fin 1 ml/min |  |  |  | Fin 2 ml/min
Chlorine |  | Post | 4 | 3.8 | 1583.6061 | 4.0139 | 1590 |  | 786.5419 | 3.8137 | 790
Phosphate |  |  | 1.1 |  | 100.485 | 1.0947 | 100 |  | 55.0275 | 1.1194 | 56
Zinc |  |  | 0.1 |  | 14.5342 | 0.096324 | 14 |  | 7.9592 | 0.10051 | 8
Ammonia | All Cl2 / | 5.46 | 0.70204 |  | 323.1849 | 0.69512 | 320 |  | 160.5188 | 0.63468 | 160
Fluoride |  |  | 0.5 |  | 121.2153 | 0.49911 | 121 |  | 66.3798 | 0.52727 | 70
grams/min
| Hylime Pounds per Day |  | 0 | Pump Speed |  |  | PPM | 0 |  |  | PLT 1 | PLT 2 | PLT 3 | RAW |  |  | FIN 1 NH3 | [6 empty] | FIN 2 NH3
266 | PAC Pounds per Day |  | 843.7004 | Pump Speed |  | 665 | PPM | 2.9754 | Cal~flow Pump % |  |  |  |  | 148 |  |  | (((((D14+D15)*8.34*((D46)/E57)/(E58/100)))/7.74)*3785/1440) | [6 empty] | ((((D16*8.34*(E46/E57)/(E58/100)))/7.74)*3785/1440)
[10 empty] | PPM | 0 | 0 | 0 | 9100.1348
Free Chlorine on Filters |  |  | PLT 1 | 0.49 |  | 0.63 | PLT 3 | 0.68
Chlorine Strenght % weight/volume |  |  |  |  | Post | 2 | Pre | 0.1 |  | min CT | TARGET CT |  | Stream Current
Post Chlorine Dose / Ammonia Dose |  |  |  | 4.9 |  | Decant Ph | 5.1 |  | CT PLT 1 | 0.65 | 0.75 | PLT 1 | 4.3
Aquos Ammonia %Strength |  |  |  | 19.5 |  | Decant cl2 | 0.01 |  | CT PLT 2 | 0.65 | 0.75 | PLT 2 | 4.51
CL2 SPG | 1.17 |  | NH3 SPG | 0.928 |  | Decant pump | 17 |  | CT PLT 3 | 0.67 | 0.77 | PLT 3 | -10
| RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [8 empty] | SETTLED | [8 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
|  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW |  |  | DOSE |  |  |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  |  |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST
TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL |  | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLY THICKENER | DECANT | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC
0:00
43689.3885 | 1,2,3,6 | 44 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 0,1,2 | 12.7325 | 1,3 | 18.8798 | 31.6123 | 2.611 | 43689.3885 | 118.7976 | 9100.1348 | 0 | 843.7004 | 0 | 0 | 0 | 14.3238 | 14.987 | 13.7381 | 1.5261 | 1.6957 | 1.5483 | 0.62233 | 0.64307 | 0.66382 | 0.68456 | 0.45637 | 0.6085 | 2.0925 | 3 | 0.050246 | 0.050246 | 0.049546 | 1.0947 | 0.49911 | 0.096324 | 4.0139 | 0.69512 | 3.4041 | 1.1194 | 0.52727 | 0.10051 | 3.8137 | 0.63468 | 3.7297
[18 empty] | 16520 | [6 empty] | 540 | 565 | 565 | 360 | 400 | 400 | 1200 | 1240 | 1280 | 1320 | 960 | 1280 | 1100 |  | 1000 | 1000 | 1080 | 100 | 121 | 14 | 1590 | 320 | 245 | 56 | 70 | 8 | 790 | 160 | 147
[34 empty] | FINISHED SOUTH 1 |  | END: | 0
[34 empty] | FINISHED SOUTH 2 |  | END: | 0
[34 empty] | FINISHED CONWAY |  | END: | 0
[34 empty] | FINISHED PERRY |  | END: | 0
[34 empty] | RAW PLANT 1 |  | END: | 0
[34 empty] | RAW PLANT 2 |  | END: | 0
[34 empty] | RAW PLANT 3 |  | END: | 0
[34 empty] | DECANT |  | END: | 0
[34 empty] | BLOW DOWN |  | END: | 0
Note on M3: Ctrl+s Will save the sheet
Note on M4: Ctrl+m Will remove all ml/min
Note on M5: Ctrl+o Will remove all Master Meter
Note on D12: PLANT 3 FLOW IS MAX FOR CT CAL. IN LESS BASIN IS DOWN
Note on D20: RAW FLOW X mg/Lx4.18=ml/min Ex. 29.9x61.6x4.18=Total PPM
Note on D26: ((7500*PPM*1440)/(1000*1000*454))/(FLOW*8.34)*#OF BASIN
Note on D30: BASIN 5-6 IS NOT TO BE LOWER THAN 1-4
Note on M39: FROM SCADA TOTAL LBS YESTERDAY
Note on D50: DOSE - AVG FILTER RES PLT 1 & PLT 2 X 8.34 X FIN FLOW PLT 1 PLT 2 /%SOL/(8.34 X SPF) X 3785 / 1440 = ML/MIN
Note on D51: Fin Flow X PPM X 4.35= ML/MIN
Note on D52: PPM X 2.63 / .38 X FLOW= ML/MIM
Note on D53: ML/MIN X 1440 / 3785 / FLOW / 8.34 = PPM
Note on F53: FOLW X 8.34 X ((CL2 mg/l / CL2/NH3) / (NH3% / 100) / 7.74) X 3785 / 1440 = ML/MIN
Note on D54: ML/MIN/2.63*1.9/8.34/FLOW=PPM

## LIME CAL (hidden)
PUMP % | MIL/MIN | FOR CALCULATION FACTOR
5 | 307.4366 | #N/A | #N/A | #N/A | 144
6 | 368.924
7 | 430.4114
8 | 491.8988
9 | 553.3862
10 | 614.8736
11 | 676.361
12 | 737.8484
13 | 799.3358
14 | 860.8232
15 | 922.3106
16 | 983.798
17 | 1045.2854
18 | 1106.7728
19 | 1168.2602
20 | 1229.7476
21 | 1291.235
22 | 1352.7224
23 | 1414.2098
24 | 1475.6972
25 | 1537.1846
26 | 1598.672
27 | 1660.1594
28 | 1721.6468
29 | 1783.1342
30 | 1844.6216
31 | 1906.109
32 | 1967.5964
33 | 2029.0838
34 | 2090.5712
35 | 2152.0586
36 | 2213.546
37 | 2275.0334
38 | 2336.5208
39 | 2398.0082
40 | 2459.4956
41 | 2520.983
42 | 2582.4704
43 | 2643.9578
44 | 2705.4452
45 | 2766.9326
46 | 2828.42
47 | 2889.9074
48 | 2951.3948
49 | 3012.8822
50 | 3074.3696
51 | 3135.857
52 | 3197.3444
53 | 3258.8318
54 | 3320.3192
55 | 3381.8066
56 | 3443.294
57 | 3504.7814
58 | 3566.2688
59 | 3627.7562
60 | 3689.2436
61 | 3750.731
62 | 3812.2184
63 | 3873.7058
64 | 3935.1932
65 | 3996.6806
66 | 4058.168
67 | 4119.6554
68 | 4181.1428
69 | 4242.6302
70 | 4304.1176
71 | 4365.605
72 | 4427.0924
73 | 4488.5798
74 | 4550.0672
75 | 4611.5546
76 | 4673.042
77 | 4734.5294
78 | 4796.0168
79 | 4857.5042
80 | 4918.9916
81 | 4980.479
82 | 5041.9664
83 | 5103.4538
84 | 5164.9412
85 | 5226.4286
86 | 5287.916
87 | 5349.4034
88 | 5410.8908
89 | 5472.3782
90 | 5533.8656
91 | 5595.353
92 | 5656.8404
93 | 5718.3278
94 | 5779.8152
95 | 5841.3026
96 | 5902.79
97 | 5964.2774
98 | 6025.7648
99 | 6087.2522
100 | 6148.7396
101 | 6210.227
102 | 6271.7144
103 | 6333.2018
104 | 6394.6892
105 | 6456.1766
106 | 6517.664
107 | 6579.1514
108 | 6640.6388
109 | 6702.1262
110 | 6763.6136
111 | 6825.101
112 | 6886.5884
113 | 6948.0758
114 | 7009.5632
115 | 7071.0506
116 | 7132.538
117 | 7194.0254
118 | 7255.5128
119 | 7317.0002
120 | 7378.4876
121 | 7439.975
122 | 7501.4624
123 | 7562.9498
124 | 7624.4372
125 | 7685.9246
126 | 7747.412
127 | 7808.8994
128 | 7870.3868
129 | 7931.8742
130 | 7993.3616
131 | 8054.849
132 | 8116.3364
133 | 8177.8238
134 | 8239.3112
135 | 8300.7986
136 | 8362.286
137 | 8423.7734
138 | 8485.2608
139 | 8546.7482
140 | 8608.2356
141 | 8669.723
142 | 8731.2104
143 | 8792.6978
144 | 8854.1852
145 | 8915.6726
146 | 8977.16
147 | 9038.6474
148 | 9100.1348
149 | 9161.6222
150 | 9223.1096
151 | 9284.597
152 | 9346.0844
153 | 9407.5718
154 | 9469.0592
155 | 9530.5466
156 | 9592.034
157 | 9653.5214
158 | 9715.0088
159 | 9776.4962
160 | 9837.9836
161 | 9899.471
162 | 9960.9584
163 | 10022.4458
164 | 10083.9332
165 | 10145.4206
166 | 10206.908
167 | 10268.3954
168 | 10329.8828
169 | 10391.3702
170 | 10452.8576
171 | 10514.345
172 | 10575.8324
173 | 10637.3198
174 | 10698.8072
175 | 10760.2946
176 | 10821.782
177 | 10883.2694
178 | 10944.7568
179 | 11006.2442
180 | 11067.7316
181 | 11129.219
182 | 11190.7064
183 | 11252.1938
184 | 11313.6812
185 | 11375.1686
186 | 11436.656
187 | 11498.1434
188 | 11559.6308
189 | 11621.1182
190 | 11682.6056
191 | 11744.093
192 | 11805.5804
193 | 11867.0678
194 | 11928.5552
195 | 11990.0426
196 | 12051.53
197 | 12113.0174
198 | 12174.5048
199 | 12235.9922
200 | 12297.4796
201 | 12358.967
202 | 12420.4544
203 | 12481.9418
204 | 12543.4292
205 | 12604.9166
206 | 12666.404
207 | 12727.8914
208 | 12789.3788

## CHEM 1 (hidden)
CHEMICAL TRANSFER SHEET PLANT 3 | [7 empty] | CHEMICAL TRANSFER SHEET PLANT 1 and 2
DATE | 2019-08-12 09:20 | TIME | 43689.3885 | OPERATORS |  | DB / GE |  | DATE | 2019-08-12 09:20 | TIME | 43689.3885 |  | OPERATORS |  | DB / GE
ALUM START 24HR. LEVEL |  |  |  | GAL. |  |  |  |  | PAC TOTAL |  | LB/DAY |  | LIME TOTAL |  |  | GAL/DAY
START |  | GAL. FINISH |  | GAL. |  |  |  |  | AMMONIA |  | GAL/DAY |  | CHLORINE |  |  | GAUDAY
START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER START 24HR. LEVEL |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | TOTAL GAL. POLYMER USED 24HR.
START |  | GAL. FINISH |  | GAL.
| FINISH 24HR. LEVEL |  |  | GAL.
|  |  |  | TOTAL GAL. ALUM USED 24HR. |  |  | GAL. | CAUSTIC START 24HR. LEVEL |  |  |  | GAL.
[8 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
POLYMER START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL.
POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | [8 empty] | TOTAL GAL. CAUSTIC USED 24HR.
TOTAL GAL. POLYMER USED 24HR.
[8 empty] | PHOSPHATE START 24HR. LEVEL |  |  |  | GAL.
CAUSTIC START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. |  | START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | PHOSPHATE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. PHOSPHATE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | ZINC CHLORIDE START 24HR. LEVEL |  |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL. |  |  |  | ZINC CHLORIDE FINISH 24HR. LEVEL |  |  |  |  | GAL. | TOTAL GAL. ZINC USED 24HR.
|  |  |  | TOTAL GAL. CAUSTIC USED 24HR. |  |  | GAL.
[8 empty] | FILTER AIDE START 24HR. LEVEL |  |  |  | GAL.
PRE HYPOCHLORITE START 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER AIDE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. FILTER AIDE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
PRE HYPOCHLORITE FINISH 24HR. LEVEL |  |  |  |  | GAL. | FINISH
|  |  | TOTAL GAL. HYPOCHLORITE USED 24HR. |  |  |  | GAL
FILTER AIDE START 24HR. LEVEL
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER CAUSTIC START 24HR. LEVEL | [5 empty] | GAL.
FILTER AIDE FINISH 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH
[8 empty] | FILTER CAUSTIC FINISH 24HR. LEVEL | [6 empty] | GAL.
LIME START |  |  | FT FINISH |  | FT TOTAL | [6 empty] | TOTAL FILT. CAUSTIC USED 24HR. |  |  |  |  | GAL.

## RUN TIME
WEEKLY DATE | 2019-08-12 09:20 | TIME | 43689.3885 | OPERATOR | DB / GE
PUMP AND MOTOR RUN TIME LOG
LOCATION | RUN TIMES |  | LOCATION | RUN TIMES
South Pump #1 |  | Hr | Sludge Bl. Dwn Pump #1 |  | Hr
South Pump #2 |  | Hr | Sludge Bl. Dwn Pump #2 |  | Hr
South Pump #3 |  | Hr | Spill Lagoon Pump #1 |  | Hr
South Pump #4 |  | Hr | Spill Lagoon Pump #2 |  | Hr
North Pump #5 |  | Hr | Sludge Spray Pump #1 |  | Hr
North Pump #6 |  | Hr | Sludge Spray Pump #2 |  | Hr
North Pump #7 |  | Hr | Sludge Spray Pump #3 |  | Hr
North Pump #8 |  | Hr
|  | Boge Compressor Lime Pack |  |  | Hr
Finish Vac Pump #1 |  | Hr | Lime Pack Compressor #1 |  | Hr
Finish Vac Pump #2 |  | Hr
|  |  | Plant #3 Compressor #1 |  | Hr
Service Water Pump #1 |  | Hr | Plant #3 Compressor #2 |  | Hr
Service Water Pump #2 |  | Hr | Boge Compressor Plant #3 |  | Hr
Service Water Pump #3 |  | Hr
|  |  | Finished #2 Pump #1 |  | Hr
Hydro Tank Compressor |  | Hr | Finished #2 Pump #2 |  | Hr
|  |  | Finished #2 Pump #3 |  | Hr
Plant #3 Filter Blower #1 |  | Hr
Plant #3 Filter Blower #2 |  | Hr | Raw Header |  | Psi
Plant #3 Backwash pump #1 |  | Hr | Raw Pump #1 |  | Hr
Plant #3 Backwash pump #2 |  | Hr | Raw Pump #2 |  | Hr
Plant #3 Backwash VFD #1 |  | Hr | Raw Pump #3 |  | Hr
Plant #3 Backwash VFD #2 |  | Hr | Raw Pump #4 |  | Hr
Plant #3 Chemical spill #1 |  | Hr | Raw Pump #5 |  | Hr
Plant #3 Chemical spill #2 |  | Hr | Raw Pump #6 |  | Hr
Plant #3 Biulding spill #1 |  | Hr | COMMENTS
Plant #3 Biulding spill #2 |  | Hr
Plant #1/2 Filter Blower #1 |  | Hr
Plant #1/2 Filter Blower #2 |  | Hr
Plant #1/2 backwash pump #1 |  | Hr
Plant #1/2 backwash pump #2 |  | Hr
Plant #1/2 backwash VFD #1 |  | Hr
Plant #1/2 backwash VFD #2 |  | Hr

## 1
DATE: | 2018-11-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-01 | [23 empty] | DATE: | 2018-11-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43405.0061 | 1,2,3,5 | 42 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | ,1,3 | 16.3944 | 1,3 | 13.9824 | 30.3768 | 1.5278 | 43405.0061 | 99.5723 | 6763.6136 | 0 | 888.1057 | 0 | 0 | 0 | 12.2712 | 12.5439 | 11.8458 | 1.7456 | 1.8329 | 1.7487 | 0.54381 | 0.51182 | 0.51182 | 0.51182 | 0.49733 | 0.49733 | 1.5218 | 3 | 0.05 | 0.05 | 0.050874 | 1.1043 | 0.50105 | 0.099158 | 4.1983 | 0.79383 | 4.6485 | 1.0673 | 0.50272 | 0.1032 | 3.8442 | 0.73314 | 6.2525 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.394 | 4 | 0.49 | 17.3 | 10.6 | 0.53667 |  | 6.11 | 0.4 | 6 | 0.51 | 17.3 | 10.6 | 0.53667 | 6.15 | 0.36 | 4 | 0.47 | 18.5 | 11.8 | 0.55704 | [13 empty] | 7.16 | 0.054 | 1 | 4.6 | 17.9 |  |  |  | 7.18 | 0.057 | 2 | 4.4 | 20.4 |  |  |  | 3.9 | 3.7 | 3.1 | [18 empty] | 13480 | [6 empty] | 450 | 460 | 475 | 400 | 420 | 440 | 1020 | 960 | 960 | 960 | 1020 | 1020 | 800 |  | 990 | 970 | 1080 | 98 | 118 | 14 | 1750 | 355 | 325 | 52 | 65 | 8 | 880 | 180 | 240 |  | 1:00 | 0.49 | 10.6 | 24 | 11.76 | 6.1 | 17.3 | 10 | 1.176 | 15 | 6.5 | 0.41667 | 1:00 | 0.51 | 10.6 | 24 | 12.24 | 6.11 | 17.3 | 10 | 1.224 | 15 | 6.5 | 0.41667 | 1:00 | 0.47 | 11.8 | 22.8814 | 10.7542 | 6.15 | 18.5 | 10 | 1.0754 | 15 | 6.5 | 0.43704
2:00 | [72 empty] | 8:20 | 1,2,3,5 | 42 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | ,1,3 | 16.3944 | 1,3 | 13.9824 | 30.3768 | 1.6258 | 43405.4055 | 99.72 | 6394.6892 | 0 | 888.1057 | 0 | 0 | 0 | 12.2712 | 12.5439 | 11.8458 | 1.8329 | 1.8329 | 1.7885 | 0.53315 | 0.50649 | 0.50649 | 0.50649 | 0.44857 | 0.44857 | 1.4267 | 0 | 0.05 | 0.050172 | 0.04946 | 1.1043 | 0.50105 | 0.099158 | 4.2133 | 0.79607 | 5.1491 | 1.1289 | 0.51046 | 0.1032 | 3.8017 | 0.72499 | 7.1643 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.48 | 18 | 17 | 13.7 | 131 | 225 | 18.4 | 0.559 |  | 6.03 | 10 | 0.092 | 6.05 | 10 |  | 6.03 | 10 | [8 empty] | 0.066 | [14 empty] | 0.026 | 2 | 0.3 |  | 0.064 | 0.012 | 1 | 0.3 |  | 0.035 | 1 | 0.36 | [38 empty] | 13500 | [6 empty] | 450 | 460 | 475 | 420 | 420 | 450 | 1000 | 950 | 950 | 950 | 920 | 920 | 750 |  | 990 | 970 | 1050 | 98 | 118 | 14 | 1750 | 356 | 360 | 55 | 66 | 8 | 845 | 178 | 275 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43405.8217 | 1,2,3,5 | 42 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | ,1,3 | 16.3944 | 1,3 | 13.9824 | 30.3768 | 1.6258 | 43405.8217 | 98.3904 | 6394.6892 | 0 | 888.1057 | 0 | 0 | 0 | 12.2712 | 12.5439 | 11.8458 | 1.7456 | 1.8329 | 1.9077 | 0.53315 | 0.4905 | 0.4905 | 0.51182 | 0.37056 | 0.39494 | 1.4267 | 1 | 0.050689 | 0.049654 | 0.050874 | 1.0818 | 0.50105 | 0.099158 | 4.2009 | 0.79383 | 5.1491 | 1.1084 | 0.49499 | 0.1032 | 3.8213 | 0.69241 | 7.034 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.06 | 0.05 | 1 | 4 | 18 |  |  |  | 7.07 | 0.053 | 1 | 3.9 | 20.4 |  |  |  | 3.9 | 3.8 | 4.1 | [18 empty] | 13320 | [6 empty] | 450 | 460 | 475 | 400 | 420 | 480 | 1000 | 920 | 920 | 960 | 760 | 810 | 750 |  | 980 | 960 | 1080 | 96 | 118 | 14 | 1740 | 355 | 360 | 54 | 64 | 8 | 840 | 170 | 270 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.38 | 20 | 17 | 13.9 | 121 | 195 | 18 | 0.541 |  | 6 | 13 | 0.093 | 6 | 13 |  | 5.98 | 13 | [8 empty] | 0.061 | [14 empty] | 0.029 | 1 | 0.36 |  | 0.067 | 0.012 | 1 | 0.38 |  | 0.034 | 1 | 0.47 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.051 | [9 empty] | 6.07 | 0.364 | 4 | 0.55 | 16.8 | 10.7 | 0.5406 |  | 6.08 | 0.313 | 3 | 0.55 | 16.8 | 10.7 | 0.5406 | 6.12 | 0.404 | 3 | 0.66 | 18.4 | 11.7 | 0.55333 |  |  |  | 0.011 |  |  |  |  | 0.037 |  |  |  | 0.02 | 7.02 | 0.064 | 1 | 4.4 | 17.3 | 25 | 36 | 0.027 | 7 | 0.07 | 1 | 4.2 | 19.3 | 22 | 39 | 0.021 | 4 | 4 | 4.1 | [55 empty] | 9:00 | 0.55 | 10.7 | 23.7757 | 13.0766 | 6.07 | 16.8 | 10 | 1.3077 | 15 | 6.5 | 0.4206 | 9:00 | 0.55 | 10.7 | 23.7757 | 13.0766 | 6.08 | 16.8 | 10 | 1.3077 | 15 | 6.5 | 0.4206 | 9:00 | 0.66 | 11.7 | 23.0769 | 15.2308 | 6.12 | 18.4 | 10 | 1.5231 | 15 | 6.5 | 0.43333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.42 | 16 | 17 | 14.5 | 132 | 207 | 18.3 | 0.558 |  | 6.01 | 12 | 0.075 | 6.04 | 12 |  | 6.03 | 12 | [8 empty] | 0.065 | [14 empty] | 0.032 | 1 | 0.31 |  | 0.084 | 0.018 | 1 | 0.3 |  | 0.055 | 1 | 0.44 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.15 | 0.358 | 4 | 0.59 | 18 | 10.7 | 0.5406 |  | 6.15 | 0.328 | 3 | 0.52 | 18 | 10.7 | 0.5406 | 6.16 | 0.44 | 3 | 0.62 | 19 | 11.7 | 0.55333 | [13 empty] | 7.21 | 0.06 | 1 | 4.2 | 18 |  |  |  | 7.49 | 0.064 | 1 | 4.1 | 22 |  |  |  | 4 | 4 | 2.9 | [55 empty] | 13:00 | 0.59 | 10.7 | 23.7757 | 14.0277 | 6.15 | 18 | 10 | 1.4028 | 15 | 6.5 | 0.4206 | 13:00 | 0.52 | 10.7 | 23.7757 | 12.3634 | 6.15 | 18 | 10 | 1.2363 | 15 | 6.5 | 0.4206 | 13:00 | 0.62 | 11.7 | 23.0769 | 14.3077 | 6.16 | 19 | 10 | 1.4308 | 15 | 6.5 | 0.43333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.68 | 20 | 18 | 14.4 | 114 | 211 | 19.5 | 0.506 |  | 6.25 | 14 | 0.091 | 6.1 | 14 |  | 6.12 | 13 | [8 empty] | 0.058 | [14 empty] | 0.04 | 1 | 0.3 |  | 0.058 | 0.013 | 1 | 0.32 |  | 0.039 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.22 | 0.056 | 1 | 4.2 | 18 |  |  |  | 7.42 | 0.06 | 1 | 4 | 22 |  |  |  | 4 | 4.1 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.55 | 17 | 17 | 14.6 | 128 | 211 | 19.3 | 0.541 |  | 6.09 | 14 | 0.091 | 6.04 | 13 |  | 6.06 | 13 | [8 empty] | 0.065 | [14 empty] | 0.051 | 2 | 0.32 |  | 0.064 | 0.013 | 2 | 0.31 |  | 0.044 | 1 | 0.43 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.049 | [9 empty] | 6.06 | 0.379 | 5 | 0.6 | 18.1 | 10.6 | 0.53667 |  | 6.08 | 0.366 | 5 | 0.61 | 18.1 | 10.6 | 0.53667 | 6.16 | 0.41 | 4 | 0.57 | 19.6 | 11.8 | 0.55704 |  |  |  | 0.016 |  |  |  |  | 0.026 |  |  |  | 0.013 | 7.17 | 0.057 | 1 | 4.1 | 18.2 | 20 | 22 | 0.019 | 7.19 | 0.059 | 2 | 3.7 | 21.3 | 22 | 34 | 0.012 | 4.2 | 4.4 | 3.3 | [55 empty] | 21:00 | 0.6 | 10.6 | 24 | 14.4 | 6.06 | 18.1 | 10 | 1.44 | 15 | 6.5 | 0.41667 | 21:00 | 0.61 | 10.6 | 24 | 14.64 | 6.08 | 18.1 | 10 | 1.464 | 15 | 6.5 | 0.41667 | 21:00 | 0.57 | 11.8 | 22.8814 | 13.0424 | 6.16 | 19.6 | 10 | 1.3042 | 15 | 6.5 | 0.43704
22:00 | [72 empty] | DOSE |  | TOTAL | 32.1 | 32.1 | 35.1 | 99.3 | 30.6 | 30.6 | 33.6 | 94.8 | 0 | 49.1832 | 0 | 41.9472 | 91.1304 | 4.7794 | TOTAL | 297.6828 | 19552.992 | 0 | 2664.3172 | 0 | 0 | 0 | 36.8136 | 37.6317 | 35.5375 | 5.3241 | 5.4986 | 5.4448 | 1.6101 | 1.5088 | 1.5088 | 1.5301 | 1.3165 | 1.3408 | 4.3752 | 4 | 0.15069 | 0.14983 | 0.15121 | 3.2905 | 1.5032 | 0.29747 | 12.6124 | 2.3837 | 14.9467 | 3.3046 | 1.5082 | 0.30961 | 11.4672 | 2.1505 | 20.4508 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.47 | 19 | 18 | 14.9 | 128 | 208 | 19.2 | 0.548 |  | 6.03 | 13 | 0.101 | 6.01 | 13 |  | 6.05 | 14 | [8 empty] | 0.062 | [14 empty] | 0.06 | 2 | 0.28 |  | 0.062 | 0.014 | 1 | 0.29 |  | 0.041 | 1 | 0.41 | [22 empty] | AVERAGE | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 16.3944 |  | 13.9824 | 30.3768 | 1.5931 | AVERAGE | 99.2276 | 6517.664 |  | 888.1057 | 0 | 0 | 0 | 12.2712 | 12.5439 | 11.8458 | 1.7747 | 1.8329 | 1.8149 | 0.5367 | 0.50294 | 0.50294 | 0.51005 | 0.43882 | 0.44695 | 1.4584 | 1.3333 | 0.05023 | 0.049942 | 0.050403 | 1.0968 | 0.50105 | 0.099158 | 4.2041 | 0.79458 | 4.9822 | 1.1015 | 0.50272 | 0.1032 | 3.8224 | 0.71684 | 6.8169 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.98 | 110 | 104 | 86 | 754 | 1257 | 112.7 | 3.253 | 0.1 | 36.41 | 76 | 0.543 | 36.24 | 75 | 0 | 36.27 | 75 | 0 | 24.38 | 1.495 | 17 | 2.23 | 70.2 | 42.6 | 2.1545 | 0.377 | 24.42 | 1.407 | 17 | 2.19 | 70.2 | 42.6 | 2.1545 | 24.59 | 1.614 | 14 | 2.32 | 75.5 | 47 | 2.2207 | 0.238 | 9 | 1.87 | 0.027 | 0.399 | 0.082 | 7 | 1.9 | 0.063 | 0.248 | 6 | 2.51 | 0.033 | 42.84 | 0.341 | 6 | 25.5 | 107.4 | 45 | 58 | 0.046 | 43.35 | 0.363 | 8 | 24.3 | 125.4 | 44 | 73 | 0.033 | 24 | 24 | 20.5 |  |  | MINIMUM | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 16.3944 |  | 13.9824 | 30.3768 | 1.5278 | MINIMUM | 98.3904 | 6394.6892 |  | 888.1057 |  |  |  | 12.2712 | 12.5439 | 11.8458 | 1.7456 | 1.8329 | 1.7487 | 0.53315 | 0.4905 | 0.4905 | 0.50649 | 0.37056 | 0.39494 | 1.4267 | 0 | 0.05 | 0.049654 | 0.04946 | 1.0818 | 0.50105 | 0.099158 | 4.1983 | 0.79383 | 4.6485 | 1.0673 | 0.49499 | 0.1032 | 3.8017 | 0.69241 | 6.2525 |  | MIN | 0.49 | 10.6 | 24 | 11.76 | 6.1 | 17.3 | 10 | 1.176 |  |  |  | MIN | 0.51 | 10.6 | 24 | 12.24 | 6.11 | 17.3 | 10 | 1.224 |  |  |  | MIN | 0.47 | 11.8 | 22.8814 | 10.7542 | 6.15 | 18.5 | 10 | 1.0754 |  |  |  | 1.0754
AVERAGE | 6.4967 | 18.3333 | 17.3333 | 14.3333 | 125.6667 | 209.5 | 18.7833 | 0.54217 | 0.05 | 6.0683 | 12.6667 | 0.0905 | 6.04 | 12.5 |  | 6.045 | 12.5 |  | 6.095 | 0.37375 | 4.25 | 0.5575 | 17.55 | 10.65 | 0.53863 | 0.062833 | 6.105 | 0.35175 | 4.25 | 0.5475 | 17.55 | 10.65 | 0.53863 | 6.1475 | 0.4035 | 3.5 | 0.58 | 18.875 | 11.75 | 0.55519 | 0.039667 | 1.5 | 0.31167 | 0.0135 | 0.0665 | 0.013667 | 1.1667 | 0.31667 | 0.0315 | 0.041333 | 1 | 0.41833 | 0.0165 | 7.14 | 0.056833 | 1 | 4.25 | 17.9 | 22.5 | 29 | 0.023 | 7.225 | 0.0605 | 1.3333 | 4.05 | 20.9 | 22 | 36.5 | 0.0165 | 4 | 4 | 3.4167 |  |  | MAXIMUM | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 16.3944 |  | 13.9824 | 30.3768 | 1.6258 | MAXIMUM | 99.72 | 6763.6136 |  | 888.1057 |  |  |  | 12.2712 | 12.5439 | 11.8458 | 1.8329 | 1.8329 | 1.9077 | 0.54381 | 0.51182 | 0.51182 | 0.51182 | 0.49733 | 0.49733 | 1.5218 | 3 | 0.05023 | 0.049942 | 0.050403 | 1.1043 | 0.50105 | 0.099158 | 4.2133 | 0.79607 | 5.1491 | 1.1289 | 0.51046 | 0.1032 | 3.8442 | 0.73314 | 7.1643
MINIMUM | 6.38 | 16 | 17 | 13.7 | 114 | 195 | 18 | 0.506 | 0.049 | 6 | 10 | 0.075 | 6 | 10 |  | 5.98 | 10 |  | 6.06 | 0.358 | 4 | 0.49 | 16.8 | 10.6 | 0.53667 | 0.058 | 6.08 | 0.313 | 3 | 0.51 | 16.8 | 10.6 | 0.53667 | 6.12 | 0.36 | 3 | 0.47 | 18.4 | 11.7 | 0.55333 | 0.026 | 1 | 0.28 | 0.011 | 0.058 | 0.012 | 1 | 0.29 | 0.026 | 0.034 | 1 | 0.36 | 0.013 | 7.02 | 0.05 | 1 | 4 | 17.3 | 20 | 22 | 0.019 | 7 | 0.053 | 1 | 3.7 | 19.3 | 22 | 34 | 0.012 | 3.9 | 3.7 | 2.9 | [15 empty] | Ml/Min |  | TOTAL | 40300 | 0 | 0 | 0 | 0 | 0 | 0 | 1350 | 1380 | 1425 | 1220 | 1260 | 1370 | 3020 | 2830 | 2830 | 2870 | 2700 | 2750 | 2300 | 0 | 2960 | 2900 | 3210 | 292 | 354 | 42 | 5240 | 1066 | 1045 | 161 | 195 | 24 | 2565 | 528 | 785
MAXIMUM | 6.68 | 20 | 18 | 14.9 | 132 | 225 | 19.5 | 0.559 | 0.051 | 6.25 | 14 | 0.101 | 6.1 | 14 |  | 6.12 | 14 |  | 6.15 | 0.394 | 5 | 0.6 | 18.1 | 10.7 | 0.5406 | 0.066 | 6.15 | 0.4 | 6 | 0.61 | 18.1 | 10.7 | 0.5406 | 6.16 | 0.44 | 4 | 0.66 | 19.6 | 11.8 | 0.55704 | 0.06 | 2 | 0.36 | 0.016 | 0.084 | 0.018 | 2 | 0.38 | 0.037 | 0.055 | 1 | 0.47 | 0.02 | 7.22 | 0.064 | 1 | 4.6 | 18.2 | 25 | 36 | 0.027 | 7.49 | 0.07 | 2 | 4.4 | 22 | 22 | 39 | 0.021 | 4.2 | 4.4 | 4.1 | [17 empty] | AVERAGE | 13433.3333 | [6 empty] | 450 | 460 | 475 | 406.6667 | 420 | 456.6667 | 1006.6667 | 943.3333 | 943.3333 | 956.6667 | 900 | 916.6667 | 766.6667 |  | 986.6667 | 966.6667 | 1070 | 97.3333 | 118 | 14 | 1746.6667 | 355.3333 | 348.3333 | 53.6667 | 65 | 8 | 855 | 176 | 261.6667
# 0F DAYS IN THE MONTH |  | 30 |  | TOTAL AVG COAG PH: |  |  |  | 6.0511 |  | TOTAL AVG COAG ALK: |  |  |  | 12.5556 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.44 |  |  |  |  | TOTAL AVG SETTLED PH: | [6 empty] | 6.1158 | TOTAL MIN SETTLED DISEN.: | [7 empty] | 0.47 | TOTAL FILTER MAX NTU | [6 empty] | 0.06 | [20 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 13320 | [6 empty] | 450 | 460 | 475 | 400 | 420 | 440 | 1000 | 920 | 920 | 950 | 760 | 810 | 750 |  | 980 | 960 | 1050 | 96 | 118 | 14 | 1740 | 355 | 325 | 52 | 64 | 8 | 840 | 170 | 240
[90 empty] | MAXIMUM | 13500 | [6 empty] | 450 | 460 | 475 | 420 | 420 | 480 | 1020 | 960 | 960 | 960 | 1020 | 1020 | 800 |  | 990 | 970 | 1080 | 98 | 118 | 14 | 1750 | 356 | 360 | 55 | 66 | 8 | 880 | 180 | 275
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.822 |  | TOTAL MGD: |  | 0.007 |  |  | FINISHED SOUTH 1 |  | START: | 23770179 |  | END: | 23770186 |  |  | Alum | 9338 | 9442 | 9442 | 8411 | 8411 | 38.5 | [44 empty] | 0.47 | 11.8 | 22.8814 | 10.7542 | 6.15 | 18.5 | 10 | 1.0754
[73 empty] | FINISHED 2 | 14.938 |  | TOTAL MGD: |  | 13.815 |  |  | FINISHED SOUTH 2 |  | START: | 43126694 |  | END: | 43140509 |  |  | Caustic | 8743 | 7220 | 7220
[73 empty] | TOTAL RAW | 32.598 |  | TOTAL MGD: |  | 4.532 |  |  | FINISHED CONWAY |  | START: | 9948894 |  | END: | 9953426 |  |  | Hypochlorite | 13 |  | 18
[76 empty] | TOTAL MGD: |  | 10.406 |  |  | FINISHED PERRY |  | START: | 33153197 |  | END: | 33163603 |  |  | Phosphate | 2922
[76 empty] | TOTAL MGD: |  | 10.265 |  |  | RAW PLANT 1 |  | START: | 30344958 |  | END: | 30344958 |  |  | Fluoride | 3750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.665 |  |  | RAW PLANT 2 |  | START: | 30290929 |  | END: | 30301594 |  |  | Cal~Flo | 12.75 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.668 |  |  | RAW PLANT 3 |  | START: | 6787876 |  | END: | 6799544 |  |  | Zinc | 1461
[76 empty] | TOTAL MGD: |  | 2.103 |  |  | DECANT |  | START: | 1794523 |  | END: | 1796626 |  |  | Polymer | 23
[76 empty] | TOTAL MGD: |  | 1.3311 |  |  | BLOW DOWN |  | START: | 9039.828 |  | END: | 9041.1591 |  |  | NH3 | 8 |  | BI-SUL | 900
[90 empty] | Lime | 0 |  | FILTER AIDE | 2 | [25 empty] | 1.0202
[82 empty] | BACKWASH WATER USED : |  |  |  |  | 0 |  |  | Cabon | 888
[91 empty] | FINISHED SOUTH 1 |  | END: | 23770186
[91 empty] | FINISHED SOUTH 2 |  | END: | 43140509
[91 empty] | FINISHED CONWAY |  | END: | 9953426
[91 empty] | FINISHED PERRY |  | END: | 33163603
[91 empty] | RAW PLANT 1 |  | END: | 30344958
[91 empty] | RAW PLANT 2 |  | END: | 30301594
[91 empty] | RAW PLANT 3 |  | END: | 6799544
[91 empty] | DECANT |  | END: | 1796626
[91 empty] | BLOW DOWN |  | END: | 9041.1591
Note on AX36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 2
DATE: | 2018-11-02 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CBW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-02 | [23 empty] | DATE: | 2018-11-02
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-02 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43406.0186 | 1,2,3,5 | 42 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | ,1,3 | 14.0861 | 1,3 | 16.5269 | 30.613 | 1.6258 | 43406.0186 | 94.8448 | 6394.6892 | 0 | 888.1057 | 0 | 0 | 0 | 12.2712 | 12.5439 | 11.8458 | 1.7456 | 1.8329 | 1.9077 | 0.53315 | 0.4905 | 0.4905 | 0.51182 | 0.37056 | 0.39494 | 1.4267 | 1 | 0.050689 | 0.049654 | 0.050874 | 1.0818 | 0.50105 | 0.099158 | 4.2009 | 0.79383 | 5.1491 | 1.1084 | 0.49499 | 0.1032 | 3.8213 | 0.69241 | 7.034 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.389 | 4 | 0.72 | 18.1 | 10.6 | 0.53667 |  | 6.08 | 0.381 | 5 | 0.7 | 18.2 | 10.5 | 0.53274 | 6.12 | 0.352 | 5 | 0.62 | 19.6 | 11.8 | 0.55704 | [13 empty] | 7.19 | 0.053 | 1 | 4.2 | 18.4 |  |  |  | 7.17 | 0.052 | 2 | 3.6 | 21.2 |  |  |  | 4.3 | 4.4 | 3.7 | [18 empty] | 12840 | [6 empty] | 450 | 460 | 475 | 400 | 420 | 480 | 1000 | 920 | 920 | 960 | 760 | 810 | 750 |  | 980 | 960 | 1080 | 96 | 118 | 14 | 1740 | 355 | 360 | 54 | 64 | 8 | 840 | 170 | 270 |  | 1:00 | 0.72 | 10.6 | 24 | 17.28 | 6.06 | 18.1 | 10 | 1.728 | 15 | 6.5 | 0.41667 | 1:00 | 0.7 | 10.5 | 24.2286 | 16.96 | 6.08 | 18.2 | 10 | 1.696 | 15 | 6.5 | 0.41274 | 1:00 | 0.62 | 11.8 | 22.8814 | 14.1864 | 6.12 | 19.6 | 10 | 1.4186 | 15 | 6.5 | 0.43704
2:00 | [72 empty] | 43406.3642 | 1,2,3,5 | 42 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | ,1,3 | 14.0861 | 1,3 | 16.5269 | 30.613 | 1.6258 | 43406.3642 | 94.18 | 6394.6892 | 0 | 888.1057 | 0 | 0 | 0 | 11.0441 | 11.3168 | 10.7236 | 1.7456 | 1.7456 | 1.7885 | 0.53315 | 0.47983 | 0.47983 | 0.47983 | 0.38031 | 0.38031 | 1.4267 | 0 | 0.039827 | 0.050172 | 0.050403 | 1.1043 | 0.50105 | 0.099158 | 4.2112 | 0.78265 | 5.1491 | 1.1084 | 0.51046 | 0.1032 | 3.8098 | 0.68426 | 7.034 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.47 | 19 | 18 | 14.6 | 128 | 207 | 18.4 | 0.561 |  | 6.05 | 10 | 0.093 | 6.04 | 10 |  | 6.03 | 11 | [8 empty] | 0.064 | [14 empty] | 0.087 | 1 | 0.37 |  | 0.063 | 0.011 | 1 | 0.36 |  | 0.039 | 1 | 0.47 | [38 empty] | 12750 | [6 empty] | 405 | 415 | 430 | 400 | 400 | 450 | 1000 | 900 | 900 | 900 | 780 | 780 | 750 |  | 770 | 970 | 1070 | 98 | 118 | 14 | 1720 | 350 | 360 | 54 | 66 | 8 | 820 | 168 | 270 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43406.5609 | 1,2,3,5 | 42 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 14.0861 | 1,3 | 16.5269 | 30.613 | 1.6258 | 43406.5609 | 90.164 | 6640.6388 | 0 | 840.5286 | 0 | 0 | 0 | 6.9185 | 7.2193 | 7.09 | 1.9353 | 1.9353 | 1.9638 | 0.5293 | 0.47049 | 0.47049 | 0.47049 | 0.34655 | 0.35988 | 1.4267 | 0 | 0.049891 | 0.040142 | 0.051723 | 1.0995 | 0.49902 | 0.09423 | 4.2078 | 0.78095 | 5.3916 | 1.1043 | 0.50955 | 0.11332 | 3.8242 | 0.67084 | 7.2945 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.1 | 0.054 | 1 | 4.3 | 18.5 |  |  |  | 7.26 | 0.055 | 1 | 4 | 21.4 |  |  |  | 4.2 | 4.3 | 4.1 | [18 empty] | 11100 | [6 empty] | 230 | 240 | 260 | 400 | 400 | 450 | 900 | 800 | 800 | 800 | 650 | 675 | 750 |  | 870 | 700 | 1000 | 88 | 106 | 12 | 1550 | 315 | 340 | 49 | 60 | 8 | 750 | 150 | 255 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43406.8434 | 1,2,5 | 42 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 10.8979 | 1,3 | 9.5328 | 20.4307 | 1.6258 | 43406.8434 | 89.3517 | 6886.5884 | 0 | 840.5286 | 0 | 0 | 0 | 6.9185 | 7.2193 | 7.09 | 1.9353 | 1.9353 | 2.0074 | 0.56459 | 0.47049 | 0.47049 | 0.51754 | 0.38387 | 0.44784 | 1.4267 | 1 | 0.050464 | 0.040142 | 0.050172 | 1.0995 | 0.49902 | 0.10208 | 4.213 | 0.76855 | 5.3916 | 1.1269 | 0.50955 | 0.099158 | 3.7901 | 0.67084 | 7.2945 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.46 | 20 | 18 | 14.6 | 123 | 205 | 18.6 | 0.54 |  | 6.03 | 10 | 0.067 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.061 | [14 empty] | 0.033 | 1 | 0.48 |  | 0.061 | 0.01 | 1 | 0.51 |  | 0.038 | 1 | 0.54 | [38 empty] | 11000 | [6 empty] | 230 | 240 | 260 | 400 | 400 | 460 | 960 | 800 | 800 | 880 | 720 | 840 | 750 |  | 880 | 700 | 970 | 88 | 106 | 13 | 1540 | 310 | 340 | 50 | 60 | 7 | 720 | 150 | 255 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.078 | [9 empty] | 6.1 | 0.396 | 5 | 0.65 | 17.8 | 10.7 | 0.5406 |  | 6.1 | 0.371 | 5 | 0.61 | 17.8 | 10.7 | 0.5406 | 6.14 | 0.368 | 4 | 0.63 | 19.5 | 11.7 | 0.55333 |  |  |  | 0.031 |  |  |  |  | 0.048 |  |  |  | 0.025 | 7.17 | 0.058 | 1 | 4.8 | 17.9 | 25 | 32 | 0.037 | 7.21 | 0.054 | 1 | 3.9 | 19.6 | 24 | 30 | 0.026 | 4.2 | 4.2 | 4 | [55 empty] | 9:00 | 0.65 | 10.7 | 23.7757 | 15.4542 | 6.1 | 17.8 | 10 | 1.5454 | 15 | 6.5 | 0.4206 | 9:00 | 0.61 | 10.7 | 23.7757 | 14.5032 | 6.1 | 17.8 | 10 | 1.4503 | 15 | 6.5 | 0.4206 | 9:00 | 0.63 | 11.7 | 23.0769 | 14.5385 | 6.14 | 19.5 | 10 | 1.4538 | 15 | 6.5 | 0.43333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.48 | 21 | 18 | 14.6 | 115 | 200 | 19.8 | 0.489 |  | 6.01 | 12 | 0.086 | 6.03 | 12 |  | 6.03 | 12 | [8 empty] | 0.061 | [14 empty] | 0.031 | 1 | 0.45 |  | 0.061 | 0.012 | 1 | 0.5 |  | 0.034 | 1 | 0.52 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.16 | 0.365 | 4 | 0.64 | 18.5 | 9.7 | 0.50129 |  | 6.2 | 0.355 | 4 | 0.62 | 18.5 | 9.7 | 0.50129 | 6.2 | 0.325 | 4 | 0.6 | 20 | 10.7 | 0.39741 | [13 empty] | 7.14 | 0.055 | 1 | 4.4 | 18 |  |  |  | 7.17 | 0.052 | 1 | 4 | 21.5 |  |  |  | 4.3 | 4.2 | 3.3 | [55 empty] | 13:00 | 0.64 | 9.7 | 26.2268 | 16.7852 | 6.16 | 18.5 | 10 | 1.6785 | 15 | 6.5 | 0.38129 | 13:00 | 0.62 | 9.7 | 26.2268 | 16.2606 | 6.2 | 18.5 | 10 | 1.6261 | 15 | 6.5 | 0.38129 | 13:00 | 0.6 | 10.7 | 25.2336 | 15.1402 | 6.2 | 20 | 7 | 2.1629 | 20 | 6.5 | 0.27741
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.48 | 22 | 18 | 14.2 | 120 | 200 | 19 | 0.528 |  | 6.04 | 11 | 0.103 | 6.03 | 11 |  | 6.04 | 11 | [8 empty] | 0.06 | [14 empty] | 0.024 | 1 | 0.42 |  | 0.061 | 0.016 | 1 | 0.37 |  | 0.036 | 1 | 0.57 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.21 | 0.052 | 1 | 4.2 | 18 |  |  |  | 7.24 | 0.054 | 1 | 4.2 | 20.5 |  |  |  | 4.4 | 4.2 | 3.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.49 | 21 | 19 | 14 | 122 | 195 | 19.7 | 0.509 |  | 6.05 | 12 | 0.083 | 6.06 | 13 |  | 6.1 | 12 | [8 empty] | 0.066 | [14 empty] | 0.032 | 1 | 0.42 |  | 0.067 | 0.016 | 1 | 0.51 |  | 0.042 | 1 | 0.56 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.048 | [9 empty] | 6.05 | 0.376 | 5 | 0.71 | 18.6 | 9.5 | 0.49343 |  | 6.08 | 0.381 | 5 | 0.66 | 18.7 | 9.7 | 0.50129 | 6.16 | 0.303 | 4 | 0.67 | 20.2 | 10.7 | 0.39741 |  |  |  | 0.008 |  |  |  |  | 0.023 |  |  |  | 0.008 | 7.24 | 0.056 | 2 | 4.4 | 18.6 | 23 | 35 | 0.016 | 7.28 | 0.057 | 2 | 3.7 | 21.1 | 25 | 38 | 0.01 | 4.4 | 4.2 | 3.2 | [55 empty] | 21:00 | 0.71 | 9.5 | 26.7789 | 19.0131 | 6.05 | 18.6 | 10 | 1.9013 | 15 | 6.5 | 0.37343 | 21:00 | 0.66 | 9.7 | 26.2268 | 17.3097 | 6.08 | 18.7 | 10 | 1.731 | 15 | 6.5 | 0.38129 | 21:00 | 0.67 | 10.7 | 25.2336 | 16.9065 | 6.16 | 20.2 | 7 | 2.4152 | 20 | 6.5 | 0.27741
22:00 | [72 empty] | DOSE |  | TOTAL | 40.8 | 40.8 | 44.8 | 126.4 | 38.8 | 38.8 | 42.8 | 120.4 | 0 | 53.1562 | 0 | 59.1134 | 112.2696 | 6.503 | TOTAL | 368.5406 | 26316.6056 | 0 | 3457.2687 | 0 | 0 | 0 | 37.1523 | 38.2993 | 36.7495 | 7.3618 | 7.4491 | 7.6673 | 2.1602 | 1.9113 | 1.9113 | 1.9797 | 1.4813 | 1.583 | 5.7067 | 2 | 0.19087 | 0.18011 | 0.20317 | 4.3851 | 2.0002 | 0.39463 | 16.8328 | 3.126 | 21.0814 | 4.448 | 2.0245 | 0.41889 | 15.2454 | 2.7184 | 28.6571 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.42 | 20 | 20 | 14.1 | 121 | 194 | 19.7 | 0.513 |  | 6.06 | 11 | 0.083 | 6.05 | 12 |  | 6.07 | 11 | [8 empty] | 0.065 | [14 empty] | 0.027 | 1 | 0.34 |  | 0.064 | 0.018 | 1 | 0.042 |  | 0.041 | 1 | 0.43 | [22 empty] | AVERAGE | 10.2 | 10.2 | 11.2 | 31.6 | 9.7 | 9.7 | 10.7 | 30.1 |  | 13.289 |  | 14.7784 | 28.0674 | 1.6258 | AVERAGE | 92.1351 | 6579.1514 |  | 864.3172 | 0 | 0 | 0 | 9.2881 | 9.5748 | 9.1874 | 1.8405 | 1.8623 | 1.9168 | 0.54005 | 0.47783 | 0.47783 | 0.49492 | 0.37032 | 0.39574 | 1.4267 | 0.5 | 0.047718 | 0.045027 | 0.050793 | 1.0963 | 0.50004 | 0.098657 | 4.2082 | 0.7815 | 5.2704 | 1.112 | 0.50613 | 0.10472 | 3.8114 | 0.67959 | 7.1643 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.8 | 123 | 111 | 86.1 | 729 | 1201 | 115.2 | 3.14 | 0.126 | 36.24 | 66 | 0.515 | 36.26 | 68 | 0 | 36.27 | 67 | 0 | 24.37 | 1.526 | 18 | 2.72 | 73 | 40.5 | 2.072 | 0.377 | 24.46 | 1.488 | 19 | 2.59 | 73.2 | 40.6 | 2.0759 | 24.62 | 1.348 | 17 | 2.52 | 79.3 | 44.9 | 1.9052 | 0.234 | 6 | 2.48 | 0.039 | 0.377 | 0.083 | 6 | 2.292 | 0.071 | 0.23 | 6 | 3.09 | 0.033 | 43.05 | 0.328 | 7 | 26.3 | 109.4 | 48 | 67 | 0.053 | 43.33 | 0.324 | 8 | 23.4 | 125.3 | 49 | 68 | 0.036 | 25.8 | 25.5 | 21.5 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 10.8979 |  | 9.5328 | 20.4307 | 1.6258 | MINIMUM | 89.3517 | 6394.6892 |  | 840.5286 |  |  |  | 6.9185 | 7.2193 | 7.09 | 1.7456 | 1.7456 | 1.7885 | 0.5293 | 0.47049 | 0.47049 | 0.47049 | 0.34655 | 0.35988 | 1.4267 | 0 | 0.039827 | 0.040142 | 0.050172 | 1.0818 | 0.49902 | 0.09423 | 4.2009 | 0.76855 | 5.1491 | 1.1043 | 0.49499 | 0.099158 | 3.7901 | 0.67084 | 7.034 |  | MIN | 0.65 | 10.7 | 23.7757 | 15.4542 | 6.1 | 17.8 | 10 | 1.5454 |  |  |  | MIN | 0.61 | 10.7 | 23.7757 | 14.5032 | 6.1 | 17.8 | 10 | 1.4503 |  |  |  | MIN | 0.62 | 11.8 | 22.8814 | 14.1864 | 6.12 | 19.6 | 10 | 1.4186 |  |  |  | 1.4186
AVERAGE | 6.4667 | 20.5 | 18.5 | 14.35 | 121.5 | 200.1667 | 19.2 | 0.52333 | 0.063 | 6.04 | 11 | 0.085833 | 6.0433 | 11.3333 |  | 6.045 | 11.1667 |  | 6.0925 | 0.3815 | 4.5 | 0.68 | 18.25 | 10.125 | 0.518 | 0.062833 | 6.115 | 0.372 | 4.75 | 0.6475 | 18.3 | 10.15 | 0.51898 | 6.155 | 0.337 | 4.25 | 0.63 | 19.825 | 11.225 | 0.4763 | 0.039 | 1 | 0.41333 | 0.0195 | 0.062833 | 0.013833 | 1 | 0.382 | 0.0355 | 0.038333 | 1 | 0.515 | 0.0165 | 7.175 | 0.054667 | 1.1667 | 4.3833 | 18.2333 | 24 | 33.5 | 0.0265 | 7.2217 | 0.054 | 1.3333 | 3.9 | 20.8833 | 24.5 | 34 | 0.018 | 4.3 | 4.25 | 3.5833 |  |  | MAXIMUM | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 14.0861 |  | 16.5269 | 30.613 | 1.6258 | MAXIMUM | 94.8448 | 6886.5884 |  | 888.1057 |  |  |  | 12.2712 | 12.5439 | 11.8458 | 1.9353 | 1.9353 | 2.0074 | 0.56459 | 0.4905 | 0.4905 | 0.51754 | 0.38387 | 0.44784 | 1.4267 | 1 | 0.050689 | 0.050172 | 0.051723 | 1.1043 | 0.50105 | 0.10208 | 4.213 | 0.79383 | 5.3916 | 1.1269 | 0.51046 | 0.11332 | 3.8242 | 0.69241 | 7.2945
MINIMUM | 6.42 | 19 | 18 | 14 | 115 | 194 | 18.4 | 0.489 | 0.048 | 6.01 | 10 | 0.067 | 6.03 | 10 |  | 6 | 10 |  | 6.05 | 0.365 | 4 | 0.64 | 17.8 | 9.5 | 0.49343 | 0.06 | 6.08 | 0.355 | 4 | 0.61 | 17.8 | 9.7 | 0.50129 | 6.12 | 0.303 | 4 | 0.6 | 19.5 | 10.7 | 0.39741 | 0.024 | 1 | 0.34 | 0.008 | 0.061 | 0.01 | 1 | 0.042 | 0.023 | 0.034 | 1 | 0.43 | 0.008 | 7.1 | 0.052 | 1 | 4.2 | 17.9 | 23 | 32 | 0.016 | 7.17 | 0.052 | 1 | 3.6 | 19.6 | 24 | 30 | 0.01 | 4.2 | 4.2 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 47690 | 0 | 0 | 0 | 0 | 0 | 0 | 1315 | 1355 | 1425 | 1600 | 1620 | 1840 | 3860 | 3420 | 3420 | 3540 | 2910 | 3105 | 3000 | 0 | 3500 | 3330 | 4120 | 370 | 448 | 53 | 6550 | 1330 | 1400 | 207 | 250 | 31 | 3130 | 638 | 1050
MAXIMUM | 6.49 | 22 | 20 | 14.6 | 128 | 207 | 19.8 | 0.561 | 0.078 | 6.06 | 12 | 0.103 | 6.06 | 13 |  | 6.1 | 12 |  | 6.16 | 0.396 | 5 | 0.72 | 18.6 | 10.7 | 0.5406 | 0.066 | 6.2 | 0.381 | 5 | 0.7 | 18.7 | 10.7 | 0.5406 | 6.2 | 0.368 | 5 | 0.67 | 20.2 | 11.8 | 0.55704 | 0.087 | 1 | 0.48 | 0.031 | 0.067 | 0.018 | 1 | 0.51 | 0.048 | 0.042 | 1 | 0.57 | 0.025 | 7.24 | 0.058 | 2 | 4.8 | 18.6 | 25 | 35 | 0.037 | 7.28 | 0.057 | 2 | 4.2 | 21.5 | 25 | 38 | 0.026 | 4.4 | 4.4 | 4.1 | [17 empty] | AVERAGE | 11922.5 | [6 empty] | 328.75 | 338.75 | 356.25 | 400 | 405 | 460 | 965 | 855 | 855 | 885 | 727.5 | 776.25 | 750 |  | 875 | 832.5 | 1030 | 92.5 | 112 | 13.25 | 1637.5 | 332.5 | 350 | 51.75 | 62.5 | 7.75 | 782.5 | 159.5 | 262.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0428 |  | TOTAL AVG COAG ALK: |  |  |  | 11.1667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.396 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.6 | [5 empty] | 6.1208 |  |  |  |  | 0.087 |  |  |  |  | 0.6 | [6 empty] | 0.087 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 11000 | [6 empty] | 230 | 240 | 260 | 400 | 400 | 450 | 900 | 800 | 800 | 800 | 650 | 675 | 750 |  | 770 | 700 | 970 | 88 | 106 | 12 | 1540 | 310 | 340 | 49 | 60 | 7 | 720 | 150 | 255
[90 empty] | MAXIMUM | 12840 | [6 empty] | 450 | 460 | 475 | 400 | 420 | 480 | 1000 | 920 | 920 | 960 | 780 | 840 | 750 |  | 980 | 970 | 1080 | 98 | 118 | 14 | 1740 | 355 | 360 | 54 | 66 | 8 | 840 | 170 | 270
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.026 |  | TOTAL MGD: |  | 0.002 |  |  | FINISHED SOUTH 1 |  | START: | 23770186 |  | END: | 23770188 |  |  | Alum | 9336 | 10140 | 10140 | 9838 | 9838 | 47.6 | [44 empty] | 0.62 | 11.8 | 22.8814 | 14.1864 | 6.12 | 19.6 | 10 | 1.4186
[73 empty] | FINISHED 2 | 14.108 |  | TOTAL MGD: |  | 14.024 |  |  | FINISHED SOUTH 2 |  | START: | 43140509 |  | END: | 43154533 |  |  | Caustic | 8162 | 7108 | 7108
[73 empty] | TOTAL RAW | 31.179 |  | TOTAL MGD: |  | 4.549 |  |  | FINISHED CONWAY |  | START: | 9953426 |  | END: | 9957975 |  |  | Hypochlorite | 12 |  | 27
[76 empty] | TOTAL MGD: |  | 9.559 |  |  | FINISHED PERRY |  | START: | 33163603 |  | END: | 33173162 |  |  | Phosphate | 2877
[76 empty] | TOTAL MGD: |  | 9.811 |  |  | RAW PLANT 1 |  | START: | 30344958 |  | END: | 30351164 |  |  | Fluoride | 3650 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.046 |  |  | RAW PLANT 2 |  | START: | 30301594 |  | END: | 30311640 |  |  | Cal~Flo | 10.09 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.322 |  |  | RAW PLANT 3 |  | START: | 6799544 |  | END: | 6810866 |  |  | Zinc | 1474
[76 empty] | TOTAL MGD: |  | 2.182 |  |  | DECANT |  | START: | 1796626 |  | END: | 1798808 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.2551 |  |  | BLOW DOWN |  | START: | 9041.1591 |  | END: | 9042.4142 |  |  | NH3 | 7.63 |  | BI-SUL | 900
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 841
23770188
43154533
9957975
33173162
30351164
30311640
6810866
1798808
9042.4142
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 3
DATE: | 2018-11-03 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-03 | [23 empty] | DATE: | 2018-11-03
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-03 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43407.0049 | 1,2,5 | 42 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 10.8979 | 1,3 | 9.5328 | 20.4307 | 1.6258 | 43407.0049 | 89.3517 | 6886.5884 | 0 | 840.5286 | 0 | 0 | 0 | 6.9185 | 7.2193 | 7.09 | 1.9353 | 1.9353 | 2.0074 | 0.56459 | 0.47049 | 0.47049 | 0.51754 | 0.38387 | 0.44784 | 1.4267 | 1 | 0.050464 | 0.040142 | 0.050172 | 1.0995 | 0.49902 | 0.10208 | 4.213 | 0.76855 | 5.3916 | 1.1269 | 0.50955 | 0.099158 | 3.7901 | 0.67084 | 7.2945 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.05 | 0.37 | 5 | 0.64 | 18.4 | 9.5 | 0.49343 |  | 6.13 | 0.373 | 5 | 0.6 | 18.5 | 9.7 | 0.50129 | 6.15 | 0.348 | 4 | 0.53 | 19.9 | 10.7 | 0.5163 | [13 empty] | 7.17 | 0.054 | 1 | 4.1 | 18.6 |  |  |  | 7.23 | 0.058 | 1 | 3.5 | 21.2 |  |  |  | 4.3 | 4.2 | 3.4 | [18 empty] | 11000 | [6 empty] | 230 | 240 | 260 | 400 | 400 | 460 | 960 | 800 | 800 | 880 | 720 | 840 | 750 |  | 880 | 700 | 970 | 88 | 106 | 13 | 1540 | 310 | 340 | 50 | 60 | 7 | 720 | 150 | 255 |  | 1:00 | 0.64 | 9.5 | 26.7789 | 17.1385 | 6.05 | 18.4 | 10 | 1.7139 | 15 | 6.5 | 0.37343 | 1:00 | 0.6 | 9.7 | 26.2268 | 15.7361 | 6.13 | 18.5 | 10 | 1.5736 | 15 | 6.5 | 0.38129 | 1:00 | 0.53 | 10.7 | 25.2336 | 13.3738 | 6.15 | 19.9 | 10 | 1.3374 | 15 | 6.5 | 0.3963
2:00 | [72 empty] | 43407.0779 | 1,2,5 | 42 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 10.8979 | 1,3 | 9.5328 | 20.4307 | 1.6258 | 43407.0779 | 89.3517 | 6886.5884 | 0 | 840.5286 | 0 | 0 | 0 | 6.9185 | 7.2193 | 7.09 | 1.9353 | 1.9353 | 2.0074 | 0.54106 | 0.47049 | 0.47049 | 0.49401 | 0.36254 | 0.40519 | 1.4267 | 1 | 0.050464 | 0.040142 | 0.050172 | 1.0995 | 0.49902 | 0.10208 | 4.213 | 0.76855 | 5.3916 | 1.1269 | 0.50955 | 0.099158 | 3.7901 | 0.67084 | 7.2945 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.45 | 18 | 17 | 13.9 | 122 | 198 | 18.9 | 0.519 |  | 6.04 | 10 | 0.095 | 6.05 | 11 |  | 6.08 | 11 | [8 empty] | 0.068 | [14 empty] | 0.026 | 1 | 0.39 |  | 0.065 | 0.017 | 1 | 0.39 |  | 0.043 | 1 | 0.48 | [38 empty] | 11000 | [6 empty] | 230 | 240 | 260 | 400 | 400 | 460 | 920 | 800 | 800 | 840 | 680 | 760 | 750 |  | 880 | 700 | 970 | 88 | 106 | 13 | 1540 | 310 | 340 | 50 | 60 | 7 | 720 | 150 | 255 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 8:20 | 1,2,5 | 42 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 10.8979 | 1,3 | 9.5328 | 20.4307 | 1.6258 | 43407.4694 | 88.9456 | 6394.6892 | 0 | 840.5286 | 0 | 0 | 0 | 6.9185 | 7.2193 | 6.9537 | 1.9353 | 1.9353 | 1.9638 | 0.5293 | 0.47049 | 0.47049 | 0.47049 | 0.3732 | 0.3732 | 1.4267 | 0 | 0.049891 | 0.040142 | 0.050172 | 1.0995 | 0.49902 | 0.09423 | 4.213 | 0.77847 | 5.7088 | 1.0818 | 0.59447 | 0.11332 | 3.7901 | 0.6619 | 7.8667 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.18 | 0.05 | 1 | 4.3 | 18.6 |  |  |  | 7.2 | 0.053 | 1 | 3.8 | 21.2 |  |  |  | 4.2 | 4.2 | 3.8 | [18 empty] | 10950 | [6 empty] | 230 | 240 | 255 | 400 | 400 | 450 | 900 | 800 | 800 | 800 | 700 | 700 | 750 |  | 870 | 700 | 970 | 88 | 106 | 12 | 1540 | 314 | 360 | 48 | 70 | 8 | 720 | 148 | 275 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43407.563 | 1,2,5 | 42 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 10.8979 | 1,3 | 9.5328 | 20.4307 | 1.6258 | 43407.563 | 84.8029 | 6148.7396 | 0 | 840.5286 | 0 | 0 | 0 | 5.1137 | 5.4145 | 5.3175 | 1.9353 | 1.9353 | 1.9638 | 0.5293 | 0.47049 | 0.47049 | 0.47049 | 0.3732 | 0.3732 | 1.4267 | 0 | 0.049891 | 0.040142 | 0.050172 | 1.0995 | 0.49902 | 0.09423 | 4.213 | 0.77847 | 5.7088 | 1.0818 | 0.59447 | 0.11332 | 3.7901 | 0.6619 | 7.8667 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.42 | 22 | 19 | 13.4 | 121 | 195 | 18.8 | 0.528 |  | 6.01 | 11 | 0.084 | 6.01 | 11 |  | 6.02 | 11 | [8 empty] | 0.064 | [14 empty] | 0.026 | 1 | 0.41 |  | 0.063 | 0.012 | 1 | 0.5 |  | 0.038 | 1 | 0.61 | [38 empty] | 10440 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 450 | 900 | 800 | 800 | 800 | 700 | 700 | 750 |  | 870 | 700 | 970 | 88 | 106 | 12 | 1540 | 314 | 360 | 48 | 70 | 8 | 720 | 148 | 275 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43407.8612 | 1,2,5 | 54 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 14.904 | 1,3 | 12.6475 | 27.5515 | 1.6258 | 43407.8612 | 83.1783 | 6271.7144 | 0 | 840.5286 | 0 | 0 | 0 | 5.1137 | 5.4145 | 5.3175 | 1.9353 | 1.9353 | 1.8329 | 0.47049 | 0.39992 | 0.39992 | 0.42344 | 0.29856 | 0.31989 | 1.4267 | 3 | 0.049317 | 0.040142 | 0.049654 | 1.0995 | 0.49902 | 0.10208 | 4.1934 | 0.76855 | 5.7088 | 1.1269 | 0.50955 | 0.099158 | 3.8148 | 0.67084 | 7.8667 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.066 | [9 empty] | 6.07 | 0.383 | 4 | 0.63 | 17.5 | 9.7 | 0.50129 |  | 6.08 | 0.405 | 3 | 0.64 | 17.5 | 9.7 | 0.50129 | 6.14 | 0.298 | 3 | 0.67 | 19 | 10.7 | 0.5163 |  |  |  | 0.017 |  |  |  |  | 0.036 |  |  |  | 0.02 | 7.17 | 0.057 | 1 | 4.3 | 18 | 21 | 35 | 0.021 | 7.24 | 0.06 | 1 | 3.9 | 19.4 | 23 | 36 | 0.014 | 4.2 | 4.1 | 4 | [18 empty] | 10240 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 420 | 800 | 680 | 680 | 720 | 560 | 600 | 750 |  | 860 | 700 | 960 | 88 | 106 | 13 | 1520 | 310 | 360 | 50 | 60 | 7 | 730 | 150 | 275 |  | 9:00 | 0.63 | 9.7 | 26.2268 | 16.5229 | 6.07 | 17.5 | 10 | 1.6523 | 15 | 6.5 | 0.38129 | 9:00 | 0.64 | 9.7 | 26.2268 | 16.7852 | 6.08 | 17.5 | 10 | 1.6785 | 15 | 6.5 | 0.38129 | 9:00 | 0.67 | 10.7 | 25.2336 | 16.9065 | 6.14 | 19 | 10 | 1.6907 | 15 | 6.5 | 0.3963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.38 | 21 | 19 | 13.2 | 93 | 193 | 18.9 | 0.446 |  | 6.06 | 10 | 0.071 | 6.07 | 10 |  | 6.05 | 11 | [8 empty] | 0.062 | [14 empty] | 0.026 | 1 | 0.39 |  | 0.069 | 0.013 | 1 | 0.47 |  | 0.038 | 1 | 0.56 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.325 | 3 | 0.55 | 18 | 9.7 | 0.50129 |  | 6.09 | 0.305 | 3 | 0.58 | 18 | 9.7 | 0.50129 | 6.13 | 0.3 | 3 | 0.6 | 19 | 10.7 | 0.5163 | [13 empty] | 7.34 | 0.052 | 1 | 4.4 | 18 |  |  |  | 7.31 | 0.055 | 1 | 4 | 19.8 |  |  |  | 4.1 | 4 | 3.1 | [55 empty] | 13:00 | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.03 | 18 | 10 | 1.4425 | 15 | 6.5 | 0.38129 | 13:00 | 0.58 | 9.7 | 26.2268 | 15.2115 | 6.09 | 18 | 10 | 1.5212 | 15 | 6.5 | 0.38129 | 13:00 | 0.6 | 10.7 | 25.2336 | 15.1402 | 6.13 | 19 | 10 | 1.514 | 15 | 6.5 | 0.3963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.45 | 22 | 20 | 13.6 | 100 | 193 | 19 | 0.486 |  | 6.02 | 12 | 0.084 | 6 | 12 |  | 6 | 12 | [8 empty] | 0.061 | [14 empty] | 0.023 | 1 | 0.4 |  | 0.064 | 0.016 | 1 | 0.45 |  | 0.036 | 1 | 0.55 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.3 | 0.05 | 1 | 4.2 | 18 |  |  |  | 7.34 | 0.052 | 1 | 4 | 20 |  |  |  | 4.1 | 4 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.46 | 20 | 18 | 13.7 | 123 | 191 | 19.6 | 0.542 |  | 5.98 | 10 | 0.095 | 6.02 | 11 |  | 6.01 | 11 | [8 empty] | 0.059 | [14 empty] | 0.026 | 2 | 0.37 |  | 0.06 | 0.013 | 1 | 0.42 |  | 0.038 | 1 | 0.48 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.054 | [9 empty] | 6.08 | 0.366 | 4 | 0.69 | 18.1 | 9.5 | 0.49343 |  | 6.07 | 0.381 | 4 | 0.7 | 18.1 | 9.5 | 0.49343 | 6.13 | 0.398 | 3 | 0.69 | 19.8 | 10.7 | 0.5163 |  |  |  | 0.012 |  |  |  |  | 0.025 |  |  |  | 0.009 | 7.09 | 0.048 | 1 | 4.1 | 18.6 | 20 | 34 | 0.018 | 7.2 | 0.053 | 1 | 3.7 | 20.4 | 22 | 35 | 0.01 | 4.1 | 4 | 3.2 | [55 empty] | 21:00 | 0.69 | 9.5 | 26.7789 | 18.4775 | 6.08 | 18.1 | 10 | 1.8477 | 15 | 6.5 | 0.37343 | 21:00 | 0.7 | 9.5 | 26.7789 | 18.7453 | 6.07 | 18.1 | 10 | 1.8745 | 15 | 6.5 | 0.37343 | 21:00 | 0.69 | 10.7 | 25.2336 | 17.4112 | 6.13 | 19.8 | 10 | 1.7411 | 15 | 6.5 | 0.3963
22:00 | [72 empty] | DOSE |  | TOTAL | 48.5 | 48.5 | 53.5 | 150.5 | 46 | 46 | 51 | 143 | 0 | 58.4957 | 0 | 50.7787 | 109.2744 | 8.1288 | TOTAL | 435.6302 | 32588.32 | 0 | 4202.6432 | 0 | 0 | 0 | 30.983 | 32.487 | 31.7688 | 9.6766 | 9.6766 | 9.7753 | 2.6347 | 2.2819 | 2.2819 | 2.376 | 1.7914 | 1.9193 | 7.1334 | 5 | 0.25003 | 0.20071 | 0.25034 | 5.4973 | 2.4951 | 0.49471 | 21.0453 | 3.8626 | 27.9096 | 5.5443 | 2.7176 | 0.52412 | 18.975 | 3.3363 | 38.1891 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.42 | 21 | 17 | 14.1 | 118 | 186 | 19.6 | 0.494 |  | 6.01 | 11 | 0.094 | 6.04 | 12 |  | 6.02 | 11 | [8 empty] | 0.065 | [14 empty] | 0.023 | 1 | 0.38 |  | 0.062 | 0.016 | 1 | 0.07 |  | 0.038 | 1 | 0.51 | [22 empty] | AVERAGE | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 11.6991 |  | 10.1557 | 21.8549 | 1.6258 | AVERAGE | 87.126 | 6517.664 |  | 840.5286 | 0 | 0 | 0 | 6.1966 | 6.4974 | 6.3538 | 1.9353 | 1.9353 | 1.9551 | 0.52695 | 0.45637 | 0.45637 | 0.47519 | 0.35828 | 0.38387 | 1.4267 | 1 | 0.050005 | 0.040142 | 0.050068 | 1.0995 | 0.49902 | 0.098942 | 4.2091 | 0.77252 | 5.5819 | 1.1089 | 0.54352 | 0.10482 | 3.795 | 0.66727 | 7.6378 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.58 | 124 | 110 | 81.9 | 677 | 1156 | 114.8 | 3.015 | 0.12 | 36.12 | 64 | 0.523 | 36.19 | 67 | 0 | 36.18 | 67 | 0 | 24.23 | 1.444 | 16 | 2.51 | 72 | 38.4 | 1.9894 | 0.379 | 24.37 | 1.464 | 15 | 2.52 | 72.1 | 38.6 | 1.9973 | 24.55 | 1.344 | 13 | 2.49 | 77.7 | 42.8 | 2.0652 | 0.15 | 7 | 2.34 | 0.029 | 0.383 | 0.087 | 6 | 2.3 | 0.061 | 0.231 | 6 | 3.19 | 0.029 | 43.25 | 0.311 | 6 | 25.4 | 109.8 | 41 | 69 | 0.039 | 43.52 | 0.331 | 6 | 22.9 | 122 | 45 | 71 | 0.024 | 25 | 24.5 | 20.6 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 10.8979 |  | 9.5328 | 20.4307 | 1.6258 | MINIMUM | 83.1783 | 6148.7396 |  | 840.5286 |  |  |  | 5.1137 | 5.4145 | 5.3175 | 1.9353 | 1.9353 | 1.8329 | 0.47049 | 0.39992 | 0.39992 | 0.42344 | 0.29856 | 0.31989 | 1.4267 | 0 | 0.049317 | 0.040142 | 0.049654 | 1.0995 | 0.49902 | 0.09423 | 4.1934 | 0.76855 | 5.3916 | 1.0818 | 0.50955 | 0.099158 | 3.7901 | 0.6619 | 7.2945 |  | MIN | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.03 | 18 | 10 | 1.4425 |  |  |  | MIN | 0.58 | 9.7 | 26.2268 | 15.2115 | 6.09 | 18 | 10 | 1.5212 |  |  |  | MIN | 0.53 | 10.7 | 25.2336 | 13.3738 | 6.15 | 19.9 | 10 | 1.3374 |  |  |  | 1.3374
AVERAGE | 6.43 | 20.6667 | 18.3333 | 13.65 | 112.8333 | 192.6667 | 19.1333 | 0.5025 | 0.06 | 6.02 | 10.6667 | 0.087167 | 6.0317 | 11.1667 |  | 6.03 | 11.1667 |  | 6.0575 | 0.361 | 4 | 0.6275 | 18 | 9.6 | 0.49736 | 0.063167 | 6.0925 | 0.366 | 3.75 | 0.63 | 18.025 | 9.65 | 0.49932 | 6.1375 | 0.336 | 3.25 | 0.6225 | 19.425 | 10.7 | 0.5163 | 0.025 | 1.1667 | 0.39 | 0.0145 | 0.063833 | 0.0145 | 1 | 0.38333 | 0.0305 | 0.0385 | 1 | 0.53167 | 0.0145 | 7.2083 | 0.051833 | 1 | 4.2333 | 18.3 | 20.5 | 34.5 | 0.0195 | 7.2533 | 0.055167 | 1 | 3.8167 | 20.3333 | 22.5 | 35.5 | 0.012 | 4.1667 | 4.0833 | 3.4333 |  |  | MAXIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 14.904 |  | 12.6475 | 27.5515 | 1.6258 | MAXIMUM | 89.3517 | 6886.5884 |  | 840.5286 |  |  |  | 6.9185 | 7.2193 | 7.09 | 1.9353 | 1.9353 | 2.0074 | 0.56459 | 0.47049 | 0.47049 | 0.51754 | 0.38387 | 0.44784 | 1.4267 | 3 | 0.050464 | 0.040142 | 0.050172 | 1.0995 | 0.49902 | 0.10208 | 4.213 | 0.77847 | 5.7088 | 1.1269 | 0.59447 | 0.11332 | 3.8148 | 0.67084 | 7.8667
MINIMUM | 6.38 | 18 | 17 | 13.2 | 93 | 186 | 18.8 | 0.446 | 0.054 | 5.98 | 10 | 0.071 | 6 | 10 |  | 6 | 11 |  | 6.03 | 0.325 | 3 | 0.55 | 17.5 | 9.5 | 0.49343 | 0.059 | 6.07 | 0.305 | 3 | 0.58 | 17.5 | 9.5 | 0.49343 | 6.13 | 0.298 | 3 | 0.53 | 19 | 10.7 | 0.5163 | 0.023 | 1 | 0.37 | 0.012 | 0.06 | 0.012 | 1 | 0.07 | 0.025 | 0.036 | 1 | 0.48 | 0.009 | 7.09 | 0.048 | 1 | 4.1 | 18 | 20 | 34 | 0.018 | 7.2 | 0.052 | 1 | 3.5 | 19.4 | 22 | 35 | 0.01 | 4.1 | 4 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 53630 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 1080 | 1165 | 2000 | 2000 | 2240 | 4480 | 3880 | 3880 | 4040 | 3360 | 3600 | 3750 | 0 | 4360 | 3500 | 4840 | 440 | 530 | 63 | 7680 | 1558 | 1760 | 246 | 320 | 37 | 3610 | 746 | 1335
MAXIMUM | 6.46 | 22 | 20 | 14.1 | 123 | 198 | 19.6 | 0.542 | 0.066 | 6.06 | 12 | 0.095 | 6.07 | 12 |  | 6.08 | 12 |  | 6.08 | 0.383 | 5 | 0.69 | 18.4 | 9.7 | 0.50129 | 0.068 | 6.13 | 0.405 | 5 | 0.7 | 18.5 | 9.7 | 0.50129 | 6.15 | 0.398 | 4 | 0.69 | 19.9 | 10.7 | 0.5163 | 0.026 | 2 | 0.41 | 0.017 | 0.069 | 0.017 | 1 | 0.5 | 0.036 | 0.043 | 1 | 0.61 | 0.02 | 7.34 | 0.057 | 1 | 4.4 | 18.6 | 21 | 35 | 0.021 | 7.34 | 0.06 | 1 | 4 | 21.2 | 23 | 36 | 0.014 | 4.3 | 4.2 | 4 | [17 empty] | AVERAGE | 10726 | [6 empty] | 206 | 216 | 233 | 400 | 400 | 448 | 896 | 776 | 776 | 808 | 672 | 720 | 750 |  | 872 | 700 | 968 | 88 | 106 | 12.6 | 1536 | 311.6 | 352 | 49.2 | 64 | 7.4 | 722 | 149.2 | 267
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0272 |  | TOTAL AVG COAG ALK: |  |  |  | 11 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.405 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.53 | [5 empty] | 6.0958 |  |  |  |  | 0.043 |  |  |  |  | 0.53 | [6 empty] | 0.043 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 10240 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 420 | 800 | 680 | 680 | 720 | 560 | 600 | 750 |  | 860 | 700 | 960 | 88 | 106 | 12 | 1520 | 310 | 340 | 48 | 60 | 7 | 720 | 148 | 255
[90 empty] | MAXIMUM | 11000 | [6 empty] | 230 | 240 | 260 | 400 | 400 | 460 | 960 | 800 | 800 | 880 | 720 | 840 | 750 |  | 880 | 700 | 970 | 88 | 106 | 13 | 1540 | 314 | 360 | 50 | 70 | 8 | 730 | 150 | 275
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.805 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23770188 |  | END: | 23770197 |  |  | Alum | 9334 | 9024 | 9024 | 8882 | 8882 | 47.5 | [44 empty] | 0.53 | 10.7 | 25.2336 | 13.3738 | 6.15 | 19.9 | 10 | 1.3374
[73 empty] | FINISHED 2 | 13.676 |  | TOTAL MGD: |  | 13.796 |  |  | FINISHED SOUTH 2 |  | START: | 43154533 |  | END: | 43168329 |  |  | Caustic | 7983 | 7012 | 7012
[73 empty] | TOTAL RAW | 30.054 |  | TOTAL MGD: |  | 4.592 |  |  | FINISHED CONWAY |  | START: | 9957975 |  | END: | 9962567 |  |  | Hypochlorite | 9 |  | 27
[76 empty] | TOTAL MGD: |  | 9.084 |  |  | FINISHED PERRY |  | START: | 33173162 |  | END: | 33182246 |  |  | Phosphate | 2816
[76 empty] | TOTAL MGD: |  | 9.611 |  |  | RAW PLANT 1 |  | START: | 30351164 |  | END: | 30360775 |  |  | Fluoride | 3650 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.655 |  |  | RAW PLANT 2 |  | START: | 30311640 |  | END: | 30321295 |  |  | Cal~Flo | 16 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.788 |  |  | RAW PLANT 3 |  | START: | 6810866 |  | END: | 6821654 |  |  | Zinc | 1480
[76 empty] | TOTAL MGD: |  | 1.574 |  |  | DECANT |  | START: | 1798808 |  | END: | 1800382 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.4551 |  |  | BLOW DOWN |  | START: | 9042.4142 |  | END: | 9043.8694 |  |  | NH3 | 7.39 |  | BI-SUL | 900
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 841
23770197
43168329
9962567
33182246
30360775
30321295
6821654
1800382
9043.8694
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.comBCOperator:
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 4
DATE: | 2018-11-04 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-04 | [23 empty] | DATE: | 2018-11-04
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-04 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43408.0076 | 1,2,5 | 54 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 14.904 | 1,3 | 12.6475 | 27.5515 | 1.6646 | 43408.0076 | 83.1783 | 6271.7144 | 0 | 840.5286 | 0 | 0 | 0 | 5.1137 | 5.4145 | 5.3175 | 1.9353 | 1.9353 | 1.8329 | 0.47049 | 0.39992 | 0.39992 | 0.42344 | 0.29856 | 0.31989 | 1.4267 | 3 | 0.049317 | 0.040142 | 0.049654 | 1.0995 | 0.49902 | 0.10208 | 4.1934 | 0.76855 | 5.7088 | 1.1269 | 0.50955 | 0.099158 | 3.8148 | 0.67084 | 7.8667 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.393 | 4 | 0.75 | 17.8 | 9.5 | 0.49343 |  | 6.08 | 0.269 | 4 | 0.89 | 17.9 | 9.5 | 0.49343 | 6.11 | 0.31 | 3 | 0.69 | 19.6 | 10.7 | 0.5163 | [13 empty] | 7.14 | 0.05 | 1 | 4 | 18.4 |  |  |  | 7.21 | 0.052 | 1 | 3.8 | 20.4 |  |  |  | 4.1 | 4 | 3.2 | [18 empty] | 10240 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 420 | 800 | 680 | 680 | 720 | 560 | 600 | 750 |  | 860 | 700 | 960 | 88 | 106 | 13 | 1520 | 310 | 360 | 50 | 60 | 7 | 730 | 150 | 275 |  | 1:00 | 0.75 | 9.5 | 26.7789 | 20.0842 | 6.06 | 17.8 | 10 | 2.0084 | 15 | 6.5 | 0.37343 | 1:00 | 0.89 | 9.5 | 26.7789 | 23.8333 | 6.08 | 17.9 | 10 | 2.3833 | 15 | 6.5 | 0.37343 | 1:00 | 0.69 | 10.7 | 25.2336 | 17.4112 | 6.11 | 19.6 | 10 | 1.7411 | 15 | 6.5 | 0.3963
2:00 | [72 empty] | 43408.3198 | 1,2,5 | 56 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 14.904 | 1,3 | 12.6475 | 27.5515 | 1.6646 | 43408.3198 | 83.3408 | 6148.7396 | 0 | 840.5286 | 0 | 0 | 0 | 5.1137 | 5.4145 | 5.3175 | 1.9353 | 1.9353 | 1.9201 | 0.47049 | 0.38227 | 0.38227 | 0.44108 | 0.29323 | 0.30923 | 1.4267 | 4 | 0.050464 | 0.040142 | 0.049654 | 1.0995 | 0.49902 | 0.09423 | 4.1984 | 0.76855 | 5.7088 | 1.1269 | 0.50955 | 0.11332 | 3.8142 | 0.68873 | 7.8667 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.47 | 19 | 19 | 13.8 | 121 | 193 | 18.5 | 0.507 |  | 6.1 | 10 | 0.095 | 6.05 | 11 |  | 6.04 | 11 | [8 empty] | 0.06 | [14 empty] | 0.024 | 1 | 0.45 |  | 0.06 | 0.015 | 1 | 0.41 |  | 0.038 | 1 | 0.46 | [38 empty] | 10260 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 440 | 800 | 650 | 650 | 750 | 550 | 580 | 750 |  | 880 | 700 | 960 | 88 | 106 | 12 | 1520 | 310 | 360 | 50 | 60 | 8 | 750 | 154 | 275 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43408.8288 | 1,2,5 | 56 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 12.227 | 1,3 | 10.5019 | 22.729 | 1.6646 | 43408.8288 | 85.2297 | 6149 | 0 | 840.5286 | 0 | 0 | 0 | 4.8158 | 5.0991 | 5.0352 | 1.8168 | 1.8168 | 1.8135 | 0.49847 | 0.43201 | 0.43201 | 0.47631 | 0.29786 | 0.3231 | 1.4267 | 0 | 0.049528 | 0.038761 | 0.049827 | 1.1025 | 0.49941 | 0.1032 | 4.2001 | 0.79132 | 5.3593 | 1.0643 | 0.48124 | 0.093649 | 3.8024 | 0.67581 | 7.4296 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.22 | 0.051 | 1 | 4.2 | 18.3 |  |  |  | 7.32 | 0.05 | 1 | 3.7 | 20.3 |  |  |  | 4.2 | 4.1 | 3.9 | [18 empty] | 11120 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 440 | 900 | 780 | 780 | 860 | 590 | 640 | 750 |  | 920 | 720 | 1020 | 94 | 113 | 14 | 1680 | 340 | 360 | 50 | 60 | 7 | 770 | 160 | 275 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43408.8962 | 1,2,5 | 56 | 11.4 | 11.4 | 12.4 | 35.2 | 10.9 | 10.9 | 11.9 | 33.7 | ,1,3 | 12.227 | 1,3 | 10.5019 | 22.729 | 1.6646 | 43408.8962 | 85.0189 | 6149 | 0 | 840.5286 | 0 | 0 | 0 | 4.3511 | 4.6071 | 4.5885 | 1.7968 | 1.7968 | 1.9451 | 0.44036 | 0.40033 | 0.38031 | 0.46038 | 0.31284 | 0.34964 | 1.4267 | 0 | 0.050338 | 0.039689 | 0.049654 | 1.0967 | 0.50066 | 0.099417 | 4.2031 | 0.79517 | 5.9561 | 1.0818 | 0.50955 | 0.097134 | 3.8467 | 0.67084 | 8.3366 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.43 | 17 | 18 | 13.6 | 84 | 190 | 18.3 | 0.42 |  | 6 | 9 | 0.07 | 5.99 | 9 |  | 5.96 | 9 | [8 empty] | 0.062 | [14 empty] | 0.023 | 1 | 0.35 |  | 0.062 | 0.013 | 1 | 0.47 |  | 0.037 | 1 | 0.66 | [38 empty] | 12240 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 520 | 880 | 800 | 760 | 920 | 680 | 760 | 750 |  | 1040 | 820 | 1120 | 104 | 126 | 15 | 1870 | 380 | 445 | 56 | 70 | 8 | 860 | 175 | 340 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.067 | [9 empty] | 6.03 | 0.388 | 4 | 0.65 | 16.8 | 9.7 | 0.50129 |  | 6.08 | 0.308 | 3 | 0.68 | 16.8 | 9.7 | 0.50129 | 6.14 | 0.317 | 3 | 0.65 | 18.4 | 10.7 | 0.5163 |  |  |  | 0.035 |  |  |  |  | 0.041 |  |  |  | 0.025 | 7.24 | 0.068 | 1 | 4.4 | 17.5 | 22 | 36 | 0.031 | 7.24 | 0.066 | 1 | 3.9 | 19.1 | 21 | 31 | 0.024 | 4 | 4 | 3.9 | [55 empty] | 9:00 | 0.65 | 9.7 | 26.2268 | 17.0474 | 6.03 | 16.8 | 10 | 1.7047 | 15 | 6.5 | 0.38129 | 9:00 | 0.68 | 9.7 | 26.2268 | 17.8342 | 6.08 | 16.8 | 10 | 1.7834 | 15 | 6.5 | 0.38129 | 9:00 | 0.65 | 10.7 | 25.2336 | 16.4019 | 6.14 | 18.4 | 10 | 1.6402 | 15 | 6.5 | 0.3963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.51 | 19 | 18 | 13.8 | 88 | 187 | 18.1 | 0.497 |  | 6.01 | 10 | 0.077 | 6.03 | 10 |  | 6.03 | 10 | [8 empty] | 0.062 | [14 empty] | 0.024 | 1 | 0.17 |  | 0.061 | 0.011 | 1 | 0.41 |  | 0.037 | 1 | 0.59 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.05 | 0.228 | 3 | 0.68 | 17.5 | 9.7 | 0.50129 |  | 6.08 | 0.215 | 3 | 0.65 | 17.8 | 9.7 | 0.50129 | 6.11 | 0.326 | 3 | 0.62 | 19 | 10.7 | 0.5163 | [13 empty] | 7.18 | 0.062 | 1 | 4.2 | 18 |  |  |  | 7.21 | 0.064 | 1 | 4 | 21 |  |  |  | 4.1 | 4 | 3 | [55 empty] | 13:00 | 0.68 | 9.7 | 26.2268 | 17.8342 | 6.05 | 17.5 | 10 | 1.7834 | 15 | 6.5 | 0.38129 | 13:00 | 0.65 | 9.7 | 26.2268 | 17.0474 | 6.08 | 17.8 | 10 | 1.7047 | 15 | 6.5 | 0.38129 | 13:00 | 0.62 | 10.7 | 25.2336 | 15.6449 | 6.11 | 19 | 10 | 1.5645 | 15 | 6.5 | 0.3963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.49 | 20 | 18 | 13 | 100 | 180 | 19 | 0.469 |  | 6.04 | 11 | 0.089 | 6.05 | 12 |  | 6.04 | 12 | [8 empty] | 0.063 | [14 empty] | 0.023 | 1 | 0.2 |  | 0.067 | 0.017 | 1 | 0.38 |  | 0.037 | 1 | 0.55 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.21 | 0.06 | 1 | 4.2 | 18 |  |  |  | 7.22 | 0.058 | 1 | 3.9 | 21 |  |  |  | 4.1 | 4.1 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.45 | 19 | 19 | 12.8 | 120 | 184 | 18.9 | 0.491 |  | 6 | 12 | 0.075 | 6.02 | 12 |  | 6.03 | 11 | [8 empty] | 0.052 | [14 empty] | 0.026 | 2 | 0.36 |  | 0.054 | 0.016 | 1 | 0.4 |  | 0.038 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.054 | [9 empty] | 6 | 0.31 | 3 | 0.63 | 17.5 | 11.3 | 0.47535 |  | 6.06 | 0.313 | 3 | 0.56 | 17.9 | 11.3 | 0.56418 | 6.14 | 0.303 | 3 | 0.53 | 19.1 | 12.7 | 0.59037 |  |  |  | 0.011 |  |  |  |  | 0.024 |  |  |  |  | 7.37 | 0.048 | 1 | 4.3 | 18.2 | 21 | 34 | 0.019 | 7.25 | 0.051 | 1 | 3.6 | 20.4 | 22 | 32 | 0.01 | 4.2 | 4 | 3.2 | [55 empty] | 21:00 | 0.63 | 11.3 | 22.5133 | 14.1834 | 6 | 17.5 | 8 | 1.7729 | 15 | 6 | 0.35535 | 21:00 | 0.56 | 11.3 | 22.5133 | 12.6074 | 6.06 | 17.9 | 10 | 1.2607 | 15 | 6.5 | 0.44418 | 21:00 | 0.53 | 12.7 | 21.2598 | 11.2677 | 6.14 | 19.1 | 10 | 1.1268 | 15 | 6.5 | 0.47037
22:00 | [72 empty] | DOSE |  | TOTAL | 41.1 | 41.1 | 45.1 | 127.3 | 39.1 | 39.1 | 43.1 | 121.3 | 0 | 54.2621 | 0 | 46.2989 | 100.561 | 6.6586 | TOTAL | 336.7677 | 24718.454 | 0 | 3362.1145 | 0 | 0 | 0 | 19.3944 | 20.5352 | 20.2587 | 7.4843 | 7.4843 | 7.5116 | 1.8798 | 1.6145 | 1.5945 | 1.8012 | 1.2025 | 1.3019 | 5.7067 | 7 | 0.19965 | 0.15873 | 0.19879 | 4.3981 | 1.9981 | 0.39894 | 16.7949 | 3.1236 | 22.7329 | 4.3999 | 2.0099 | 0.40326 | 15.2781 | 2.7062 | 31.4996 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.45 | 19.21 | 21 | 13.7 | 116 | 186 | 19 | 0.487 |  | 5.86 | 11 | 0.083 | 5.96 | 11 |  | 5.89 | 12 | [8 empty] | 0.057 | [14 empty] | 0.032 | 1 | 0.3 |  | 0.056 | 0.018 | 1 | 0.4 |  | 0.035 | 1 | 0.44 | [22 empty] | AVERAGE | 10.275 | 10.275 | 11.275 | 31.825 | 9.775 | 9.775 | 10.775 | 30.325 |  | 13.5655 |  | 11.5747 | 25.1402 | 1.6646 | AVERAGE | 84.1919 | 6179.6135 |  | 840.5286 | 0 | 0 | 0 | 4.8486 | 5.1338 | 5.0647 | 1.8711 | 1.8711 | 1.8779 | 0.46995 | 0.40363 | 0.39863 | 0.4503 | 0.30062 | 0.32546 | 1.4267 | 1.75 | 0.049912 | 0.039683 | 0.049697 | 1.0995 | 0.49953 | 0.099734 | 4.1987 | 0.7809 | 5.6832 | 1.1 | 0.50247 | 0.10082 | 3.8195 | 0.67656 | 7.8749 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.8 | 113.21 | 113 | 80.7 | 629 | 1120 | 111.8 | 2.871 | 0.121 | 36.01 | 63 | 0.489 | 36.1 | 65 | 0 | 35.99 | 65 | 0 | 24.14 | 1.319 | 14 | 2.71 | 69.6 | 40.2 | 1.9714 | 0.356 | 24.3 | 1.105 | 13 | 2.78 | 70.4 | 40.2 | 2.0602 | 24.5 | 1.256 | 12 | 2.49 | 76.1 | 44.8 | 2.1393 | 0.152 | 7 | 1.83 | 0.046 | 0.36 | 0.09 | 6 | 2.47 | 0.065 | 0.222 | 6 | 3.16 | 0.025 | 43.36 | 0.339 | 6 | 25.3 | 108.4 | 43 | 70 | 0.05 | 43.45 | 0.341 | 6 | 22.9 | 122.2 | 43 | 63 | 0.034 | 24.7 | 24.2 | 20.3 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 12.227 |  | 10.5019 | 22.729 | 1.6646 | MINIMUM | 83.1783 | 6148.7396 |  | 840.5286 |  |  |  | 4.3511 | 4.6071 | 4.5885 | 1.7968 | 1.7968 | 1.8135 | 0.44036 | 0.38227 | 0.38031 | 0.42344 | 0.29323 | 0.30923 | 1.4267 | 0 | 0.049317 | 0.038761 | 0.049654 | 1.0967 | 0.49902 | 0.09423 | 4.1934 | 0.76855 | 5.3593 | 1.0643 | 0.48124 | 0.093649 | 3.8024 | 0.67084 | 7.4296 |  | MIN | 0.65 | 9.7 | 26.2268 | 17.0474 | 6.03 | 16.8 | 10 | 1.7047 |  |  |  | MIN | 0.56 | 11.3 | 22.5133 | 12.6074 | 6.06 | 17.9 | 10 | 1.2607 |  |  |  | MIN | 0.53 | 12.7 | 21.2598 | 11.2677 | 6.14 | 19.1 | 10 | 1.1268 |  |  |  | 1.1268
AVERAGE | 6.4667 | 18.8683 | 18.8333 | 13.45 | 104.8333 | 186.6667 | 18.6333 | 0.4785 | 0.0605 | 6.0017 | 10.5 | 0.0815 | 6.0167 | 10.8333 |  | 5.9983 | 10.8333 |  | 6.035 | 0.32975 | 3.5 | 0.6775 | 17.4 | 10.05 | 0.49284 | 0.059333 | 6.075 | 0.27625 | 3.25 | 0.695 | 17.6 | 10.05 | 0.51505 | 6.125 | 0.314 | 3 | 0.6225 | 19.025 | 11.2 | 0.53481 | 0.025333 | 1.1667 | 0.305 | 0.023 | 0.06 | 0.015 | 1 | 0.41167 | 0.0325 | 0.037 | 1 | 0.52667 | 0.025 | 7.2267 | 0.0565 | 1 | 4.2167 | 18.0667 | 21.5 | 35 | 0.025 | 7.2417 | 0.056833 | 1 | 3.8167 | 20.3667 | 21.5 | 31.5 | 0.017 | 4.1167 | 4.0333 | 3.3833 |  |  | MAXIMUM | 11.4 | 11.4 | 12.4 | 35.2 | 10.9 | 10.9 | 11.9 | 33.7 |  | 14.904 |  | 12.6475 | 27.5515 | 1.6646 | MAXIMUM | 85.2297 | 6271.7144 |  | 840.5286 |  |  |  | 5.1137 | 5.4145 | 5.3175 | 1.9353 | 1.9353 | 1.9451 | 0.49847 | 0.43201 | 0.43201 | 0.47631 | 0.31284 | 0.34964 | 1.4267 | 4 | 0.050464 | 0.040142 | 0.049827 | 1.1025 | 0.50066 | 0.1032 | 4.2031 | 0.79517 | 5.9561 | 1.1269 | 0.50955 | 0.11332 | 3.8467 | 0.68873 | 8.3366
MINIMUM | 6.43 | 17 | 18 | 12.8 | 84 | 180 | 18.1 | 0.42 | 0.054 | 5.86 | 9 | 0.07 | 5.96 | 9 |  | 5.89 | 9 |  | 6 | 0.228 | 3 | 0.63 | 16.8 | 9.5 | 0.47535 | 0.052 | 6.06 | 0.215 | 3 | 0.56 | 16.8 | 9.5 | 0.49343 | 6.11 | 0.303 | 3 | 0.53 | 18.4 | 10.7 | 0.5163 | 0.023 | 1 | 0.17 | 0.011 | 0.054 | 0.011 | 1 | 0.38 | 0.024 | 0.035 | 1 | 0.44 | 0.025 | 7.14 | 0.048 | 1 | 4 | 17.5 | 21 | 34 | 0.019 | 7.21 | 0.05 | 1 | 3.6 | 19.1 | 21 | 31 | 0.01 | 4 | 4 | 3 | [15 empty] | MIL/MIN |  | TOTAL | 43860 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 720 | 780 | 1640 | 1640 | 1820 | 3380 | 2910 | 2870 | 3250 | 2380 | 2580 | 3000 | 0 | 3700 | 2940 | 4060 | 374 | 451 | 54 | 6590 | 1340 | 1525 | 206 | 250 | 30 | 3110 | 639 | 1165
MAXIMUM | 6.51 | 20 | 21 | 13.8 | 121 | 193 | 19 | 0.507 | 0.067 | 6.1 | 12 | 0.095 | 6.05 | 12 |  | 6.04 | 12 |  | 6.06 | 0.393 | 4 | 0.75 | 17.8 | 11.3 | 0.50129 | 0.063 | 6.08 | 0.313 | 4 | 0.89 | 17.9 | 11.3 | 0.56418 | 6.14 | 0.326 | 3 | 0.69 | 19.6 | 12.7 | 0.59037 | 0.032 | 2 | 0.45 | 0.035 | 0.067 | 0.018 | 1 | 0.47 | 0.041 | 0.038 | 1 | 0.66 | 0.025 | 7.37 | 0.068 | 1 | 4.4 | 18.4 | 22 | 36 | 0.031 | 7.32 | 0.066 | 1 | 4 | 21 | 22 | 32 | 0.024 | 4.2 | 4.1 | 3.9 | [17 empty] | AVERAGE | 10965 | [6 empty] | 170 | 180 | 195 | 410 | 410 | 455 | 845 | 727.5 | 717.5 | 812.5 | 595 | 645 | 750 |  | 925 | 735 | 1015 | 93.5 | 112.75 | 13.5 | 1647.5 | 335 | 381.25 | 51.5 | 62.5 | 7.5 | 777.5 | 159.75 | 291.25
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0056 |  | TOTAL AVG COAG ALK: |  |  |  | 10.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.393 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.53 | [5 empty] | 6.0783 |  |  |  |  | 0.038 |  |  |  |  | 0.53 | [6 empty] | 0.038 | [16 empty] | Pump Station MIN |  | 3 | [17 empty] | MINIMUM | 10240 | [6 empty] | 170 | 180 | 195 | 400 | 400 | 420 | 800 | 650 | 650 | 720 | 550 | 580 | 750 |  | 860 | 700 | 960 | 88 | 106 | 12 | 1520 | 310 | 360 | 50 | 60 | 7 | 730 | 150 | 275
[90 empty] | MAXIMUM | 12240 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 520 | 900 | 800 | 780 | 920 | 680 | 760 | 750 |  | 1040 | 820 | 1120 | 104 | 126 | 15 | 1870 | 380 | 445 | 56 | 70 | 8 | 860 | 175 | 340
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.083 |  | TOTAL MGD: |  | 0.015 |  |  | FINISHED SOUTH 1 |  | START: | 23770197 |  | END: | 23770212 |  |  | Alum | 9333 | 7929 | 7929 | 7960 | 7960 | 47.5 | [44 empty] | 0.53 | 12.7 | 21.2598 | 11.2677 | 6.14 | 19.1 | 10 | 1.1268
[73 empty] | FINISHED 2 | 14.519 |  | TOTAL MGD: |  | 14.068 |  |  | FINISHED SOUTH 2 |  | START: | 43168329 |  | END: | 43182397 |  |  | Caustic | 7696 | 6967 | 6967
[73 empty] | TOTAL RAW | 31.693 |  | TOTAL MGD: |  | 4.53 |  |  | FINISHED CONWAY |  | START: | 9962567 |  | END: | 9967097 |  |  | Hypochlorite | 8 |  | 27
[76 empty] | TOTAL MGD: |  | 9.989 |  |  | FINISHED PERRY |  | START: | 33182246 |  | END: | 33192235 |  |  | Phosphate | 2817
[76 empty] | TOTAL MGD: |  | 10.148 |  |  | RAW PLANT 1 |  | START: | 30360775 |  | END: | 30370923 |  |  | Fluoride | 3650 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.2 |  |  | RAW PLANT 2 |  | START: | 30321295 |  | END: | 30331495 |  |  | Cal~Flo | 13.41 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.345 |  |  | RAW PLANT 3 |  | START: | 6821654 |  | END: | 6832999 |  |  | Zinc | 1484
[76 empty] | TOTAL MGD: |  | 1.712 |  |  | DECANT |  | START: | 1800382 |  | END: | 1802094 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.6121 |  |  | BLOW DOWN |  | START: | 9043.8694 |  | END: | 9045.4815 |  |  | NH3 | 7.13 |  | BI-SUL | 850
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 841
23770212
43182397
9967097
33192235
30370923
30331495
6832999
1802094
9045.4815
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 5
DATE: | 2018-11-05 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-05 | [23 empty] | DATE: | 2018-11-05
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-05 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43409.0118 | 1,2,5 | 56 | 11.4 | 11.4 | 12.4 | 35.2 | 10.9 | 10.9 | 11.9 | 33.7 | ,1,3 | 12.227 | 1,3 | 10.5019 | 22.729 | 1.7597 | 43409.0118 | 85.0189 | 7378 | 0 | 840.5286 | 0 | 0 | 0 | 4.3511 | 4.6071 | 4.5885 | 1.7968 | 1.7968 | 1.9451 | 0.44036 | 0.40033 | 0.38031 | 0.46038 | 0.31284 | 0.34964 | 1.4267 | 0 | 0.050338 | 0.039689 | 0.049654 | 1.0967 | 0.50066 | 0.099417 | 4.2031 | 0.79517 | 5.9561 | 1.0818 | 0.50955 | 0.097134 | 3.8467 | 0.67084 | 8.3366 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6 | 0.327 | 4 | 0.67 | 17.8 | 11.4 | 0.47849 |  | 6.03 | 0.347 | 4 | 0.7 | 17.9 | 11.2 | 0.56025 | 6.05 | 0.373 | 4 | 0.67 | 19.3 | 12.6 | 0.58667 | [13 empty] | 7.08 | 0.047 | 1 | 4.5 | 18.3 |  |  |  | 7.33 | 0.049 | 1 | 3.7 | 20.6 |  |  |  | 4.1 | 4.1 | 3.3 | [18 empty] | 12240 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 520 | 880 | 800 | 760 | 920 | 680 | 760 | 750 |  | 1040 | 820 | 1120 | 104 | 126 | 15 | 1870 | 380 | 445 | 56 | 70 | 8 | 860 | 175 | 340 |  | 1:00 | 0.67 | 11.4 | 22.3158 | 14.9516 | 6 | 17.8 | 8 | 1.8689 | 15 | 6 | 0.35849 | 1:00 | 0.7 | 11.2 | 22.7143 | 15.9 | 6.03 | 17.9 | 10 | 1.59 | 15 | 6.5 | 0.44025 | 1:00 | 0.67 | 12.6 | 21.4286 | 14.3571 | 6.05 | 19.3 | 10 | 1.4357 | 15 | 6.5 | 0.46667
2:00 | [72 empty] | 43409.0696 | 1,2,3,5 | 52 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | ,1,3 | 15.5563 | 1,3 | 18.2592 | 33.8155 | 1.7597 | 43409.0696 | 85.3763 | 7378.4876 | 0 | 840.5286 | 0 | 0 | 0 | 4.1336 | 4.3767 | 4.3767 | 1.7805 | 1.7805 | 1.7805 | 0.43736 | 0.39457 | 0.38507 | 0.46588 | 0.31595 | 0.35106 | 1.4267 | 0 | 0.053217 | 0.040371 | 0.048959 | 1.0995 | 0.50091 | 0.10051 | 4.1977 | 0.79335 | 5.8991 | 1.1034 | 0.48509 | 0.10403 | 3.7974 | 0.67514 | 8.4033 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.35 | 18 | 16 | 13.7 | 119 | 197 | 18.5 | 0.498 |  | 5.93 | 9 | 0.087 | 5.95 | 9 |  | 5.94 | 9 | [8 empty] | 0.061 | [14 empty] | 0.04 | 2 | 0.43 |  | 0.062 | 0.012 | 1 | 0.32 |  | 0.035 | 1 | 0.42 | [38 empty] | 12920 | [6 empty] | 170 | 180 | 195 | 460 | 460 | 500 | 920 | 830 | 810 | 980 | 720 | 800 | 750 |  | 1160 | 880 | 1160 | 110 | 133 | 16 | 1940 | 400 | 465 | 60 | 70 | 9 | 920 | 185 | 360 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43409.3226 | 1,2,3,5 | 52 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | ,1,3 | 15.5563 | 1,3 | 18.2592 | 33.8155 | 1.7597 | 43409.3226 | 85.112 | 7379 | 0 | 840.5286 | 0 | 0 | 0 | 4.1336 | 4.3767 | 4.3767 | 1.7418 | 1.7418 | 1.7805 | 0.42785 | 0.38031 | 0.38031 | 0.45162 | 0.30718 | 0.32912 | 1.4267 | 3 | 0.050464 | 0.040371 | 0.049803 | 1.0995 | 0.51597 | 0.10051 | 4.2176 | 0.77351 | 5.8991 | 1.1034 | 0.49895 | 0.092471 | 3.7974 | 0.68609 | 8.4033 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.1 | 0.046 | 1 | 4.1 | 18.2 |  |  |  | 7.18 | 0.048 | 1 | 3.6 | 20.5 |  |  |  | 4.2 | 4.1 | 4.1 | [18 empty] | 12880 | [6 empty] | 170 | 180 | 195 | 450 | 450 | 500 | 900 | 800 | 800 | 950 | 700 | 750 | 750 |  | 1100 | 880 | 1180 | 110 | 137 | 16 | 1950 | 390 | 465 | 60 | 72 | 8 | 920 | 188 | 360 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43409.5636 | 1,2,3,5 | 52 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | ,1,3 | 15.5563 | 1,3 | 18.2592 | 33.8155 | 1.7597 | 43409.5636 | 84.9993 | 7379 | 0 | 840.5286 | 0 | 0 | 0 | 4.5094 | 4.7746 | 4.7415 | 1.9077 | 1.9077 | 1.9353 | 0.46675 | 0.41489 | 0.41489 | 0.43563 | 0.309 | 0.32089 | 1.4267 | 0 | 0.050246 | 0.040196 | 0.050464 | 1.0947 | 0.49911 | 0.082564 | 4.1113 | 0.76029 | 6.4609 | 1.0995 | 0.48961 | 0.12564 | 3.8021 | 0.67434 | 9.134 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.43 | 20 | 17 | 13.1 | 112 | 185 | 18.5 | 0.494 |  | 5.98 | 12 | 0.096 | 5.96 | 12 |  | 5.95 | 12 | [8 empty] | 0.062 | [14 empty] | 0.043 | 1 | 0.35 |  | 0.06 | 0.012 | 1 | 0.47 |  | 0.034 | 1 | 0.5 | [38 empty] | 11820 | [6 empty] | 170 | 180 | 195 | 450 | 450 | 500 | 900 | 800 | 800 | 840 | 650 | 675 | 750 |  | 1000 | 800 | 1100 | 100 | 121 | 12 | 1720 | 350 | 465 | 55 | 65 | 10 | 840 | 170 | 360 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43409.8552 | 1,2,3,5 | 44 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 14.4 | 1,3 | 13.7246 | 28.1246 | 1.7597 | 43409.8552 | 84.6165 | 7378.4876 | 0 | 840.5286 | 0 | 0 | 0 | 4.8158 | 5.0991 | 5.0352 | 1.9985 | 1.9985 | 1.9783 | 0.48739 | 0.44308 | 0.44308 | 0.50954 | 0.3231 | 0.38368 | 1.4267 | 2 | 0.050604 | 0.040914 | 0.04885 | 1.126 | 0.49941 | 0.1032 | 4.107 | 0.76805 | 6.9224 | 1.1069 | 0.48124 | 0.093649 | 3.7991 | 0.67581 | 9.7261 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.094 | [9 empty] | 5.98 | 0.317 | 4 | 0.47 | 17.6 | 12 | 0.49736 |  | 6 | 0.349 | 4 | 0.49 | 17.6 | 12 | 0.49736 | 6.06 | 0.287 | 4 | 0.71 | 19.3 | 13 | 0.60148 |  |  |  | 0.044 |  |  |  |  | 0.034 |  |  |  | 0.04 | 7.23 | 0.055 | 2 | 4.8 | 18 | 26 | 50 | 0.063 | 7.91 | 0.067 | 2 | 4.8 | 19.6 | 29 | 44 | 0.039 | 4.3 | 4.1 | 3 | [18 empty] | 11040 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 480 | 880 | 800 | 800 | 920 | 640 | 760 | 750 |  | 940 | 760 | 1000 | 96 | 113 | 14 | 1640 | 330 | 465 | 52 | 60 | 7 | 800 | 160 | 360 |  | 9:00 | 0.47 | 12 | 21.2 | 9.964 | 5.98 | 17.6 | 8 | 1.2455 | 15 | 6 | 0.37736 | 9:00 | 0.49 | 12 | 21.2 | 10.388 | 6 | 17.6 | 8 | 1.2985 | 15 | 6 | 0.37736 | 9:00 | 0.71 | 13 | 20.7692 | 14.7462 | 6.06 | 19.3 | 10 | 1.4746 | 15 | 6.5 | 0.48148
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.46 | 20 | 18 | 11.3 | 116 | 172 | 18.6 | 0.509 |  | 5.96 | 10 | 0.084 | 5.97 | 10 |  | 5.94 | 10 | [8 empty] | 0.066 | [14 empty] | 0.06 | 1 | 0.3 |  | 0.066 | 0.011 | 1 | 0.29 |  | 0.061 | 1 | 0.46 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.327 | 4 | 0.49 | 18.5 | 11 | 0.46591 |  | 6.02 | 0.309 | 4 | 0.48 | 18.5 | 11 | 0.55239 | 6.04 | 0.33 | 4 | 0.62 | 20 | 12 | 0.43111 | [13 empty] | 7.06 | 0.058 | 2 | 4.2 | 18 |  |  |  | 7.16 | 0.064 | 2 | 4 | 20.5 |  |  |  | 4.3 | 4.1 | 2.9 | [55 empty] | 13:00 | 0.49 | 11 | 23.1273 | 11.3324 | 6 | 18.5 | 8 | 1.4165 | 15 | 6 | 0.34591 | 13:00 | 0.48 | 11 | 23.1273 | 11.1011 | 6.02 | 18.5 | 10 | 1.1101 | 15 | 6.5 | 0.43239 | 13:00 | 0.62 | 12 | 22.5 | 13.95 | 6.04 | 20 | 7 | 1.9929 | 20 | 6.5 | 0.31111
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.49 | 22 | 18 | 12 | 110 | 179 | 19.8 | 0.475 |  | 6.06 | 12 | 0.092 | 6.09 | 12 |  | 6 | 12 | [8 empty] | 0.061 | [14 empty] | 0.056 | 1 | 0.28 |  | 0.062 | 0.01 | 1 | 0.3 |  | 0.054 | 1 | 0.42 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.07 | 0.055 | 2 | 4.3 | 18.2 |  |  |  | 7.39 | 0.06 | 2 | 4.1 | 20.5 |  |  |  | 4.3 | 4.3 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.45 | 20 | 20 | 11.7 | 109 | 177 | 19.1 | 0.49 |  | 5.95 | 11 | 0.088 | 6.02 | 11 |  | 5.99 | 11 | [8 empty] | 0.066 | [14 empty] | 0.049 | 2 | 0.54 |  | 0.066 | 0.013 | 2 | 0.49 |  | 0.054 | 2 | 0.66 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.047 | [9 empty] | 6.04 | 0.354 | 5 | 0.76 | 18.4 | 9.8 | 0.50522 |  | 6.07 | 0.322 | 5 | 0.72 | 18.4 | 9.8 | 0.50522 | 6.12 | 0.293 | 3 | 0.6 | 19.9 | 11.1 | 0.53111 |  |  |  | 0.012 |  |  |  |  | 0.025 |  |  |  | 0.008 | 7.23 | 0.05 | 2 | 4.9 | 18.6 | 20 | 37 | 0.021 | 7.53 | 0.056 | 2 | 4.1 | 20.7 | 26 | 35 | 0.012 | 4.3 | 4.4 | 3.5 | [55 empty] | 21:00 | 0.76 | 9.8 | 25.9592 | 19.729 | 6.04 | 18.4 | 10 | 1.9729 | 15 | 6.5 | 0.38522 | 21:00 | 0.72 | 9.8 | 25.9592 | 18.6906 | 6.07 | 18.4 | 10 | 1.8691 | 15 | 6.5 | 0.38522 | 21:00 | 0.6 | 11.1 | 24.3243 | 14.5946 | 6.12 | 19.9 | 10 | 1.4595 | 15 | 6.5 | 0.41111
22:00 | [72 empty] | DOSE |  | TOTAL | 56.7 | 56.7 | 61.7 | 175.1 | 54.2 | 54.2 | 59.2 | 167.6 | 0 | 73.296 | 0 | 79.0042 | 152.3002 | 8.7984 | TOTAL | 425.123 | 36892.9752 | 0 | 4202.6432 | 0 | 0 | 0 | 21.9435 | 23.2342 | 23.1186 | 9.2253 | 9.2253 | 9.4198 | 2.2597 | 2.0332 | 2.0037 | 2.3231 | 1.5681 | 1.7344 | 7.1334 | 5 | 0.25487 | 0.20154 | 0.24773 | 5.5163 | 2.5161 | 0.48621 | 20.8366 | 3.8904 | 31.1375 | 5.495 | 2.4644 | 0.51293 | 19.0427 | 3.3822 | 44.0034 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.43 | 21 | 19 | 11.5 | 117 | 176 | 19.1 | 0.482 |  | 5.9 | 11 | 0.081 | 5.93 | 10 |  | 5.95 | 11 | [8 empty] | 0.06 | [14 empty] | 0.033 | 2 | 0.45 |  | 0.06 | 0.014 | 1 | 0.46 |  | 0.048 | 1 | 0.55 | [22 empty] | AVERAGE | 11.34 | 11.34 | 12.34 | 35.02 | 10.84 | 10.84 | 11.84 | 33.52 |  | 14.6592 |  | 15.8008 | 30.46 | 1.7597 | AVERAGE | 85.0246 | 7378.595 |  | 840.5286 | 0 | 0 | 0 | 4.3887 | 4.6468 | 4.6237 | 1.8451 | 1.8451 | 1.884 | 0.45194 | 0.40664 | 0.40073 | 0.46461 | 0.31361 | 0.34688 | 1.4267 | 1 | 0.050974 | 0.040308 | 0.049546 | 1.1033 | 0.50321 | 0.097242 | 4.1673 | 0.77807 | 6.2275 | 1.099 | 0.49288 | 0.10259 | 3.8085 | 0.67645 | 8.8007 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.61 | 121 | 108 | 73.3 | 683 | 1086 | 113.6 | 2.948 | 0.141 | 35.78 | 65 | 0.528 | 35.92 | 64 | 0 | 35.77 | 65 | 0 | 24.02 | 1.325 | 17 | 2.39 | 72.3 | 44.2 | 1.947 | 0.376 | 24.12 | 1.327 | 17 | 2.39 | 72.4 | 44 | 2.1152 | 24.27 | 1.283 | 15 | 2.6 | 78.5 | 48.7 | 2.1504 | 0.281 | 9 | 2.35 | 0.056 | 0.376 | 0.072 | 7 | 2.33 | 0.059 | 0.286 | 7 | 3.01 | 0.048 | 42.77 | 0.311 | 10 | 26.8 | 109.3 | 46 | 87 | 0.084 | 44.5 | 0.344 | 10 | 24.3 | 122.4 | 55 | 79 | 0.051 | 25.5 | 25.1 | 19.9 |  |  | MINIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 12.227 |  | 10.5019 | 22.729 | 1.7597 | MINIMUM | 84.6165 | 7378 |  | 840.5286 |  |  |  | 4.1336 | 4.3767 | 4.3767 | 1.7418 | 1.7418 | 1.7805 | 0.42785 | 0.38031 | 0.38031 | 0.43563 | 0.30718 | 0.32089 | 1.4267 | 0 | 0.050246 | 0.039689 | 0.04885 | 1.0947 | 0.49911 | 0.082564 | 4.107 | 0.76029 | 5.8991 | 1.0818 | 0.48124 | 0.092471 | 3.7974 | 0.67084 | 8.3366 |  | MIN | 0.47 | 12 | 21.2 | 9.964 | 5.98 | 17.6 | 8 | 1.2455 |  |  |  | MIN | 0.48 | 11 | 23.1273 | 11.1011 | 6.02 | 18.5 | 10 | 1.1101 |  |  |  | MIN | 0.67 | 12.6 | 21.4286 | 14.3571 | 6.05 | 19.3 | 10 | 1.4357 |  |  |  | 1.1101
AVERAGE | 6.435 | 20.1667 | 18 | 12.2167 | 113.8333 | 181 | 18.9333 | 0.49133 | 0.0705 | 5.9633 | 10.8333 | 0.088 | 5.9867 | 10.6667 |  | 5.9617 | 10.8333 |  | 6.005 | 0.33125 | 4.25 | 0.5975 | 18.075 | 11.05 | 0.48675 | 0.062667 | 6.03 | 0.33175 | 4.25 | 0.5975 | 18.1 | 11 | 0.52881 | 6.0675 | 0.32075 | 3.75 | 0.65 | 19.625 | 12.175 | 0.53759 | 0.046833 | 1.5 | 0.39167 | 0.028 | 0.062667 | 0.012 | 1.1667 | 0.38833 | 0.0295 | 0.047667 | 1.1667 | 0.50167 | 0.024 | 7.1283 | 0.051833 | 1.6667 | 4.4667 | 18.2167 | 23 | 43.5 | 0.042 | 7.4167 | 0.057333 | 1.6667 | 4.05 | 20.4 | 27.5 | 39.5 | 0.0255 | 4.25 | 4.1833 | 3.3167 |  |  | MAXIMUM | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 |  | 15.5563 |  | 18.2592 | 33.8155 | 1.7597 | MAXIMUM | 85.3763 | 7379 |  | 840.5286 |  |  |  | 4.8158 | 5.0991 | 5.0352 | 1.9985 | 1.9985 | 1.9783 | 0.48739 | 0.44308 | 0.44308 | 0.50954 | 0.3231 | 0.38368 | 1.4267 | 3 | 0.053217 | 0.040914 | 0.050464 | 1.126 | 0.51597 | 0.1032 | 4.2176 | 0.79517 | 6.9224 | 1.1069 | 0.50955 | 0.12564 | 3.8467 | 0.68609 | 9.7261
MINIMUM | 6.35 | 18 | 16 | 11.3 | 109 | 172 | 18.5 | 0.475 | 0.047 | 5.9 | 9 | 0.081 | 5.93 | 9 |  | 5.94 | 9 |  | 5.98 | 0.317 | 4 | 0.47 | 17.6 | 9.8 | 0.46591 | 0.06 | 6 | 0.309 | 4 | 0.48 | 17.6 | 9.8 | 0.49736 | 6.04 | 0.287 | 3 | 0.6 | 19.3 | 11.1 | 0.43111 | 0.033 | 1 | 0.28 | 0.012 | 0.06 | 0.01 | 1 | 0.29 | 0.025 | 0.034 | 1 | 0.42 | 0.008 | 7.06 | 0.046 | 1 | 4.1 | 18 | 20 | 37 | 0.021 | 7.16 | 0.048 | 1 | 3.6 | 19.6 | 26 | 35 | 0.012 | 4.1 | 4.1 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 60900 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 900 | 975 | 2240 | 2240 | 2500 | 4480 | 4030 | 3970 | 4610 | 3390 | 3745 | 3750 | 0 | 5240 | 4140 | 5560 | 520 | 630 | 73 | 9120 | 1850 | 2305 | 283 | 337 | 42 | 4340 | 878 | 1780
MAXIMUM | 6.49 | 22 | 20 | 13.7 | 119 | 197 | 19.8 | 0.509 | 0.094 | 6.06 | 12 | 0.096 | 6.09 | 12 |  | 6 | 12 |  | 6.04 | 0.354 | 5 | 0.76 | 18.5 | 12 | 0.50522 | 0.066 | 6.07 | 0.349 | 5 | 0.72 | 18.5 | 12 | 0.56025 | 6.12 | 0.373 | 4 | 0.71 | 20 | 13 | 0.60148 | 0.06 | 2 | 0.54 | 0.044 | 0.066 | 0.014 | 2 | 0.49 | 0.034 | 0.061 | 2 | 0.66 | 0.04 | 7.23 | 0.058 | 2 | 4.9 | 18.6 | 26 | 50 | 0.063 | 7.91 | 0.067 | 2 | 4.8 | 20.7 | 29 | 44 | 0.039 | 4.3 | 4.4 | 4.1 | [17 empty] | AVERAGE | 12180 | [6 empty] | 170 | 180 | 195 | 448 | 448 | 500 | 896 | 806 | 794 | 922 | 678 | 749 | 750 |  | 1048 | 828 | 1112 | 104 | 126 | 14.6 | 1824 | 370 | 461 | 56.6 | 67.4 | 8.4 | 868 | 175.6 | 356
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9706 |  | TOTAL AVG COAG ALK: |  |  |  | 10.7778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.373 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.0342 |  |  |  |  | 0.061 |  |  |  |  | 0.47 | [6 empty] | 0.061 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 11040 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 480 | 880 | 800 | 760 | 840 | 640 | 675 | 750 |  | 940 | 760 | 1000 | 96 | 113 | 12 | 1640 | 330 | 445 | 52 | 60 | 7 | 800 | 160 | 340
[90 empty] | MAXIMUM | 12920 | [6 empty] | 170 | 180 | 195 | 460 | 460 | 520 | 920 | 830 | 810 | 980 | 720 | 800 | 750 |  | 1160 | 880 | 1180 | 110 | 137 | 16 | 1950 | 400 | 465 | 60 | 72 | 10 | 920 | 188 | 360
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.727 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23770212 |  | END: | 23770212 |  |  | Alum | 9328 | 8932 | 8932 | 9159 | 9159 | 47.5 | [44 empty] | 0.48 | 11 | 23.1273 | 11.1011 | 6.02 | 18.5 | 10 | 1.1101
[73 empty] | FINISHED 2 | 15.766 |  | TOTAL MGD: |  | 14.727 |  |  | FINISHED SOUTH 2 |  | START: | 43182397 |  | END: | 43197124 |  |  | Caustic | 7381 | 6859 | 6859
[73 empty] | TOTAL RAW | 34.632 |  | TOTAL MGD: |  | 4.843 |  |  | FINISHED CONWAY |  | START: | 9967097 |  | END: | 9971940 |  |  | Hypochlorite | 11 |  | 27
[76 empty] | TOTAL MGD: |  | 10.923 |  |  | FINISHED PERRY |  | START: | 33192235 |  | END: | 33203158 |  |  | Phosphate | 2725
[76 empty] | TOTAL MGD: |  | 11.115 |  |  | RAW PLANT 1 |  | START: | 30370923 |  | END: | 30382038 |  |  | Fluoride | 3250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.198 |  |  | RAW PLANT 2 |  | START: | 30331495 |  | END: | 30342693 |  |  | Cal~Flo | 17 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.319 |  |  | RAW PLANT 3 |  | START: | 6832999 |  | END: | 6845318 |  |  | Zinc | 1470
[76 empty] | TOTAL MGD: |  | 1.63 |  |  | DECANT |  | START: | 1802094 |  | END: | 1803724 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.3607 |  |  | BLOW DOWN |  | START: | 9045.4815 |  | END: | 9046.8421 |  |  | NH3 | 6.89 |  | BI-SUL | 850
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 841
23770212
43197124
9971940
33203158
30382038
30342693
6845318
1803724
9046.8421
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 6
DATE: | 2018-11-06 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-06 | [23 empty] | DATE: | 2018-11-06
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-06 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43410.0129 | 1,2,3,5 | 44 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | 1,3 | 14.4 | 1,3 | 13.7246 | 28.1246 | 0.0013968 | 43410.0129 | 84.6165 | 7378.4876 | 0 | 840.5286 | 0 | 0 | 0 | 4.8158 | 5.0991 | 5.0352 | 1.9985 | 1.9985 | 1.9783 | 0.44308 | 0.39877 | 0.37662 | 0.44308 | 0.28271 | 0.3029 | 1.4267 | 2 | 0.050604 | 0.040914 | 0.04885 | 1.126 | 0.49941 | 0.1032 | 4.107 | 0.76805 | 6.9224 | 1.1069 | 0.48124 | 0.093649 | 3.7991 | 0.67581 | 9.7261 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.385 | 4 | 0.61 | 18 | 10.3 | 0.4439 |  | 6.02 | 0.385 | 5 | 0.64 | 18 | 10.3 | 0.52487 | 6.08 | 0.287 | 0.273 | 0.59 | 19.7 | 11.3 | 0.53852 | [13 empty] | 7.13 | 0.053 | 1 | 3.9 | 18.4 |  |  |  | 7.22 | 0.058 | 1 | 3.7 | 19.9 |  |  |  | 4.2 | 4.5 | 3.7 | [18 empty] | 11040 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 480 | 800 | 720 | 680 | 800 | 560 | 600 | 750 |  | 940 | 760 | 1000 | 96 | 113 | 14 | 1640 | 330 | 465 | 52 | 60 | 7 | 800 | 160 | 360 |  | 1:00 | 0.61 | 10.3 | 24.699 | 15.0664 | 5.96 | 18 | 8 | 1.8833 | 15 | 6 | 0.3239 | 1:00 | 0.64 | 10.3 | 24.699 | 15.8074 | 6.02 | 18 | 10 | 1.5807 | 15 | 6.5 | 0.40487 | 1:00 | 0.59 | 11.3 | 23.8938 | 14.0973 | 6.08 | 19.7 | 10 | 1.4097 | 15 | 6.5 | 0.41852
2:00 | [72 empty] | 5:51 | 1,2,3,5 | 44 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | 1,3 | 14.4 | 1,3 | 13.8 | 28.2 |  | 5:51 | 85 | 7378 | 0 | 841 | 0 | 0 | 0 | 4.2 | 4.5 | 4.5 | 2 | 2 | 2.1 | 0.43 | 0.39 | 0.39 | 0.41 | 0.27 | 0.28 | 1.43 |  | 0.05 | 0.04 | 0.05 | 1.12 | 0.5 | 0.1 | 4.11 | 0.77 | 6.92 | 1.11 | 0.5 | 0.09 | 3.7 | 0.67 | 9.73 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.4 | 18 | 17 | 12.8 | 118 | 177 | 19.3 | 0.491 |  | 5.99 | 10 | 0.087 | 5.94 | 10 |  | 5.97 | 10 | [8 empty] | 0.06 | [14 empty] | 0.029 | 1 | 0.43 |  | 0.06 | 0.013 | 2 | 0.042 |  | 0.045 | 1 | 0.6 | [38 empty] | 11150 | [6 empty] | 150 | 160 | 175 | 440 | 440 | 500 | 780 | 700 | 700 | 750 | 550 | 580 | 750 |  | 920 | 750 | 1020 | 94 | 114 | 14 | 1620 | 330 | 465 | 52 | 62 | 7 | 760 | 156 | 360 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43410.8138 | 1,2,3 | 75 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | 2,3 | 16.0186 | 1,3 | 10.165 | 26.1835 | 0.0013968 | 43410.8138 | 85.2297 | 7870.3868 | 0 | 840.5286 | 0 | 0 | 0 | 4.2492 | 4.5325 | 4.5187 | 1.6352 | 1.726 | 1.8135 | 0.44308 | 0.39877 | 0.37662 | 0.44308 | 0.26252 | 0.3029 | 1.4267 | 4 | 0.050604 | 0.040914 | 0.05 | 1.126 | 0.49941 | 0.1032 | 4.0987 | 0.77969 | 6.9224 | 1.1069 | 0.48124 | 0.093649 | 3.7546 | 0.67581 | 9.7261 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.08 | 0.048 | 1 | 4.4 | 18.6 |  |  |  | 7.19 | 0.051 | 1 | 4.3 | 20.6 |  |  |  | 4.2 | 4.5 | 4.3 | [18 empty] | 11120 | [6 empty] | 150 | 160 | 175 | 360 | 380 | 440 | 800 | 720 | 680 | 800 | 520 | 600 | 750 |  | 940 | 760 | 1000 | 96 | 113 | 14 | 1630 | 335 | 465 | 52 | 60 | 7 | 780 | 160 | 360 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.46 | 20 | 17 | 11.5 | 117 | 176 | 19 | 0.513 |  | 6.01 | 13 | 0.102 | 6.01 | 13 |  | 5.98 | 12 | [8 empty] | 0.068 | [14 empty] | 0.028 | 1 | 0.39 |  | 0.067 | 0.01 | 1 | 0.38 |  | 0.044 | 1 | 0.72 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.074 | [9 empty] | 5.95 | 0.313 | 4 | 0.66 | 18.4 | 10.3 | 0.4439 |  | 5.99 | 0.371 | 4 | 0.57 | 18.5 | 10.3 | 0.4439 | 6.05 | 0.255 | 4 | 0.7 | 19.9 | 11.3 | 0.53852 |  |  |  | 0.017 |  |  |  |  | 0.036 |  |  |  | 0.021 | 7.42 | 0.055 | 2 | 4.5 | 18.6 | 27 | 47 | 0.03 | 7.48 | 0.06 | 2 | 4.2 | 21 | 29 | 52 | 0.024 | 4.2 | 4.2 | 3.4 | [55 empty] | 9:00 | 0.66 | 10.3 | 24.699 | 16.3014 | 5.95 | 18.4 | 8 | 2.0377 | 15 | 6 | 0.3239 | 9:00 | 0.57 | 10.3 | 24.699 | 14.0784 | 5.99 | 18.5 | 8 | 1.7598 | 15 | 6 | 0.3239 | 9:00 | 0.7 | 11.3 | 23.8938 | 16.7257 | 6.05 | 19.9 | 10 | 1.6726 | 15 | 6.5 | 0.41852
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.4 | 19 | 16 | 11.7 | 115 | 158 | 19.2 | 0.506 |  | 5.92 | 11 | 0.096 | 5.92 | 13 |  | 5.9 | 11 | [8 empty] | 0.074 | [14 empty] | 0.026 | 1 | 0.29 |  | 0.076 | 0.014 | 1 | 0.34 |  | 0.04 | 1 | 0.52 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.01 | 0.327 | 4 | 0.64 | 19 | 10 | 0.51308 |  | 6 | 0.349 | 4 | 0.55 | 19 | 10 | 0.43447 | 6.01 | 0.322 | 4 | 0.65 | 20.2 | 11.2 | 0.41037 | [13 empty] | 7.42 | 0.052 | 1 | 4.2 | 19 |  |  |  | 7.52 | 0.055 | 1 | 4.2 | 21.5 |  |  |  | 4.2 | 4.2 | 3.4 | [55 empty] | 13:00 | 0.64 | 10 | 25.44 | 16.2816 | 6.01 | 19 | 10 | 1.6282 | 15 | 6.5 | 0.39308 | 13:00 | 0.55 | 10 | 25.44 | 13.992 | 6 | 19 | 8 | 1.749 | 15 | 6 | 0.31447 | 13:00 | 0.65 | 11.2 | 24.1071 | 15.6696 | 6.01 | 20.2 | 7 | 2.2385 | 20 | 6.5 | 0.29037
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.43 | 21 | 18 | 10.6 | 115 | 171 | 19.8 | 0.467 |  | 5.99 | 12 | 0.089 | 6.05 | 12 |  | 6.06 | 12 | [8 empty] | 0.061 | [14 empty] | 0.028 | 1 | 0.32 |  | 0.062 | 0.012 | 1 | 0.32 |  | 0.044 | 1 | 0.48 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.4 | 0.05 | 1 | 4.2 | 19 |  |  |  | 7.45 | 0.055 | 1 | 4.2 | 21.5 |  |  |  | 4.3 | 4.1 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.46 | 20 | 16 | 9.96 | 117 | 170 | 20.3 | 0.504 |  | 5.98 | 11 | 0.092 | 5.97 | 10 |  | 5.94 | 11 | [8 empty] | 0.063 | [14 empty] | 0.027 | 1 | 0.25 |  | 0.065 | 0.012 | 1 | 0.36 |  | 0.045 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.042 | [9 empty] | 5.97 | 0.349 | 4 | 0.46 | 19.1 | 10 | 0.43447 |  | 5.96 | 0.347 | 4 | 0.57 | 19.2 | 10 | 0.43447 | 6.04 | 0.292 | 3 | 0.49 | 20.7 | 11.2 | 0.41037 |  |  |  | 0.008 |  |  |  |  | 0.021 |  |  |  | 0.006 | 7.32 | 0.046 | 1 | 4.4 | 19.2 | 23 | 35 | 0.022 | 7.35 | 0.056 | 1 | 3.4 | 21.3 | 22 | 43 | 0.008 | 4.2 | 4.2 | 3.2 | [55 empty] | 21:00 | 0.46 | 10 | 25.44 | 11.7024 | 5.97 | 19.1 | 8 | 1.4628 | 15 | 6 | 0.31447 | 21:00 | 0.57 | 10 | 25.44 | 14.5008 | 5.96 | 19.2 | 8 | 1.8126 | 15 | 6 | 0.31447 | 21:00 | 0.49 | 11.2 | 24.1071 | 11.8125 | 6.04 | 20.7 | 7 | 1.6875 | 20 | 6.5 | 0.29037
22:00 | [72 empty] | DOSE |  | TOTAL | 30.9 | 30.9 | 33.9 | 95.7 | 29.4 | 29.4 | 32.4 | 91.2 | 0 | 44.8186 | 0 | 37.6896 | 82.5082 | 0.0027936 | TOTAL | 254.8462 | 22626.8744 | 0 | 2522.0573 | 0 | 0 | 0 | 13.2651 | 14.1316 | 14.0539 | 5.6337 | 5.7245 | 5.8918 | 1.3162 | 1.1875 | 1.1432 | 1.2962 | 0.81523 | 0.88581 | 4.2834 | 6 | 0.15121 | 0.12183 | 0.14885 | 3.3719 | 1.4988 | 0.30641 | 12.3157 | 2.3177 | 20.7647 | 3.3237 | 1.4625 | 0.2773 | 11.2537 | 2.0216 | 29.1821 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.45 | 22 | 17 | 10.06 | 123 | 177 | 20.3 | 0.49 |  | 5.92 | 10 | 0.075 | 5.9 | 10 |  | 5.88 | 10 | [8 empty] | 0.06 | [14 empty] | 0.023 | 1 | 0.15 |  | 0.062 | 0.013 | 1 | 0.27 |  | 0.042 | 1 | 0.32 | [22 empty] | AVERAGE | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 14.9395 |  | 12.5632 | 27.5027 |  | AVERAGE | 84.9487 | 7542.2915 |  | 840.6858 | 0 | 0 | 0 | 4.4217 | 4.7105 | 4.6846 | 1.8779 | 1.9082 | 1.9639 | 0.43872 | 0.39585 | 0.38108 | 0.43206 | 0.27174 | 0.29527 | 1.4278 | 3 | 0.050403 | 0.040609 | 0.049617 | 1.124 | 0.4996 | 0.10214 | 4.1052 | 0.77258 | 6.9216 | 1.1079 | 0.48749 | 0.092433 | 3.7512 | 0.67388 | 9.7274 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.6 | 120 | 101 | 66.62 | 705 | 1029 | 117.9 | 2.971 | 0.116 | 35.81 | 67 | 0.541 | 35.79 | 68 | 0 | 35.73 | 66 | 0 | 23.89 | 1.374 | 16 | 2.37 | 74.5 | 40.6 | 1.8353 | 0.386 | 23.97 | 1.452 | 17 | 2.33 | 74.7 | 40.6 | 1.8377 | 24.18 | 1.156 | 11.273 | 2.43 | 80.5 | 45 | 1.8978 | 0.161 | 6 | 1.83 | 0.025 | 0.392 | 0.074 | 7 | 1.712 | 0.057 | 0.26 | 6 | 3.1 | 0.027 | 43.77 | 0.304 | 7 | 25.6 | 112.8 | 50 | 82 | 0.052 | 44.21 | 0.335 | 7 | 24 | 125.8 | 51 | 95 | 0.032 | 25.3 | 25.7 | 21.3 |  |  | MINIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 14.4 |  | 10.165 | 26.1835 |  | MINIMUM | 84.6165 | 7378 |  | 840.5286 |  |  |  | 4.2 | 4.5 | 4.5 | 1.6352 | 1.726 | 1.8135 | 0.43 | 0.39 | 0.37662 | 0.41 | 0.26252 | 0.28 | 1.4267 | 2 | 0.05 | 0.04 | 0.04885 | 1.12 | 0.49941 | 0.1 | 4.0987 | 0.76805 | 6.92 | 1.1069 | 0.48124 | 0.09 | 3.7 | 0.67 | 9.7261 |  | MIN | 0.46 | 10 | 25.44 | 11.7024 | 5.97 | 19.1 | 8 | 1.4628 |  |  |  | MIN | 0.64 | 10.3 | 24.699 | 15.8074 | 6.02 | 18 | 10 | 1.5807 |  |  |  | MIN | 0.59 | 11.3 | 23.8938 | 14.0973 | 6.08 | 19.7 | 10 | 1.4097 |  |  |  | 1.4097
AVERAGE | 6.4333 | 20 | 16.8333 | 11.1033 | 117.5 | 171.5 | 19.65 | 0.49517 | 0.058 | 5.9683 | 11.1667 | 0.090167 | 5.965 | 11.3333 |  | 5.955 | 11 |  | 5.9725 | 0.3435 | 4 | 0.5925 | 18.625 | 10.15 | 0.45884 | 0.064333 | 5.9925 | 0.363 | 4.25 | 0.5825 | 18.675 | 10.15 | 0.45943 | 6.045 | 0.289 | 2.8182 | 0.6075 | 20.125 | 11.25 | 0.47444 | 0.026833 | 1 | 0.305 | 0.0125 | 0.065333 | 0.012333 | 1.1667 | 0.28533 | 0.0285 | 0.043333 | 1 | 0.51667 | 0.0135 | 7.295 | 0.050667 | 1.1667 | 4.2667 | 18.8 | 25 | 41 | 0.026 | 7.3683 | 0.055833 | 1.1667 | 4 | 20.9667 | 25.5 | 47.5 | 0.016 | 4.2167 | 4.2833 | 3.55 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 16.0186 |  | 13.8 | 28.2 |  | MAXIMUM | 85.2297 | 7870.3868 |  | 841 |  |  |  | 4.8158 | 5.0991 | 5.0352 | 2 | 2 | 2.1 | 0.44308 | 0.39877 | 0.39 | 0.44308 | 0.28271 | 0.3029 | 1.43 | 4 | 0.050604 | 0.040914 | 0.05 | 1.126 | 0.5 | 0.1032 | 4.11 | 0.77969 | 6.9224 | 1.11 | 0.5 | 0.093649 | 3.7991 | 0.67581 | 9.73
MINIMUM | 6.4 | 18 | 16 | 9.96 | 115 | 158 | 19 | 0.467 | 0.042 | 5.92 | 10 | 0.075 | 5.9 | 10 |  | 5.88 | 10 |  | 5.95 | 0.313 | 4 | 0.46 | 18 | 10 | 0.43447 | 0.06 | 5.96 | 0.347 | 4 | 0.55 | 18 | 10 | 0.43447 | 6.01 | 0.255 | 0.273 | 0.49 | 19.7 | 11.2 | 0.41037 | 0.023 | 1 | 0.15 | 0.008 | 0.06 | 0.01 | 1 | 0.042 | 0.021 | 0.04 | 1 | 0.32 | 0.006 | 7.08 | 0.046 | 1 | 3.9 | 18.4 | 23 | 35 | 0.022 | 7.19 | 0.051 | 1 | 3.4 | 19.9 | 22 | 43 | 0.008 | 4.2 | 4.1 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 33310 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 500 | 545 | 1240 | 1260 | 1420 | 2380 | 2140 | 2060 | 2350 | 1630 | 1780 | 2250 | 0 | 2800 | 2270 | 3020 | 286 | 340 | 42 | 4890 | 995 | 1395 | 156 | 182 | 21 | 2340 | 476 | 1080
MAXIMUM | 6.46 | 22 | 18 | 12.8 | 123 | 177 | 20.3 | 0.513 | 0.074 | 6.01 | 13 | 0.102 | 6.05 | 13 |  | 6.06 | 12 |  | 6.01 | 0.385 | 4 | 0.66 | 19.1 | 10.3 | 0.51308 | 0.074 | 6.02 | 0.385 | 5 | 0.64 | 19.2 | 10.3 | 0.52487 | 6.08 | 0.322 | 4 | 0.7 | 20.7 | 11.3 | 0.53852 | 0.029 | 1 | 0.43 | 0.017 | 0.076 | 0.014 | 2 | 0.38 | 0.036 | 0.045 | 1 | 0.72 | 0.021 | 7.42 | 0.055 | 2 | 4.5 | 19.2 | 27 | 47 | 0.03 | 7.52 | 0.06 | 2 | 4.3 | 21.5 | 29 | 52 | 0.024 | 4.3 | 4.5 | 4.3 | [17 empty] | AVERAGE | 11103.3333 | [6 empty] | 156.6667 | 166.6667 | 181.6667 | 413.3333 | 420 | 473.3333 | 793.3333 | 713.3333 | 686.6667 | 783.3333 | 543.3333 | 593.3333 | 750 |  | 933.3333 | 756.6667 | 1006.6667 | 95.3333 | 113.3333 | 14 | 1630 | 331.6667 | 465 | 52 | 60.6667 | 7 | 780 | 158.6667 | 360
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9628 |  | TOTAL AVG COAG ALK: |  |  |  | 11.1667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.385 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.0033 |  |  |  |  | 0.045 |  |  |  |  | 0.46 | [6 empty] | 0.045 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 11040 | [6 empty] | 150 | 160 | 175 | 360 | 380 | 440 | 780 | 700 | 680 | 750 | 520 | 580 | 750 |  | 920 | 750 | 1000 | 94 | 113 | 14 | 1620 | 330 | 465 | 52 | 60 | 7 | 760 | 156 | 360
[90 empty] | MAXIMUM | 11150 | [6 empty] | 170 | 180 | 195 | 440 | 440 | 500 | 800 | 720 | 700 | 800 | 560 | 600 | 750 |  | 940 | 760 | 1020 | 96 | 114 | 14 | 1640 | 335 | 465 | 52 | 62 | 7 | 800 | 160 | 360
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.19 |  | TOTAL MGD: |  | 0.002 |  |  | FINISHED SOUTH 1 |  | START: | 23770212 |  | END: | 23770214 |  |  | Alum | 9322 | 9963 | 9963 | 10448 | 10448 | 47.5 | [44 empty] | 0.59 | 11.3 | 23.8938 | 14.0973 | 6.08 | 19.7 | 10 | 1.4097
[73 empty] | FINISHED 2 | 14.847 |  | TOTAL MGD: |  | 13.188 |  |  | FINISHED SOUTH 2 |  | START: | 43197124 |  | END: | 43210312 |  |  | Caustic | 7081 | 6807 | 6807
[73 empty] | TOTAL RAW | 31.46 |  | TOTAL MGD: |  | 4.606 |  |  | FINISHED CONWAY |  | START: | 9971940 |  | END: | 9976546 |  |  | Hypochlorite | 10 |  | 25.5
[76 empty] | TOTAL MGD: |  | 10.241 |  |  | FINISHED PERRY |  | START: | 33203158 |  | END: | 33213399 |  |  | Phosphate | 2636
[76 empty] | TOTAL MGD: |  | 10.021 |  |  | RAW PLANT 1 |  | START: | 30382038 |  | END: | 30392059 |  |  | Fluoride | 3250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.102 |  |  | RAW PLANT 2 |  | START: | 30342693 |  | END: | 30352795 |  |  | Cal~Flo | 14.4 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.337 |  |  | RAW PLANT 3 |  | START: | 6845318 |  | END: | 6856655 |  |  | Zinc | 1440
[76 empty] | TOTAL MGD: |  | 1.262 |  |  | DECANT |  | START: | 1803724 |  | END: | 1804986 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.1607 |  |  | BLOW DOWN |  | START: | 9046.8421 |  | END: | 9048.0028 |  |  | NH3 | 6.7 |  | BI-SUL | 850
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 841
23770214
43210312
9976546
33213399
30392059
30352795
6856655
1804986
9048.0028
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 7
DATE: | 2018-11-07 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-07 | [23 empty] | DATE: | 2018-11-07
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-07 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43411.0105 | 1,2,3 | 75 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 16.0186 | 1,3 | 10.165 | 26.1835 | 0.00098496 | 43411.0105 | 85.2297 | 7870.3868 | 0 | 840.5286 | 0 | 0 | 0 | 4.2492 | 4.5325 | 4.5187 | 1.6352 | 1.726 | 1.8135 | 0.44308 | 0.39877 | 0.37662 | 0.44308 | 0.26252 | 0.3029 | 1.4267 | 4 | 0.050604 | 0.040914 | 0.04885 | 1.126 | 0.49941 | 0.1032 | 4.0987 | 0.77969 | 6.9224 | 1.1069 | 0.48124 | 0.093649 | 3.7546 | 0.67581 | 9.7261 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.95 | 0.336 | 3 | 0.56 | 18.9 | 10.3 | 0.4439 |  | 5.94 | 0.358 | 4 | 0.61 | 18.8 | 10.3 | 0.4439 | 6.02 | 0.282 | 3 | 0.53 | 20.5 | 11.3 | 0.41296 | [13 empty] | 7.12 | 0.052 | 1 | 4 | 19 |  |  |  | 7.17 | 0.058 | 1 | 3.8 | 20.2 |  |  |  | 4.1 | 4.1 | 3.4 | [18 empty] | 11120 | [6 empty] | 150 | 160 | 175 | 360 | 380 | 440 | 800 | 720 | 680 | 800 | 520 | 600 | 750 |  | 940 | 760 | 1000 | 96 | 113 | 14 | 1630 | 335 | 465 | 52 | 60 | 7 | 780 | 160 | 360 |  | 1:00 | 0.56 | 10.3 | 24.699 | 13.8315 | 5.95 | 18.9 | 8 | 1.7289 | 15 | 6 | 0.3239 | 1:00 | 0.61 | 10.3 | 24.699 | 15.0664 | 5.94 | 18.8 | 8 | 1.8833 | 15 | 6 | 0.3239 | 1:00 | 0.53 | 11.3 | 23.8938 | 12.6637 | 6.02 | 20.5 | 7 | 1.8091 | 20 | 6.5 | 0.29296
2:00 | [72 empty] | 43411.3197 | 1,2,3 | 75 | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.8736 | 1,3 | 14.9414 | 27.815 | 0.00098496 | 43411.3197 | 85.6534 | 8608.2356 | 0 | 840.5286 | 0 | 0 | 0 | 4.3767 | 4.6685 | 4.642 | 1.8623 | 1.7714 | 2.102 | 0.44497 | 0.38792 | 0.3651 | 0.44497 | 0.24893 | 0.29042 | 1.43 | 4 | 0.050604 | 0.040914 | 0.050071 | 1.1025 | 0.49941 | 0.095833 | 4.1985 | 0.7215 | 6.1036 | 1.1069 | 0.48124 | 0.093649 | 3.8646 | 0.59134 | 9.4559 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.4 | 22 | 18 | 11 | 117 | 174 | 20.5 | 0.507 |  | 5.78 | 9 | 0.092 | 5.79 | 9 |  | 5.82 | 9 | [8 empty] | 0.064 | [14 empty] | 0.021 | 1 | 0.34 |  | 0.061 | 0.012 | 1 | 0.35 |  | 0.039 | 1 | 0.51 | [38 empty] | 10860 | [6 empty] | 150 | 160 | 175 | 410 | 390 | 510 | 780 | 680 | 640 | 780 | 480 | 560 | 750 |  | 940 | 760 | 1025 | 94 | 113 | 13 | 1660 | 310 | 410 | 52 | 60 | 7 | 780 | 140 | 350 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43411.4449 | 1,2,3 | 75 | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 15.0581 | 1,3 | 13.7246 | 28.7827 | 0.00098496 | 43411.4449 | 79.9748 | 8362.286 | 0 | 840.5286 | 0 | 0 | 0 | 4.3767 | 4.6685 | 4.642 | 1.8623 | 1.7714 | 2.102 | 0.44497 | 0.38792 | 0.3651 | 0.44497 | 0.24893 | 0.29042 | 1.43 | 4 | 0.050604 | 0.040914 | 0.050071 | 1.1025 | 0.49941 | 0.095833 | 4.1985 | 0.7215 | 6.4013 | 1.1069 | 0.48124 | 0.093649 | 3.8646 | 0.59134 | 9.4559 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.13 | 0.053 | 1 | 3.7 | 19.2 |  |  |  | 7.15 | 0.056 | 1 | 3.7 | 21.1 |  |  |  | 4.1 | 4.1 | 3.9 | [18 empty] | 10140 | [6 empty] | 150 | 160 | 175 | 410 | 390 | 510 | 780 | 680 | 640 | 780 | 480 | 560 | 750 |  | 940 | 760 | 1025 | 94 | 113 | 13 | 1660 | 310 | 430 | 52 | 60 | 7 | 780 | 140 | 350 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43411.8241 | 1,2,3 | 71 | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.9974 | 1,3 | 17.8142 | 30.8117 | 1.9181 | 43411.8241 | 80.9212 | 8608.2356 | 0 | 840.5286 | 0 | 0 | 0 | 4.3767 | 4.6685 | 4.642 | 2.0439 | 2.0439 | 1.9577 | 0.43356 | 0.37651 | 0.37651 | 0.39933 | 0.38896 | 0.38896 | 1.2365 | 1 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.095833 | 4.1289 | 0.74477 | 6.4758 | 1.1069 | 0.48124 | 0.093649 | 3.7946 | 0.61246 | 9.4559 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.37 | 17 | 15 | 11.1 | 121 | 174 | 19.6 | 0.533 |  | 5.75 | 7 | 0.081 | 5.98 | 8 |  | 5.95 | 10 | [8 empty] | 0.071 | [14 empty] | 0.024 | 1 | 0.3 |  | 0.07 | 0.013 | 2 | 0.37 |  | 0.041 | 2 | 0.57 | [38 empty] | 10260 | [6 empty] | 150 | 160 | 175 | 450 | 450 | 475 | 760 | 660 | 660 | 700 | 750 | 750 | 650 |  | 950 | 950 | 1000 | 95 | 113 | 13 | 1600 | 320 | 435 | 52 | 60 | 7 | 780 | 145 | 350 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.044 | [9 empty] | 6.03 | 0.369 | 3 | 0.68 | 18.6 | 10 | 0.51308 |  | 6.02 | 0.338 | 3 | 0.73 | 18.7 | 10 | 0.51308 | 6.07 | 0.334 | 3 | 0.58 | 20.3 | 11 | 0.40519 |  |  |  | 0.014 |  |  |  |  | 0.022 |  |  |  | 0.005 | 7.07 | 0.065 | 1 | 4.5 | 18.7 | 18 | 37 | 0.019 | 7.21 | 0.07 | 1 | 3.9 | 20.4 | 19 | 37 | 0.013 | 4.1 | 4.1 | 3.7 | [55 empty] | 9:00 | 0.68 | 10 | 25.44 | 17.2992 | 6.03 | 18.6 | 10 | 1.7299 | 15 | 6.5 | 0.39308 | 9:00 | 0.73 | 10 | 25.44 | 18.5712 | 6.02 | 18.7 | 10 | 1.8571 | 15 | 6.5 | 0.39308 | 9:00 | 0.58 | 11 | 24.5455 | 14.2364 | 6.07 | 20.3 | 7 | 2.0338 | 20 | 6.5 | 0.28519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.32 | 17 | 16 | 10.5 | 122 | 172 | 19.5 | 0.529 |  | 5.9 | 10 | 0.08 | 5.93 | 10 |  | 5.99 | 11 | [8 empty] | 0.07 | [14 empty] | 0.023 | 1 | 0.34 |  | 0.069 | 0.02 | 1 | 0.6 |  | 0.04 | 1 | 0.49 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.05 | 0.433 | 3 | 0.63 | 18.4 | 10 | 0.51308 |  | 6.13 | 0.38 | 4 | 0.56 | 18.7 | 10 | 0.51308 | 6.08 | 0.29 | 4 | 0.61 | 20.4 | 11 | 0.40519 | [13 empty] | 7.34 | 0.059 | 1 | 4.7 | 18.8 |  |  |  | 7.28 | 0.068 | 1 | 4.1 | 20.1 |  |  |  | 4.2 | 4.1 | 3.6 | [55 empty] | 13:00 | 0.63 | 10 | 25.44 | 16.0272 | 6.05 | 18.4 | 10 | 1.6027 | 15 | 6.5 | 0.39308 | 13:00 | 0.56 | 10 | 25.44 | 14.2464 | 6.13 | 18.7 | 10 | 1.4246 | 15 | 6.5 | 0.39308 | 13:00 | 0.61 | 11 | 24.5455 | 14.9727 | 6.08 | 20.4 | 7 | 2.139 | 20 | 6.5 | 0.28519
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.4 | 18 | 15 | 10.6 | 121 | 171 | 19.7 | 0.527 |  | 5.89 | 9 | 0.08 | 5.96 | 10 |  | 6 | 10 | [8 empty] | 0.071 | [14 empty] | 0.024 | 1 | 0.32 |  | 0.069 | 0.018 | 1 | 0.5 |  | 0.043 | 1 | 0.49 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.21 | 0.069 | 1 | 4.5 | 18.8 |  |  |  | 7.3 | 0.061 | 1 | 4 | 20.4 |  |  |  | 4.4 | 4.1 | 3.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.45 | 16 | 16 | 9.63 | 122 | 167 | 19.7 | 0.528 |  | 5.83 | 10 | 0.073 | 5.93 | 10 |  | 5.9 | 10 | [8 empty] | 0.065 | [14 empty] | 0.024 | 1 | 0.4 |  | 0.067 | 0.018 | 1 | 0.56 |  | 0.047 | 1 | 0.5 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.02 | 0.335 | 5 | 0.7 | 18.8 | 9.9 | 0.50915 |  | 6.04 | 0.337 | 5 | 0.8 | 18.8 | 9.9 | 0.50915 | 6.08 | 0.418 | 4 | 0.52 | 20.4 | 11.1 | 0.40778 |  |  |  | 0.014 | [9 empty] | 7.24 | 0.068 | 1 | 4.3 | 18.8 | 22 | 35 | 0.016 | 7.24 | 0.063 | 1 | 4 | 18.8 | 23 | 38 | 0.012 | 4.3 | 4 | 3.2 | [55 empty] | 21:00 | 0.7 | 9.9 | 25.697 | 17.9879 | 6.02 | 18.8 | 10 | 1.7988 | 15 | 6.5 | 0.38915 | 21:00 | 0.8 | 9.9 | 25.697 | 20.5576 | 6.04 | 18.8 | 10 | 2.0558 | 15 | 6.5 | 0.38915 | 21:00 | 0.52 | 11.1 | 24.3243 | 12.6486 | 6.08 | 20.4 | 7 | 1.8069 | 20 | 6.5 | 0.28778
22:00 | [72 empty] | DOSE |  | TOTAL | 40.3 | 40.3 | 44.3 | 124.9 | 39.2 | 39.2 | 43.2 | 121.6 | 0 | 56.9477 | 0 | 56.6453 | 113.593 | 1.921 | TOTAL | 331.7791 | 33449.144 | 0 | 3362.1145 | 0 | 0 | 0 | 17.3794 | 18.5381 | 18.4447 | 7.4036 | 7.3128 | 7.9752 | 1.7666 | 1.5511 | 1.4833 | 1.7323 | 1.1493 | 1.2727 | 5.5231 | 13 | 0.20296 | 0.17389 | 0.19784 | 4.4452 | 1.9976 | 0.3907 | 16.6246 | 2.9675 | 25.9031 | 4.4274 | 1.9249 | 0.3746 | 15.2784 | 2.4709 | 38.0937 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.49 | 16 | 16 | 10.7 | 126 | 173 | 19.5 | 0.538 |  | 5.8 | 9 | 0.079 | 5.87 | 9 |  | 5.97 | 9 | [8 empty] | 0.068 | [14 empty] | 0.032 | 1 | 0.39 |  | 0.068 | 0.021 | 1 | 0.56 |  | 0.044 | 1 | 0.5 | [22 empty] | AVERAGE | 10.075 | 10.075 | 11.075 | 31.225 | 9.8 | 9.8 | 10.8 | 30.4 |  | 14.2369 |  | 14.1613 | 28.3982 | 0.48026 | AVERAGE | 82.9448 | 8362.286 |  | 840.5286 | 0 | 0 | 0 | 4.3449 | 4.6345 | 4.6112 | 1.8509 | 1.8282 | 1.9938 | 0.44164 | 0.38778 | 0.37083 | 0.43309 | 0.28733 | 0.31818 | 1.3808 | 3.25 | 0.050739 | 0.043471 | 0.04946 | 1.1113 | 0.49941 | 0.097676 | 4.1561 | 0.74186 | 6.4758 | 1.1069 | 0.48124 | 0.093649 | 3.8196 | 0.61774 | 9.5234 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.43 | 106 | 96 | 63.53 | 729 | 1031 | 118.5 | 3.162 | 0.087 | 34.95 | 54 | 0.485 | 35.46 | 56 | 0 | 35.63 | 59 | 0 | 24.05 | 1.473 | 14 | 2.57 | 74.7 | 40.2 | 1.9792 | 0.409 | 24.13 | 1.413 | 16 | 2.7 | 75 | 40.2 | 1.9792 | 24.25 | 1.324 | 14 | 2.24 | 81.6 | 44.4 | 1.6311 | 0.148 | 6 | 2.09 | 0.028 | 0.404 | 0.102 | 7 | 2.94 | 0.022 | 0.254 | 7 | 3.06 | 0.005 | 43.11 | 0.366 | 6 | 25.7 | 113.3 | 40 | 72 | 0.035 | 43.35 | 0.376 | 6 | 23.5 | 121 | 42 | 75 | 0.025 | 25.2 | 24.5 | 21 |  |  | MINIMUM | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 |  | 12.8736 |  | 10.165 | 26.1835 | 0.00098496 | MINIMUM | 79.9748 | 7870.3868 |  | 840.5286 |  |  |  | 4.2492 | 4.5325 | 4.5187 | 1.6352 | 1.726 | 1.8135 | 0.43356 | 0.37651 | 0.3651 | 0.39933 | 0.24893 | 0.29042 | 1.2365 | 1 | 0.050604 | 0.040914 | 0.04885 | 1.1025 | 0.49941 | 0.095833 | 4.0987 | 0.7215 | 6.1036 | 1.1069 | 0.48124 | 0.093649 | 3.7546 | 0.59134 | 9.4559 |  | MIN | 0.63 | 10 | 25.44 | 16.0272 | 6.05 | 18.4 | 10 | 1.6027 |  |  |  | MIN | 0.56 | 10 | 25.44 | 14.2464 | 6.13 | 18.7 | 10 | 1.4246 |  |  |  | MIN | 0.52 | 11.1 | 24.3243 | 12.6486 | 6.08 | 20.4 | 7 | 1.8069 |  |  |  | 1.4246
AVERAGE | 6.405 | 17.6667 | 16 | 10.5883 | 121.5 | 171.8333 | 19.75 | 0.527 | 0.0435 | 5.825 | 9 | 0.080833 | 5.91 | 9.3333 |  | 5.9383 | 9.8333 |  | 6.0125 | 0.36825 | 3.5 | 0.6425 | 18.675 | 10.05 | 0.4948 | 0.068167 | 6.0325 | 0.35325 | 4 | 0.675 | 18.75 | 10.05 | 0.4948 | 6.0625 | 0.331 | 3.5 | 0.56 | 20.4 | 11.1 | 0.40778 | 0.024667 | 1 | 0.34833 | 0.014 | 0.067333 | 0.017 | 1.1667 | 0.49 | 0.022 | 0.042333 | 1.1667 | 0.51 |  | 7.185 | 0.061 | 1 | 4.2833 | 18.8833 | 20 | 36 | 0.0175 | 7.225 | 0.062667 | 1 | 3.9167 | 20.1667 | 21 | 37.5 | 0.0125 | 4.2 | 4.0833 | 3.5 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 16.0186 |  | 17.8142 | 30.8117 | 1.9181 | MAXIMUM | 85.6534 | 8608.2356 |  | 840.5286 |  |  |  | 4.3767 | 4.6685 | 4.642 | 2.0439 | 2.0439 | 2.102 | 0.44497 | 0.39877 | 0.37662 | 0.44497 | 0.38896 | 0.38896 | 1.43 | 4 | 0.051143 | 0.051143 | 0.050071 | 1.126 | 0.49941 | 0.1032 | 4.1985 | 0.77969 | 6.9224 | 1.1069 | 0.48124 | 0.093649 | 3.8646 | 0.67581 | 9.7261
MINIMUM | 6.32 | 16 | 15 | 9.63 | 117 | 167 | 19.5 | 0.507 | 0.043 | 5.75 | 7 | 0.073 | 5.79 | 8 |  | 5.82 | 9 |  | 5.95 | 0.335 | 3 | 0.56 | 18.4 | 9.9 | 0.4439 | 0.064 | 5.94 | 0.337 | 3 | 0.56 | 18.7 | 9.9 | 0.4439 | 6.02 | 0.282 | 3 | 0.52 | 20.3 | 11 | 0.40519 | 0.021 | 1 | 0.3 | 0.014 | 0.061 | 0.012 | 1 | 0.35 | 0.022 | 0.039 | 1 | 0.49 |  | 7.07 | 0.052 | 1 | 3.7 | 18.7 | 18 | 35 | 0.016 | 7.15 | 0.056 | 1 | 3.7 | 18.8 | 19 | 37 | 0.012 | 4.1 | 4 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 42380 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 640 | 700 | 1630 | 1610 | 1935 | 3120 | 2740 | 2620 | 3060 | 2230 | 2470 | 2900 | 0 | 3770 | 3230 | 4050 | 379 | 452 | 53 | 6550 | 1275 | 1740 | 208 | 240 | 28 | 3120 | 585 | 1410
MAXIMUM | 6.49 | 22 | 18 | 11.1 | 126 | 174 | 20.5 | 0.538 | 0.044 | 5.9 | 10 | 0.092 | 5.98 | 10 |  | 6 | 11 |  | 6.05 | 0.433 | 5 | 0.7 | 18.9 | 10.3 | 0.51308 | 0.071 | 6.13 | 0.38 | 5 | 0.8 | 18.8 | 10.3 | 0.51308 | 6.08 | 0.418 | 4 | 0.61 | 20.5 | 11.3 | 0.41296 | 0.032 | 1 | 0.4 | 0.014 | 0.07 | 0.021 | 2 | 0.6 | 0.022 | 0.047 | 2 | 0.57 |  | 7.34 | 0.069 | 1 | 4.7 | 19.2 | 22 | 37 | 0.019 | 7.3 | 0.07 | 1 | 4.1 | 21.1 | 23 | 38 | 0.013 | 4.4 | 4.1 | 3.9 | [17 empty] | AVERAGE | 10595 | [6 empty] | 150 | 160 | 175 | 407.5 | 402.5 | 483.75 | 780 | 685 | 655 | 765 | 557.5 | 617.5 | 725 |  | 942.5 | 807.5 | 1012.5 | 94.75 | 113 | 13.25 | 1637.5 | 318.75 | 435 | 52 | 60 | 7 | 780 | 146.25 | 352.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.8911 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.433 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.52 | [5 empty] | 6.0358 |  |  |  |  | 0.047 |  |  |  |  | 0.52 | [6 empty] | 0.047 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 10140 | [6 empty] | 150 | 160 | 175 | 360 | 380 | 440 | 760 | 660 | 640 | 700 | 480 | 560 | 650 |  | 940 | 760 | 1000 | 94 | 113 | 13 | 1600 | 310 | 410 | 52 | 60 | 7 | 780 | 140 | 350
[90 empty] | MAXIMUM | 11120 | [6 empty] | 150 | 160 | 175 | 450 | 450 | 510 | 800 | 720 | 680 | 800 | 750 | 750 | 750 |  | 950 | 950 | 1025 | 96 | 113 | 14 | 1660 | 335 | 465 | 52 | 60 | 7 | 780 | 160 | 360
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.764 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23770214 |  | END: | 23770215 |  |  | Alum | 9252 | 8938 | 8938 | 9555 | 9555 | 47.6 | [44 empty] | 0.56 | 10 | 25.44 | 14.2464 | 6.13 | 18.7 | 10 | 1.4246
[73 empty] | FINISHED 2 | 13.162 |  | TOTAL MGD: |  | 10.763 |  |  | FINISHED SOUTH 2 |  | START: | 43210312 |  | END: | 43221075 |  |  | Caustic | 6761 | 8628 | 8628
[73 empty] | TOTAL RAW | 27.548 |  | TOTAL MGD: |  | 4.369 |  |  | FINISHED CONWAY |  | START: | 9976546 |  | END: | 9980915 |  |  | Hypochlorite | 14 |  | 34
[76 empty] | TOTAL MGD: |  | 8.793 |  |  | FINISHED PERRY |  | START: | 33213399 |  | END: | 33222192 |  |  | Phosphate | 2615
[76 empty] | TOTAL MGD: |  | 9.817 |  |  | RAW PLANT 1 |  | START: | 30392059 |  | END: | 30401876 |  |  | Fluoride | 2931 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 7.851 |  |  | RAW PLANT 2 |  | START: | 30352795 |  | END: | 30360646 |  |  | Cal~Flo | 11.8 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.88 |  |  | RAW PLANT 3 |  | START: | 6856655 |  | END: | 6866535 |  |  | Zinc | 1465
[76 empty] | TOTAL MGD: |  | 0.678 |  |  | DECANT |  | START: | 1804986 |  | END: | 1805664 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.1807 |  |  | BLOW DOWN |  | START: | 9048.0028 |  | END: | 9049.1835 |  |  | NH3 | 6.49 |  | BI-SUL | 800
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 841
23770215
43221075
9980915
33222192
30401876
30360646
6866535
1805664
9049.1835
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 8
DATE: | 2018-11-08 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-08 | [23 empty] | DATE: | 2018-11-08
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-08 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43412.0082 | 1,2,3 | 71 | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.9974 | 1,3 | 17.8142 | 30.8117 | 1.9181 | 43412.0082 | 80.9212 | 8854.1852 | 0 | 840.5286 | 0 | 0 | 0 | 4.3767 | 4.6685 | 4.642 | 2.0439 | 2.0439 | 1.9577 | 0.43356 | 0.37651 | 0.37651 | 0.39933 | 0.38896 | 0.38896 | 1.2365 | 1 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.095833 | 4.1289 | 0.74477 | 6.4758 | 1.1069 | 0.48124 | 0.093649 | 3.7946 | 0.61246 | 9.4559 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.98 | 0.363 | 4 | 0.68 | 18.7 | 10 | 0.43447 |  | 5.99 | 0.356 | 4 | 0.79 | 18.8 | 10 | 0.43447 | 6.1 | 0.336 | 3 | 0.53 | 20.3 | 11 | 0.40519 | [13 empty] | 7.22 | 0.073 | 1 | 3.9 | 18.8 |  |  |  | 7.41 | 0.07 | 1 | 3.8 | 20 |  |  |  | 4.2 | 4 | 3.3 | [18 empty] | 10260 | [6 empty] | 150 | 160 | 175 | 450 | 450 | 475 | 760 | 660 | 660 | 700 | 750 | 750 | 650 |  | 950 | 950 | 1000 | 95 | 113 | 13 | 1600 | 320 | 435 | 52 | 60 | 7 | 780 | 145 | 350 |  | 1:00 | 0.68 | 10 | 25.44 | 17.2992 | 5.98 | 18.7 | 8 | 2.1624 | 15 | 6 | 0.31447 | 1:00 | 0.79 | 10 | 25.44 | 20.0976 | 5.99 | 18.8 | 8 | 2.5122 | 15 | 6 | 0.31447 | 1:00 | 0.53 | 11 | 24.5455 | 13.0091 | 6.1 | 20.3 | 7 | 1.8584 | 20 | 6.5 | 0.28519
2:00 | [72 empty] | 43412.1455 | 1,2,3 | 71 | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.9974 | 1,3 | 17.8142 | 30.8117 | 1.9181 | 43412.1455 | 80.9212 | 8854.1852 | 0 | 840.5286 | 0 | 0 | 0 | 5.5439 | 5.8356 | 5.703 | 2.0439 | 2.0439 | 1.9577 | 0.43356 | 0.37651 | 0.37651 | 0.39933 | 0.38896 | 0.38896 | 1.2365 | 1 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.095833 | 4.1289 | 0.74477 | 6.4758 | 1.1069 | 0.48124 | 0.093649 | 3.9213 | 0.61246 | 9.4559 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.41 | 15 | 16 | 10.3 | 122 | 170 | 19.6 | 0.528 |  | 5.9 | 10 | 0.083 | 5.98 | 10 |  | 6 | 10 | [8 empty] | 0.066 | [14 empty] | 0.034 | 1 | 0.4 |  | 0.065 | 0.02 | 1 | 0.48 |  | 0.04 | 1 | 0.4 | [38 empty] | 10260 | [6 empty] | 190 | 200 | 215 | 450 | 450 | 475 | 760 | 660 | 660 | 700 | 750 | 750 | 650 |  | 950 | 950 | 1000 | 95 | 113 | 13 | 1600 | 320 | 435 | 52 | 60 | 7 | 810 | 145 | 350 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43412.4043 | 1,2,3 | 71 | 9.7 | 9.7 | 10.7 | 30.1 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 15.0883 | 1,3 | 12.8002 | 27.8885 | 1.9181 | 43412.4043 | 75.5428 | 9592.034 | 0 | 951.5419 | 0 | 0 | 0 | 5.7153 | 6.0161 | 5.8629 | 1.7714 | 1.7033 | 1.8547 | 0.45873 | 0.39992 | 0.34111 | 0.34111 | 0.3732 | 0.3732 | 1.2365 | 2.5 | 0.051143 | 0.049528 | 0.050071 | 1.126 | 0.49941 | 0.095833 | 4.1304 | 0.69823 | 6.2525 | 1.1069 | 0.48124 | 0.093649 | 4.108 | 0.59134 | 9.1857 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.23 | 0.071 | 1 | 4.4 | 18.8 |  |  |  | 7.22 | 0.07 | 1 | 4.5 | 20.1 |  |  |  | 4.1 | 4 | 3.3 | [18 empty] | 9300 | [6 empty] | 190 | 200 | 215 | 390 | 375 | 450 | 780 | 680 | 580 | 580 | 700 | 700 | 650 |  | 950 | 920 | 1025 | 96 | 113 | 13 | 1620 | 300 | 420 | 52 | 60 | 7 | 840 | 140 | 340 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43412.8231 | 1,2,3 | 71 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,2,3 | 14.5656 | 1,3 | 12.4531 | 27.0187 | 1.5134 | 43412.8231 | 76.3551 | 9715.0088 | 0 | 951.5419 | 0 | 0 | 0 | 6.6779 | 6.3169 | 6.1356 | 1.9353 | 1.9353 | 2.0947 | 0.44108 | 0.38227 | 0.34111 | 0.34111 | 0.36254 | 0.3732 | 1.2365 | 2 | 0.051611 | 0.051611 | 0.051723 | 1.0995 | 0.49902 | 0.10208 | 4.1128 | 0.74376 | 6.8188 | 1.1269 | 0.50955 | 0.099158 | 4.1173 | 0.62612 | 9.7261 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.41 | 17 | 15 | 10 | 119 | 169 | 19.6 | 0.517 |  | 6.06 | 8 | 0.087 | 6 | 7 |  | 6 | 9 | [8 empty] | 0.072 | [14 empty] | 0.023 | 1 | 0.34 |  | 0.068 | 0.044 | 1 | 0.38 |  | 0.035 | 1 | 0.56 | [38 empty] | 9400 | [6 empty] | 222 | 210 | 225 | 400 | 400 | 480 | 750 | 650 | 580 | 580 | 680 | 700 | 650 |  | 900 | 900 | 1000 | 88 | 106 | 13 | 1550 | 300 | 430 | 50 | 60 | 7 | 820 | 140 | 340 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.048 | [9 empty] | 5.99 | 0.406 | 4 | 0.69 | 18.5 | 9.6 | 0.42189 |  | 6.02 | 0.38 | 4 | 0.65 | 18.7 | 9.8 | 0.50522 | 6.1 | 0.274 | 3 | 0.55 | 20.2 | 10 | 0.37926 |  |  |  | 0.01 |  |  |  |  | 0.022 |  |  |  | 0.004 | 7.18 | 0.068 | 1 | 4.4 | 18.9 | 20 | 39 | 0.019 | 7.29 | 0.076 | 1 | 4.3 | 20.2 | 20 | 40 | 0.009 | 4.2 | 3.9 | 3.6 | [55 empty] | 9:00 | 0.69 | 9.6 | 26.5 | 18.285 | 5.99 | 18.5 | 8 | 2.2856 | 15 | 6 | 0.30189 | 9:00 | 0.65 | 9.8 | 25.9592 | 16.8735 | 6.02 | 18.7 | 10 | 1.6873 | 15 | 6.5 | 0.38522 | 9:00 | 0.55 | 10 | 27 | 14.85 | 6.1 | 20.2 | 7 | 2.1214 | 20 | 6.5 | 0.25926
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.43 | 16 | 16 | 10.2 | 117 | 175 | 19.7 | 0.502 |  | 5.98 | 8 | 0.079 | 6.05 | 8 |  | 6.03 | 10 | [8 empty] | 0.073 | [14 empty] | 0.026 | 1 | 0.31 |  | 0.071 | 0.013 | 1 | 0.31 |  | 0.038 | 1 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.01 | 0.531 | 4 | 0.54 | 18.4 | 9.6 | 0.49736 |  | 6.11 | 0.419 | 4 | 0.53 | 18.8 | 9.8 | 0.50522 | 6.14 | 0.29 | 3 | 0.54 | 20.3 | 10 | 0.37926 | [13 empty] | 7.5 | 0.071 | 1 | 4.3 | 18.9 |  |  |  | 7.46 | 0.074 | 1 | 4.1 | 20.4 |  |  |  | 4.2 | 4 | 2.8 | [55 empty] | 13:00 | 0.54 | 9.6 | 26.5 | 14.31 | 6.01 | 18.4 | 10 | 1.431 | 15 | 6.5 | 0.37736 | 13:00 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.11 | 18.8 | 10 | 1.3758 | 15 | 6.5 | 0.38522 | 13:00 | 0.54 | 10 | 27 | 14.58 | 6.14 | 20.3 | 7 | 2.0829 | 20 | 6.5 | 0.25926
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.42 | 17 | 16 | 10.4 | 118 | 170 | 19.8 | 0.513 |  | 5.98 | 10 | 0.079 | 6.05 | 10 |  | 6.05 | 10 | [8 empty] | 0.071 | [14 empty] | 0.039 | 1 | 0.19 |  | 0.069 | 0.018 | 1 | 0.35 |  | 0.039 | 1 | 0.45 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.58 | 0.071 | 1 | 4.3 | 18.5 |  |  |  | 7.47 | 0.062 | 1 | 4 | 20.2 |  |  |  | 4.2 | 4 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.49 | 16 | 16 | 10.2 | 120 | 162 | 19.8 | 0.52 |  | 6 | 10 | 0.078 | 6.14 | 10 |  | 6.13 | 10 | [8 empty] | 0.067 | [14 empty] | 0.028 | 1 | 0.19 |  | 0.073 | 0.016 | 1 | 0.28 |  | 0.039 | 1 | 0.49 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.046 | [9 empty] | 6.14 | 0.418 | 4 | 0.53 | 18.7 | 9.6 | 0.49736 |  | 6.15 | 0.381 | 4 | 0.53 | 18.8 | 9.8 | 0.50522 | 6.18 | 0.413 | 3 | 0.56 | 20.3 | 10.8 | 0.4 |  |  |  | 0.012 |  |  |  |  | 0.021 |  |  |  | 0.006 | 7.34 | 0.07 | 1 | 4.1 | 18.7 | 22 | 40 | 0.016 | 7.46 | 0.073 | 1 | 3.8 | 20 | 22 | 40 | 0.012 | 4.2 | 3.9 | 3.1 | [55 empty] | 21:00 | 0.53 | 9.6 | 26.5 | 14.045 | 6.14 | 18.7 | 10 | 1.4045 | 15 | 6.5 | 0.37736 | 21:00 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.15 | 18.8 | 10 | 1.3758 | 15 | 6.5 | 0.38522 | 21:00 | 0.56 | 10.8 | 25 | 14 | 6.18 | 20.3 | 7 | 2 | 20 | 6.5 | 0.28
22:00 | [72 empty] | DOSE |  | TOTAL | 39.4 | 39.4 | 43.4 | 122.2 | 38.6 | 38.6 | 42.6 | 119.8 | 0 | 55.6488 | 0 | 60.8818 | 116.5306 | 7.2677 | TOTAL | 313.7403 | 37015.4132 | 0 | 3584.141 | 0 | 0 | 0 | 22.3138 | 22.8372 | 22.3435 | 7.7946 | 7.7265 | 7.8649 | 1.7669 | 1.5352 | 1.4352 | 1.4809 | 1.5137 | 1.5243 | 4.9458 | 6.5 | 0.20504 | 0.20342 | 0.19949 | 4.4539 | 1.9972 | 0.38958 | 16.5009 | 2.9315 | 26.0228 | 4.4474 | 1.9533 | 0.3801 | 15.9412 | 2.4424 | 37.8236 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.44 | 16 | 16 | 10.3 | 119 | 173 | 19.7 | 0.514 |  | 6.05 | 10 | 0.08 | 6.04 | 10 |  | 6.1 | 10 | [8 empty] | 0.066 | [14 empty] | 0.028 | 1 | 0.2 |  | 0.072 | 0.018 | 1 | 0.26 |  | 0.039 | 1 | 0.43 | [22 empty] | AVERAGE | 9.85 | 9.85 | 10.85 | 30.55 | 9.65 | 9.65 | 10.65 | 29.95 |  | 13.9122 |  | 15.2204 | 29.1326 | 1.8169 | AVERAGE | 78.4351 | 9253.8533 |  | 896.0352 | 0 | 0 | 0 | 5.5784 | 5.7093 | 5.5859 | 1.9487 | 1.9316 | 1.9662 | 0.44173 | 0.3838 | 0.35881 | 0.37022 | 0.37841 | 0.38108 | 1.2365 | 1.625 | 0.05126 | 0.050856 | 0.049873 | 1.1135 | 0.49931 | 0.097396 | 4.1252 | 0.73288 | 6.5057 | 1.1119 | 0.48831 | 0.095026 | 3.9853 | 0.61059 | 9.4559 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.6 | 97 | 95 | 61.4 | 715 | 1019 | 118.2 | 3.094 | 0.094 | 35.97 | 56 | 0.486 | 36.26 | 55 | 0 | 36.31 | 59 | 0 | 24.12 | 1.718 | 16 | 2.44 | 74.3 | 38.8 | 1.8511 | 0.415 | 24.27 | 1.536 | 16 | 2.5 | 75.1 | 39.4 | 1.9501 | 24.52 | 1.313 | 12 | 2.18 | 81.1 | 41.8 | 1.5637 | 0.178 | 6 | 1.63 | 0.022 | 0.418 | 0.129 | 6 | 2.06 | 0.043 | 0.23 | 6 | 2.83 | 0.01 | 44.05 | 0.424 | 6 | 25.4 | 112.6 | 42 | 79 | 0.035 | 44.31 | 0.425 | 6 | 24.5 | 120.9 | 42 | 80 | 0.021 | 25.1 | 23.8 | 19.1 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 12.9974 |  | 12.4531 | 27.0187 | 1.5134 | MINIMUM | 75.5428 | 8854.1852 |  | 840.5286 |  |  |  | 4.3767 | 4.6685 | 4.642 | 1.7714 | 1.7033 | 1.8547 | 0.43356 | 0.37651 | 0.34111 | 0.34111 | 0.36254 | 0.3732 | 1.2365 | 1 | 0.051143 | 0.049528 | 0.04885 | 1.0995 | 0.49902 | 0.095833 | 4.1128 | 0.69823 | 6.2525 | 1.1069 | 0.48124 | 0.093649 | 3.7946 | 0.59134 | 9.1857 |  | MIN | 0.53 | 9.6 | 26.5 | 14.045 | 6.14 | 18.7 | 10 | 1.4045 |  |  |  | MIN | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.11 | 18.8 | 10 | 1.3758 |  |  |  | MIN | 0.53 | 11 | 24.5455 | 13.0091 | 6.1 | 20.3 | 7 | 1.8584 |  |  |  | 1.3758
AVERAGE | 6.4333 | 16.1667 | 15.8333 | 10.2333 | 119.1667 | 169.8333 | 19.7 | 0.51567 | 0.047 | 5.995 | 9.3333 | 0.081 | 6.0433 | 9.1667 |  | 6.0517 | 9.8333 |  | 6.03 | 0.4295 | 4 | 0.61 | 18.575 | 9.7 | 0.46277 | 0.069167 | 6.0675 | 0.384 | 4 | 0.625 | 18.775 | 9.85 | 0.48753 | 6.13 | 0.32825 | 3 | 0.545 | 20.275 | 10.45 | 0.39093 | 0.029667 | 1 | 0.27167 | 0.011 | 0.069667 | 0.0215 | 1 | 0.34333 | 0.0215 | 0.038333 | 1 | 0.47167 |  | 7.3417 | 0.070667 | 1 | 4.2333 | 18.7667 | 21 | 39.5 | 0.0175 | 7.385 | 0.070833 | 1 | 4.0833 | 20.15 | 21 | 40 | 0.0105 | 4.1833 | 3.9667 | 3.1833 |  |  | MAXIMUM | 10 | 10 | 11 | 31 | 9.8 | 9.8 | 10.8 | 30.4 |  | 15.0883 |  | 17.8142 | 30.8117 | 1.9181 | MAXIMUM | 80.9212 | 9715.0088 |  | 951.5419 |  |  |  | 6.6779 | 6.3169 | 6.1356 | 2.0439 | 2.0439 | 2.0947 | 0.45873 | 0.39992 | 0.37651 | 0.39933 | 0.38896 | 0.38896 | 1.2365 | 2.5 | 0.051611 | 0.051611 | 0.051723 | 1.126 | 0.49941 | 0.10208 | 4.1304 | 0.74477 | 6.8188 | 1.1269 | 0.50955 | 0.099158 | 4.1173 | 0.62612 | 9.7261
MINIMUM | 6.41 | 15 | 15 | 10 | 117 | 162 | 19.6 | 0.502 | 0.046 | 5.9 | 8 | 0.078 | 5.98 | 7 |  | 6 | 9 |  | 5.98 | 0.363 | 4 | 0.53 | 18.4 | 9.6 | 0.42189 | 0.066 | 5.99 | 0.356 | 4 | 0.53 | 18.7 | 9.8 | 0.43447 | 6.1 | 0.274 | 3 | 0.53 | 20.2 | 10 | 0.37926 | 0.023 | 1 | 0.19 | 0.01 | 0.065 | 0.013 | 1 | 0.26 | 0.021 | 0.035 | 1 | 0.4 |  | 7.18 | 0.068 | 1 | 3.9 | 18.5 | 20 | 39 | 0.016 | 7.22 | 0.062 | 1 | 3.8 | 20 | 20 | 40 | 0.009 | 4.1 | 3.9 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 39220 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 770 | 830 | 1690 | 1675 | 1880 | 3050 | 2650 | 2480 | 2560 | 2880 | 2900 | 2600 | 0 | 3750 | 3720 | 4025 | 374 | 445 | 52 | 6370 | 1240 | 1720 | 206 | 240 | 28 | 3250 | 570 | 1380
MAXIMUM | 6.49 | 17 | 16 | 10.4 | 122 | 175 | 19.8 | 0.528 | 0.048 | 6.06 | 10 | 0.087 | 6.14 | 10 |  | 6.13 | 10 |  | 6.14 | 0.531 | 4 | 0.69 | 18.7 | 10 | 0.49736 | 0.073 | 6.15 | 0.419 | 4 | 0.79 | 18.8 | 10 | 0.50522 | 6.18 | 0.413 | 3 | 0.56 | 20.3 | 11 | 0.40519 | 0.039 | 1 | 0.4 | 0.012 | 0.073 | 0.044 | 1 | 0.48 | 0.022 | 0.04 | 1 | 0.56 |  | 7.58 | 0.073 | 1 | 4.4 | 18.9 | 22 | 40 | 0.019 | 7.47 | 0.076 | 1 | 4.5 | 20.4 | 22 | 40 | 0.012 | 4.2 | 4 | 3.6 | [17 empty] | AVERAGE | 9805 | [6 empty] | 188 | 192.5 | 207.5 | 422.5 | 418.75 | 470 | 762.5 | 662.5 | 620 | 640 | 720 | 725 | 650 |  | 937.5 | 930 | 1006.25 | 93.5 | 111.25 | 13 | 1592.5 | 310 | 430 | 51.5 | 60 | 7 | 812.5 | 142.5 | 345
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.03 |  | TOTAL AVG COAG ALK: |  |  |  | 9.4444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.531 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.53 | [5 empty] | 6.0758 |  |  |  |  | 0.044 |  |  |  |  | 0.53 | [6 empty] | 0.044 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 9300 | [6 empty] | 150 | 160 | 175 | 390 | 375 | 450 | 750 | 650 | 580 | 580 | 680 | 700 | 650 |  | 900 | 900 | 1000 | 88 | 106 | 13 | 1550 | 300 | 420 | 50 | 60 | 7 | 780 | 140 | 340
[90 empty] | MAXIMUM | 10260 | [6 empty] | 222 | 210 | 225 | 450 | 450 | 480 | 780 | 680 | 660 | 700 | 750 | 750 | 650 |  | 950 | 950 | 1025 | 96 | 113 | 13 | 1620 | 320 | 435 | 52 | 60 | 7 | 840 | 145 | 350
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.266 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23770215 |  | END: | 23770221 |  |  | Alum | 9329 | 8806 | 8806 | 9096 | 9096 | 41.1 | [44 empty] | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.11 | 18.8 | 10 | 1.3758
[73 empty] | FINISHED 2 | 14.026 |  | TOTAL MGD: |  | 13.26 |  |  | FINISHED SOUTH 2 |  | START: | 43221075 |  | END: | 43234335 |  |  | Caustic | 6422 | 8537 | 8537
[73 empty] | TOTAL RAW | 27.924 |  | TOTAL MGD: |  | 4.03 |  |  | FINISHED CONWAY |  | START: | 9980915 |  | END: | 9984945 |  |  | Hypochlorite | 15 |  | 32
[76 empty] | TOTAL MGD: |  | 9.996 |  |  | FINISHED PERRY |  | START: | 33222192 |  | END: | 33232188 |  |  | Phosphate | 2564
[76 empty] | TOTAL MGD: |  | 7.934 |  |  | RAW PLANT 1 |  | START: | 30401876 |  | END: | 30409810 |  |  | Fluoride | 3050 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.962 |  |  | RAW PLANT 2 |  | START: | 30360646 |  | END: | 30370608 |  |  | Cal~Flo | 9.33 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.028 |  |  | RAW PLANT 3 |  | START: | 6866535 |  | END: | 6876563 |  |  | Zinc | 1482
[76 empty] | TOTAL MGD: |  | 0.766 |  |  | DECANT |  | START: | 1805664 |  | END: | 1806430 |  |  | Polymer | 20
[76 empty] | TOTAL MGD: |  | 1.5252 |  |  | BLOW DOWN |  | START: | 9049.1835 |  | END: | 9050.7087 |  |  | NH3 | 12.68 |  | BI-SUL | 800
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 940
23770221
43234335
9984945
33232188
30409810
30370608
6876563
1806430
9050.7087
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 9
DATE: | 2018-11-09 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-09 | [23 empty] | DATE: | 2018-11-09
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-09 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43413.0128 | 1,2,3 | 80 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | ,2,3 | 14.5656 | 1,3 | 12.4531 | 27.0187 | 1.5134 | 43413.0128 | 75.7158 | 9715.0088 | 0 | 951.5419 | 0 | 0 | 0 | 6.4776 | 6.1274 | 5.9683 | 1.8742 | 1.8742 | 2.0349 | 0.42785 | 0.39933 | 0.33087 | 0.33087 | 0.36303 | 0.36303 | 1.2365 | 2 | 0.049981 | 0.049981 | 0.050246 | 1.0647 | 0.48326 | 0.098859 | 4.0715 | 0.72027 | 6.6035 | 1.0947 | 0.49499 | 0.096324 | 3.9925 | 0.60823 | 9.4482 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.419 | 6 | 0.56 | 18.6 | 10 | 0.51308 |  | 6.11 | 0.423 | 6 | 0.53 | 18.7 | 10 | 0.51308 | 6.1 | 0.396 | 3 | 0.59 | 20.1 | 11 | 0.40519 | [13 empty] | 7.98 | 0.073 | 2 | 4.3 | 18.9 |  |  |  | 7.63 | 0.067 | 2 | 4.4 | 19.7 |  |  |  | 4.2 | 4 | 3.1 | [18 empty] | 9600 | [6 empty] | 222 | 210 | 225 | 400 | 400 | 480 | 750 | 700 | 580 | 580 | 700 | 700 | 650 |  | 900 | 900 | 1000 | 88 | 106 | 13 | 1600 | 300 | 430 | 50 | 60 | 7 | 820 | 140 | 340 |  | 1:00 | 0.56 | 10 | 25.44 | 14.2464 | 6.1 | 18.6 | 10 | 1.4246 | 15 | 6.5 | 0.39308 | 1:00 | 0.53 | 10 | 25.44 | 13.4832 | 6.11 | 18.7 | 10 | 1.3483 | 15 | 6.5 | 0.39308 | 1:00 | 0.59 | 11 | 24.5455 | 14.4818 | 6.1 | 20.1 | 7 | 2.0688 | 20 | 6.5 | 0.28519
2:00 | [72 empty] | 43413.1345 | 1,2,3,6 | 50 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | ,2,3 | 14.5656 | 1,3 | 12.4531 | 27.0187 | 1.5134 | 43413.1345 | 74.7879 | 9715.0088 | 0 | 951.5419 | 0 | 0 | 0 | 6.5253 | 6.3661 | 5.9572 | 1.9077 | 1.9077 | 1.974 | 0.43044 | 0.38896 | 0.3371 | 0.3371 | 0.35654 | 0.35654 | 1.2365 | 2 | 0.050246 | 0.050246 | 0.050464 | 1.0947 | 0.49911 | 0.096324 | 4.0966 | 0.54306 | 6.6276 | 1.0995 | 0.49714 | 0.10051 | 4.0794 | 0.61484 | 9.3878 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.44 | 16 | 16 | 10.2 | 120 | 170 | 19.8 | 0.512 |  | 6.14 | 10 | 0.084 | 6.14 | 10 |  | 6.1 | 10 | [8 empty] | 0.08 | [14 empty] | 0.03 | 2 | 0.2 |  | 0.07 | 0.019 | 2 | 0.26 |  | 0.04 | 2 | 0.4 | [38 empty] | 10400 | [6 empty] | 246 | 240 | 245 | 450 | 450 | 510 | 830 | 750 | 650 | 650 | 750 | 750 | 650 |  | 1000 | 1000 | 1100 | 100 | 121 | 14 | 1780 | 250 | 477 | 55 | 66 | 8 | 920 | 155 | 370 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43413.3481 | 1,2,3,6 | 50 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | ,2,3 | 16.1453 | 1,3 | 16.3152 | 32.4605 | 1.5134 | 43413.3481 | 75.507 | 9715.0088 | 0 | 976.9163 | 0 | 0 | 0 | 6.6314 | 6.8967 | 6.2733 | 1.7805 | 1.6957 | 2.0127 | 0.41489 | 0.38377 | 0.41489 | 0.32154 | 0.34038 | 0.34513 | 1.2365 | 5 | 0.050246 | 0.050246 | 0.050005 | 1.0728 | 0.49911 | 0.096324 | 4.1865 | 0.69512 | 6.7388 | 1.1194 | 0.48207 | 0.10051 | 4.5487 | 0.57518 | 9.134 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.23 | 0.07 | 2 | 4.1 | 18.4 |  |  |  | 7.6 | 0.069 | 2 | 3.8 | 19.8 |  |  |  | 4.3 | 4 | 3.2 | [18 empty] | 10500 | [6 empty] | 250 | 260 | 258 | 420 | 400 | 520 | 800 | 740 | 800 | 620 | 716 | 726 | 650 |  | 1000 | 1000 | 1090 | 98 | 121 | 14 | 1750 | 320 | 485 | 56 | 64 | 8 | 940 | 145 | 360 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43413.8256 | 1,2,3,6 | 52 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | ,2,3 | 15.7176 | 1,3 | 16.4851 | 32.2027 | 2.0203 | 43413.8256 | 79.8217 | 10083.9332 | 0 | 976.9163 | 0 | 0 | 0 | 8.4882 | 8.7535 | 8.024 | 1.9077 | 1.7805 | 2.0127 | 0.41489 | 0.38896 | 0.41489 | 0.32154 | 0.34228 | 0.34704 | 1.2365 | 1 | 0.050246 | 0.050246 | 0.050464 | 1.0947 | 0.49911 | 0.096324 | 4.1815 | 0.76029 | 6.7388 | 1.0995 | 0.49714 | 0.10051 | 4.2994 | 0.59501 | 9.134 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.44 | 17 | 15 | 10.5 | 114 | 172 | 19.5 | 0.492 |  | 6.07 | 10 | 0.073 | 6.06 | 9 |  | 6 | 10 | [8 empty] | 0.068 | [14 empty] | 0.027 | 1 | 0.27 |  | 0.069 | 0.012 | 1 | 0.5 |  | 0.092 | 1 | 0.82 | [38 empty] | 11100 | [6 empty] | 320 | 330 | 330 | 450 | 420 | 520 | 800 | 750 | 800 | 620 | 720 | 730 | 650 |  | 1000 | 1000 | 1100 | 100 | 121 | 14 | 1750 | 350 | 485 | 55 | 66 | 8 | 920 | 150 | 360 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.052 | [9 empty] | 6.08 | 0.552 | 4 | 0.6 | 18.5 | 11 | 0.55239 |  | 6.12 | 0.567 | 4 | 0.61 | 18.6 | 11 | 0.55239 | 6.11 | 0.305 | 3 | 0.65 | 19.8 | 12 | 0.56444 |  |  |  | 0.006 |  |  |  |  | 0.018 |  |  |  | 0.003 | 7.38 | 0.068 | 1 | 4.4 | 18.8 | 20 | 34 | 0.012 | 7.41 | 0.063 | 1 | 4 | 18.9 | 21 | 36 | 0.008 | 4.2 | 3.7 | 3.9 | [55 empty] | 9:00 | 0.6 | 11 | 23.1273 | 13.8764 | 6.08 | 18.5 | 10 | 1.3876 | 15 | 6.5 | 0.43239 | 9:00 | 0.61 | 11 | 23.1273 | 14.1076 | 6.12 | 18.6 | 10 | 1.4108 | 15 | 6.5 | 0.43239 | 9:00 | 0.65 | 12 | 22.5 | 14.625 | 6.11 | 19.8 | 10 | 1.4625 | 15 | 6.5 | 0.44444
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.51 | 17 | 16 | 11.4 | 108 | 175 | 19.5 | 0.476 |  | 5.93 | 9 | 0.07 | 6 | 9 |  | 6.04 | 10 | [8 empty] | 0.066 | [14 empty] | 0.028 | 1 | 0.27 |  | 0.067 | 0.016 | 1 | 0.37 |  | 0.059 | 1 | 0.68 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.04 | 0.512 | 4 | 0.62 | 18.54 | 11 | 0.55239 |  | 6.09 | 0.498 | 4 | 0.7 | 18.8 | 11 | 0.55239 | 6.19 | 0.351 | 3 | 0.58 | 19.9 | 12 | 0.56444 | [13 empty] | 7.33 | 0.068 | 1 | 4.2 | 18.8 |  |  |  | 7.29 | 0.072 | 1 | 3.7 | 20.2 |  |  |  | 4.2 | 3.8 | 2.8 | [55 empty] | 13:00 | 0.62 | 11 | 23.1273 | 14.3389 | 6.04 | 18.54 | 10 | 1.4339 | 15 | 6.5 | 0.43239 | 13:00 | 0.7 | 11 | 23.1273 | 16.1891 | 6.09 | 18.8 | 10 | 1.6189 | 15 | 6.5 | 0.43239 | 13:00 | 0.58 | 12 | 22.5 | 13.05 | 6.19 | 19.9 | 10 | 1.305 | 15 | 6.5 | 0.44444
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.42 | 16 | 16 | 11.2 | 106 | 173 | 19.6 | 0.482 |  | 5.96 | 10 | 0.076 | 6.01 | 10 |  | 5.99 | 9 | [8 empty] | 0.072 | [14 empty] | 0.046 | 1 | 0.4 |  | 0.068 | 0.011 | 1 | 0.36 |  | 0.051 | 1 | 0.65 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.31 | 0.065 | 1 | 4.3 | 18.9 |  |  |  | 7.23 | 0.063 | 1 | 3.9 | 20.2 |  |  |  | 4.2 | 3.8 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.41 | 16 | 16 | 11.6 | 110 | 180 | 19.8 | 0.493 |  | 6 | 10 | 0.072 | 6.05 | 10 |  | 6.02 | 10 | [8 empty] | 0.065 | [14 empty] | 0.037 | 1 | 0.39 |  | 0.066 | 0.013 | 1 | 0.36 |  | 0.048 | 1 | 0.49 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.054 | [9 empty] | 6.08 | 0.41 | 5 | 0.62 | 18.8 | 11 | 0.55239 |  | 6.09 | 0.376 | 5 | 0.6 | 18.8 | 11 | 0.55239 | 6.12 | 0.407 | 3 | 0.54 | 20.1 | 12.5 | 0.44407 |  |  |  | 0.009 | [9 empty] | 7.38 | 0.069 | 1 | 4.2 | 18.9 | 22 | 36 | 0.016 | 7.27 | 0.07 | 1 | 3.8 | 20.1 | 22 | 36 | 0.011 | 4.2 | 3.8 | 3 | [55 empty] | 21:00 | 0.62 | 11 | 23.1273 | 14.3389 | 6.08 | 18.8 | 10 | 1.4339 | 15 | 6.5 | 0.43239 | 21:00 | 0.6 | 11 | 23.1273 | 13.8764 | 6.09 | 18.8 | 10 | 1.3876 | 15 | 6.5 | 0.43239 | 21:00 | 0.54 | 12.5 | 21.6 | 11.664 | 6.12 | 20.1 | 7 | 1.6663 | 20 | 6.5 | 0.32407
22:00 | [72 empty] | DOSE |  | TOTAL | 43 | 43 | 47 | 133 | 41 | 41 | 45 | 127 | 0 | 60.9941 | 0 | 57.7066 | 118.7006 | 6.5606 | TOTAL | 305.8322 | 39228.9596 | 0 | 3856.9163 | 0 | 0 | 0 | 28.1225 | 28.1437 | 26.2228 | 7.4701 | 7.2581 | 8.0344 | 1.6881 | 1.561 | 1.4977 | 1.311 | 1.4022 | 1.4117 | 4.9458 | 10 | 0.20072 | 0.20072 | 0.20118 | 4.3269 | 1.9806 | 0.38783 | 16.536 | 2.7188 | 26.7086 | 4.413 | 1.9713 | 0.39786 | 16.92 | 2.3933 | 37.104 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.42 | 16 | 16 | 11.7 | 108 | 175 | 19.6 | 0.488 |  | 6 | 10 | 0.079 | 6.08 | 10 |  | 6.06 | 10 | [8 empty] | 0.069 | [14 empty] | 0.032 | 1 | 0.38 |  | 0.066 | 0.011 | 1 | 0.39 |  | 0.048 | 1 | 0.5 | [22 empty] | AVERAGE | 10.75 | 10.75 | 11.75 | 33.25 | 10.25 | 10.25 | 11.25 | 31.75 |  | 15.2485 |  | 14.4266 | 29.6752 | 1.6402 | AVERAGE | 76.4581 | 9807.2399 |  | 964.2291 | 0 | 0 | 0 | 7.0306 | 7.0359 | 6.5557 | 1.8675 | 1.8145 | 2.0086 | 0.42202 | 0.39025 | 0.37443 | 0.32776 | 0.35056 | 0.35293 | 1.2365 | 2.5 | 0.050179 | 0.050179 | 0.050295 | 1.0817 | 0.49515 | 0.096958 | 4.134 | 0.67969 | 6.6772 | 1.1033 | 0.49283 | 0.099465 | 4.23 | 0.59832 | 9.276 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.64 | 98 | 95 | 66.6 | 666 | 1045 | 117.8 | 2.943 | 0.106 | 36.1 | 59 | 0.454 | 36.34 | 58 | 0 | 36.21 | 59 | 0 | 24.3 | 1.893 | 19 | 2.4 | 74.44 | 43 | 2.1703 | 0.42 | 24.41 | 1.864 | 19 | 2.44 | 74.9 | 43 | 2.1703 | 24.52 | 1.459 | 12 | 2.36 | 79.9 | 47.5 | 1.9781 | 0.2 | 7 | 1.91 | 0.015 | 0.406 | 0.082 | 7 | 2.24 | 0.018 | 0.338 | 7 | 3.54 | 0.003 | 44.61 | 0.413 | 8 | 25.5 | 112.7 | 42 | 70 | 0.028 | 44.43 | 0.404 | 8 | 23.6 | 118.9 | 43 | 72 | 0.019 | 25.3 | 23.1 | 19 |  |  | MINIMUM | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 14.5656 |  | 12.4531 | 27.0187 | 1.5134 | MINIMUM | 74.7879 | 9715.0088 |  | 951.5419 |  |  |  | 6.4776 | 6.1274 | 5.9572 | 1.7805 | 1.6957 | 1.974 | 0.41489 | 0.38377 | 0.33087 | 0.32154 | 0.34038 | 0.34513 | 1.2365 | 1 | 0.049981 | 0.049981 | 0.050005 | 1.0647 | 0.48326 | 0.096324 | 4.0715 | 0.54306 | 6.6035 | 1.0947 | 0.48207 | 0.096324 | 3.9925 | 0.57518 | 9.134 |  | MIN | 0.6 | 11 | 23.1273 | 13.8764 | 6.08 | 18.5 | 10 | 1.3876 |  |  |  | MIN | 0.53 | 10 | 25.44 | 13.4832 | 6.11 | 18.7 | 10 | 1.3483 |  |  |  | MIN | 0.58 | 12 | 22.5 | 13.05 | 6.19 | 19.9 | 10 | 1.305 |  |  |  | 1.305
AVERAGE | 6.44 | 16.3333 | 15.8333 | 11.1 | 111 | 174.1667 | 19.6333 | 0.4905 | 0.053 | 6.0167 | 9.8333 | 0.075667 | 6.0567 | 9.6667 |  | 6.035 | 9.8333 |  | 6.075 | 0.47325 | 4.75 | 0.6 | 18.61 | 10.75 | 0.54256 | 0.07 | 6.1025 | 0.466 | 4.75 | 0.61 | 18.725 | 10.75 | 0.54256 | 6.13 | 0.36475 | 3 | 0.59 | 19.975 | 11.875 | 0.49454 | 0.033333 | 1.1667 | 0.31833 | 0.0075 | 0.067667 | 0.013667 | 1.1667 | 0.37333 | 0.018 | 0.056333 | 1.1667 | 0.59 |  | 7.435 | 0.068833 | 1.3333 | 4.25 | 18.7833 | 21 | 35 | 0.014 | 7.405 | 0.067333 | 1.3333 | 3.9333 | 19.8167 | 21.5 | 36 | 0.0095 | 4.2167 | 3.85 | 3.1667 |  |  | MAXIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 16.1453 |  | 16.4851 | 32.4605 | 2.0203 | MAXIMUM | 79.8217 | 10083.9332 |  | 976.9163 |  |  |  | 8.4882 | 8.7535 | 8.024 | 1.9077 | 1.9077 | 2.0349 | 0.43044 | 0.39933 | 0.41489 | 0.3371 | 0.36303 | 0.36303 | 1.2365 | 5 | 0.050246 | 0.050246 | 0.050464 | 1.0947 | 0.49911 | 0.098859 | 4.1865 | 0.76029 | 6.7388 | 1.1194 | 0.49714 | 0.10051 | 4.5487 | 0.61484 | 9.4482
MINIMUM | 6.41 | 16 | 15 | 10.2 | 106 | 170 | 19.5 | 0.476 | 0.052 | 5.93 | 9 | 0.07 | 6 | 9 |  | 5.99 | 9 |  | 6.04 | 0.41 | 4 | 0.56 | 18.5 | 10 | 0.51308 | 0.065 | 6.09 | 0.376 | 4 | 0.53 | 18.6 | 10 | 0.51308 | 6.1 | 0.305 | 3 | 0.54 | 19.8 | 11 | 0.40519 | 0.027 | 1 | 0.2 | 0.006 | 0.066 | 0.011 | 1 | 0.26 | 0.018 | 0.04 | 1 | 0.4 |  | 7.23 | 0.065 | 1 | 4.1 | 18.4 | 20 | 34 | 0.012 | 7.23 | 0.063 | 1 | 3.7 | 18.9 | 21 | 36 | 0.008 | 4.2 | 3.7 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 41600 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 1040 | 1058 | 1720 | 1670 | 2030 | 3180 | 2940 | 2830 | 2470 | 2886 | 2906 | 2600 | 0 | 3900 | 3900 | 4290 | 386 | 469 | 55 | 6880 | 1220 | 1877 | 216 | 256 | 31 | 3600 | 590 | 1430
MAXIMUM | 6.51 | 17 | 16 | 11.7 | 120 | 180 | 19.8 | 0.512 | 0.054 | 6.14 | 10 | 0.084 | 6.14 | 10 |  | 6.1 | 10 |  | 6.1 | 0.552 | 6 | 0.62 | 18.8 | 11 | 0.55239 | 0.08 | 6.12 | 0.567 | 6 | 0.7 | 18.8 | 11 | 0.55239 | 6.19 | 0.407 | 3 | 0.65 | 20.1 | 12.5 | 0.56444 | 0.046 | 2 | 0.4 | 0.009 | 0.07 | 0.019 | 2 | 0.5 | 0.018 | 0.092 | 2 | 0.82 |  | 7.98 | 0.073 | 2 | 4.4 | 18.9 | 22 | 36 | 0.016 | 7.63 | 0.072 | 2 | 4.4 | 20.2 | 22 | 36 | 0.011 | 4.3 | 4 | 3.9 | [17 empty] | AVERAGE | 10400 | [6 empty] | 259.5 | 260 | 264.5 | 430 | 417.5 | 507.5 | 795 | 735 | 707.5 | 617.5 | 721.5 | 726.5 | 650 |  | 975 | 975 | 1072.5 | 96.5 | 117.25 | 13.75 | 1720 | 305 | 469.25 | 54 | 64 | 7.75 | 900 | 147.5 | 357.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0361 |  | TOTAL AVG COAG ALK: |  |  |  | 9.7778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.567 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.53 | [5 empty] | 6.1025 |  |  |  |  | 0.092 |  |  |  |  | 0.53 | [6 empty] | 0.092 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 9600 | [6 empty] | 222 | 210 | 225 | 400 | 400 | 480 | 750 | 700 | 580 | 580 | 700 | 700 | 650 |  | 900 | 900 | 1000 | 88 | 106 | 13 | 1600 | 250 | 430 | 50 | 60 | 7 | 820 | 140 | 340
[90 empty] | MAXIMUM | 11100 | [6 empty] | 320 | 330 | 330 | 450 | 450 | 520 | 830 | 750 | 800 | 650 | 750 | 750 | 650 |  | 1000 | 1000 | 1100 | 100 | 121 | 14 | 1780 | 350 | 485 | 56 | 66 | 8 | 940 | 155 | 370
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.245 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23770221 |  | END: | 23770230 |  |  | Alum | 9262 | 8673 | 8673 | 8954 | 8954 | 34.3 | [44 empty] | 0.58 | 12 | 22.5 | 13.05 | 6.19 | 19.9 | 10 | 1.305
[73 empty] | FINISHED 2 | 15.444 |  | TOTAL MGD: |  | 14.236 |  |  | FINISHED SOUTH 2 |  | START: | 43234335 |  | END: | 43248571 |  |  | Caustic | 6058 | 8447 | 8447
[73 empty] | TOTAL RAW | 33.593 |  | TOTAL MGD: |  | 4.582 |  |  | FINISHED CONWAY |  | START: | 9984945 |  | END: | 9989527 |  |  | Hypochlorite | 19.5 |  | 46
[76 empty] | TOTAL MGD: |  | 10.862 |  |  | FINISHED PERRY |  | START: | 33232188 |  | END: | 33243050 |  |  | Phosphate | 2540
[76 empty] | TOTAL MGD: |  | 10.913 |  |  | RAW PLANT 1 |  | START: | 30409810 |  | END: | 30420723 |  |  | Fluoride | 2936 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.654 |  |  | RAW PLANT 2 |  | START: | 30370608 |  | END: | 30381262 |  |  | Cal~Flo | 7.16 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.026 |  |  | RAW PLANT 3 |  | START: | 6876563 |  | END: | 6888589 |  |  | Zinc | 1475
[76 empty] | TOTAL MGD: |  | 0.813 |  |  | DECANT |  | START: | 1806430 |  | END: | 1807243 |  |  | Polymer | 20
[76 empty] | TOTAL MGD: |  | 0.96539 |  |  | BLOW DOWN |  | START: | 9050.7087 |  | END: | 9051.674 |  |  | NH3 | 12.45 |  | BI-SUL | 800
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 980
23770230
43248571
9989527
33243050
30420723
30381262
6888589
1807243
9051.674
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 10
DATE: | 2018-11-10 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-10 | [23 empty] | DATE: | 2018-11-10
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-10 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43414.0099 | 1,2,3,6 | 52 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | ,2,3 | 15.7176 | 1,3 | 16.4851 | 32.2027 | 2.0203 | 43414.0099 | 79.8217 | 9715.0088 | 0 | 976.9163 | 0 | 0 | 0 | 8.4882 | 8.7535 | 8.024 | 1.9077 | 1.7805 | 2.0127 | 0.41489 | 0.38896 | 0.41489 | 0.32154 | 0.34228 | 0.34704 | 1.2365 | 1 | 0.050246 | 0.050246 | 0.050464 | 1.0947 | 0.49911 | 0.096324 | 4.1815 | 0.76029 | 6.7388 | 1.0995 | 0.49714 | 0.10051 | 4.2994 | 0.59501 | 9.134 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.98 | 0.513 | 6 | 0.6 | 18.7 | 11 | 0.46591 |  | 6.06 | 0.463 | 6 | 0.62 | 18.8 | 11 | 0.55239 | 6.17 | 0.369 | 2 | 0.69 | 20.2 | 12.5 | 0.44407 | [13 empty] | 7.68 | 0.069 | 1 | 4.2 | 18.8 |  |  |  | 7.57 | 0.07 | 1 | 4.4 | 20 |  |  |  | 4.1 | 3.5 | 3 | [18 empty] | 11100 | [6 empty] | 320 | 330 | 330 | 450 | 420 | 520 | 800 | 750 | 800 | 620 | 720 | 730 | 650 |  | 1000 | 1000 | 1100 | 100 | 121 | 14 | 1750 | 350 | 485 | 55 | 66 | 8 | 920 | 150 | 360 |  | 1:00 | 0.6 | 11 | 23.1273 | 13.8764 | 5.98 | 18.7 | 8 | 1.7345 | 15 | 6 | 0.34591 | 1:00 | 0.62 | 11 | 23.1273 | 14.3389 | 6.06 | 18.8 | 10 | 1.4339 | 15 | 6.5 | 0.43239 | 1:00 | 0.69 | 12.5 | 21.6 | 14.904 | 6.17 | 20.2 | 7 | 2.1291 | 20 | 6.5 | 0.32407
2:00 | [72 empty] | 43414.3316 | 1,2,3,6 | 50 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | ,2,3 | 15.7176 | 1,3 | 16.4851 | 32.2027 | 2.9534 | 43414.3316 | 80.5408 | 9223.1096 | 0 | 856.3877 | 0 | 0 | 0 | 9.8145 | 9.5492 | 8.9966 | 1.9077 | 1.9077 | 2.1289 | 0.41489 | 0.39414 | 0.40451 | 0.36303 | 0.33277 | 0.33277 | 1.2365 | 3 | 0.049743 | 0.049743 | 0.050464 | 1.0947 | 0.49499 | 0.089444 | 4.0946 | 0.69512 | 6.7388 | 1.1194 | 0.49714 | 0.10051 | 4.4184 | 0.68228 | 9.134 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.38 | 16 | 16 | 11.6 | 120 | 173 | 19.8 | 0.505 |  | 6.14 | 10 | 0.082 | 6.18 | 10 |  | 6.15 | 10 | [8 empty] | 0.07 | [14 empty] | 0.032 | 1 | 0.4 |  | 0.076 | 0.012 | 1 | 0.36 |  | 0.05 | 1 | 0.39 | [38 empty] | 11200 | [6 empty] | 370 | 360 | 370 | 450 | 450 | 550 | 800 | 760 | 780 | 700 | 700 | 700 | 650 |  | 990 | 990 | 1100 | 100 | 120 | 13 | 1710 | 320 | 485 | 56 | 66 | 8 | 950 | 172 | 360 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43414.5266 | 1,2,3,6 | 50 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 15.7176 | 1,3 | 16.4851 | 32.2027 | 2.9534 | 43414.5266 | 80 | 7378.4876 | 0 | 856.3877 | 0 | 0 | 0 | 8.5 | 8.2 | 6.5 | 1.8 | 1.8 | 2 | 0.41 | 0.39 | 0.41 | 0.33 | 0.35 | 0.35 | 1.24 | 3 | 0.05 | 0.05 | 0.05 | 1.1 | 0.5 | 0.1 | 4.1 | 0.76 | 6.7 | 0 | 0 | 0 | 0.65 | 0 | 0 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.71 | 0.069 | 1 | 4.4 | 18.9 |  |  |  | 7.9 | 0.071 | 1 | 4.3 | 20 |  |  |  | 4.1 | 3.6 | 3 | [18 empty] | 10437 | [6 empty] | 300 | 290 | 250 | 400 | 400 | 485 | 740 | 700 | 740 | 600 | 690 | 700 | 650 |  | 930 | 930 | 1020 | 94 | 114 | 14 | 1600 | 326 | 450 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43414.5866 | 1,2,3,6 | 50 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 15.7176 | 1,3 | 16.4851 | 32.2027 | 2.9534 | 43414.5866 | 79.9948 | 7378.4876 | 0 | 856.3877 | 0 | 0 | 0 | 8.4985 | 8.2152 | 6.4553 | 1.8168 | 1.8168 | 1.9989 | 0.40985 | 0.3877 | 0.40985 | 0.33231 | 0.34834 | 0.35339 | 1.2365 | 0 | 0.050066 | 0.050066 | 0.049827 | 1.1025 | 0.50383 | 0.1032 | 4.1039 | 0.75874 | 6.6991 | 1.1069 | 0.49728 | 0.10703 | 4.5359 | 0.7096 | 9.1857 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.42 | 18 | 16 | 11.7 | 113 | 174 | 19.8 | 0.487 |  | 6.02 | 12 | 0.073 | 6.16 | 12 |  | 6.13 | 12 | [8 empty] | 0.066 | [14 empty] | 0.033 | 1 | 0.36 |  | 0.067 | 0.015 | 1 | 0.34 |  | 0.052 | 1 | 0.7 | [38 empty] | 10437 | [6 empty] | 300 | 290 | 250 | 400 | 400 | 485 | 740 | 700 | 740 | 600 | 690 | 700 | 650 |  | 930 | 930 | 1020 | 94 | 114 | 14 | 1600 | 326 | 450 | 52 | 62 | 8 | 920 | 168 | 340 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43414.8193 | 1,2,3,6 | 40 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.911 | 1,3 | 12.0485 | 24.9595 | 2.1197 | 43414.8193 | 80.8609 | 6640.6388 | 0 | 856.3877 | 0 | 0 | 0 | 4.2492 | 3.966 | 3.8732 | 2.0439 | 2.0439 | 2.0608 | 0.3877 | 0.33231 | 0.36 | 0.33231 | 0.36853 | 0.36853 | 1.2365 | 3 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.1032 | 2.7138 | 0.76805 | 5.5826 | 1.0643 | 0.49728 | 0.093649 | 4.6226 | 0.63358 | 7.4296 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.051 | [9 empty] | 5.9 | 0.711 | 5 | 0.57 | 18.7 | 11 | 0.46591 |  | 6.22 | 0.674 | 5 | 0.61 | 18.7 | 11 | 0.55239 | 6.22 | 0.377 | 3 | 0.75 | 20 | 12 | 0.43111 |  |  |  | 0.008 | [9 empty] | 7.81 | 0.066 | 1 | 4.5 | 18.9 | 23 | 34 | 0.017 | 7.77 | 0.074 | 1 | 3.7 | 19.8 | 23 | 35 | 0.011 | 4.2 | 3.6 | 3.9 | [18 empty] | 10550 | [6 empty] | 150 | 140 | 150 | 450 | 450 | 500 | 700 | 600 | 650 | 600 | 730 | 730 | 650 |  | 950 | 950 | 1000 | 95 | 113 | 14 | 1050 | 330 | 375 | 50 | 62 | 7 | 950 | 150 | 275 |  | 9:00 | 0.57 | 11 | 23.1273 | 13.1825 | 5.9 | 18.7 | 8 | 1.6478 | 15 | 6 | 0.34591 | 9:00 | 0.61 | 11 | 23.1273 | 14.1076 | 6.22 | 18.7 | 10 | 1.4108 | 15 | 6.5 | 0.43239 | 9:00 | 0.75 | 12 | 22.5 | 16.875 | 6.22 | 20 | 7 | 2.4107 | 20 | 6.5 | 0.31111
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.41 | 17 | 17 | 11 | 113 | 174 | 19.7 | 0.491 |  | 5.99 | 11 | 0.076 | 6.01 | 11 |  | 6.05 | 11 | [8 empty] | 0.068 | [14 empty] | 0.027 | 1 | 0.26 |  | 0.072 | 0.01 | 1 | 0.28 |  | 0.044 | 1 | 0.61 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.41 | 0.804 | 6 | 0.45 | 18.7 | 10.3 | 0.52487 |  | 6.39 | 0.796 | 6 | 0.46 | 18.9 | 10.3 | 0.52487 | 6.3 | 0.437 | 3 | 0.6 | 19.9 | 11.3 | 0.53852 | [13 empty] | 8.32 | 0.078 | 1 | 4.6 | 18.9 |  |  |  | 7.82 | 0.082 | 1 | 4.2 | 20.1 |  |  |  | 4.3 | 3.5 | 2.5 | [55 empty] | 13:00 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.41 | 18.7 | 10 | 1.1115 | 15 | 6.5 | 0.40487 | 13:00 | 0.46 | 10.3 | 24.699 | 11.3616 | 6.39 | 18.9 | 10 | 1.1362 | 15 | 6.5 | 0.40487 | 13:00 | 0.6 | 11.3 | 23.8938 | 14.3363 | 6.3 | 19.9 | 10 | 1.4336 | 15 | 6.5 | 0.41852
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.46 | 18 | 16 | 11 | 108 | 168 | 19.7 | 0.484 |  | 6 | 10 | 0.071 | 6.03 | 11 |  | 6.09 | 11 | [8 empty] | 0.064 | [14 empty] | 0.029 | 1 | 0.13 |  | 0.071 | 0.017 | 1 | 0.16 |  | 0.056 | 1 | 0.33 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 8.47 | 0.081 | 1 | 4.1 | 19 |  |  |  | 8.34 | 0.084 | 1 | 4.2 | 20 |  |  |  | 4.2 | 3.8 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.44 | 16 | 16 | 10.7 | 109 | 179 | 19.7 | 0.513 |  | 6.1 | 10 | 0.074 | 6.08 | 11 |  | 6.07 | 11 | [8 empty] | 0.066 | [14 empty] | 0.032 | 1 | 0.2 |  | 0.071 | 0.02 | 1 | 0.23 |  | 0.047 | 1 | 0.4 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.049 | [9 empty] | 6.17 | 0.598 | 6 | 0.59 | 18.5 | 10 | 0.51308 |  | 6.18 | 0.42 | 5 | 0.6 | 18.8 | 10 | 0.51308 | 6.24 | 0.732 | 3 | 0.6 | 19.8 | 11 | 0.52741 |  |  |  | 0.013 | [9 empty] | 7.69 | 0.083 | 1 | 4.1 | 18.8 | 23 | 33 | 0.016 | 8.09 | 0.09 | 1 | 3.9 | 19.5 | 23 | 33 | 0.012 | 4.2 | 3.8 | 2.7 | [55 empty] | 21:00 | 0.59 | 10 | 25.44 | 15.0096 | 6.17 | 18.5 | 10 | 1.501 | 15 | 6.5 | 0.39308 | 21:00 | 0.6 | 10 | 25.44 | 15.264 | 6.18 | 18.8 | 10 | 1.5264 | 15 | 6.5 | 0.39308 | 21:00 | 0.6 | 11 | 24.5455 | 14.7273 | 6.24 | 19.8 | 10 | 1.4727 | 15 | 6.5 | 0.40741
22:00 | [72 empty] | DOSE |  | TOTAL | 52.9 | 52.9 | 57.9 | 163.7 | 50.4 | 50.4 | 55.4 | 156.2 | 0 | 75.7814 | 0 | 77.989 | 153.7704 | 13.0003 | TOTAL | 401.2181 | 40335.7324 | 0 | 4402.467 | 0 | 0 | 0 | 39.5504 | 38.6839 | 33.8492 | 9.4761 | 9.349 | 10.2013 | 2.0373 | 1.8931 | 1.9993 | 1.6792 | 1.7419 | 1.7517 | 6.1858 | 10 | 0.2512 | 0.2512 | 0.2496 | 5.5061 | 2.4973 | 0.49218 | 19.1937 | 3.7422 | 32.4592 | 4.39 | 1.9888 | 0.4017 | 18.5264 | 2.6205 | 34.8834 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.44 | 16 | 16 | 10.3 | 117 | 173 | 19.3 | 0.508 |  | 6 | 10 | 0.079 | 6.03 | 10 |  | 6 | 10 | [8 empty] | 0.069 | [14 empty] | 0.03 | 1 | 0.2 |  | 0.074 | 0.02 | 1 | 0.24 |  | 0.04 | 1 | 0.43 | [22 empty] | AVERAGE | 10.58 | 10.58 | 11.58 | 32.74 | 10.08 | 10.08 | 11.08 | 31.24 |  | 15.1563 |  | 15.5978 | 30.7541 | 2.6001 | AVERAGE | 80.2436 | 8067.1465 |  | 880.4934 | 0 | 0 | 0 | 7.9101 | 7.7368 | 6.7698 | 1.8952 | 1.8698 | 2.0403 | 0.40746 | 0.37862 | 0.39985 | 0.33584 | 0.34839 | 0.35035 | 1.2372 | 2 | 0.050239 | 0.050239 | 0.049921 | 1.1012 | 0.49947 | 0.098436 | 3.8387 | 0.74844 | 6.4918 | 0.87801 | 0.39777 | 0.08034 | 3.7053 | 0.52409 | 6.9767 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.55 | 101 | 97 | 66.3 | 680 | 1041 | 118 | 2.988 | 0.1 | 36.25 | 63 | 0.455 | 36.49 | 65 | 0 | 36.49 | 65 | 0 | 24.46 | 2.626 | 23 | 2.21 | 74.6 | 42.3 | 1.9698 | 0.403 | 24.85 | 2.353 | 22 | 2.29 | 75.2 | 42.3 | 2.1427 | 24.93 | 1.915 | 11 | 2.64 | 79.9 | 46.8 | 1.9411 | 0.183 | 6 | 1.55 | 0.021 | 0.431 | 0.094 | 6 | 1.61 | 0 | 0.289 | 6 | 2.86 | 0 | 47.68 | 0.446 | 6 | 25.9 | 113.3 | 46 | 67 | 0.033 | 47.49 | 0.471 | 6 | 24.7 | 119.4 | 46 | 68 | 0.023 | 25.1 | 21.8 | 17.8 |  |  | MINIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 12.911 |  | 12.0485 | 24.9595 | 2.0203 | MINIMUM | 79.8217 | 6640.6388 |  | 856.3877 |  |  |  | 4.2492 | 3.966 | 3.8732 | 1.8 | 1.7805 | 1.9989 | 0.3877 | 0.33231 | 0.36 | 0.32154 | 0.33277 | 0.33277 | 1.2365 | 0 | 0.049743 | 0.049743 | 0.04885 | 1.0947 | 0.49499 | 0.089444 | 2.7138 | 0.69512 | 5.5826 | 0 | 0 | 0 | 0.65 | 0 | 0 |  | MIN | 0.45 | 10.3 | 24.699 | 11.1146 | 6.41 | 18.7 | 10 | 1.1115 |  |  |  | MIN | 0.46 | 10.3 | 24.699 | 11.3616 | 6.39 | 18.9 | 10 | 1.1362 |  |  |  | MIN | 0.6 | 11.3 | 23.8938 | 14.3363 | 6.3 | 19.9 | 10 | 1.4336 |  |  |  | 1.1115
AVERAGE | 6.425 | 16.8333 | 16.1667 | 11.05 | 113.3333 | 173.5 | 19.6667 | 0.498 | 0.05 | 6.0417 | 10.5 | 0.075833 | 6.0817 | 10.8333 |  | 6.0817 | 10.8333 |  | 6.115 | 0.6565 | 5.75 | 0.5525 | 18.65 | 10.575 | 0.49244 | 0.067167 | 6.2125 | 0.58825 | 5.5 | 0.5725 | 18.8 | 10.575 | 0.53568 | 6.2325 | 0.47875 | 2.75 | 0.66 | 19.975 | 11.7 | 0.48528 | 0.0305 | 1 | 0.25833 | 0.0105 | 0.071833 | 0.015667 | 1 | 0.26833 |  | 0.048167 | 1 | 0.47667 |  | 7.9467 | 0.074333 | 1 | 4.3167 | 18.8833 | 23 | 33.5 | 0.0165 | 7.915 | 0.0785 | 1 | 4.1167 | 19.9 | 23 | 34 | 0.0115 | 4.1833 | 3.6333 | 2.9667 |  |  | MAXIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 15.7176 |  | 16.4851 | 32.2027 | 2.9534 | MAXIMUM | 80.8609 | 9715.0088 |  | 976.9163 |  |  |  | 9.8145 | 9.5492 | 8.9966 | 2.0439 | 2.0439 | 2.1289 | 0.41489 | 0.39414 | 0.41489 | 0.36303 | 0.36853 | 0.36853 | 1.24 | 3 | 0.051143 | 0.051143 | 0.050464 | 1.1142 | 0.50383 | 0.1032 | 4.1815 | 0.76805 | 6.7388 | 1.1194 | 0.49728 | 0.10703 | 4.6226 | 0.7096 | 9.1857
MINIMUM | 6.38 | 16 | 16 | 10.3 | 108 | 168 | 19.3 | 0.484 | 0.049 | 5.99 | 10 | 0.071 | 6.01 | 10 |  | 6 | 10 |  | 5.9 | 0.513 | 5 | 0.45 | 18.5 | 10 | 0.46591 | 0.064 | 6.06 | 0.42 | 5 | 0.46 | 18.7 | 10 | 0.51308 | 6.17 | 0.369 | 2 | 0.6 | 19.8 | 11 | 0.43111 | 0.027 | 1 | 0.13 | 0.008 | 0.067 | 0.01 | 1 | 0.16 |  | 0.04 | 1 | 0.33 |  | 7.68 | 0.066 | 1 | 4.1 | 18.8 | 23 | 33 | 0.016 | 7.57 | 0.07 | 1 | 3.7 | 19.5 | 23 | 33 | 0.011 | 4.1 | 3.5 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 53724 | 0 | 0 | 0 | 0 | 0 | 0 | 1440 | 1410 | 1350 | 2150 | 2120 | 2540 | 3780 | 3510 | 3710 | 3120 | 3530 | 3560 | 3250 | 0 | 4800 | 4800 | 5240 | 483 | 582 | 69 | 7710 | 1652 | 2245 | 213 | 256 | 31 | 3740 | 640 | 1335
MAXIMUM | 6.46 | 18 | 17 | 11.7 | 120 | 179 | 19.8 | 0.513 | 0.051 | 6.14 | 12 | 0.082 | 6.18 | 12 |  | 6.15 | 12 |  | 6.41 | 0.804 | 6 | 0.6 | 18.7 | 11 | 0.52487 | 0.07 | 6.39 | 0.796 | 6 | 0.62 | 18.9 | 11 | 0.55239 | 6.3 | 0.732 | 3 | 0.75 | 20.2 | 12.5 | 0.53852 | 0.033 | 1 | 0.4 | 0.013 | 0.076 | 0.02 | 1 | 0.36 |  | 0.056 | 1 | 0.7 |  | 8.47 | 0.083 | 1 | 4.6 | 19 | 23 | 34 | 0.017 | 8.34 | 0.09 | 1 | 4.4 | 20.1 | 23 | 35 | 0.012 | 4.3 | 3.8 | 3.9 | [17 empty] | AVERAGE | 10744.8 | [6 empty] | 288 | 282 | 270 | 430 | 424 | 508 | 756 | 702 | 742 | 624 | 706 | 712 | 650 |  | 960 | 960 | 1048 | 96.6 | 116.4 | 13.8 | 1542 | 330.4 | 449 | 42.6 | 51.2 | 6.2 | 748 | 128 | 267
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0683 |  | TOTAL AVG COAG ALK: |  |  |  | 10.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.804 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.45 | [5 empty] | 6.1867 |  |  |  |  | 0.056 |  |  |  |  | 0.45 | [6 empty] | 0.056 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 10437 | [6 empty] | 150 | 140 | 150 | 400 | 400 | 485 | 700 | 600 | 650 | 600 | 690 | 700 | 650 |  | 930 | 930 | 1000 | 94 | 113 | 13 | 1050 | 320 | 375 | 0 | 0 | 0 | 0 | 0 | 0
[90 empty] | MAXIMUM | 11200 | [6 empty] | 370 | 360 | 370 | 450 | 450 | 550 | 800 | 760 | 800 | 700 | 730 | 730 | 650 |  | 1000 | 1000 | 1100 | 100 | 121 | 14 | 1750 | 350 | 485 | 56 | 66 | 8 | 950 | 172 | 360
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.589 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23770230 |  | END: | 23770239 |  |  | Alum | 9266 | 9389 | 9389 | 9488 | 9488 | 20.4 | [44 empty] | 0.45 | 10.3 | 24.699 | 11.1146 | 6.41 | 18.7 | 10 | 1.1115
[73 empty] | FINISHED 2 | 15.219 |  | TOTAL MGD: |  | 13.58 |  |  | FINISHED SOUTH 2 |  | START: | 43248571 |  | END: | 43262151 |  |  | Caustic | 5672 | 8342 | 8342
[73 empty] | TOTAL RAW | 31.877 |  | TOTAL MGD: |  | 4.653 |  |  | FINISHED CONWAY |  | START: | 9989527 |  | END: | 9994180 |  |  | Hypochlorite | 16.8 |  | 44.5
[76 empty] | TOTAL MGD: |  | 10.566 |  |  | FINISHED PERRY |  | START: | 33243050 |  | END: | 33253616 |  |  | Phosphate | 2493
[76 empty] | TOTAL MGD: |  | 10.373 |  |  | RAW PLANT 1 |  | START: | 30420723 |  | END: | 30431096 |  |  | Fluoride | 2936 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.71 |  |  | RAW PLANT 2 |  | START: | 30381262 |  | END: | 30391972 |  |  | Cal~Flo | 12.87 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.794 |  |  | RAW PLANT 3 |  | START: | 6888589 |  | END: | 6899383 |  |  | Zinc | 1482
[76 empty] | TOTAL MGD: |  | 1.162 |  |  | DECANT |  | START: | 1807243 |  | END: | 1808405 |  |  | Polymer | 20
[76 empty] | TOTAL MGD: |  | 1.4405 |  |  | BLOW DOWN |  | START: | 9051.674 |  | END: | 9053.1146 |  |  | NH3 | 12.22 |  | BI-SUL | 775
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 856
23770239
43262151
9994180
33253616
30431096
30391972
6899383
1808405
9053.1146
1 | 1,5,6 |  |  | 28 | 8.8 | 8 |  | 9.6 |  | 26.4 | 8.3 | 7.5 | 9.1 | 24.9 | 7 | 19.4256 | 0 | 0.02772 | 19.4533 | 1 | 0 | 1900 | 650 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | [5 empty] | 0 | 0 |  | 0 | 0.3 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.4 | #DIV/0! | 0
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 11
DATE: | 2018-11-11 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-11 | [23 empty] | DATE: | 2018-11-11
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-11 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43415.0068 | 1,2,3,6 | 40 | 10.3 | 10.3 | 11.3 | 32 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.911 | 1,3 | 12.0485 | 24.9595 | 2.1197 | 43415.0068 | 80.8609 | 6640.6388 | 0 | 856.3877 | 0 | 0 | 0 | 4.2492 | 3.966 | 3.8732 | 2.0439 | 2.0439 | 2.0608 | 0.3877 | 0.33231 | 0.36 | 0.33231 | 0.36853 | 0.36853 | 1.2365 | 3 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.1032 | 2.7138 | 0.76805 | 5.5826 | 1.0643 | 0.49728 | 0.093649 | 4.6226 | 0.63358 | 7.4296 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.13 | 0.536 | 8 | 0.53 | 17.9 | 10 | 0.51308 |  | 6.11 | 0.436 | 5 | 0.62 | 17.8 | 10 | 0.51308 | 6.17 | 0.416 | 3 | 0.61 | 19.3 | 11 | 0.52741 | [13 empty] | 7.23 | 0.08 | 1 | 4.7 | 18.3 |  |  |  | 7.27 | 0.083 | 1 | 4.3 | 19 |  |  |  | 4.2 | 3.9 | 2.9 | [18 empty] | 10550 | [6 empty] | 150 | 140 | 150 | 450 | 450 | 500 | 700 | 600 | 650 | 600 | 730 | 730 | 650 |  | 950 | 950 | 1000 | 95 | 113 | 14 | 1050 | 330 | 375 | 50 | 62 | 7 | 950 | 150 | 275 |  | 1:00 | 0.53 | 10 | 25.44 | 13.4832 | 6.13 | 17.9 | 10 | 1.3483 | 15 | 6.5 | 0.39308 | 1:00 | 0.62 | 10 | 25.44 | 15.7728 | 6.11 | 17.8 | 10 | 1.5773 | 15 | 6.5 | 0.39308 | 1:00 | 0.61 | 11 | 24.5455 | 14.9727 | 6.17 | 19.3 | 10 | 1.4973 | 15 | 6.5 | 0.40741
2:00 | [72 empty] | 43415.3383 | 1,2,3,6 | 40 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | ,2,3 | 13.3546 | 1,3 | 13.0306 | 26.3851 | 2.1197 | 43415.3383 | 80.448 | 7009.5632 | 0 | 856.3877 | 0 | 0 | 0 | 3.5014 | 3.2096 | 3.1831 | 1.9679 | 1.8742 | 1.9925 | 0.39933 | 0.34228 | 0.39933 | 0.40503 | 0.36977 | 0.36977 | 1.3316 | 6 | 0.049981 | 0.051092 | 0.049743 | 1.1131 | 0.5015 | 0.098859 | 4.1865 | 0.72027 | 5.6053 | 1.0947 | 0.49499 | 0.096324 | 4.3763 | 0.70816 | 7.3918 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.46 | 17 | 16 | 10.8 | 122 | 169 | 19.2 | 0.517 |  | 6.09 | 10 | 0.088 | 6.03 | 11 |  | 6.03 | 11 | [8 empty] | 0.073 | [14 empty] | 0.03 | 1 | 0.23 |  | 0.075 | 0.023 | 1 | 0.3 |  | 0.043 | 1 | 0.39 | [38 empty] | 10200 | [6 empty] | 120 | 110 | 120 | 420 | 400 | 470 | 700 | 600 | 700 | 710 | 713 | 713 | 700 |  | 900 | 920 | 990 | 92 | 110 | 13 | 1600 | 300 | 365 | 50 | 60 | 7 | 860 | 163 | 266 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43415.8153 | 1,2,3,6 | 42 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | ,2,3 | 15.2683 | 1,3 | 11.965 | 27.2333 | 2.1182 | 43415.8153 | 80.448 | 7501.4624 | 0 | 951.5419 | 0 | 0 | 0 | 3.5014 | 3.3555 | 3.1831 | 1.6399 | 1.8274 | 1.9925 | 0.39933 | 0.34228 | 0.39933 | 0.39933 | 0.37858 | 0.37858 | 1.712 | 7 | 0.049981 | 0.049981 | 0.050246 | 1.101 | 0.5015 | 0.098859 | 4.0184 | 0.72027 | 5.6053 | 1.0947 | 0.50324 | 0.096324 | 4.0825 | 0.71684 | 7.7253 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.38 | 0.073 | 1 | 4.3 | 18.1 |  |  |  | 7.37 | 0.079 | 1 | 4.3 | 19 |  |  |  | 4.2 | 4 | 3 | [18 empty] | 10200 | [6 empty] | 120 | 115 | 120 | 350 | 390 | 470 | 700 | 600 | 700 | 700 | 730 | 730 | 900 |  | 900 | 900 | 1000 | 91 | 110 | 13 | 1530 | 300 | 365 | 50 | 61 | 7 | 820 | 165 | 278 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.32 | 18 | 16 | 10.2 | 114 | 174 | 18.8 | 0.501 |  | 6.03 | 10 | 0.08 | 6.04 | 11 |  | 6.02 | 10 | [8 empty] | 0.072 | [14 empty] | 0.032 | 1 | 0.21 |  | 0.073 | 0.015 | 1 | 0.48 |  | 0.039 | 1 | 0.64 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.051 | [9 empty] | 6.06 | 0.636 | 7 | 0.53 | 17.1 | 10 | 0.51308 |  | 6.08 | 0.426 | 5 | 0.71 | 17.2 | 10 | 0.51308 | 6.14 | 0.305 | 3 | 0.64 | 18.7 | 11 | 0.52741 |  |  |  | 0.012 |  |  |  |  | 0.021 |  |  |  | 0.007 | 7.21 | 0.071 | 1 | 4.6 | 17.8 | 20 | 36 | 0.019 | 7.2 | 0.067 | 1 | 4.5 | 18.7 | 20 | 36 | 0.021 | 4.4 | 4.1 | 4 | [55 empty] | 9:00 | 0.53 | 10 | 25.44 | 13.4832 | 6.06 | 17.1 | 10 | 1.3483 | 15 | 6.5 | 0.39308 | 9:00 | 0.71 | 10 | 25.44 | 18.0624 | 6.08 | 17.2 | 10 | 1.8062 | 15 | 6.5 | 0.39308 | 9:00 | 0.64 | 11 | 24.5455 | 15.7091 | 6.14 | 18.7 | 10 | 1.5709 | 15 | 6.5 | 0.40741
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.41 | 18 | 16 | 10.2 | 119 | 187 | 18.5 | 0.512 |  | 6.02 | 10 | 0.078 | 6.06 | 10 |  | 6.05 | 10 | [8 empty] | 0.069 | [14 empty] | 0.031 | 1 | 0.2 |  | 0.071 | 0.045 | 1 | 0.52 |  | 0.038 | 1 | 0.61 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.05 | 0.508 | 4 | 0.51 | 17.3 | 9.8 | 0.50522 |  | 6.08 | 0.348 | 4 | 0.6 | 17.2 | 9.8 | 0.50522 | 6.17 | 0.287 | 3 | 0.58 | 18.4 | 11 | 0.52741 | [13 empty] | 7.16 | 0.061 | 1 | 4.4 | 17.4 |  |  |  | 7.21 | 0.07 | 1 | 4 | 19.5 |  |  |  | 4.5 | 4.2 | 2.9 | [55 empty] | 13:00 | 0.51 | 9.8 | 25.9592 | 13.2392 | 6.05 | 17.3 | 10 | 1.3239 | 15 | 6.5 | 0.38522 | 13:00 | 0.6 | 9.8 | 25.9592 | 15.5755 | 6.08 | 17.2 | 10 | 1.5576 | 15 | 6.5 | 0.38522 | 13:00 | 0.58 | 11 | 24.5455 | 14.2364 | 6.17 | 18.4 | 10 | 1.4236 | 15 | 6.5 | 0.40741
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.44 | 18 | 17 | 10.4 | 118 | 170 | 18.5 | 0.5 |  | 6.05 | 11 | 0.075 | 6.04 | 10 |  | 6.01 | 10 | [8 empty] | 0.066 | [14 empty] | 0.029 | 1 | 0.21 |  | 0.07 | 0.032 | 1 | 0.48 |  | 0.039 | 1 | 0.52 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.24 | 0.069 | 1 | 4.3 | 17.5 |  |  |  | 7.24 | 0.063 | 1 | 4.2 | 18.9 |  |  |  | 4.4 | 4.1 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.45 | 17 | 17 | 10.1 | 117 | 170 | 18.5 | 0.499 |  | 6.06 | 10 | 0.08 | 6.1 | 10 |  | 6.07 | 11 | [8 empty] | 0.07 | [14 empty] | 0.04 | 1 | 0.23 |  | 0.074 | 0.037 | 1 | 0.49 |  | 0.04 | 1 | 0.63 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.041 | [9 empty] | 6.16 | 0.413 | 4 | 0.55 | 17 | 10 | 0.51308 |  | 6.17 | 0.276 | 4 | 0.62 | 17 | 10 | 0.51308 | 6.16 | 0.293 | 3 | 0.56 | 18.4 | 11 | 0.52741 |  |  |  | 0.008 | [9 empty] | 7.72 | 0.07 | 2 | 4.4 | 17.4 | 22 | 36 | 0.012 | 7.44 | 0.069 | 1 | 4.3 | 18.8 | 22 | 36 | 0.006 | 4.4 | 4.1 | 3.4 | [55 empty] | 21:00 | 0.55 | 10 | 25.44 | 13.992 | 6.16 | 17 | 10 | 1.3992 | 15 | 6.5 | 0.39308 | 21:00 | 0.62 | 10 | 25.44 | 15.7728 | 6.17 | 17 | 10 | 1.5773 | 15 | 6.5 | 0.39308 | 21:00 | 0.56 | 11 | 24.5455 | 13.7455 | 6.16 | 18.4 | 10 | 1.3745 | 15 | 6.5 | 0.40741
22:00 | [72 empty] | DOSE |  | TOTAL | 30.3 | 30.3 | 33.3 | 94 | 28.8 | 28.8 | 31.8 | 89.4 | 0 | 41.5339 | 0 | 37.044 | 78.5779 | 6.3576 | TOTAL | 241.7569 | 21151.6644 | 0 | 2664.3172 | 0 | 0 | 0 | 11.252 | 10.5311 | 10.2394 | 5.6518 | 5.7455 | 6.0457 | 1.1864 | 1.0169 | 1.1587 | 1.1367 | 1.1169 | 1.1169 | 4.2801 | 16 | 0.1511 | 0.15222 | 0.14884 | 3.3284 | 1.5024 | 0.30092 | 10.9187 | 2.2086 | 16.7931 | 3.2537 | 1.4955 | 0.2863 | 13.0814 | 2.0586 | 22.5467 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.45 | 17 | 16 | 10.2 | 118 | 172 | 18.2 | 0.505 |  | 6.03 | 11 | 0.088 | 6.09 | 10 |  | 6.09 | 11 | [8 empty] | 0.072 | [14 empty] | 0.041 | 1 | 0.16 |  | 0.076 | 0.036 | 1 | 0.4 |  | 0.043 | 1 | 0.059 | [22 empty] | AVERAGE | 10.1 | 10.1 | 11.1 | 31.3333 | 9.6 | 9.6 | 10.6 | 29.8 |  | 13.8446 |  | 12.348 | 26.1926 | 2.1192 | AVERAGE | 80.5856 | 7050.5548 |  | 888.1057 | 0 | 0 | 0 | 3.7507 | 3.5104 | 3.4131 | 1.8839 | 1.9152 | 2.0152 | 0.39545 | 0.33896 | 0.38622 | 0.37889 | 0.37229 | 0.37229 | 1.4267 | 5.3333 | 0.050368 | 0.050739 | 0.049613 | 1.1095 | 0.5008 | 0.10031 | 3.6396 | 0.7362 | 5.5977 | 1.0846 | 0.4985 | 0.095433 | 4.3605 | 0.68619 | 7.5156 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.53 | 105 | 98 | 61.9 | 708 | 1042 | 111.7 | 3.034 | 0.092 | 36.28 | 62 | 0.489 | 36.36 | 62 | 0 | 36.27 | 63 | 0 | 24.4 | 2.093 | 23 | 2.12 | 69.3 | 39.8 | 2.0445 | 0.422 | 24.44 | 1.486 | 18 | 2.55 | 69.2 | 39.8 | 2.0445 | 24.64 | 1.301 | 12 | 2.39 | 74.8 | 44 | 2.1096 | 0.203 | 6 | 1.24 | 0.02 | 0.439 | 0.188 | 6 | 2.67 | 0.021 | 0.242 | 6 | 2.849 | 0.007 | 43.94 | 0.424 | 7 | 26.7 | 106.5 | 42 | 72 | 0.031 | 43.73 | 0.431 | 6 | 25.6 | 113.9 | 42 | 72 | 0.027 | 26.1 | 24.4 | 19.5 |  |  | MINIMUM | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 12.911 |  | 11.965 | 24.9595 | 2.1182 | MINIMUM | 80.448 | 6640.6388 |  | 856.3877 |  |  |  | 3.5014 | 3.2096 | 3.1831 | 1.6399 | 1.8274 | 1.9925 | 0.3877 | 0.33231 | 0.36 | 0.33231 | 0.36853 | 0.36853 | 1.2365 | 3 | 0.049981 | 0.049981 | 0.04885 | 1.101 | 0.49941 | 0.098859 | 2.7138 | 0.72027 | 5.5826 | 1.0643 | 0.49499 | 0.093649 | 4.0825 | 0.63358 | 7.3918 |  | MIN | 0.51 | 9.8 | 25.9592 | 13.2392 | 6.05 | 17.3 | 10 | 1.3239 |  |  |  | MIN | 0.6 | 9.8 | 25.9592 | 15.5755 | 6.08 | 17.2 | 10 | 1.5576 |  |  |  | MIN | 0.56 | 11 | 24.5455 | 13.7455 | 6.16 | 18.4 | 10 | 1.3745 |  |  |  | 1.3239
AVERAGE | 6.4217 | 17.5 | 16.3333 | 10.3167 | 118 | 173.6667 | 18.6167 | 0.50567 | 0.046 | 6.0467 | 10.3333 | 0.0815 | 6.06 | 10.3333 |  | 6.045 | 10.5 |  | 6.1 | 0.52325 | 5.75 | 0.53 | 17.325 | 9.95 | 0.51112 | 0.070333 | 6.11 | 0.3715 | 4.5 | 0.6375 | 17.3 | 9.95 | 0.51112 | 6.16 | 0.32525 | 3 | 0.5975 | 18.7 | 11 | 0.52741 | 0.033833 | 1 | 0.20667 | 0.01 | 0.073167 | 0.031333 | 1 | 0.445 | 0.021 | 0.040333 | 1 | 0.47483 |  | 7.3233 | 0.070667 | 1.1667 | 4.45 | 17.75 | 21 | 36 | 0.0155 | 7.2883 | 0.071833 | 1 | 4.2667 | 18.9833 | 21 | 36 | 0.0135 | 4.35 | 4.0667 | 3.25 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 32 | 9.8 | 9.8 | 10.8 | 30.4 |  | 15.2683 |  | 13.0306 | 27.2333 | 2.1197 | MAXIMUM | 80.8609 | 7501.4624 |  | 951.5419 |  |  |  | 4.2492 | 3.966 | 3.8732 | 2.0439 | 2.0439 | 2.0608 | 0.39933 | 0.34228 | 0.39933 | 0.40503 | 0.37858 | 0.37858 | 1.712 | 7 | 0.051143 | 0.051143 | 0.050246 | 1.1142 | 0.5015 | 0.1032 | 4.1865 | 0.76805 | 5.6053 | 1.0947 | 0.50324 | 0.096324 | 4.6226 | 0.71684 | 7.7253
MINIMUM | 6.32 | 17 | 16 | 10.1 | 114 | 169 | 18.2 | 0.499 | 0.041 | 6.02 | 10 | 0.075 | 6.03 | 10 |  | 6.01 | 10 |  | 6.05 | 0.413 | 4 | 0.51 | 17 | 9.8 | 0.50522 | 0.066 | 6.08 | 0.276 | 4 | 0.6 | 17 | 9.8 | 0.50522 | 6.14 | 0.287 | 3 | 0.56 | 18.4 | 11 | 0.52741 | 0.029 | 1 | 0.16 | 0.008 | 0.07 | 0.015 | 1 | 0.3 | 0.021 | 0.038 | 1 | 0.059 |  | 7.16 | 0.061 | 1 | 4.3 | 17.4 | 20 | 36 | 0.012 | 7.2 | 0.063 | 1 | 4 | 18.7 | 20 | 36 | 0.006 | 4.2 | 3.9 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 30950 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 365 | 390 | 1220 | 1240 | 1440 | 2100 | 1800 | 2050 | 2010 | 2173 | 2173 | 2250 | 0 | 2750 | 2770 | 2990 | 278 | 333 | 40 | 4180 | 930 | 1105 | 150 | 183 | 21 | 2630 | 478 | 819
MAXIMUM | 6.46 | 18 | 17 | 10.8 | 122 | 187 | 19.2 | 0.517 | 0.051 | 6.09 | 11 | 0.088 | 6.1 | 11 |  | 6.09 | 11 |  | 6.16 | 0.636 | 8 | 0.55 | 17.9 | 10 | 0.51308 | 0.073 | 6.17 | 0.436 | 5 | 0.71 | 17.8 | 10 | 0.51308 | 6.17 | 0.416 | 3 | 0.64 | 19.3 | 11 | 0.52741 | 0.041 | 1 | 0.23 | 0.012 | 0.076 | 0.045 | 1 | 0.52 | 0.021 | 0.043 | 1 | 0.64 |  | 7.72 | 0.08 | 2 | 4.7 | 18.3 | 22 | 36 | 0.019 | 7.44 | 0.083 | 1 | 4.5 | 19.5 | 22 | 36 | 0.021 | 4.5 | 4.2 | 4 | [17 empty] | AVERAGE | 10316.6667 | [6 empty] | 130 | 121.6667 | 130 | 406.6667 | 413.3333 | 480 | 700 | 600 | 683.3333 | 670 | 724.3333 | 724.3333 | 750 |  | 916.6667 | 923.3333 | 996.6667 | 92.6667 | 111 | 13.3333 | 1393.3333 | 310 | 368.3333 | 50 | 61 | 7 | 876.6667 | 159.3333 | 273
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0506 |  | TOTAL AVG COAG ALK: |  |  |  | 10.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.636 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.51 | [5 empty] | 6.1233 |  |  |  |  | 0.045 |  |  |  |  | 0.51 | [6 empty] | 0.045 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 10200 | [6 empty] | 120 | 110 | 120 | 350 | 390 | 470 | 700 | 600 | 650 | 600 | 713 | 713 | 650 |  | 900 | 900 | 990 | 91 | 110 | 13 | 1050 | 300 | 365 | 50 | 60 | 7 | 820 | 150 | 266
[90 empty] | MAXIMUM | 10550 | [6 empty] | 150 | 140 | 150 | 450 | 450 | 500 | 700 | 600 | 700 | 710 | 730 | 730 | 900 |  | 950 | 950 | 1000 | 95 | 113 | 14 | 1600 | 330 | 375 | 50 | 62 | 7 | 950 | 165 | 278
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.748 |  | TOTAL MGD: |  | 0.014 |  |  | FINISHED SOUTH 1 |  | START: | 23770239 |  | END: | 23770253 |  |  | Alum | 9327 | 8483 | 8483 | 8113 | 8113 | 20.4 | [44 empty] | 0.51 | 9.8 | 25.9592 | 13.2392 | 6.05 | 17.3 | 10 | 1.3239
[73 empty] | FINISHED 2 | 14.35 |  | TOTAL MGD: |  | 13.734 |  |  | FINISHED SOUTH 2 |  | START: | 43262151 |  | END: | 43275885 |  |  | Caustic | 5418 | 8380 | 8380
[73 empty] | TOTAL RAW | 33.059 |  | TOTAL MGD: |  | 4.308 |  |  | FINISHED CONWAY |  | START: | 9994180 |  | END: | 9998488 |  |  | Hypochlorite | 15 |  | 42
[76 empty] | TOTAL MGD: |  | 10.042 |  |  | FINISHED PERRY |  | START: | 33253616 |  | END: | 33263658 |  |  | Phosphate | 2374
[76 empty] | TOTAL MGD: |  | 10.099 |  |  | RAW PLANT 1 |  | START: | 30431096 |  | END: | 30441195 |  |  | Fluoride | 2835 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.184 |  |  | RAW PLANT 2 |  | START: | 30391972 |  | END: | 30402156 |  |  | Cal~Flo | 9.86 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.776 |  |  | RAW PLANT 3 |  | START: | 6899383 |  | END: | 6912159 |  |  | Zinc | 1472
[76 empty] | TOTAL MGD: |  | 0.919 |  |  | DECANT |  | START: | 1808405 |  | END: | 1809324 |  |  | Polymer | 20
[76 empty] | TOTAL MGD: |  | 1.1999 |  |  | BLOW DOWN |  | START: | 9053.1146 |  | END: | 9054.3144 |  |  | NH3 | 11.97 |  | BI-SUL | 750
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 970
23770253
43275885
9998488
33263658
30441195
30402156
6912159
1809324
9054.3144
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 12
DATE: | 2018-11-12 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-12 | [23 empty] | DATE: | 2018-11-12
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-12 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43416.0064 | 1,2,3,6 | 42 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | ,2,3 | 15.2683 | 1,3 | 11.965 | 27.2333 | 2.1182 | 43416.0064 | 80.448 | 7501.4624 | 0 | 951.5419 | 0 | 0 | 0 | 3.5014 | 3.3555 | 3.1831 | 1.6399 | 1.8274 | 1.9925 | 0.39933 | 0.34228 | 0.39933 | 0.39933 | 0.37858 | 0.37858 | 1.712 | 7 | 0.049981 | 0.049981 | 0.050246 | 1.101 | 0.5015 | 0.098859 | 4.0184 | 0.72027 | 5.6053 | 1.0947 | 0.50324 | 0.096324 | 4.0825 | 0.71684 | 7.7253 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.17 | 0.41 | 6 | 0.59 | 16.6 | 10 | 0.51308 |  | 6.19 | 0.363 | 5 | 0.6 | 16.7 | 10 | 0.51308 | 6.2 | 0.4 | 3 | 0.53 | 18.3 | 11 | 0.52741 | [13 empty] | 7.53 | 0.07 | 1 | 4.4 | 17.3 |  |  |  | 7.4 | 0.069 | 1 | 4.3 | 18.6 |  |  |  | 4.4 | 4 | 3.4 | [18 empty] | 10200 | [6 empty] | 120 | 115 | 120 | 350 | 390 | 470 | 700 | 600 | 700 | 700 | 730 | 730 | 900 |  | 900 | 900 | 1000 | 91 | 110 | 13 | 1530 | 300 | 365 | 50 | 61 | 7 | 820 | 165 | 278 |  | 1:00 | 0.59 | 10 | 25.44 | 15.0096 | 6.17 | 16.6 | 10 | 1.501 | 15 | 6.5 | 0.39308 | 1:00 | 0.6 | 10 | 25.44 | 15.264 | 6.19 | 16.7 | 10 | 1.5264 | 15 | 6.5 | 0.39308 | 1:00 | 0.53 | 11 | 24.5455 | 13.0091 | 6.2 | 18.3 | 10 | 1.3009 | 15 | 6.5 | 0.40741
2:00 | [72 empty] | 43416.3077 | 1,2,3,6 | 42 | 10.3 | 10.3 | 11.3 | 32 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 13.7664 | 1,3 | 15.1517 | 28.9181 | 2.1182 | 43416.3077 | 80.4777 | 7255.5128 | 0 | 824.6696 | 0 | 0 | 0 | 3.3994 | 3.2578 | 3.0986 | 1.6352 | 1.726 | 1.8959 | 0.3877 | 0.32123 | 0.3877 | 0.40985 | 0.35995 | 0.35995 | 1.712 | 6 | 0.048451 | 0.048451 | 0.049827 | 1.0791 | 0.49941 | 0.095833 | 4.1087 | 0.7215 | 5.4337 | 1.1069 | 0.48124 | 0.093649 | 4.0035 | 0.63358 | 7.5107 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.47 | 18 | 17 | 10.6 | 120 | 170 | 18.2 | 0.514 |  | 6 | 10 | 0.082 | 6.04 | 11 |  | 6.08 | 11 | [8 empty] | 0.072 | [14 empty] | 0.04 | 1 | 0.21 |  | 0.076 | 0.036 | 1 | 0.2 |  | 0.041 | 1 | 0.32 | [38 empty] | 10500 | [6 empty] | 120 | 115 | 120 | 360 | 380 | 460 | 700 | 580 | 700 | 740 | 713 | 713 | 900 |  | 900 | 900 | 1020 | 92 | 113 | 13 | 1630 | 310 | 365 | 52 | 60 | 7 | 820 | 150 | 278 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43416.7955 | 1,2,3,6 | 41 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.0067 | 1,3 | 14.485 | 26.4917 | 1.993 | 43416.7955 | 80.4777 | 7747.412 | 0 | 824.6696 | 0 | 0 | 0 | 3.4277 | 3.2578 | 3.0986 | 1.8168 | 1.8168 | 2.0608 | 0.3877 | 0.33231 | 0.3877 | 0.3877 | 0.35339 | 0.35339 | 1.712 | 1 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.1032 | 4.0939 | 0.70986 | 5.8059 | 1.0643 | 0.49728 | 0.093649 | 4.1091 | 0.63358 | 8.105 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.3 | 0.071 | 1 | 4.4 | 17.3 |  |  |  | 7.32 | 0.07 | 1 | 4.2 | 18.6 |  |  |  | 4.3 | 4 | 3.4 | [18 empty] | 10500 | [6 empty] | 121 | 115 | 120 | 400 | 400 | 500 | 700 | 600 | 700 | 700 | 700 | 700 | 900 |  | 950 | 950 | 1000 | 95 | 113 | 14 | 1600 | 305 | 390 | 50 | 62 | 7 | 800 | 150 | 300 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.41 | 18 | 17 | 10.4 | 109 | 170 | 17.9 | 0.487 |  | 6.05 | 10 | 0.084 | 6.12 | 11 |  | 6.05 | 11 | [8 empty] | 0.075 | [14 empty] | 0.056 | 1 | 0.19 |  | 0.074 | 0.033 | 1 | 0.44 |  | 0.041 | 1 | 0.51 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.051 | [9 empty] | 6.11 | 0.578 | 4 | 0.55 | 16.4 | 10.3 | 0.52487 |  | 6.07 | 0.387 | 4 | 0.55 | 16.5 | 10.3 | 0.52487 | 6.16 | 0.206 | 4 | 0.62 | 18.2 | 11.3 | 0.53852 |  |  |  | 0.022 |  |  |  |  | 0.023 |  |  |  | 0.015 | 7.1 | 0.06 | 1 | 4.5 | 17.1 | 36 | 21 | 0.015 | 7.16 | 0.076 | 1 | 4.2 | 18.5 | 20 | 38 | 0.016 | 4.3 | 3.8 | 3.8 | [55 empty] | 9:00 | 0.55 | 10.3 | 24.699 | 13.5845 | 6.11 | 16.4 | 10 | 1.3584 | 15 | 6.5 | 0.40487 | 9:00 | 0.55 | 10.3 | 24.699 | 13.5845 | 6.07 | 16.5 | 10 | 1.3584 | 15 | 6.5 | 0.40487 | 9:00 | 0.62 | 11.3 | 23.8938 | 14.8142 | 6.16 | 18.2 | 10 | 1.4814 | 15 | 6.5 | 0.41852
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.41 | 18 | 17 | 10.5 | 117 | 179 | 17.8 | 0.503 |  | 6.09 | 10 | 0.081 | 6.07 | 10 |  | 6.04 | 10 | [8 empty] | 0.07 | [14 empty] | 0.061 | 1 | 0.22 |  | 0.072 | 0.028 | 1 | 0.37 |  | 0.052 | 1 | 0.65 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.97 | 0.587 | 4 | 0.48 | 16.5 | 10.4 | 0.44704 |  | 6.02 | 0.409 | 4 | 0.45 | 16.6 | 10.4 | 0.52881 | 6.18 | 0.235 | 3 | 0.55 | 18.1 | 11.4 | 0.54222 | [13 empty] | 7.14 | 0.072 | 1 | 4.4 | 17.8 |  |  |  | 7.18 | 0.086 | 1 | 4.2 | 18.4 |  |  |  | 4.3 | 3.7 | 2.8 | [55 empty] | 13:00 | 0.48 | 10.4 | 24.4615 | 11.7415 | 5.97 | 16.5 | 8 | 1.4677 | 15 | 6 | 0.32704 | 13:00 | 0.45 | 10.4 | 24.4615 | 11.0077 | 6.02 | 16.6 | 10 | 1.1008 | 15 | 6.5 | 0.40881 | 13:00 | 0.55 | 11.4 | 23.6842 | 13.0263 | 6.18 | 18.1 | 10 | 1.3026 | 15 | 6.5 | 0.42222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.34 | 18 | 16 | 10.3 | 108 | 170 | 17.6 | 0.466 |  | 6.16 | 10 | 0.082 | 6.11 | 11 |  | 6.11 | 11 | [8 empty] | 0.072 | [14 empty] | 0.07 | 1 | 0.24 |  | 0.077 | 0.029 | 2 | 0.5 |  | 0.076 | 1 | 0.73 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.26 | 0.071 | 1 | 4.6 | 16.8 |  |  |  | 7.45 | 0.087 | 1 | 4.4 | 18.4 |  |  |  | 4.2 | 3.8 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.46 | 18 | 17 | 10.1 | 114 | 170 | 17.7 | 0.489 |  | 6.1 | 10 | 0.075 | 6.12 | 10 |  | 6.09 | 11 | [8 empty] | 0.067 | [14 empty] | 0.051 | 1 | 0.26 |  | 0.069 | 0.024 | 1 | 0.3 |  | 0.069 | 1 | 0.57 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.041 | [9 empty] | 6.19 | 0.353 | 4 | 0.52 | 16.4 | 10.1 | 0.51701 |  | 6.15 | 0.313 | 3 | 0.53 | 16.5 | 10.3 | 0.52487 | 6.16 | 0.289 | 3 | 0.55 | 18 | 11.3 | 0.53852 |  |  |  | 0.009 | [9 empty] | 7.3 | 0.073 | 1 | 4.5 | 16.9 | 21 | 38 | 0.023 | 7.49 | 0.09 | 1 | 4.3 | 18.4 | 21 | 38 | 0.015 | 4.2 | 3.8 | 2.9 | [55 empty] | 21:00 | 0.52 | 10.1 | 25.1881 | 13.0978 | 6.19 | 16.4 | 10 | 1.3098 | 15 | 6.5 | 0.39701 | 21:00 | 0.53 | 10.3 | 24.699 | 13.0905 | 6.15 | 16.5 | 10 | 1.309 | 15 | 6.5 | 0.40487 | 21:00 | 0.55 | 11.3 | 23.8938 | 13.1416 | 6.16 | 18 | 10 | 1.3142 | 15 | 6.5 | 0.41852
22:00 | [72 empty] | DOSE |  | TOTAL | 30.6 | 30.6 | 33.6 | 94.9 | 29.1 | 29.1 | 32.1 | 90.3 | 0 | 41.0414 | 0 | 41.6016 | 82.643 | 6.2294 | TOTAL | 241.4033 | 22504.3872 | 0 | 2600.8811 | 0 | 0 | 0 | 10.3285 | 9.871 | 9.3802 | 5.0919 | 5.3702 | 5.9491 | 1.1747 | 0.99583 | 1.1747 | 1.1969 | 1.0919 | 1.0919 | 5.1361 | 14 | 0.14957 | 0.14957 | 0.14892 | 3.2943 | 1.5003 | 0.2979 | 12.221 | 2.1516 | 16.8448 | 3.2658 | 1.4818 | 0.28362 | 12.1951 | 1.984 | 23.341 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.41 | 17 | 17 | 10.2 | 116 | 172 | 17.7 | 0.488 |  | 6.06 | 11 | 0.081 | 6.03 | 11 |  | 6.08 | 11 | [8 empty] | 0.071 | [14 empty] | 0.05 | 1 | 0.22 |  | 0.071 | 0.023 | 1 | 0.3 |  | 0.069 | 1 | 0.43 | [22 empty] | AVERAGE | 10.2 | 10.2 | 11.2 | 31.6333 | 9.7 | 9.7 | 10.7 | 30.1 |  | 13.6805 |  | 13.8672 | 27.5477 | 2.0765 | AVERAGE | 80.4678 | 7501.4624 |  | 866.9604 | 0 | 0 | 0 | 3.4428 | 3.2903 | 3.1267 | 1.6973 | 1.7901 | 1.983 | 0.39157 | 0.33194 | 0.39157 | 0.39896 | 0.36397 | 0.36397 | 1.712 | 4.6667 | 0.049858 | 0.049858 | 0.049641 | 1.0981 | 0.5001 | 0.099299 | 4.0737 | 0.71721 | 5.6149 | 1.0886 | 0.49392 | 0.094541 | 4.065 | 0.66133 | 7.7803 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.5 | 107 | 101 | 62.1 | 684 | 1031 | 106.9 | 2.947 | 0.092 | 36.46 | 61 | 0.485 | 0 | 64 | 0 | 36.45 | 65 | 0 | 24.44 | 1.928 | 18 | 2.14 | 65.9 | 40.8 | 2.002 | 0.427 | 24.43 | 1.472 | 16 | 2.13 | 66.3 | 41 | 2.0916 | 24.7 | 1.13 | 13 | 2.25 | 72.6 | 45 | 2.1467 | 0.328 | 6 | 1.34 | 0.031 | 0.439 | 0.173 | 7 | 2.11 | 0.023 | 0.348 | 6 | 3.21 | 0.015 | 43.63 | 0.417 | 6 | 26.8 | 103.2 | 57 | 59 | 0.038 | 44 | 0.478 | 6 | 25.6 | 110.9 | 41 | 76 | 0.031 | 25.7 | 23.1 | 19.1 |  |  | MINIMUM | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 12.0067 |  | 11.965 | 26.4917 | 1.993 | MINIMUM | 80.448 | 7255.5128 |  | 824.6696 |  |  |  | 3.3994 | 3.2578 | 3.0986 | 1.6352 | 1.726 | 1.8959 | 0.3877 | 0.32123 | 0.3877 | 0.3877 | 0.35339 | 0.35339 | 1.712 | 1 | 0.048451 | 0.048451 | 0.04885 | 1.0791 | 0.49941 | 0.095833 | 4.0184 | 0.70986 | 5.4337 | 1.0643 | 0.48124 | 0.093649 | 4.0035 | 0.63358 | 7.5107 |  | MIN | 0.52 | 10.1 | 25.1881 | 13.0978 | 6.19 | 16.4 | 10 | 1.3098 |  |  |  | MIN | 0.45 | 10.4 | 24.4615 | 11.0077 | 6.02 | 16.6 | 10 | 1.1008 |  |  |  | MIN | 0.53 | 11 | 24.5455 | 13.0091 | 6.2 | 18.3 | 10 | 1.3009 |  |  |  | 1.1008
AVERAGE | 6.4167 | 17.8333 | 16.8333 | 10.35 | 114 | 171.8333 | 17.8167 | 0.49117 | 0.046 | 6.0767 | 10.1667 | 0.080833 |  | 10.6667 |  | 6.075 | 10.8333 |  | 6.11 | 0.482 | 4.5 | 0.535 | 16.475 | 10.2 | 0.5005 | 0.071167 | 6.1075 | 0.368 | 4 | 0.5325 | 16.575 | 10.25 | 0.52291 | 6.175 | 0.2825 | 3.25 | 0.5625 | 18.15 | 11.25 | 0.53667 | 0.054667 | 1 | 0.22333 | 0.0155 | 0.073167 | 0.028833 | 1.1667 | 0.35167 | 0.023 | 0.058 | 1 | 0.535 | 0.015 | 7.2717 | 0.0695 | 1 | 4.4667 | 17.2 | 28.5 | 29.5 | 0.019 | 7.3333 | 0.079667 | 1 | 4.2667 | 18.4833 | 20.5 | 38 | 0.0155 | 4.2833 | 3.85 | 3.1833 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 32 | 9.8 | 9.8 | 10.8 | 30.4 |  | 15.2683 |  | 15.1517 | 28.9181 | 2.1182 | MAXIMUM | 80.4777 | 7747.412 |  | 951.5419 |  |  |  | 3.5014 | 3.3555 | 3.1831 | 1.8168 | 1.8274 | 2.0608 | 0.39933 | 0.34228 | 0.39933 | 0.40985 | 0.37858 | 0.37858 | 1.712 | 7 | 0.051143 | 0.051143 | 0.050246 | 1.1142 | 0.5015 | 0.1032 | 4.1087 | 0.7215 | 5.8059 | 1.1069 | 0.50324 | 0.096324 | 4.1091 | 0.71684 | 8.105
MINIMUM | 6.34 | 17 | 16 | 10.1 | 108 | 170 | 17.6 | 0.466 | 0.041 | 6 | 10 | 0.075 |  | 10 |  | 6.04 | 10 |  | 5.97 | 0.353 | 4 | 0.48 | 16.4 | 10 | 0.44704 | 0.067 | 6.02 | 0.313 | 3 | 0.45 | 16.5 | 10 | 0.51308 | 6.16 | 0.206 | 3 | 0.53 | 18 | 11 | 0.52741 | 0.04 | 1 | 0.19 | 0.009 | 0.069 | 0.023 | 1 | 0.2 | 0.023 | 0.041 | 1 | 0.32 | 0.015 | 7.1 | 0.06 | 1 | 4.4 | 16.8 | 21 | 21 | 0.015 | 7.16 | 0.069 | 1 | 4.2 | 18.4 | 20 | 38 | 0.015 | 4.2 | 3.7 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 31200 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 345 | 360 | 1110 | 1170 | 1430 | 2100 | 1780 | 2100 | 2140 | 2143 | 2143 | 2700 | 0 | 2750 | 2750 | 3020 | 278 | 336 | 40 | 4760 | 915 | 1120 | 152 | 183 | 21 | 2440 | 465 | 856
MAXIMUM | 6.47 | 18 | 17 | 10.6 | 120 | 179 | 18.2 | 0.514 | 0.051 | 6.16 | 11 | 0.084 |  | 11 |  | 6.11 | 11 |  | 6.19 | 0.587 | 6 | 0.59 | 16.6 | 10.4 | 0.52487 | 0.075 | 6.19 | 0.409 | 5 | 0.6 | 16.7 | 10.4 | 0.52881 | 6.2 | 0.4 | 4 | 0.62 | 18.3 | 11.4 | 0.54222 | 0.07 | 1 | 0.26 | 0.022 | 0.077 | 0.036 | 2 | 0.5 | 0.023 | 0.076 | 1 | 0.73 | 0.015 | 7.53 | 0.073 | 1 | 4.6 | 17.8 | 36 | 38 | 0.023 | 7.49 | 0.09 | 1 | 4.4 | 18.6 | 21 | 38 | 0.016 | 4.4 | 4 | 3.8 | [17 empty] | AVERAGE | 10400 | [6 empty] | 120.3333 | 115 | 120 | 370 | 390 | 476.6667 | 700 | 593.3333 | 700 | 713.3333 | 714.3333 | 714.3333 | 900 |  | 916.6667 | 916.6667 | 1006.6667 | 92.6667 | 112 | 13.3333 | 1586.6667 | 305 | 373.3333 | 50.6667 | 61 | 7 | 813.3333 | 155 | 285.3333
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0758 |  | TOTAL AVG COAG ALK: |  |  |  | 10.5556 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.587 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.45 | [5 empty] | 6.1308 |  |  |  |  | 0.076 |  |  |  |  | 0.45 | [6 empty] | 0.076 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 10200 | [6 empty] | 120 | 115 | 120 | 350 | 380 | 460 | 700 | 580 | 700 | 700 | 700 | 700 | 900 |  | 900 | 900 | 1000 | 91 | 110 | 13 | 1530 | 300 | 365 | 50 | 60 | 7 | 800 | 150 | 278
[90 empty] | MAXIMUM | 10500 | [6 empty] | 121 | 115 | 120 | 400 | 400 | 500 | 700 | 600 | 700 | 740 | 730 | 730 | 900 |  | 950 | 950 | 1020 | 95 | 113 | 14 | 1630 | 310 | 390 | 52 | 62 | 7 | 820 | 165 | 300
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.501 |  | TOTAL MGD: |  | 0.014 |  |  | FINISHED SOUTH 1 |  | START: | 23770253 |  | END: | 23770267 |  |  | Alum | 9324 | 10476 | 10476 | 9807 | 9807 | 1.1 | [44 empty] | 0.45 | 10.4 | 24.4615 | 11.0077 | 6.02 | 16.6 | 10 | 1.1008
[73 empty] | FINISHED 2 | 15.104 |  | TOTAL MGD: |  | 13.487 |  |  | FINISHED SOUTH 2 |  | START: | 43275885 |  | END: | 43289372 |  |  | Caustic | 5164 | 8240 | 8240
[73 empty] | TOTAL RAW | 31.922 |  | TOTAL MGD: |  | 4.571 |  |  | FINISHED CONWAY |  | START: | 9998488 |  | END: | 10003059 |  |  | Hypochlorite | 13 |  | 40.5
[76 empty] | TOTAL MGD: |  | 10.533 |  |  | FINISHED PERRY |  | START: | 33263658 |  | END: | 33274191 |  |  | Phosphate | 2339
[76 empty] | TOTAL MGD: |  | 10.097 |  |  | RAW PLANT 1 |  | START: | 30441195 |  | END: | 30451292 |  |  | Fluoride | 3914 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.137 |  |  | RAW PLANT 2 |  | START: | 30402156 |  | END: | 30412293 |  |  | Cal~Flo | 6.85 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.688 |  |  | RAW PLANT 3 |  | START: | 6912159 |  | END: | 6923847 |  |  | Zinc | 1460
[76 empty] | TOTAL MGD: |  | 0.719 |  |  | DECANT |  | START: | 1809324 |  | END: | 1810043 |  |  | Polymer | 20
[76 empty] | TOTAL MGD: |  | 1.2507 |  |  | BLOW DOWN |  | START: | 9054.3144 |  | END: | 9055.5652 |  |  | NH3 | 11.73 |  | BI-SUL | 750
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 831
23770267
43289372
10003059
33274191
30451292
30412293
6923847
1810043
9055.5652
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 13
DATE: | 2018-11-13 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-13 | [23 empty] | DATE: | 2018-11-13
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-13 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43417.0078 | 1,2,3,6 | 41 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,2,3 | 12.0067 | 1,3 | 14.485 | 26.4917 | 1.993 | 43417.0078 | 80.4777 | 7747.412 | 0 | 824.6696 | 0 | 0 | 0 | 3.4277 | 3.2578 | 3.0986 | 1.8168 | 1.8168 | 2.0608 | 0.3877 | 0.33231 | 0.3877 | 0.3877 | 0.35339 | 0.35339 | 1.712 | 1 | 0.051143 | 0.051143 | 0.04885 | 1.1142 | 0.49941 | 0.1032 | 4.0939 | 0.70986 | 5.8059 | 1.0643 | 0.49728 | 0.093649 | 4.1091 | 0.63358 | 8.105 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.326 | 4 | 0.54 | 16.5 | 10.3 | 0.52487 |  | 6.15 | 0.319 | 3 | 0.54 | 16.6 | 10.3 | 0.52487 | 6.16 | 0.298 | 3 | 0.54 | 18.2 | 11.3 | 0.53852 | [13 empty] | 7.59 | 0.071 | 1 | 4.5 | 16.9 |  |  |  | 7.41 | 0.073 | 1 | 4.2 | 18.7 |  |  |  | 4.3 | 4.1 | 3.3 | [18 empty] | 10500 | [6 empty] | 121 | 115 | 120 | 400 | 400 | 500 | 700 | 600 | 700 | 700 | 700 | 700 | 900 |  | 950 | 950 | 1000 | 95 | 113 | 14 | 1600 | 305 | 390 | 50 | 62 | 7 | 800 | 150 | 300 |  | 1:00 | 0.54 | 10.3 | 24.699 | 13.3375 | 6.1 | 16.5 | 10 | 1.3337 | 15 | 6.5 | 0.40487 | 1:00 | 0.54 | 10.3 | 24.699 | 13.3375 | 6.15 | 16.6 | 10 | 1.3337 | 15 | 6.5 | 0.40487 | 1:00 | 0.54 | 11.3 | 23.8938 | 12.9027 | 6.16 | 18.2 | 10 | 1.2903 | 15 | 6.5 | 0.41852
2:00 | [72 empty] | 43417.3193 | 1,2,3 | 41 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,2,3 | 13.477 | 1,3 | 14.1768 | 27.6538 | 1.993 | 43417.3193 | 80.6338 | 7993.3616 | 0 | 697.7974 | 0 | 0 | 0 | 2.51 | 2.3531 | 2.2663 | 1.6186 | 1.5681 | 1.9077 | 0.39258 | 0.31897 | 0.38031 | 0.36804 | 0.36 | 0.36 | 1.712 | 65 | 0.049161 | 0.049161 | 0.050066 | 1.0972 | 0.50202 | 0.098514 | 4.1273 | 0.69981 | 5.7196 | 1.0791 | 0.49499 | 0.1032 | 4.3208 | 0.60513 | 8.9321 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.41 | 18 | 17 | 9.83 | 112 | 158 | 17.6 | 0.497 |  | 6.01 | 11 | 0.081 | 6.03 | 11 |  | 6.05 | 11 | [8 empty] | 0.069 | [14 empty] | 0.05 | 1 | 0.26 |  | 0.069 | 0.039 | 1 | 0.31 |  | 0.059 | 1 | 0.43 | [38 empty] | 9531 | [6 empty] | 80 | 75 | 80 | 320 | 310 | 420 | 640 | 520 | 620 | 600 | 650 | 650 | 900 |  | 820 | 820 | 930 | 84 | 102 | 12 | 1440 | 270 | 345 | 46 | 56 | 7 | 780 | 130 | 300 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43417.639 | 1,2,3 | 39 | 8.7 | 8.7 | 9.7 | 27.1 | 8.2 | 8.2 | 9.2 | 25.6 | ,2,3 | 9.9101 | 1,3 | 13.5014 | 23.4115 | 1.993 | 43417.639 | 80.6575 | 7993.3616 | 0 | 697.7974 | 0 | 0 | 0 |  |  |  | 1.6285 | 1.5742 | 1.9353 | 0.39343 | 0.30163 | 0.35408 | 0.38687 | 0.34699 | 0.34699 | 1.5218 | 65 | 0.048254 | 0.048897 | 0.050177 | 1.0934 | 0.50178 | 0.10572 | 4.0423 | 0.7232 | 5.8712 | 1.0995 | 0.48961 | 0.09423 | 4.0909 | 0.59501 | 8.5632 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.26 | 0.072 | 2 | 4.3 | 16.9 |  |  |  | 7.29 | 0.076 | 1 | 4.1 | 18.7 |  |  |  | 4.3 | 4 | 3.3 | [18 empty] | 8940 | [9 empty] | 300 | 290 | 400 | 600 | 460 | 540 | 590 | 590 | 590 | 800 |  | 750 | 760 | 875 | 78 | 95 | 12 | 1340 | 260 | 330 | 44 | 52 | 6 | 700 | 120 | 270 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43417.8135 | 1,2,3 | 39 | 8.7 | 8.7 | 9.7 | 27.1 | 8.2 | 8.2 | 9.2 | 25.6 | ,2,3 | 9.7474 | 1,3 | 13.6051 | 23.3525 | 1.9685 | 43417.8135 | 82.1011 | 7378.4876 | 0 | 697.7974 | 0 | 0 | 0 |  |  |  | 2.1713 | 1.6285 | 1.9353 | 0.39343 | 0.29507 | 0.32786 | 0.36064 | 0.35287 | 0.35287 | 1.5218 | 4 | 0.048254 | 0.048254 | 0.048744 | 1.0934 | 0.50178 | 0.096912 | 4.0751 | 0.7232 | 5.8712 | 1.1244 | 0.49902 | 0.09423 | 4.2206 | 0.59501 | 8.5632 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.44 | 18 | 18 | 10.5 | 111 | 167 | 17.6 | 0.473 |  | 6.03 | 11 | 0.071 | 6.07 | 11 |  | 6.07 | 11 | [8 empty] | 0.067 | [14 empty] | 0.048 | 1 | 0.35 |  | 0.069 | 0.029 | 1 | 0.44 |  | 0.058 | 1 | 0.69 | [38 empty] | 9100 | [9 empty] | 400 | 300 | 400 | 600 | 450 | 500 | 550 | 600 | 600 | 800 |  | 750 | 750 | 850 | 78 | 95 | 11 | 1350 | 260 | 330 | 45 | 53 | 6 | 708 | 120 | 270 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.061 | [9 empty] | 6.17 | 0.427 | 4 | 0.51 | 16.3 | 9.3 | 0.48557 |  | 6.11 | 0.345 | 5 | 0.46 | 16.5 | 9.3 | 0.48557 | 6.19 | 0.214 | 4 | 0.66 | 18.2 | 10.2 | 0.49778 |  |  |  | 0.01 |  |  |  |  | 0.024 |  |  |  | 0.008 | 7.09 | 0.068 | 2 | 4.6 | 16.8 | 20 | 38 | 0.02 | 7.26 | 0.067 | 2 | 4.1 | 18.6 | 21 | 40 | 0.006 | 4.3 | 4 | 3.8 | [55 empty] | 9:00 | 0.51 | 9.3 | 27.3548 | 13.951 | 6.17 | 16.3 | 10 | 1.3951 | 15 | 6.5 | 0.36557 | 9:00 | 0.46 | 9.3 | 27.3548 | 12.5832 | 6.11 | 16.5 | 10 | 1.2583 | 15 | 6.5 | 0.36557 | 9:00 | 0.66 | 10.2 | 26.4706 | 17.4706 | 6.19 | 18.2 | 10 | 1.7471 | 15 | 6.5 | 0.37778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.31 | 16 | 18 | 9.73 | 98 | 169 | 17.7 | 0.464 |  | 6 | 11 | 0.074 | 6.02 | 11 |  | 6.01 | 10 | [8 empty] | 0.071 | [14 empty] | 0.044 | 2 | 0.25 |  | 0.073 | 0.027 | 1 | 0.38 |  | 0.058 | 1 | 0.62 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.412 | 4 | 0.58 | 16.6 | 9.2 | 0.48164 |  | 6.19 | 0.356 | 4 | 0.53 | 16.7 | 9.3 | 0.48557 | 6.24 | 0.199 | 4 | 0.7 | 18.3 | 10.2 | 0.49778 | [13 empty] | 7.47 | 0.061 | 1 | 4.8 | 16.7 |  |  |  | 7.38 | 0.074 | 2 | 4.2 | 18.7 |  |  |  | 4.2 | 3.9 | 2.9 | [55 empty] | 13:00 | 0.58 | 9.2 | 27.6522 | 16.0383 | 6.1 | 16.6 | 10 | 1.6038 | 15 | 6.5 | 0.36164 | 13:00 | 0.53 | 9.3 | 27.3548 | 14.4981 | 6.19 | 16.7 | 10 | 1.4498 | 15 | 6.5 | 0.36557 | 13:00 | 0.7 | 10.2 | 26.4706 | 18.5294 | 6.24 | 18.3 | 10 | 1.8529 | 15 | 6.5 | 0.37778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.69 | 18 | 17 | 9.37 | 108 | 160 | 17.9 | 0.463 |  | 5.92 | 11 | 0.062 | 6.17 | 12 |  | 6.06 | 11 | [8 empty] | 0.064 | [14 empty] | 0.043 | 1 | 0.3 |  | 0.064 | 0.024 | 1 | 0.34 |  | 0.055 | 1 | 0.71 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.32 | 0.07 | 1 | 4.6 | 16.8 |  |  |  | 7.32 | 0.081 | 1 | 4.1 | 18.7 |  |  |  | 4.2 | 3.8 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.5 | 18 | 17 | 9.73 | 108 | 152 | 17.8 | 0.46 |  | 6.1 | 11 | 0.073 | 6.06 | 11 |  | 6.03 | 11 | [8 empty] | 0.068 | [14 empty] | 0.043 | 1 | 0.26 |  | 0.064 | 0.026 | 1 | 0.3 |  | 0.055 | 1 | 0.6 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.044 | [9 empty] | 6.18 | 0.263 | 4 | 0.59 | 16.5 | 8.7 | 0.46198 |  | 6.19 | 0.259 | 4 | 0.53 | 16.6 | 8.7 | 0.46198 | 6.2 | 0.233 | 3 | 0.63 | 18.3 | 9.7 | 0.47926 |  |  |  | 0.01 | [9 empty] | 7.39 | 0.071 | 1 | 4.3 | 16.7 | 22 | 38 | 0.019 | 7.45 | 0.079 | 1 | 4.1 | 18.6 | 22 | 38 | 0.012 | 4.2 | 3.8 | 3 | [55 empty] | 21:00 | 0.59 | 8.7 | 29.2414 | 17.2524 | 6.18 | 16.5 | 10 | 1.7252 | 15 | 6.5 | 0.34198 | 21:00 | 0.53 | 8.7 | 29.2414 | 15.4979 | 6.19 | 16.6 | 10 | 1.5498 | 15 | 6.5 | 0.34198 | 21:00 | 0.63 | 9.7 | 27.8351 | 17.5361 | 6.2 | 18.3 | 10 | 1.7536 | 15 | 6.5 | 0.35926
22:00 | [72 empty] | DOSE |  | TOTAL | 37 | 37 | 41 | 115 | 35 | 35 | 39 | 109 | 0 | 45.1411 | 0 | 55.7683 | 100.9094 | 7.9474 | TOTAL | 323.8701 | 31112.6228 | 0 | 2918.0617 | 0 | 0 | 0 | 5.9377 | 5.6108 | 5.3648 | 7.2353 | 6.5876 | 7.8391 | 1.5671 | 1.248 | 1.4499 | 1.5033 | 1.4132 | 1.4132 | 6.4676 | 135 | 0.19681 | 0.19745 | 0.19784 | 4.3981 | 2.005 | 0.40435 | 16.3386 | 2.8561 | 23.2679 | 4.3672 | 1.9809 | 0.38531 | 16.7413 | 2.4287 | 34.1635 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.37 | 17 | 17 | 9.76 | 110 | 154 | 17.7 | 0.452 |  | 6.03 | 11 | 0.074 | 6.03 | 11 |  | 6.04 | 11 | [8 empty] | 0.063 | [14 empty] | 0.049 | 1 | 0.23 |  | 0.066 | 0.03 | 1 | 0.29 |  | 0.059 | 1 | 0.46 | [22 empty] | AVERAGE | 9.25 | 9.25 | 10.25 | 28.75 | 8.75 | 8.75 | 9.75 | 27.25 |  | 11.2853 |  | 13.9421 | 25.2274 | 1.9868 | AVERAGE | 80.9675 | 7778.1557 |  | 729.5154 | 0 | 0 | 0 | 2.9688 | 2.8054 | 2.6824 | 1.8088 | 1.6469 | 1.9598 | 0.39178 | 0.312 | 0.36249 | 0.37581 | 0.35331 | 0.35331 | 1.6169 | 33.75 | 0.049203 | 0.049364 | 0.049459 | 1.0995 | 0.50125 | 0.10109 | 4.0846 | 0.71402 | 5.817 | 1.0918 | 0.49522 | 0.096329 | 4.1853 | 0.60718 | 8.5409 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.72 | 105 | 104 | 58.92 | 647 | 960 | 106.3 | 2.809 | 0.105 | 36.09 | 66 | 0.435 | 36.38 | 67 | 0 | 36.26 | 65 | 0 | 24.55 | 1.428 | 16 | 2.22 | 65.9 | 37.5 | 1.9541 | 0.402 | 24.64 | 1.279 | 16 | 2.06 | 66.4 | 37.6 | 1.958 | 24.79 | 0.944 | 14 | 2.53 | 73 | 41.4 | 2.0133 | 0 | 7 | 1.65 | 0.02 | 0.405 | 0.175 | 6 | 2.06 | 0.024 | 0.344 | 6 | 3.51 | 0.008 | 44.12 | 0.413 | 8 | 27.1 | 100.8 | 42 | 76 | 0.039 | 44.11 | 0.45 | 8 | 24.8 | 112 | 43 | 78 | 0.018 | 25.5 | 23.6 | 19.3 |  |  | MINIMUM | 8.7 | 8.7 | 9.7 | 27.1 | 8.2 | 8.2 | 9.2 | 25.6 |  | 9.7474 |  | 13.5014 | 23.3525 | 1.9685 | MINIMUM | 80.4777 | 7378.4876 |  | 697.7974 |  |  |  | 2.51 | 2.3531 | 2.2663 | 1.6186 | 1.5681 | 1.9077 | 0.3877 | 0.29507 | 0.32786 | 0.36064 | 0.34699 | 0.34699 | 1.5218 | 1 | 0.048254 | 0.048254 | 0.048744 | 1.0934 | 0.49941 | 0.096912 | 4.0423 | 0.69981 | 5.7196 | 1.0643 | 0.48961 | 0.093649 | 4.0909 | 0.59501 | 8.105 |  | MIN | 0.54 | 10.3 | 24.699 | 13.3375 | 6.1 | 16.5 | 10 | 1.3337 |  |  |  | MIN | 0.46 | 9.3 | 27.3548 | 12.5832 | 6.11 | 16.5 | 10 | 1.2583 |  |  |  | MIN | 0.54 | 11.3 | 23.8938 | 12.9027 | 6.16 | 18.2 | 10 | 1.2903 |  |  |  | 1.2583
AVERAGE | 6.4533 | 17.5 | 17.3333 | 9.82 | 107.8333 | 160 | 17.7167 | 0.46817 | 0.0525 | 6.015 | 11 | 0.0725 | 6.0633 | 11.1667 |  | 6.0433 | 10.8333 |  | 6.1375 | 0.357 | 4 | 0.555 | 16.475 | 9.375 | 0.48851 | 0.067 | 6.16 | 0.31975 | 4 | 0.515 | 16.6 | 9.4 | 0.4895 | 6.1975 | 0.236 | 3.5 | 0.6325 | 18.25 | 10.35 | 0.50333 |  | 1.1667 | 0.275 | 0.01 | 0.0675 | 0.029167 | 1 | 0.34333 | 0.024 | 0.057333 | 1 | 0.585 |  | 7.3533 | 0.068833 | 1.3333 | 4.5167 | 16.8 | 21 | 38 | 0.0195 | 7.3517 | 0.075 | 1.3333 | 4.1333 | 18.6667 | 21.5 | 39 | 0.009 | 4.25 | 3.9333 | 3.2167 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 13.477 |  | 14.485 | 27.6538 | 1.993 | MAXIMUM | 82.1011 | 7993.3616 |  | 824.6696 |  |  |  | 3.4277 | 3.2578 | 3.0986 | 2.1713 | 1.8168 | 2.0608 | 0.39343 | 0.33231 | 0.3877 | 0.3877 | 0.36 | 0.36 | 1.712 | 65 | 0.051143 | 0.051143 | 0.050177 | 1.1142 | 0.50202 | 0.10572 | 4.1273 | 0.7232 | 5.8712 | 1.1244 | 0.49902 | 0.1032 | 4.3208 | 0.63358 | 8.9321
MINIMUM | 6.31 | 16 | 17 | 9.37 | 98 | 152 | 17.6 | 0.452 | 0.044 | 5.92 | 11 | 0.062 | 6.02 | 11 |  | 6.01 | 10 |  | 6.1 | 0.263 | 4 | 0.51 | 16.3 | 8.7 | 0.46198 | 0.063 | 6.11 | 0.259 | 3 | 0.46 | 16.5 | 8.7 | 0.46198 | 6.16 | 0.199 | 3 | 0.54 | 18.2 | 9.7 | 0.47926 |  | 1 | 0.23 | 0.01 | 0.064 | 0.024 | 1 | 0.29 | 0.024 | 0.055 | 1 | 0.43 |  | 7.09 | 0.061 | 1 | 4.3 | 16.7 | 20 | 38 | 0.019 | 7.26 | 0.067 | 1 | 4.1 | 18.6 | 21 | 38 | 0.006 | 4.2 | 3.8 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 38071 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 190 | 200 | 1420 | 1300 | 1720 | 2540 | 2030 | 2360 | 2440 | 2540 | 2540 | 3400 | 0 | 3270 | 3280 | 3655 | 335 | 405 | 49 | 5730 | 1095 | 1395 | 185 | 223 | 26 | 2988 | 520 | 1140
MAXIMUM | 6.69 | 18 | 18 | 10.5 | 112 | 169 | 17.9 | 0.497 | 0.061 | 6.1 | 11 | 0.081 | 6.17 | 12 |  | 6.07 | 11 |  | 6.18 | 0.427 | 4 | 0.59 | 16.6 | 10.3 | 0.52487 | 0.071 | 6.19 | 0.356 | 5 | 0.54 | 16.7 | 10.3 | 0.52487 | 6.24 | 0.298 | 4 | 0.7 | 18.3 | 11.3 | 0.53852 |  | 2 | 0.35 | 0.01 | 0.073 | 0.039 | 1 | 0.44 | 0.024 | 0.059 | 1 | 0.71 |  | 7.59 | 0.072 | 2 | 4.8 | 16.9 | 22 | 38 | 0.02 | 7.45 | 0.081 | 2 | 4.2 | 18.7 | 22 | 40 | 0.012 | 4.3 | 4.1 | 3.8 | [17 empty] | AVERAGE | 9517.75 | [6 empty] | 100.5 | 95 | 100 | 355 | 325 | 430 | 635 | 507.5 | 590 | 610 | 635 | 635 | 850 |  | 817.5 | 820 | 913.75 | 83.75 | 101.25 | 12.25 | 1432.5 | 273.75 | 348.75 | 46.25 | 55.75 | 6.5 | 747 | 130 | 285
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0406 |  | TOTAL AVG COAG ALK: |  |  |  | 11 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.427 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.165 |  |  |  |  | 0.059 |  |  |  |  | 0.46 | [23 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 8940 | [6 empty] | 80 | 75 | 80 | 300 | 290 | 400 | 600 | 450 | 500 | 550 | 590 | 590 | 800 |  | 750 | 750 | 850 | 78 | 95 | 11 | 1340 | 260 | 330 | 44 | 52 | 6 | 700 | 120 | 270
[90 empty] | MAXIMUM | 10500 | [6 empty] | 121 | 115 | 120 | 400 | 400 | 500 | 700 | 600 | 700 | 700 | 700 | 700 | 900 |  | 950 | 950 | 1000 | 95 | 113 | 14 | 1600 | 305 | 390 | 50 | 62 | 7 | 800 | 150 | 300
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.452 |  | TOTAL MGD: |  | 0.012 |  |  | FINISHED SOUTH 1 |  | START: | 23770267 |  | END: | 23770279 |  |  | Alum | 9321 | 9084 | 9084 | 9290 | 9290 | 0.9 | [44 empty] | 0.46 | 9.3 | 27.3548 | 12.5832 | 6.11 | 16.5 | 10 | 1.2583
[73 empty] | FINISHED 2 | 16.554 |  | TOTAL MGD: |  | 11.44 |  |  | FINISHED SOUTH 2 |  | START: | 43289372 |  | END: | 43300812 |  |  | Caustic | 4959 | 8190 | 8190
[73 empty] | TOTAL RAW | 31.256 |  | TOTAL MGD: |  | 4.953 |  |  | FINISHED CONWAY |  | START: | 10003059 |  | END: | 10008012 |  |  | Hypochlorite | 18.5 |  | 32
[76 empty] | TOTAL MGD: |  | 11.601 |  |  | FINISHED PERRY |  | START: | 33274191 |  | END: | 33285792 |  |  | Phosphate | 2325
[76 empty] | TOTAL MGD: |  | 9.696 |  |  | RAW PLANT 1 |  | START: | 30451292 |  | END: | 30460988 |  |  | Fluoride | 2500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.797 |  |  | RAW PLANT 2 |  | START: | 30412293 |  | END: | 30422090 |  |  | Cal~Flo | 11.89 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.763 |  |  | RAW PLANT 3 |  | START: | 6923847 |  | END: | 6935610 |  |  | Zinc | 1470
[76 empty] | TOTAL MGD: |  | 0.861 |  |  | DECANT |  | START: | 1810043 |  | END: | 1810904 |  |  | Polymer | 19
[76 empty] | TOTAL MGD: |  | 1.3717 |  |  | BLOW DOWN |  | START: | 9055.5652 |  | END: | 9056.9369 |  |  | NH3 | 11.51 |  | BI-SUL | 770
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 698
23770279
43300812
10008012
33285792
30460988
30422090
6935610
1810904
9056.9369
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 14
DATE: | 2018-11-14 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-14 | [23 empty] | DATE: | 2018-11-14
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-14 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43418.0076 | 1,2,3 | 39 | 8.7 | 8.7 | 9.7 | 27.1 | 8.2 | 8.2 | 9.2 | 25.6 | ,2,3 | 9.7474 | 1,3 | 13.6051 | 23.3525 | 1.9685 | 43418.0076 | 82.1011 | 7378.4876 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1713 | 1.6285 | 1.9353 | 0.39343 | 0.29507 | 0.32786 | 0.36064 | 0.35287 | 0.35287 | 1.5218 | 4 | 0.048254 | 0.048254 | 0.048744 | 1.0934 | 0.50178 | 0.096912 | 4.0751 | 0.7232 | 5.8712 | 1.1244 | 0.49902 | 0.09423 | 4.2206 | 0.59501 | 8.5632 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.18 | 0.293 | 4 | 0.56 | 16.4 | 9 | 0.47377 |  | 6.2 | 0.288 | 3 | 0.53 | 16.4 | 9 | 0.47377 | 6.2 | 0.306 | 3 | 0.69 | 18.2 | 10 | 0.49037 | [13 empty] | 7.2 | 0.073 | 1 | 4.2 | 16.8 |  |  |  | 7.33 | 0.076 | 1 | 4.2 | 18.3 |  |  |  | 4.3 | 3.9 | 3.8 | [18 empty] | 9100 | [6 empty] | 0 | 0 | 0 | 400 | 300 | 400 | 600 | 450 | 500 | 550 | 600 | 600 | 800 |  | 750 | 750 | 850 | 78 | 95 | 11 | 1350 | 260 | 330 | 45 | 53 | 6 | 708 | 120 | 270 |  | 1:00 | 0.56 | 9 | 28.2667 | 15.8293 | 6.18 | 16.4 | 10 | 1.5829 | 15 | 6.5 | 0.35377 | 1:00 | 0.53 | 9 | 28.2667 | 14.9813 | 6.2 | 16.4 | 10 | 1.4981 | 15 | 6.5 | 0.35377 | 1:00 | 0.69 | 10 | 27 | 18.63 | 6.2 | 18.2 | 10 | 1.863 | 15 | 6.5 | 0.37037
2:00 | [72 empty] | 43418.3432 | 1,2,3 | 45 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 9.4032 | 1,3 | 14.6362 | 24.0394 | 1.9685 | 43418.3432 | 80.5408 | 7193 | 0 | 810 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.5681 | 1.8168 | 0.36804 | 0.28217 | 0.31897 | 0.39258 | 0.33231 | 0.35447 | 1.5218 | 4.5 | 0.04976 | 0.049161 | 0.049528 | 1.0972 | 0.50202 | 0.098514 | 4.1119 | 0.79053 | 6.0512 | 1.126 | 0.53034 | 0.1032 | 4.0877 | 0.74477 | 8.6344 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.47 | 17 | 17 | 9.53 | 108 | 166 | 17.7 | 0.472 |  | 6.06 | 11 | 0.09 | 6.14 | 11 |  | 6.11 | 11 | [8 empty] | 0.066 | [14 empty] | 0.039 | 1 | 0.34 |  | 0.066 | 0.033 | 1 | 0.41 |  | 0.053 | 1 | 0.61 | [38 empty] | 9520 | [6 empty] | 0 | 0 | 0 | 320 | 310 | 400 | 600 | 460 | 520 | 640 | 600 | 640 | 800 |  | 830 | 820 | 920 | 84 | 102 | 12 | 1490 | 305 | 365 | 48 | 60 | 7 | 760 | 160 | 290 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43418.8208 | 1,2,3 | 45 | 9.5 | 9.5 | 10.5 | 29.5 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 9.4032 | 1,3 | 14.6362 | 24.0394 | 1.8878 | 43418.8208 | 81.2176 | 7317.0002 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 1.5175 | 1.8168 | 0.33737 | 0.27603 | 0.3067 | 0.35271 | 0.33231 | 0.34339 | 1.5218 | 2 | 0.049161 | 0.049161 | 0.050604 | 1.0972 | 0.50202 | 0.098514 | 4.2028 | 0.76461 | 6.4656 | 1.126 | 0.51267 | 0.11795 | 4.0942 | 0.74477 | 9.3787 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.18 | 0.071 | 1 | 4.4 | 16.7 |  |  |  | 7.16 | 0.073 | 1 | 4 | 18.3 |  |  |  | 4.3 | 3.9 | 3.8 | [18 empty] | 9600 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 400 | 550 | 450 | 500 | 575 | 600 | 620 | 800 |  | 820 | 820 | 940 | 84 | 102 | 12 | 1500 | 295 | 390 | 48 | 58 | 8 | 770 | 160 | 315 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.41 | 16 | 16 | 10.1 | 106 | 160 | 17.5 | 0.451 |  | 6.01 | 10 | 0.09 | 6.01 | 9 |  | 5.99 | 9 | [8 empty] | 0.067 | [14 empty] | 0.056 | 1 | 0.22 |  | 0.065 | 0.026 | 2 | 0.28 |  | 0.066 | 2 | 0.55 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.047 | [9 empty] | 6.04 | 0.387 | 5 | 0.6 | 16.1 | 9.3 | 0.48557 |  | 6.17 | 0.365 | 4 | 0.57 | 16.2 | 9.3 | 0.48557 | 6.2 | 0.209 | 3 | 0.57 | 18.1 | 10.3 | 0.50148 |  |  |  | 0.008 | [9 empty] | 7.21 | 0.054 | 2 | 4.3 | 16.6 | 20 | 42 | 0.014 | 7.49 | 0.058 | 2 | 4 | 18.4 | 21 | 40 | 0.007 | 4.3 | 3.8 | 3.8 | [55 empty] | 9:00 | 0.6 | 9.3 | 27.3548 | 16.4129 | 6.04 | 16.1 | 10 | 1.6413 | 15 | 6.5 | 0.36557 | 9:00 | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.17 | 16.2 | 10 | 1.5592 | 15 | 6.5 | 0.36557 | 9:00 | 0.57 | 10.3 | 26.2136 | 14.9417 | 6.2 | 18.1 | 10 | 1.4942 | 15 | 6.5 | 0.38148
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.43 | 16 | 16 | 9.5 | 116 | 164 | 17.3 | 0.496 |  | 5.96 | 8 | 0.089 | 5.99 | 8 |  | 5.94 | 8 | [8 empty] | 0.069 | [14 empty] | 0.034 | 1 | 0.23 |  | 0.068 | 0.011 | 1 | 0.31 |  | 0.047 | 1 | 0.54 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.07 | 0.419 | 4 | 0.6 | 15.8 | 9.3 | 0.48557 |  | 6.1 | 0.295 | 4 | 0.54 | 16 | 9.3 | 0.48557 | 6.2 | 0.182 | 3 | 0.55 | 17.8 | 10.3 | 0.50148 | [13 empty] | 7.32 | 0.056 | 2 | 4.3 | 16.4 |  |  |  | 7.35 | 0.058 | 2 | 3.9 | 18.2 |  |  |  | 4.3 | 3.8 | 2.8 | [55 empty] | 13:00 | 0.6 | 9.3 | 27.3548 | 16.4129 | 6.07 | 15.8 | 10 | 1.6413 | 15 | 6.5 | 0.36557 | 13:00 | 0.54 | 9.3 | 27.3548 | 14.7716 | 6.1 | 16 | 10 | 1.4772 | 15 | 6.5 | 0.36557 | 13:00 | 0.55 | 10.3 | 26.2136 | 14.4175 | 6.2 | 17.8 | 10 | 1.4417 | 15 | 6.5 | 0.38148
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.36 | 16 | 16 | 13.6 | 112 | 174 | 17.3 | 0.465 |  | 6.17 | 8 | 0.086 | 6.17 | 9 |  | 6.04 | 9 | [8 empty] | 0.063 | [14 empty] | 0.038 | 1 | 0.32 |  | 0.059 | 0.012 | 1 | 0.31 |  | 0.055 | 1 | 0.51 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.2 | 0.055 | 2 | 4.2 | 16.6 |  |  |  | 7.25 | 0.061 | 2 | 3.5 | 18 |  |  |  | 4.4 | 3.7 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.33 | 17 | 16 | 18 | 109 | 154 | 17.1 | 0.464 |  | 6.19 | 11 | 0.082 | 6.13 | 11 |  | 6.07 | 11 | [8 empty] | 0.065 | [14 empty] | 0.034 | 2 | 0.21 |  | 0.062 | 0.013 | 2 | 0.36 |  | 0.052 | 1 | 0.56 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.186 | [9 empty] | 6.12 | 0.43 | 5 | 0.48 | 16.2 | 9.3 | 0.48557 |  | 6.12 | 0.317 | 5 | 0.48 | 16.4 | 9.3 | 0.48557 | 6.11 | 0.314 | 3 | 0.56 | 18.4 | 10.3 | 0.50148 |  |  |  | 0.028 | [9 empty] | 7.08 | 0.064 | 2 | 4.2 | 16.2 | 20 | 39 | 0.029 | 7.16 | 0.066 | 2 | 4.1 | 17.9 | 22 | 41 | 0.029 | 4.3 | 3.9 | 3 | [55 empty] | 21:00 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.2 | 10 | 1.313 | 15 | 6.5 | 0.36557 | 21:00 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.4 | 10 | 1.313 | 15 | 6.5 | 0.36557 | 21:00 | 0.56 | 10.3 | 26.2136 | 14.6796 | 6.11 | 18.4 | 10 | 1.468 | 15 | 6.5 | 0.38148
22:00 | [72 empty] | DOSE |  | TOTAL | 27.5 | 27.5 | 30.5 | 85.5 | 25.8 | 25.8 | 28.8 | 80.4 | 0 | 28.5538 | 0 | 42.8774 | 71.4312 | 5.8248 | TOTAL | 243.8594 | 21888.4878 | 0 | 2316.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3075 | 4.714 | 5.569 | 1.0988 | 0.85327 | 0.95353 | 1.1059 | 1.0175 | 1.0507 | 4.5654 | 10.5 | 0.14717 | 0.14658 | 0.14888 | 3.2877 | 1.5058 | 0.29394 | 12.3899 | 2.2783 | 18.388 | 3.3764 | 1.542 | 0.31538 | 12.4025 | 2.0846 | 26.5762 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.27 | 16 | 16 | 8.95 | 110 | 156 | 17.1 | 0.461 |  | 6 | 10 | 0.087 | 6 | 10 |  | 5.99 | 10 | [8 empty] | 0.064 | [14 empty] | 0.035 | 1 | 0.3 |  | 0.062 | 0.015 | 1 | 0.39 |  | 0.05 | 1 | 0.5 | [22 empty] | AVERAGE | 9.1667 | 9.1667 | 10.1667 | 28.5 | 8.6 | 8.6 | 9.6 | 26.8 |  | 9.5179 |  | 14.2925 | 23.8104 | 1.9416 | AVERAGE | 81.2865 | 7296.1626 |  | 772.2026 | 0 | 0 | 0 |  |  |  | 1.7692 | 1.5713 | 1.8563 | 0.36628 | 0.28442 | 0.31784 | 0.36864 | 0.33916 | 0.35024 | 1.5218 | 3.5 | 0.049058 | 0.048858 | 0.049625 | 1.0959 | 0.50194 | 0.09798 | 4.13 | 0.75945 | 6.1293 | 1.1255 | 0.51401 | 0.10513 | 4.1342 | 0.69485 | 8.8587 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.27 | 98 | 97 | 69.68 | 661 | 974 | 104 | 2.809 | 0.233 | 36.39 | 58 | 0.524 | 36.44 | 58 | 0 | 36.14 | 58 | 0 | 24.41 | 1.529 | 18 | 2.24 | 64.5 | 36.9 | 1.9305 | 0.394 | 24.59 | 1.265 | 16 | 2.12 | 65 | 36.9 | 1.9305 | 24.71 | 1.011 | 12 | 2.37 | 72.5 | 40.9 | 1.9948 | 0.236 | 7 | 1.62 | 0.036 | 0.382 | 0.11 | 8 | 2.06 | 0 | 0.323 | 7 | 3.27 | 0 | 43.19 | 0.373 | 10 | 25.6 | 99.3 | 40 | 81 | 0.043 | 43.74 | 0.392 | 10 | 23.7 | 109.1 | 43 | 81 | 0.036 | 25.9 | 23 | 20 |  |  | MINIMUM | 8.7 | 8.7 | 9.7 | 27.1 | 8.2 | 8.2 | 9.2 | 25.6 |  | 9.4032 |  | 13.6051 | 23.3525 | 1.8878 | MINIMUM | 80.5408 | 7193 |  | 697.7974 | [6 empty] | 1.5175 | 1.5175 | 1.8168 | 0.33737 | 0.27603 | 0.3067 | 0.35271 | 0.33231 | 0.34339 | 1.5218 | 2 | 0.048254 | 0.048254 | 0.048744 | 1.0934 | 0.50178 | 0.096912 | 4.0751 | 0.7232 | 5.8712 | 1.1244 | 0.49902 | 0.09423 | 4.0877 | 0.59501 | 8.5632 |  | MIN | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.2 | 10 | 1.313 |  |  |  | MIN | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.4 | 10 | 1.313 |  |  |  | MIN | 0.55 | 10.3 | 26.2136 | 14.4175 | 6.2 | 17.8 | 10 | 1.4417 |  |  |  | 1.313
AVERAGE | 6.3783 | 16.3333 | 16.1667 | 11.6133 | 110.1667 | 162.3333 | 17.3333 | 0.46817 | 0.1165 | 6.065 | 9.6667 | 0.087333 | 6.0733 | 9.6667 |  | 6.0233 | 9.6667 |  | 6.1025 | 0.38225 | 4.5 | 0.56 | 16.125 | 9.225 | 0.48262 | 0.065667 | 6.1475 | 0.31625 | 4 | 0.53 | 16.25 | 9.225 | 0.48262 | 6.1775 | 0.25275 | 3 | 0.5925 | 18.125 | 10.225 | 0.4987 | 0.039333 | 1.1667 | 0.27 | 0.018 | 0.063667 | 0.018333 | 1.3333 | 0.34333 |  | 0.053833 | 1.1667 | 0.545 |  | 7.1983 | 0.062167 | 1.6667 | 4.2667 | 16.55 | 20 | 40.5 | 0.0215 | 7.29 | 0.065333 | 1.6667 | 3.95 | 18.1833 | 21.5 | 40.5 | 0.018 | 4.3167 | 3.8333 | 3.3333 |  |  | MAXIMUM | 9.5 | 9.5 | 10.5 | 29.5 | 8.8 | 8.8 | 9.8 | 27.4 |  | 9.7474 |  | 14.6362 | 24.0394 | 1.9685 | MAXIMUM | 82.1011 | 7378.4876 |  | 810 | [6 empty] | 2.1713 | 1.6285 | 1.9353 | 0.39343 | 0.29507 | 0.32786 | 0.39258 | 0.35287 | 0.35447 | 1.5218 | 4.5 | 0.04976 | 0.049161 | 0.050604 | 1.0972 | 0.50202 | 0.098514 | 4.2028 | 0.79053 | 6.4656 | 1.126 | 0.53034 | 0.11795 | 4.2206 | 0.74477 | 9.3787
MINIMUM | 6.27 | 16 | 16 | 8.95 | 106 | 154 | 17.1 | 0.451 | 0.047 | 5.96 | 8 | 0.082 | 5.99 | 8 |  | 5.94 | 8 |  | 6.04 | 0.293 | 4 | 0.48 | 15.8 | 9 | 0.47377 | 0.063 | 6.1 | 0.288 | 3 | 0.48 | 16 | 9 | 0.47377 | 6.11 | 0.182 | 3 | 0.55 | 17.8 | 10 | 0.49037 | 0.034 | 1 | 0.21 | 0.008 | 0.059 | 0.011 | 1 | 0.28 |  | 0.047 | 1 | 0.5 |  | 7.08 | 0.054 | 1 | 4.2 | 16.2 | 20 | 39 | 0.014 | 7.16 | 0.058 | 1 | 3.5 | 17.9 | 21 | 40 | 0.007 | 4.3 | 3.7 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 28220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 910 | 1200 | 1750 | 1360 | 1520 | 1765 | 1800 | 1860 | 2400 | 0 | 2400 | 2390 | 2710 | 246 | 299 | 35 | 4340 | 860 | 1085 | 141 | 171 | 21 | 2238 | 440 | 875
MAXIMUM | 6.47 | 17 | 17 | 18 | 116 | 174 | 17.7 | 0.496 | 0.186 | 6.19 | 11 | 0.09 | 6.17 | 11 |  | 6.11 | 11 |  | 6.18 | 0.43 | 5 | 0.6 | 16.4 | 9.3 | 0.48557 | 0.069 | 6.2 | 0.365 | 5 | 0.57 | 16.4 | 9.3 | 0.48557 | 6.2 | 0.314 | 3 | 0.69 | 18.4 | 10.3 | 0.50148 | 0.056 | 2 | 0.34 | 0.028 | 0.068 | 0.033 | 2 | 0.41 |  | 0.066 | 2 | 0.61 |  | 7.32 | 0.073 | 2 | 4.4 | 16.8 | 20 | 42 | 0.029 | 7.49 | 0.076 | 2 | 4.2 | 18.4 | 22 | 41 | 0.029 | 4.4 | 3.9 | 3.8 | [17 empty] | AVERAGE | 9406.6667 | [9 empty] | 340 | 303.3333 | 400 | 583.3333 | 453.3333 | 506.6667 | 588.3333 | 600 | 620 | 800 |  | 800 | 796.6667 | 903.3333 | 82 | 99.6667 | 11.6667 | 1446.6667 | 286.6667 | 361.6667 | 47 | 57 | 7 | 746 | 146.6667 | 291.6667
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0539 |  | TOTAL AVG COAG ALK: |  |  |  | 9.6667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.43 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.48 | [5 empty] | 6.1425 |  |  |  |  | 0.066 |  |  |  |  | 0.48 | [6 empty] | 0.066 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 9100 | [9 empty] | 300 | 300 | 400 | 550 | 450 | 500 | 550 | 600 | 600 | 800 |  | 750 | 750 | 850 | 78 | 95 | 11 | 1350 | 260 | 330 | 45 | 53 | 6 | 708 | 120 | 270
[90 empty] | MAXIMUM | 9600 | [9 empty] | 400 | 310 | 400 | 600 | 460 | 520 | 640 | 600 | 640 | 800 |  | 830 | 820 | 940 | 84 | 102 | 12 | 1500 | 305 | 390 | 48 | 60 | 8 | 770 | 160 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.703 |  | TOTAL MGD: |  | 0.015 |  |  | FINISHED SOUTH 1 |  | START: | 23770279 |  | END: | 23770294 |  |  | Alum | 9321 | 8279 | 8279 | 8585 | 8585 | 0.9 | [44 empty] | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.2 | 10 | 1.313
[73 empty] | FINISHED 2 | 16.057 |  | TOTAL MGD: |  | 13.688 |  |  | FINISHED SOUTH 2 |  | START: | 43300812 |  | END: | 43314500 |  |  | Caustic | 4852 | 8144 | 8144
[73 empty] | TOTAL RAW | 30.76 |  | TOTAL MGD: |  | 5.509 |  |  | FINISHED CONWAY |  | START: | 10008012 |  | END: | 10013521 |  |  | Hypochlorite | 17 |  | 31
[76 empty] | TOTAL MGD: |  | 10.548 |  |  | FINISHED PERRY |  | START: | 33285792 |  | END: | 33296340 |  |  | Phosphate | 2227
[76 empty] | TOTAL MGD: |  | 10.6 |  |  | RAW PLANT 1 |  | START: | 30460988 |  | END: | 30471588 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.95 |  |  | RAW PLANT 2 |  | START: | 30422090 |  | END: | 30432040 |  |  | Cal~Flo | 8.92 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.21 |  |  | RAW PLANT 3 |  | START: | 6935610 |  | END: | 6945820 |  |  | Zinc | 1464
[76 empty] | TOTAL MGD: |  | 0.952 |  |  | DECANT |  | START: | 1810904 |  | END: | 1811856 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.5145 |  |  | BLOW DOWN |  | START: | 9056.9369 |  | END: | 9058.4514 |  |  | NH3 | 11.32 |  | BI-SUL | 770
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23770294
43314500
10013521
33296340
30471588
30432040
6945820
1811856
9058.4514
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 15
DATE: | 2018-11-15 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 21 | [33 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-15 | [23 empty] | DATE: | 2018-11-15
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-15 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 0:21 | 1,2,3 | 56 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.8547 | 43419.8158 | 80.3716 | 7071.0506 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.6186 | 1.8168 | 0.33737 | 0.25763 | 0.25763 | 0.33124 | 0.33231 | 0.33231 | 1.5218 | 3 | 0.05036 | 0.05036 | 0.050604 | 1.0711 | 0.50202 | 0.098514 | 4.0933 | 0.76461 | 6.4656 | 1.126 | 0.51267 | 0.11795 | 4.1008 | 0.74477 | 9.3787 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.04 | 0.395 | 4 | 0.5 | 17 | 9.3 | 0.48557 |  | 6.06 | 0.31 | 4 | 0.45 | 18.5 | 9.3 | 0.48557 | 6.12 | 0.305 | 4 | 0.55 | 18.5 | 10.3 | 0.50148 | [13 empty] | 7.38 | 0.067 | 2 | 4.3 | 16.5 |  |  |  | 7.45 | 0.064 | 2 | 4 | 18.5 |  |  |  | 3.8 | 3.9 | 3.4 | [18 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 400 | 550 | 420 | 420 | 540 | 600 | 600 | 800 |  | 840 | 840 | 940 | 82 | 102 | 12 | 1450 | 295 | 390 | 48 | 58 | 8 | 780 | 160 | 315 |  | 1:00 | 0.5 | 9.3 | 27.3548 | 13.6774 | 6.04 | 17 | 10 | 1.3677 | 15 | 6.5 | 0.36557 | 1:00 | 0.45 | 9.3 | 27.3548 | 12.3097 | 6.06 | 18.5 | 10 | 1.231 | 15 | 6.5 | 0.36557 | 1:00 | 0.55 | 10.3 | 26.2136 | 14.4175 | 6.12 | 18.5 | 10 | 1.4417 | 15 | 6.5 | 0.38148
2:00 | [72 empty] | 43419.3205 | 1,2,3 | 56 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.8878 | 43419.3205 | 80.5408 | 7317.0002 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5681 | 1.5681 | 1.726 | 0.34964 | 0.26377 | 0.2699 | 0.36191 | 0.33231 | 0.35447 | 1.5218 | 1 | 0.05036 | 0.049161 | 0.051681 | 1.0711 | 0.50202 | 0.098514 | 4.1033 | 0.77757 | 6.4656 | 1.0791 | 0.53034 | 0.1032 | 4.1077 | 0.7215 | 9.3787 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.54 | 18 | 16 | 8.87 | 109 | 156 | 18 | 0.44 |  | 6 | 10 | 0.086 | 6.07 | 11 |  | 6.04 | 11 | [8 empty] | 0.071 | [14 empty] | 0.037 | 1 | 0.28 |  | 0.064 | 0.018 | 1 | 0.32 |  | 0.048 | 1 | 0.45 | [38 empty] | 9520 | [6 empty] | 0 | 0 | 0 | 310 | 310 | 380 | 570 | 430 | 440 | 590 | 600 | 640 | 800 |  | 840 | 820 | 960 | 82 | 102 | 12 | 1450 | 300 | 390 | 46 | 60 | 7 | 760 | 155 | 315 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43419.8157 | 1,2,3 | 56 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.8547 | 43419.8157 | 80.3716 | 7071.0506 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.6186 | 1.8168 | 0.33737 | 0.25763 | 0.25763 | 0.33124 | 0.33231 | 0.33231 | 1.5218 | 3 | 0.05036 | 0.05036 | 0.050604 | 1.0711 | 0.50202 | 0.098514 | 4.0933 | 0.76461 | 6.4656 | 1.126 | 0.51267 | 0.11795 | 4.1008 | 0.74477 | 9.3787 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.35 | 0.065 | 2 | 4.4 | 16.5 |  |  |  | 7.48 | 0.06 | 2 | 4.2 | 18.5 |  |  |  | 3.9 | 4.2 | 4 | [18 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 400 | 550 | 420 | 420 | 540 | 600 | 600 | 800 |  | 840 | 840 | 940 | 82 | 102 | 12 | 1450 | 295 | 390 | 48 | 58 | 8 | 780 | 160 | 315 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.54 | 18 | 15 | 9.31 | 109 | 156 | 16.7 | 0.454 |  | 6 | 10 | 0.09 | 6.01 | 9 |  | 6.02 | 9 | [8 empty] | 0.063 | [14 empty] | 0.036 | 1 | 0.33 |  | 0.062 | 0.012 | 1 | 0.36 |  | 0.046 | 1 | 0.57 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.038 | [9 empty] | 5.95 | 0.363 | 5 | 0.56 | 16.1 | 9.4 | 0.4156 |  | 6.07 | 0.299 | 5 | 0.59 | 15.7 | 9.5 | 0.49343 | 6.17 | 0.205 | 5 | 0.63 | 18 | 10.5 | 0.50889 |  |  |  | 0.01 |  |  |  |  | 0.019 |  |  |  | 0.004 | 7.32 | 0.059 | 2 | 4.7 | 15.7 | 20 | 40 | 0.015 | 7.5 | 0.059 | 2 | 4.4 | 17.6 | 20 | 41 | 0.007 | 4.1 | 4.2 | 3.9 | [55 empty] | 9:00 | 0.56 | 9.4 | 27.0638 | 15.1557 | 5.95 | 16.1 | 8 | 1.8945 | 15 | 6 | 0.2956 | 9:00 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.07 | 15.7 | 10 | 1.58 | 15 | 6.5 | 0.37343 | 9:00 | 0.63 | 10.5 | 25.7143 | 16.2 | 6.17 | 18 | 10 | 1.62 | 15 | 6.5 | 0.38889
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.48 | 19 | 19 | 9.19 | 109 | 157 | 16.2 | 0.462 |  | 6.06 | 9 | 0.095 | 6.09 | 10 |  | 6.03 | 10 | [8 empty] | 0.066 | [14 empty] | 0.032 | 1 | 0.29 |  | 0.063 | 0.026 | 1 | 0.32 |  | 0.045 | 1 | 0.53 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.11 | 0.343 | 5 | 0.53 | 15.6 | 9.4 | 0.4895 |  | 6.14 | 0.309 | 5 | 0.59 | 15.5 | 9.4 | 0.4895 | 6.18 | 0.202 | 4 | 0.67 | 17.8 | 10.5 | 0.50889 | [13 empty] | 7.43 | 0.065 | 2 | 4.5 | 15.7 |  |  |  | 7.52 | 0.063 | 2 | 4.4 | 17.7 |  |  |  | 4.4 | 4.3 | 2.9 | [55 empty] | 13:00 | 0.53 | 9.4 | 27.0638 | 14.3438 | 6.11 | 15.6 | 10 | 1.4344 | 15 | 6.5 | 0.3695 | 13:00 | 0.59 | 9.4 | 27.0638 | 15.9677 | 6.14 | 15.5 | 10 | 1.5968 | 15 | 6.5 | 0.3695 | 13:00 | 0.67 | 10.5 | 25.7143 | 17.2286 | 6.18 | 17.8 | 10 | 1.7229 | 15 | 6.5 | 0.38889
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.56 | 19 | 18 | 9.27 | 98 | 158 | 16.6 | 0.438 |  | 6.19 | 10 | 0.082 | 6.18 | 11 |  | 6.11 | 10 | [8 empty] | 0.069 | [14 empty] | 0.035 | 1 | 0.28 |  | 0.071 | 0.034 | 2 | 0.39 |  | 0.05 | 1 | 0.47 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.33 | 0.07 | 2 | 4.2 | 15.6 |  |  |  | 7.61 | 0.062 | 1 | 4 | 17.5 |  |  |  | 4.5 | 4.3 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.53 | 21 | 18 | 9.31 | 105 | 157 | 16.3 | 0.448 |  | 6.17 | 11 | 0.105 | 6.16 | 12 |  | 6.14 | 11 | [8 empty] | 0.064 | [14 empty] | 0.035 | 1 | 0.27 |  | 0.069 | 0.027 | 2 | 0.4 |  | 0.05 | 1 | 0.44 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.084 | [9 empty] | 6.22 | 0.361 | 5 | 0.48 | 15.7 | 9.3 | 0.48557 |  | 6.24 | 0.264 | 5 | 0.57 | 15.3 | 9.3 | 0.48557 | 6.23 | 0.331 | 3 | 0.63 | 17.7 | 10.3 | 0.50148 |  |  |  | 0.017 | [9 empty] | 7.54 | 0.068 | 2 | 4.6 | 15.6 | 21 | 40 | 0.022 | 7.67 | 0.064 | 2 | 4.2 | 17.5 | 20 | 37 | 0.026 | 4.5 | 4.4 | 3.4 | [55 empty] | 21:00 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.22 | 15.7 | 10 | 1.313 | 15 | 6.5 | 0.36557 | 21:00 | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.24 | 15.3 | 10 | 1.5592 | 15 | 6.5 | 0.36557 | 21:00 | 0.63 | 10.3 | 26.2136 | 16.5146 | 6.23 | 17.7 | 10 | 1.6515 | 15 | 6.5 | 0.38148
22:00 | [72 empty] | DOSE |  | TOTAL | 27.9 | 27.9 | 30.9 | 86.7 | 26.4 | 26.4 | 29.4 | 82.2 | 0 | 38.2536 | 0 | 41.8306 | 80.0842 | 5.5973 | TOTAL | 241.2839 | 21459.1014 | 0 | 2426.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8053 | 4.8053 | 5.3597 | 1.0244 | 0.77903 | 0.78516 | 1.0244 | 0.99694 | 1.0191 | 4.5654 | 7 | 0.15108 | 0.14988 | 0.15289 | 3.2132 | 1.5061 | 0.29554 | 12.2898 | 2.3068 | 19.3969 | 3.331 | 1.5557 | 0.3391 | 12.3092 | 2.211 | 28.1361 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.55 | 18 | 17 | 9.85 | 105 | 162 | 16.1 | 0.452 |  | 6.11 | 9 | 0.084 | 6.11 | 9 |  | 6.05 | 9 | [8 empty] | 0.066 | [14 empty] | 0.029 | 1 | 0.24 |  | 0.07 | 0.017 | 1 | 0.57 |  | 0.04 | 1 | 0.6 | [22 empty] | AVERAGE | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.8658 | AVERAGE | 80.428 | 7153.0338 |  | 808.8106 | 0 | 0 | 0 |  |  |  | 1.6018 | 1.6018 | 1.7866 | 0.34146 | 0.25968 | 0.26172 | 0.34146 | 0.33231 | 0.3397 | 1.5218 | 2.3333 | 0.05036 | 0.04996 | 0.050963 | 1.0711 | 0.50202 | 0.098514 | 4.0966 | 0.76893 | 6.4656 | 1.1103 | 0.51856 | 0.11303 | 4.1031 | 0.73702 | 9.3787 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.2 | 113 | 103 | 55.8 | 635 | 946 | 99.9 | 2.694 | 0.122 | 36.53 | 59 | 0.542 | 36.62 | 62 | 0 | 36.39 | 60 | 0 | 24.32 | 1.462 | 19 | 2.07 | 64.4 | 37.4 | 1.8762 | 0.399 | 24.51 | 1.182 | 19 | 2.2 | 65 | 37.5 | 1.9541 | 24.7 | 1.043 | 16 | 2.48 | 72 | 41.6 | 2.0207 | 0.204 | 6 | 1.69 | 0.027 | 0.399 | 0.134 | 8 | 2.36 | 0.019 | 0.279 | 6 | 3.06 | 0.004 | 44.35 | 0.394 | 12 | 26.7 | 95.6 | 41 | 80 | 0.037 | 45.23 | 0.372 | 11 | 25.2 | 107.3 | 40 | 78 | 0.033 | 25.2 | 25.3 | 20.9 |  |  | MINIMUM | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.8547 | MINIMUM | 80.3716 | 7071.0506 |  | 808.8106 | [6 empty] | 1.5681 | 1.5681 | 1.726 | 0.33737 | 0.25763 | 0.25763 | 0.33124 | 0.33231 | 0.33231 | 1.5218 | 1 | 0.05036 | 0.049161 | 0.050604 | 1.0711 | 0.50202 | 0.098514 | 4.0933 | 0.76461 | 6.4656 | 1.0791 | 0.51267 | 0.1032 | 4.1008 | 0.7215 | 9.3787 |  | MIN | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.22 | 15.7 | 10 | 1.313 |  |  |  | MIN | 0.45 | 9.3 | 27.3548 | 12.3097 | 6.06 | 18.5 | 10 | 1.231 |  |  |  | MIN | 0.55 | 10.3 | 26.2136 | 14.4175 | 6.12 | 18.5 | 10 | 1.4417 |  |  |  | 1.231
AVERAGE | 6.5333 | 18.8333 | 17.1667 | 9.3 | 105.8333 | 157.6667 | 16.65 | 0.449 | 0.061 | 6.0883 | 9.8333 | 0.090333 | 6.1033 | 10.3333 |  | 6.065 | 10 |  | 6.08 | 0.3655 | 4.75 | 0.5175 | 16.1 | 9.35 | 0.46906 | 0.0665 | 6.1275 | 0.2955 | 4.75 | 0.55 | 16.25 | 9.375 | 0.48851 | 6.175 | 0.26075 | 4 | 0.62 | 18 | 10.4 | 0.50519 | 0.034 | 1 | 0.28167 | 0.0135 | 0.0665 | 0.022333 | 1.3333 | 0.39333 | 0.019 | 0.0465 | 1 | 0.51 |  | 7.3917 | 0.065667 | 2 | 4.45 | 15.9333 | 20.5 | 40 | 0.0185 | 7.5383 | 0.062 | 1.8333 | 4.2 | 17.8833 | 20 | 39 | 0.0165 | 4.2 | 4.2167 | 3.4833 |  |  | MAXIMUM | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.8878 | MAXIMUM | 80.5408 | 7317.0002 |  | 808.8106 | [6 empty] | 1.6186 | 1.6186 | 1.8168 | 0.34964 | 0.26377 | 0.2699 | 0.36191 | 0.33231 | 0.35447 | 1.5218 | 3 | 0.05036 | 0.05036 | 0.051681 | 1.0711 | 0.50202 | 0.098514 | 4.1033 | 0.77757 | 6.4656 | 1.126 | 0.53034 | 0.11795 | 4.1077 | 0.74477 | 9.3787
MINIMUM | 6.48 | 18 | 15 | 8.87 | 98 | 156 | 16.1 | 0.438 | 0.038 | 6 | 9 | 0.082 | 6.01 | 9 |  | 6.02 | 9 |  | 5.95 | 0.343 | 4 | 0.48 | 15.6 | 9.3 | 0.4156 | 0.063 | 6.06 | 0.264 | 4 | 0.45 | 15.3 | 9.3 | 0.48557 | 6.12 | 0.202 | 3 | 0.55 | 17.7 | 10.3 | 0.50148 | 0.029 | 1 | 0.24 | 0.01 | 0.062 | 0.012 | 1 | 0.32 | 0.019 | 0.04 | 1 | 0.44 |  | 7.32 | 0.059 | 2 | 4.2 | 15.6 | 20 | 40 | 0.015 | 7.45 | 0.059 | 1 | 4 | 17.5 | 20 | 37 | 0.007 | 3.8 | 3.9 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 28520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 950 | 1180 | 1670 | 1270 | 1280 | 1670 | 1800 | 1840 | 2400 | 0 | 2520 | 2500 | 2840 | 246 | 306 | 36 | 4350 | 890 | 1170 | 142 | 176 | 23 | 2320 | 475 | 945
MAXIMUM | 6.56 | 21 | 19 | 9.85 | 109 | 162 | 18 | 0.462 | 0.084 | 6.19 | 11 | 0.105 | 6.18 | 12 |  | 6.14 | 11 |  | 6.22 | 0.395 | 5 | 0.56 | 17 | 9.4 | 0.4895 | 0.071 | 6.24 | 0.31 | 5 | 0.59 | 18.5 | 9.5 | 0.49343 | 6.23 | 0.331 | 5 | 0.67 | 18.5 | 10.5 | 0.50889 | 0.037 | 1 | 0.33 | 0.017 | 0.071 | 0.034 | 2 | 0.57 | 0.019 | 0.05 | 1 | 0.6 |  | 7.54 | 0.07 | 2 | 4.7 | 16.5 | 21 | 40 | 0.022 | 7.67 | 0.064 | 2 | 4.4 | 18.5 | 20 | 41 | 0.026 | 4.5 | 4.4 | 4 | [17 empty] | AVERAGE | 9506.6667 | [9 empty] | 316.6667 | 316.6667 | 393.3333 | 556.6667 | 423.3333 | 426.6667 | 556.6667 | 600 | 613.3333 | 800 |  | 840 | 833.3333 | 946.6667 | 82 | 102 | 12 | 1450 | 296.6667 | 390 | 47.3333 | 58.6667 | 7.6667 | 773.3333 | 158.3333 | 315
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0856 |  | TOTAL AVG COAG ALK: |  |  |  | 10.0556 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.395 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.45 | [5 empty] | 6.1275 |  |  |  |  | 0.05 |  |  |  |  | 0.45 | [6 empty] | 0.05 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 9500 | [9 empty] | 310 | 310 | 380 | 550 | 420 | 420 | 540 | 600 | 600 | 800 |  | 840 | 820 | 940 | 82 | 102 | 12 | 1450 | 295 | 390 | 46 | 58 | 7 | 760 | 155 | 315
[90 empty] | MAXIMUM | 9520 | [9 empty] | 320 | 320 | 400 | 570 | 430 | 440 | 590 | 600 | 640 | 800 |  | 840 | 840 | 960 | 82 | 102 | 12 | 1450 | 300 | 390 | 48 | 60 | 8 | 780 | 160 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.901 |  | TOTAL MGD: |  | 0.015 |  |  | FINISHED SOUTH 1 |  | START: | 23770294 |  | END: | 23770309 |  |  | Alum | 9321 | 9085 | 9085 | 7600 | 7600 | 0.9 | [44 empty] | 0.45 | 9.3 | 27.3548 | 12.3097 | 6.06 | 18.5 | 10 | 1.231
[73 empty] | FINISHED 2 | 14.059 |  | TOTAL MGD: |  | 11.886 |  |  | FINISHED SOUTH 2 |  | START: | 43314500 |  | END: | 43326386 |  |  | Caustic | 4746 | 8092 | 8092
[73 empty] | TOTAL RAW | 29.199 |  | TOTAL MGD: |  | 4.353 |  |  | FINISHED CONWAY |  | START: | 10013521 |  | END: | 10017874 |  |  | Hypochlorite | 16 |  | 42
[76 empty] | TOTAL MGD: |  | 9.706 |  |  | FINISHED PERRY |  | START: | 33296340 |  | END: | 33306046 |  |  | Phosphate | 2226
[76 empty] | TOTAL MGD: |  | 9.762 |  |  | RAW PLANT 1 |  | START: | 30471588 |  | END: | 30481350 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.545 |  |  | RAW PLANT 2 |  | START: | 30432040 |  | END: | 30441585 |  |  | Cal~Flo | 6.08 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.892 |  |  | RAW PLANT 3 |  | START: | 6945820 |  | END: | 6955712 |  |  | Zinc | 1398
[76 empty] | TOTAL MGD: |  | 0.881 |  |  | DECANT |  | START: | 1811856 |  | END: | 1812737 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.2308 |  |  | BLOW DOWN |  | START: | 9058.4514 |  | END: | 9059.6822 |  |  | NH3 | 11.1 |  | BI-SUL | 770
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23770309
43326386
10017874
33306046
30481350
30441585
6955712
1812737
9059.6822
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 16
DATE: | 2018-11-16 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 16 |  | 3 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 16 |  | 3 | [37 empty] | 6:00 - 18:00 |  | 16 |  | 3
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-16 | [23 empty] | DATE: | 2018-11-16
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-16 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43420.0097 | 1,2,3 | 56 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.8547 | 43420.0097 | 80.3716 | 7071.0506 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.6186 | 1.8168 | 0.33737 | 0.25763 | 0.25763 | 0.33124 | 0.33231 | 0.33231 | 1.5218 | 3 | 0.05036 | 0.05036 | 0.050604 | 1.0711 | 0.50202 | 0.098514 | 4.0933 | 0.76461 | 6.4656 | 1.126 | 0.51267 | 0.11795 | 4.1008 | 0.74477 | 9.3787 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.355 | 4 | 0.5 | 16 | 9.3 | 0.48557 |  | 6.14 | 0.27 | 4 | 0.55 | 16 | 9.3 | 0.48557 | 6.19 | 0.31 | 3 | 0.6 | 18 | 10.3 | 0.50148 | [13 empty] | 7.27 | 0.065 | 2 | 4.4 | 16 |  |  |  | 7.41 | 0.058 | 1 | 4.2 | 18 |  |  |  | 4.4 | 4.4 | 3.5 | [18 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 400 | 550 | 420 | 420 | 540 | 600 | 600 | 800 |  | 840 | 840 | 940 | 82 | 102 | 12 | 1450 | 295 | 390 | 48 | 58 | 8 | 780 | 160 | 315 |  | 1:00 | 0.5 | 9.3 | 27.3548 | 13.6774 | 6.1 | 16 | 10 | 1.3677 | 15 | 6.5 | 0.36557 | 1:00 | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.14 | 16 | 10 | 1.5045 | 15 | 6.5 | 0.36557 | 1:00 | 0.6 | 10.3 | 26.2136 | 15.7282 | 6.19 | 18 | 10 | 1.5728 | 15 | 6.5 | 0.38148
2:00 | [72 empty] | 6:00 | 1,2,3 | 56 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.8547 | 43420.5205 | 80.3716 | 7194.0254 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 1.5175 | 1.7714 | 0.31897 | 0.2515 | 0.2699 | 0.34351 | 0.32677 | 0.33785 | 1.5218 | 3 | 0.050959 | 0.05006 | 0.048451 | 1.1102 | 0.49217 | 0.098514 | 4.1192 | 0.75165 | 6.2169 | 1.0791 | 0.48615 | 0.11795 | 4.0077 | 0.7215 | 8.9321 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.6 | 20 | 18 | 10.2 | 106 | 162 | 17 | 0.436 |  | 6.02 | 10 | 0.079 | 6.06 | 10 |  | 6.01 | 10 | [8 empty] | 0.057 | [14 empty] | 0.028 | 1 | 0.26 |  | 0.063 | 0.017 | 1 | 0.5 |  | 0.042 | 1 | 0.54 | [38 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 390 | 520 | 410 | 440 | 560 | 590 | 610 | 800 |  | 850 | 835 | 900 | 85 | 100 | 12 | 1460 | 290 | 375 | 46 | 55 | 8 | 760 | 155 | 300 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43420.8055 | 1,2,3 | 56 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.6243 | 43420.8055 | 79.9486 | 7194.0254 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 1.5175 | 1.8168 | 0.29444 | 0.25763 | 0.25763 | 0.29444 | 0.30462 | 0.30462 | 1.3316 | 2 | 0.05036 | 0.05036 | 0.048451 | 1.0972 | 0.50202 | 0.098514 | 4.0705 | 0.76461 | 6.2169 | 1.126 | 0.47731 | 0.088461 | 4.1111 | 0.7215 | 8.9321 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.32 | 0.061 | 1 | 4.5 | 16 |  |  |  | 7.44 | 0.058 | 1 | 4 | 18 |  |  |  | 4.4 | 4.3 | 4.1 | [18 empty] | 9450 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 400 | 480 | 420 | 420 | 480 | 550 | 550 | 700 |  | 840 | 840 | 900 | 84 | 102 | 12 | 1420 | 295 | 375 | 48 | 54 | 6 | 750 | 155 | 300 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43420.8603 | 1,2,3,5 | 40 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.6243 | 43420.8603 | 80.0178 | 7194.0254 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3626 | 1.3626 | 1.6486 | 0.26585 | 0.23262 | 0.23262 | 0.26585 | 0.27766 | 0.27766 | 1.3316 | 2 | 0.045221 | 0.045221 | 0.043965 | 0.98522 | 0.49499 | 0.088461 | 4.1139 | 0.75641 | 5.5826 | 1.0217 | 0.49728 | 0.08027 | 3.7879 | 0.65469 | 8.105 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.54 | 18 | 19 | 10.3 | 107 | 164 | 16.7 | 0.437 |  | 6.06 | 11 | 0.089 | 6.03 | 10 |  | 5.99 | 11 | [8 empty] | 0.059 | [14 empty] | 0.028 | 1 | 0.26 |  | 0.06 | 0.012 | 1 | 0.23 |  | 0.041 | 1 | 0.59 | [38 empty] | 10440 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 400 | 480 | 420 | 420 | 480 | 550 | 550 | 700 |  | 840 | 840 | 900 | 84 | 112 | 12 | 1600 | 325 | 375 | 48 | 62 | 6 | 750 | 155 | 300 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6.06 | 0.342 | 5 | 0.49 | 15.7 | 9.5 | 0.49343 |  | 6.1 | 0.234 | 4 | 0.64 | 15.7 | 9.5 | 0.49343 | 6.2 | 0.315 | 3 | 0.63 | 18.1 | 10.4 | 0.50519 |  |  |  | 0.009 |  |  |  |  | 0.018 |  |  |  |  | 7.5 | 0.057 | 1 | 4.3 | 15.6 | 20 | 36 | 0.016 | 7.49 | 0.05 | 1 | 4.1 | 18.4 | 21 | 38 | 0.014 | 4.5 | 4.3 | 4.1 | [55 empty] | 9:00 | 0.49 | 9.5 | 26.7789 | 13.1217 | 6.06 | 15.7 | 10 | 1.3122 | 15 | 6.5 | 0.37343 | 9:00 | 0.64 | 9.5 | 26.7789 | 17.1385 | 6.1 | 15.7 | 10 | 1.7139 | 15 | 6.5 | 0.37343 | 9:00 | 0.63 | 10.4 | 25.9615 | 16.3558 | 6.2 | 18.1 | 10 | 1.6356 | 15 | 6.5 | 0.38519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.53 | 18 | 19 | 11.9 | 112 | 176 | 16.3 | 0.449 |  | 6.03 | 10 | 0.075 | 6.05 | 11 |  | 6 | 11 | [8 empty] | 0.055 | [14 empty] | 0.024 | 1 | 0.25 |  | 0.05 | 0.016 | 1 | 0.53 |  | 0.039 | 1 | 0.62 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.322 | 4 | 0.57 | 15.8 | 9.5 | 0.41874 |  | 6.02 | 0.244 | 4 | 0.65 | 15.7 | 9.5 | 0.49343 | 6.09 | 0.345 | 3 | 0.74 | 17.1 | 10.5 | 0.50889 | [13 empty] | 7.55 | 0.053 | 1 | 4.6 | 15.4 |  |  |  | 7.44 | 0.049 | 1 | 3.9 | 17.9 |  |  |  | 4.5 | 4.4 | 3.1 | [55 empty] | 13:00 | 0.57 | 9.5 | 26.7789 | 15.264 | 6 | 15.8 | 8 | 1.908 | 15 | 6 | 0.29874 | 13:00 | 0.65 | 9.5 | 26.7789 | 17.4063 | 6.02 | 15.7 | 10 | 1.7406 | 15 | 6.5 | 0.37343 | 13:00 | 0.74 | 10.5 | 25.7143 | 19.0286 | 6.09 | 17.1 | 10 | 1.9029 | 15 | 6.5 | 0.38889
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 19 | 21 | 12.5 | 109 | 183 | 16.7 | 0.462 |  | 6 | 10 | 0.079 | 5.99 | 10 |  | 5.94 | 10 | [8 empty] | 0.06 | [14 empty] | 0.029 | 1 | 0.24 |  | 0.059 | 0.012 | 1 | 0.54 |  | 0.038 | 1 | 0.59 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.15 | 0.052 | 1 | 4.1 | 15.4 |  |  |  | 7.18 | 0.051 | 1 | 3.9 | 18.3 |  |  |  | 4.5 | 4.4 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.42 | 20 | 19 | 13.2 | 107 | 184 | 15.9 | 0.455 |  | 6.01 | 10 | 0.088 | 5.99 | 10 |  | 5.97 | 10 | [8 empty] | 0.057 | [14 empty] | 0.029 | 1 | 0.25 |  | 0.058 | 0.013 | 1 | 0.53 |  | 0.04 | 1 | 0.64 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.049 | [9 empty] | 6.03 | 0.33 | 4 | 0.55 | 15.3 | 9.3 | 0.48557 |  | 6.05 | 0.23 | 4 | 0.65 | 15 | 9.3 | 0.48557 | 6.05 | 0.364 | 3 | 0.71 | 15 | 10.3 | 0.50148 |  |  |  | 0.017 | [9 empty] | 7.13 | 0.056 | 1 | 4.5 | 14.7 | 21 | 38 | 0.024 | 7.14 | 0.055 | 1 | 4.1 | 17.1 | 21 | 35 | 0.021 | 4.6 | 4.4 | 3.4 | [55 empty] | 21:00 | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.03 | 15.3 | 10 | 1.5045 | 15 | 6.5 | 0.36557 | 21:00 | 0.65 | 9.3 | 27.3548 | 17.7806 | 6.05 | 15 | 10 | 1.7781 | 15 | 6.5 | 0.36557 | 21:00 | 0.71 | 10.3 | 26.2136 | 18.6117 | 6.05 | 15 | 10 | 1.8612 | 15 | 6.5 | 0.38148
22:00 | [72 empty] | DOSE |  | TOTAL | 38.2 | 38.2 | 42.2 | 118.6 | 36.2 | 36.2 | 40.2 | 112.6 | 0 | 51.0048 | 0 | 55.7741 | 106.7789 | 6.9581 | TOTAL | 320.7095 | 28653.1268 | 0 | 3235.2423 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0162 | 6.0162 | 7.0537 | 1.2166 | 0.99938 | 1.0178 | 1.235 | 1.2414 | 1.2524 | 5.7067 | 10 | 0.1969 | 0.196 | 0.19147 | 4.2637 | 1.9912 | 0.384 | 16.3968 | 3.0373 | 24.4821 | 4.3527 | 1.9734 | 0.40463 | 16.0075 | 2.8425 | 35.3479 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.63 | 16 | 18 | 14.2 | 110 | 179 | 15.7 | 0.47 |  | 6.04 | 9 | 0.082 | 6.02 | 9 |  | 5.98 | 9 | [8 empty] | 0.064 | [14 empty] | 0.026 | 1 | 0.21 |  | 0.066 | 0.015 | 1 | 0.46 |  | 0.061 | 1 | 0.5 | [22 empty] | AVERAGE | 9.55 | 9.55 | 10.55 | 29.65 | 9.05 | 9.05 | 10.05 | 28.15 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.7395 | AVERAGE | 80.1774 | 7163.2817 |  | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5041 | 1.5041 | 1.7634 | 0.30416 | 0.24984 | 0.25444 | 0.30876 | 0.31034 | 0.31311 | 1.4267 | 2.5 | 0.049225 | 0.049 | 0.047868 | 1.0659 | 0.4978 | 0.096001 | 4.0992 | 0.75932 | 6.1205 | 1.0882 | 0.49335 | 0.10116 | 4.0019 | 0.71062 | 8.837 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.26 | 111 | 114 | 72.3 | 651 | 1048 | 98.3 | 2.709 | 0.086 | 36.16 | 60 | 0.492 | 36.14 | 60 | 0 | 35.89 | 61 | 0 | 24.19 | 1.349 | 17 | 2.11 | 62.8 | 37.6 | 1.8833 | 0.352 | 24.31 | 0.978 | 16 | 2.49 | 62.4 | 37.6 | 1.958 | 24.53 | 1.334 | 12 | 2.68 | 68.2 | 41.5 | 2.017 | 0.164 | 6 | 1.47 | 0.026 | 0.356 | 0.085 | 6 | 2.79 | 0.018 | 0.261 | 6 | 3.48 | 0 | 43.92 | 0.344 | 7 | 26.4 | 93.1 | 41 | 74 | 0.04 | 44.1 | 0.321 | 6 | 24.2 | 107.7 | 42 | 73 | 0.035 | 26.9 | 26.2 | 21.3 |  |  | MINIMUM | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.6243 | MINIMUM | 79.9486 | 7071.0506 |  | 808.8106 | [6 empty] | 1.3626 | 1.3626 | 1.6486 | 0.26585 | 0.23262 | 0.23262 | 0.26585 | 0.27766 | 0.27766 | 1.3316 | 2 | 0.045221 | 0.045221 | 0.043965 | 0.98522 | 0.49217 | 0.088461 | 4.0705 | 0.75165 | 5.5826 | 1.0217 | 0.47731 | 0.08027 | 3.7879 | 0.65469 | 8.105 |  | MIN | 0.49 | 9.5 | 26.7789 | 13.1217 | 6.06 | 15.7 | 10 | 1.3122 |  |  |  | MIN | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.14 | 16 | 10 | 1.5045 |  |  |  | MIN | 0.6 | 10.3 | 26.2136 | 15.7282 | 6.19 | 18 | 10 | 1.5728 |  |  |  | 1.3122
AVERAGE | 6.5433 | 18.5 | 19 | 12.05 | 108.5 | 174.6667 | 16.3833 | 0.4515 | 0.043 | 6.0267 | 10 | 0.082 | 6.0233 | 10 |  | 5.9817 | 10.1667 |  | 6.0475 | 0.33725 | 4.25 | 0.5275 | 15.7 | 9.4 | 0.47083 | 0.058667 | 6.0775 | 0.2445 | 4 | 0.6225 | 15.6 | 9.4 | 0.4895 | 6.1325 | 0.3335 | 3 | 0.67 | 17.05 | 10.375 | 0.50426 | 0.027333 | 1 | 0.245 | 0.013 | 0.059333 | 0.014167 | 1 | 0.465 | 0.018 | 0.0435 | 1 | 0.58 |  | 7.32 | 0.057333 | 1.1667 | 4.4 | 15.5167 | 20.5 | 37 | 0.02 | 7.35 | 0.0535 | 1 | 4.0333 | 17.95 | 21 | 36.5 | 0.0175 | 4.4833 | 4.3667 | 3.55 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.8547 | MAXIMUM | 80.3716 | 7194.0254 |  | 808.8106 | [6 empty] | 1.6186 | 1.6186 | 1.8168 | 0.33737 | 0.25763 | 0.2699 | 0.34351 | 0.33231 | 0.33785 | 1.5218 | 3 | 0.050959 | 0.05036 | 0.050604 | 1.1102 | 0.50202 | 0.098514 | 4.1192 | 0.76461 | 6.4656 | 1.126 | 0.51267 | 0.11795 | 4.1111 | 0.74477 | 9.3787
MINIMUM | 6.42 | 16 | 18 | 10.2 | 106 | 162 | 15.7 | 0.436 | 0.037 | 6 | 9 | 0.075 | 5.99 | 9 |  | 5.94 | 9 |  | 6 | 0.322 | 4 | 0.49 | 15.3 | 9.3 | 0.41874 | 0.055 | 6.02 | 0.23 | 4 | 0.55 | 15 | 9.3 | 0.48557 | 6.05 | 0.31 | 3 | 0.6 | 15 | 10.3 | 0.50148 | 0.024 | 1 | 0.21 | 0.009 | 0.05 | 0.012 | 1 | 0.23 | 0.018 | 0.038 | 1 | 0.5 |  | 7.13 | 0.052 | 1 | 4.1 | 14.7 | 20 | 36 | 0.016 | 7.14 | 0.049 | 1 | 3.9 | 17.1 | 21 | 35 | 0.014 | 4.4 | 4.3 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 38890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 1220 | 1590 | 2030 | 1670 | 1700 | 2060 | 2290 | 2310 | 3000 | 0 | 3370 | 3355 | 3640 | 335 | 416 | 48 | 5930 | 1205 | 1515 | 190 | 229 | 28 | 3040 | 625 | 1215
MAXIMUM | 6.63 | 20 | 21 | 14.2 | 112 | 184 | 17 | 0.47 | 0.049 | 6.06 | 11 | 0.089 | 6.06 | 11 |  | 6.01 | 11 |  | 6.1 | 0.355 | 5 | 0.57 | 16 | 9.5 | 0.49343 | 0.064 | 6.14 | 0.27 | 4 | 0.65 | 16 | 9.5 | 0.49343 | 6.2 | 0.364 | 3 | 0.74 | 18.1 | 10.5 | 0.50889 | 0.029 | 1 | 0.26 | 0.017 | 0.066 | 0.017 | 1 | 0.54 | 0.018 | 0.061 | 1 | 0.64 |  | 7.55 | 0.065 | 2 | 4.6 | 16 | 21 | 38 | 0.024 | 7.49 | 0.058 | 1 | 4.2 | 18.4 | 21 | 38 | 0.021 | 4.6 | 4.4 | 4.1 | [17 empty] | AVERAGE | 9722.5 | [9 empty] | 305 | 305 | 397.5 | 507.5 | 417.5 | 425 | 515 | 572.5 | 577.5 | 750 |  | 842.5 | 838.75 | 910 | 83.75 | 104 | 12 | 1482.5 | 301.25 | 378.75 | 47.5 | 57.25 | 7 | 760 | 156.25 | 303.75
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0106 |  | TOTAL AVG COAG ALK: |  |  |  | 10.0556 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.364 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.49 | [5 empty] | 6.0858 |  |  |  |  | 0.061 |  |  |  |  | 0.49 | [6 empty] | 0.061 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 9450 | [9 empty] | 300 | 300 | 390 | 480 | 410 | 420 | 480 | 550 | 550 | 700 |  | 840 | 835 | 900 | 82 | 100 | 12 | 1420 | 290 | 375 | 46 | 54 | 6 | 750 | 155 | 300
[90 empty] | MAXIMUM | 10440 | [9 empty] | 320 | 320 | 400 | 550 | 420 | 440 | 560 | 600 | 610 | 800 |  | 850 | 840 | 940 | 85 | 112 | 12 | 1600 | 325 | 390 | 48 | 62 | 8 | 780 | 160 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.472 |  | TOTAL MGD: |  | 0.013 |  |  | FINISHED SOUTH 1 |  | START: | 23770309 |  | END: | 23770322 |  |  | Alum | 9249 | 10679 | 10679 | 9406 | 9406 | 0.9 | [44 empty] | 0.49 | 9.5 | 26.7789 | 13.1217 | 6.06 | 15.7 | 10 | 1.3122
[73 empty] | FINISHED 2 | 16.005 |  | TOTAL MGD: |  | 11.459 |  |  | FINISHED SOUTH 2 |  | START: | 43326386 |  | END: | 43337845 |  |  | Caustic | 4542 | 8090 | 8090
[73 empty] | TOTAL RAW | 31.386 |  | TOTAL MGD: |  | 4.854 |  |  | FINISHED CONWAY |  | START: | 10017874 |  | END: | 10022728 |  |  | Hypochlorite | 21 |  | 33
[76 empty] | TOTAL MGD: |  | 11.151 |  |  | FINISHED PERRY |  | START: | 33306046 |  | END: | 33317197 |  |  | Phosphate | 2137
[76 empty] | TOTAL MGD: |  | 9.527 |  |  | RAW PLANT 1 |  | START: | 30481350 |  | END: | 30490877 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.617 |  |  | RAW PLANT 2 |  | START: | 30441585 |  | END: | 30452202 |  |  | Cal~Flo | 10.83 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.242 |  |  | RAW PLANT 3 |  | START: | 6955712 |  | END: | 6966954 |  |  | Zinc | 1398
[76 empty] | TOTAL MGD: |  | 1.19 |  |  | DECANT |  | START: | 1812737 |  | END: | 1813927 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.0589 |  |  | BLOW DOWN |  | START: | 9059.6822 |  | END: | 9060.7411 |  |  | NH3 | 11 |  | BI-SUL | 770
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23770322
43337845
10022728
33317197
30490877
30452202
6966954
1813927
9060.7411
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 17
DATE: | 2018-11-17 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-17 | [23 empty] | DATE: | 2018-11-17
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-17 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43421.0187 | 1,2,3,5 | 40 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 12.7512 | 1,3 | 13.9435 | 26.6947 | 1.6243 | 43421.0187 | 80.0178 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3626 | 1.3626 | 1.6486 | 0.26585 | 0.23262 | 0.23262 | 0.26585 | 0.27766 | 0.27766 | 1.3316 | 2 | 0.045221 | 0.045221 | 0.043965 | 0.98522 | 0.49499 | 0.088461 | 4.1139 | 0.75641 | 5.5826 | 1.0217 | 0.49728 | 0.08027 | 3.7879 | 0.65469 | 8.105 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6 | 0.36 | 4 | 0.56 | 15.5 | 10.3 | 0.4439 |  | 6.01 | 0.29 | 4 | 0.64 | 15.5 | 10.3 | 0.52487 | 6.05 | 0.39 | 3 | 0.62 | 16.5 | 11.3 | 0.53852 | [13 empty] | 7.27 | 0.054 | 1 | 4.4 | 15 |  |  |  | 7.21 | 0.052 | 1 | 4 | 18 |  |  |  | 4.6 | 4.5 | 3.6 | [18 empty] | 10440 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 400 | 480 | 420 | 420 | 480 | 550 | 550 | 700 |  | 840 | 840 | 900 | 84 | 112 | 12 | 1600 | 325 | 375 | 48 | 62 | 6 | 750 | 155 | 300 |  | 1:00 | 0.56 | 10.3 | 24.699 | 13.8315 | 6 | 15.5 | 8 | 1.7289 | 15 | 6 | 0.3239 | 1:00 | 0.64 | 10.3 | 24.699 | 15.8074 | 6.01 | 15.5 | 10 | 1.5807 | 15 | 6.5 | 0.40487 | 1:00 | 0.62 | 11.3 | 23.8938 | 14.8142 | 6.05 | 16.5 | 10 | 1.4814 | 15 | 6.5 | 0.41852
2:00 | [72 empty] | 9:04 | 1,2,3,5 | 40 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 13.0896 | 1,3 | 15.9408 | 29.0304 | 1.6243 | 43421.4184 | 80.3244 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4535 | 1.5443 | 1.6486 | 0.26585 | 0.23262 | 0.29908 | 0.2437 | 0.28271 | 0.3029 | 1.3316 | 2.5 | 0.050604 | 0.049528 | 0.049827 | 1.126 | 0.49941 | 0.1032 | 4.0973 | 0.74477 | 5.5826 | 1.1069 | 0.48124 | 0.08027 | 3.7446 | 0.67581 | 8.105 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.61 | 20 | 18 | 14.4 | 106 | 196 | 16.5 | 0.443 |  | 6.01 | 10 | 0.08 | 6 | 10 |  | 5.95 | 10 | [8 empty] | 0.058 | [14 empty] | 0.042 | 1 | 0.2 |  | 0.061 | 0.015 | 1 | 0.42 |  | 0.058 | 1 | 0.45 | [38 empty] | 10480 | [6 empty] | 0 | 0 | 0 | 320 | 340 | 400 | 480 | 420 | 540 | 440 | 560 | 600 | 700 |  | 940 | 920 | 1020 | 96 | 113 | 14 | 1580 | 320 | 375 | 52 | 60 | 6 | 780 | 160 | 300 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43421.8176 | 1,2,3 | 40 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 13.0896 | 1,3 | 15.9408 | 29.0304 | 1.7294 | 43421.8176 | 79.9486 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 1.5175 | 1.8168 | 0.29444 | 0.25763 | 0.2699 | 0.2699 | 0.29908 | 0.29908 | 1.3316 | 3.5 | 0.05036 | 0.05036 | 0.050604 | 1.0972 | 0.50202 | 0.098514 | 4.1005 | 0.75165 | 5.8025 | 1.126 | 0.51267 | 0.11795 | 3.8015 | 0.68892 | 8.1878 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.18 | 0.055 | 1 | 4.5 | 15 |  |  |  | 7.2 | 0.05 | 1 | 4.2 | 18 |  |  |  | 4.6 | 4.6 | 3.6 | [18 empty] | 9450 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 400 | 480 | 420 | 440 | 440 | 540 | 540 | 700 |  | 840 | 840 | 940 | 84 | 102 | 12 | 1420 | 290 | 350 | 48 | 58 | 8 | 720 | 148 | 275 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.54 | 21 | 18 | 15.4 | 111 | 200 | 16.1 | 0.463 |  | 6.04 | 9 | 0.09 | 6 | 10 |  | 5.98 | 10 | [8 empty] | 0.057 | [14 empty] | 0.029 | 2 | 0.3 |  | 0.055 | 0.012 | 2 | 0.37 |  | 0.039 | 2 | 0.56 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.051 | [9 empty] | 6.04 | 0.466 | 5 | 0.48 | 15.4 | 10.2 | 0.52094 |  | 6.09 | 0.337 | 4 | 0.55 | 15.1 | 10.3 | 0.52487 | 6.11 | 0.404 | 3 | 0.66 | 17.1 | 11.3 | 0.53852 |  |  |  | 0.013 |  |  |  |  | 0.019 |  |  |  | 0.011 | 7.25 | 0.052 | 1 | 4.3 | 14.8 | 21 | 38 | 0.023 | 7.33 | 0.057 | 1 | 4.3 | 17.6 | 22 | 40 | 0.012 | 4.5 | 4.4 | 4 | [55 empty] | 9:00 | 0.48 | 10.2 | 24.9412 | 11.9718 | 6.04 | 15.4 | 10 | 1.1972 | 15 | 6.5 | 0.40094 | 9:00 | 0.55 | 10.3 | 24.699 | 13.5845 | 6.09 | 15.1 | 10 | 1.3584 | 15 | 6.5 | 0.40487 | 9:00 | 0.66 | 11.3 | 23.8938 | 15.7699 | 6.11 | 17.1 | 10 | 1.577 | 15 | 6.5 | 0.41852
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.48 | 20 | 19 | 15.7 | 113 | 201 | 16.2 | 0.463 |  | 6.05 | 11 | 0.09 | 6.04 | 10 |  | 5.99 | 11 | [8 empty] | 0.061 | [14 empty] | 0.046 | 2 | 0.47 |  | 0.06 | 0.014 | 1 | 0.53 |  | 0.054 | 1 | 0.48 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.06 | 0.442 | 5 | 0.47 | 15.2 | 10.3 | 0.52487 |  | 6.14 | 0.381 | 5 | 0.48 | 15.6 | 10.3 | 0.52487 | 6.04 | 0.322 | 4 | 0.7 | 13.3 | 11.3 | 0.74778 | [13 empty] | 7.17 | 0.056 | 2 | 4.5 | 14.7 |  |  |  | 7.19 | 0.063 | 2 | 4.3 | 17.6 |  |  |  | 4.5 | 4.4 | 3.2 | [55 empty] | 13:00 | 0.47 | 10.3 | 24.699 | 11.6085 | 6.06 | 15.2 | 10 | 1.1609 | 15 | 6.5 | 0.40487 | 13:00 | 0.48 | 10.3 | 24.699 | 11.8555 | 6.14 | 15.6 | 10 | 1.1856 | 15 | 6.5 | 0.40487 | 13:00 | 0.7 | 11.3 | 23.8938 | 16.7257 | 6.04 | 13.3 | 15 | 1.115 | 10 | 6.5 | 0.62778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 20 | 19 | 15.8 | 114 | 206 | 15.9 | 0.474 |  | 6.04 | 10 | 0.085 | 6.01 | 11 |  | 6 | 11 | [8 empty] | 0.067 | [14 empty] | 0.04 | 1 | 0.34 |  | 0.064 | 0.015 | 1 | 0.54 |  | 0.049 | 1 | 0.59 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.18 | 0.055 | 2 | 4.7 | 14.9 |  |  |  | 7.22 | 0.061 | 2 | 4.5 | 17.3 |  |  |  | 4.6 | 4.3 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.39 | 20 | 19 | 16.1 | 111 | 205 | 15.3 | 0.473 |  | 6.07 | 12 | 0.087 | 6.05 | 12 |  | 6.02 | 11 | [8 empty] | 0.06 | [14 empty] | 0.035 | 1 | 0.3 |  | 0.062 | 0.012 | 1 | 0.51 |  | 0.047 | 1 | 0.61 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.066 | [9 empty] | 6.06 | 0.422 | 4 | 0.57 | 14.9 | 9.3 | 0.66835 |  | 6.07 | 0.308 | 4 | 0.71 | 14.7 | 9.3 | 0.66835 | 6.11 | 0.468 | 4 | 0.92 | 15.1 | 10.3 | 0.50148 |  |  |  | 0.015 | [9 empty] | 7.11 | 0.06 | 1 | 4.3 | 14.3 | 21 | 40 | 0.029 | 7.13 | 0.063 | 1 | 4.4 | 16.7 | 20 | 40 | 0.021 | 4.7 | 4.4 | 3.3 | [55 empty] | 21:00 | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.06 | 14.9 | 15 | 1.0395 | 10 | 6.5 | 0.54835 | 21:00 | 0.71 | 9.3 | 27.3548 | 19.4219 | 6.07 | 14.7 | 15 | 1.2948 | 10 | 6.5 | 0.54835 | 21:00 | 0.92 | 10.3 | 26.2136 | 24.1165 | 6.11 | 15.1 | 10 | 2.4117 | 15 | 6.5 | 0.38148
22:00 | [72 empty] | DOSE |  | TOTAL | 29.9 | 29.9 | 32.9 | 92.7 | 28.4 | 28.4 | 31.4 | 88.2 | 0 | 38.9304 | 0 | 45.8251 | 84.7555 | 4.9781 | TOTAL | 240.2907 | 24717.9336 | 0 | 2426.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3336 | 4.4244 | 5.1141 | 0.82613 | 0.72287 | 0.8016 | 0.77944 | 0.85945 | 0.87965 | 3.9947 | 8 | 0.14619 | 0.14511 | 0.1444 | 3.2084 | 1.4964 | 0.29018 | 12.3117 | 2.2528 | 16.9676 | 3.2545 | 1.4912 | 0.27849 | 11.3339 | 2.0194 | 24.3979 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.64 | 19 | 19 | 15.4 | 114 | 204 | 15.4 | 0.484 |  | 6.13 | 13 | 0.084 | 6.09 | 12 |  | 6.07 | 12 | [8 empty] | 0.06 | [14 empty] | 0.037 | 1 | 0.33 |  | 0.06 | 0.012 | 1 | 0.49 |  | 0.05 | 1 | 0.54 | [22 empty] | AVERAGE | 9.9667 | 9.9667 | 10.9667 | 30.9 | 9.4667 | 9.4667 | 10.4667 | 29.4 |  | 12.9768 |  | 15.275 | 28.2518 | 1.6594 | AVERAGE | 80.0969 | 8239.3112 |  | 808.8106 | 0 | 0 | 0 |  |  |  | 1.4445 | 1.4748 | 1.7047 | 0.27538 | 0.24096 | 0.2672 | 0.25981 | 0.28648 | 0.29322 | 1.3316 | 2.6667 | 0.048728 | 0.048369 | 0.048132 | 1.0695 | 0.4988 | 0.096727 | 4.1039 | 0.75095 | 5.6559 | 1.0848 | 0.49706 | 0.09283 | 3.778 | 0.67314 | 8.1326 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.2 | 120 | 112 | 92.8 | 669 | 1212 | 95.4 | 2.8 | 0.117 | 36.34 | 65 | 0.516 | 36.19 | 65 | 0 | 5.942 | 5 | 0 | 24.16 | 1.69 | 18 | 2.08 | 61 | 40.1 | 2.1581 | 0.363 | 24.31 | 1.316 | 17 | 2.38 | 60.9 | 40.2 | 2.243 | 24.31 | 1.584 | 14 | 2.9 | 62 | 44.2 | 2.3263 | 0.229 | 8 | 1.94 | 0.028 | 0.362 | 0.08 | 7 | 2.86 | 0.019 | 0.1 | 7 | 3.23 | 0.011 | 43.16 | 0.332 | 8 | 26.7 | 88.7 | 42 | 78 | 0.052 | 43.28 | 0.346 | 8 | 25.7 | 105.2 | 42 | 80 | 0.033 | 27.5 | 26.6 | 21 |  |  | MINIMUM | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 |  | 12.7512 |  | 13.9435 | 26.6947 | 1.6243 | MINIMUM | 79.9486 | 8239.3112 |  | 808.8106 | [6 empty] | 1.3626 | 1.3626 | 1.6486 | 0.26585 | 0.23262 | 0.23262 | 0.2437 | 0.27766 | 0.27766 | 1.3316 | 2 | 0.045221 | 0.045221 | 0.043965 | 0.98522 | 0.49499 | 0.088461 | 4.0973 | 0.74477 | 5.5826 | 1.0217 | 0.48124 | 0.08027 | 3.7446 | 0.65469 | 8.105 |  | MIN | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.06 | 14.9 | 15 | 1.0395 |  |  |  | MIN | 0.48 | 10.3 | 24.699 | 11.8555 | 6.14 | 15.6 | 10 | 1.1856 |  |  |  | MIN | 0.7 | 11.3 | 23.8938 | 16.7257 | 6.04 | 13.3 | 15 | 1.115 |  |  |  | 1.0395
AVERAGE | 6.5333 | 20 | 18.6667 | 15.4667 | 111.5 | 202 | 15.9 | 0.46667 | 0.0585 | 6.0567 | 10.8333 | 0.086 | 6.0317 | 10.8333 |  | 6.0017 | 10.8333 |  | 6.04 | 0.4225 | 4.5 | 0.52 | 15.25 | 10.025 | 0.53952 | 0.0605 | 6.0775 | 0.329 | 4.25 | 0.595 | 15.225 | 10.05 | 0.56074 | 6.0775 | 0.396 | 3.5 | 0.725 | 15.5 | 11.05 | 0.58157 | 0.038167 | 1.3333 | 0.32333 | 0.014 | 0.060333 | 0.013333 | 1.1667 | 0.47667 | 0.019 | 0.0495 | 1.1667 | 0.53833 | 0.011 | 7.1933 | 0.055333 | 1.3333 | 4.45 | 14.7833 | 21 | 39 | 0.026 | 7.2133 | 0.057667 | 1.3333 | 4.2833 | 17.5333 | 21 | 40 | 0.0165 | 4.5833 | 4.4333 | 3.5 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 13.0896 |  | 15.9408 | 29.0304 | 1.7294 | MAXIMUM | 80.3244 | 8239.3112 |  | 808.8106 | [6 empty] | 1.5175 | 1.5443 | 1.8168 | 0.29444 | 0.25763 | 0.29908 | 0.2699 | 0.29908 | 0.3029 | 1.3316 | 3.5 | 0.050604 | 0.05036 | 0.050604 | 1.126 | 0.50202 | 0.1032 | 4.1139 | 0.75641 | 5.8025 | 1.126 | 0.51267 | 0.11795 | 3.8015 | 0.68892 | 8.1878
MINIMUM | 6.39 | 19 | 18 | 14.4 | 106 | 196 | 15.3 | 0.443 | 0.051 | 6.01 | 9 | 0.08 | 6 | 10 |  | 5.95 | 10 |  | 6 | 0.36 | 4 | 0.47 | 14.9 | 9.3 | 0.4439 | 0.057 | 6.01 | 0.29 | 4 | 0.48 | 14.7 | 9.3 | 0.52487 | 6.04 | 0.322 | 3 | 0.62 | 13.3 | 10.3 | 0.50148 | 0.029 | 1 | 0.2 | 0.013 | 0.055 | 0.012 | 1 | 0.37 | 0.019 | 0.039 | 1 | 0.45 | 0.011 | 7.11 | 0.052 | 1 | 4.3 | 14.3 | 21 | 38 | 0.023 | 7.13 | 0.05 | 1 | 4 | 16.7 | 20 | 40 | 0.012 | 4.5 | 4.3 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 30370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 940 | 1200 | 1440 | 1260 | 1400 | 1360 | 1650 | 1690 | 2100 | 0 | 2620 | 2600 | 2860 | 264 | 327 | 38 | 4600 | 935 | 1100 | 148 | 180 | 20 | 2250 | 463 | 875
MAXIMUM | 6.64 | 21 | 19 | 16.1 | 114 | 206 | 16.5 | 0.484 | 0.066 | 6.13 | 13 | 0.09 | 6.09 | 12 |  | 6.07 | 12 |  | 6.06 | 0.466 | 5 | 0.57 | 15.5 | 10.3 | 0.66835 | 0.067 | 6.14 | 0.381 | 5 | 0.71 | 15.6 | 10.3 | 0.66835 | 6.11 | 0.468 | 4 | 0.92 | 17.1 | 11.3 | 0.74778 | 0.046 | 2 | 0.47 | 0.015 | 0.064 | 0.015 | 2 | 0.54 | 0.019 | 0.058 | 2 | 0.61 | 0.011 | 7.27 | 0.06 | 2 | 4.7 | 15 | 21 | 40 | 0.029 | 7.33 | 0.063 | 2 | 4.5 | 18 | 22 | 40 | 0.021 | 4.7 | 4.6 | 4 | [17 empty] | AVERAGE | 10123.3333 | [9 empty] | 306.6667 | 313.3333 | 400 | 480 | 420 | 466.6667 | 453.3333 | 550 | 563.3333 | 700 |  | 873.3333 | 866.6667 | 953.3333 | 88 | 109 | 12.6667 | 1533.3333 | 311.6667 | 366.6667 | 49.3333 | 60 | 6.6667 | 750 | 154.3333 | 291.6667
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.03 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.468 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.065 |  |  |  |  | 0.058 |  |  |  |  | 0.47 | [6 empty] | 0.058 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 9450 | [9 empty] | 300 | 300 | 400 | 480 | 420 | 420 | 440 | 540 | 540 | 700 |  | 840 | 840 | 900 | 84 | 102 | 12 | 1420 | 290 | 350 | 48 | 58 | 6 | 720 | 148 | 275
[90 empty] | MAXIMUM | 10480 | [9 empty] | 320 | 340 | 400 | 480 | 420 | 540 | 480 | 560 | 600 | 700 |  | 940 | 920 | 1020 | 96 | 113 | 14 | 1600 | 325 | 375 | 52 | 62 | 8 | 780 | 160 | 300
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.463 |  | TOTAL MGD: |  | 0.008 |  |  | FINISHED SOUTH 1 |  | START: | 23770322 |  | END: | 23770330 |  |  | Alum | 9312 | 9245 | 9245 | 8150 | 8150 | 0.9 | [44 empty] | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.06 | 14.9 | 15 | 1.0395
[73 empty] | FINISHED 2 | 15.525 |  | TOTAL MGD: |  | 12.455 |  |  | FINISHED SOUTH 2 |  | START: | 43337845 |  | END: | 43350300 |  |  | Caustic | 4411 | 8034 | 8034
[73 empty] | TOTAL RAW | 31.096 |  | TOTAL MGD: |  | 4.442 |  |  | FINISHED CONWAY |  | START: | 10022728 |  | END: | 10027170 |  |  | Hypochlorite | 19 |  | 42
[76 empty] | TOTAL MGD: |  | 11.083 |  |  | FINISHED PERRY |  | START: | 33317197 |  | END: | 33328280 |  |  | Phosphate | 2092
[76 empty] | TOTAL MGD: |  | 9.898 |  |  | RAW PLANT 1 |  | START: | 30490877 |  | END: | 30500775 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.999 |  |  | RAW PLANT 2 |  | START: | 30452202 |  | END: | 30462201 |  |  | Cal~Flo | 7.25 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.199 |  |  | RAW PLANT 3 |  | START: | 6966954 |  | END: | 6978153 |  |  | Zinc | 1390
[76 empty] | TOTAL MGD: |  | 0.526 |  |  | DECANT |  | START: | 1813927 |  | END: | 1814453 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.3481 |  |  | BLOW DOWN |  | START: | 9060.7411 |  | END: | 9062.0892 |  |  | NH3 | 11 |  | BI-SUL | 750
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23770330
43350300
10027170
33328280
30500775
30462201
6978153
1814453
9062.0892
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 18
DATE: | 2018-11-18 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-18 | [23 empty] | DATE: | 2018-11-18
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-18 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [7 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  | 5.625 |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43422.0211 | 1,2,3 | 40 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 13.0896 | 1,3 | 15.9408 | 29.0304 | 1.7294 | 43422.0211 | 79.9486 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 1.5175 | 1.8168 | 0.29444 | 0.25763 | 0.2699 | 0.2699 | 0.29908 | 0.29908 | 1.3316 | 3.5 | 0.05036 | 0.05036 | 0.050604 | 1.0972 | 0.50202 | 0.098514 | 4.1005 | 0.75165 | 5.8025 | 1.126 | 0.51267 | 0.11795 | 3.8015 | 0.68892 | 8.1878 |  |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.08 | 0.446 | 4 | 0.55 | 15 | 9.3 | 0.48557 |  | 6.12 | 0.355 | 4 | 0.65 | 15 | 9.3 | 0.48557 | 6.13 | 0.47 | 4 | 0.75 | 15.5 | 10.3 | 0.50148 | [13 empty] | 7.24 | 0.057 | 1 | 4.2 | 14.5 |  |  |  | 7.23 | 0.055 | 1 | 4.2 | 16.5 |  |  |  | 4.6 | 4.4 | 3.6 | [18 empty] | 9450 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 400 | 480 | 420 | 440 | 440 | 540 | 540 | 700 |  | 840 | 840 | 940 | 84 | 102 | 12 | 1420 | 290 | 350 | 48 | 58 | 8 | 720 | 148 | 275 |  |  | 1:00 | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.08 | 15 | 10 | 1.5045 | 15 | 6.5 | 0.36557 | 1:00 | 0.65 | 9.3 | 27.3548 | 17.7806 | 6.12 | 15 | 10 | 1.7781 | 15 | 6.5 | 0.36557 | 1:00 | 0.75 | 10.3 | 26.2136 | 19.6602 | 6.13 | 15.5 | 10 | 1.966 | 15 | 6.5 | 0.38148
2:00 | [72 empty] | 43422.3584 | 1,2,3 | 50 | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 10.9109 | 1,3 | 14.1667 | 25.0776 | 1.7294 | 43422.3584 | 79.5256 | 7624.4372 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7198 | 1.6186 | 1.5443 | 0.29444 | 0.29444 | 0.31897 | 0.22083 | 0.288 | 0.288 | 1.3316 | 5 | 0.049161 | 0.05036 | 0.049528 | 1.0972 | 0.50202 | 0.098514 | 4.0931 | 0.71277 | 5.8025 | 1.126 | 0.53034 | 0.088461 | 3.7991 | 0.60513 | 8.1878 |  |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.56 | 22 | 20 | 15.2 | 112 | 198 | 16 | 0.44 |  | 6 | 12 | 0.088 | 6.01 | 12 |  | 5.99 | 12 | [8 empty] | 0.058 | [14 empty] | 0.034 | 1 | 0.35 |  | 0.06 | 0.016 | 1 | 0.45 |  | 0.048 | 1 | 0.5 | [38 empty] | 9400 | [6 empty] | 0 | 0 | 0 | 340 | 320 | 340 | 480 | 480 | 520 | 360 | 520 | 520 | 700 |  | 820 | 840 | 920 | 84 | 102 | 12 | 1340 | 275 | 350 | 48 | 60 | 6 | 640 | 130 | 275 |  |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43422.8006 | 1,2,3 | 50 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 10.9109 | 1,3 | 14.1667 | 25.0776 | 1.8792 | 43422.8006 | 80.0178 | 7009.5632 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5443 | 1.5443 | 1.8547 | 0.26585 | 0.26585 | 0.26585 | 0.26585 | 0.29281 | 0.29281 | 1.3316 | 4.5 | 0.050066 | 0.050604 | 0.049827 | 1.126 | 0.49499 | 0.1032 | 4.0889 | 0.76805 | 5.9547 | 1.1069 | 0.49728 | 0.10703 | 3.7891 | 0.69271 | 8.5103 |  |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.28 | 0.055 | 1 | 4.3 | 14.5 |  |  |  | 7.2 | 0.053 | 1 | 4 | 16.5 |  |  |  | 4.6 | 4.4 | 3.6 | [18 empty] | 10440 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 450 | 480 | 480 | 480 | 480 | 580 | 580 | 700 |  | 930 | 940 | 1020 | 96 | 112 | 14 | 1600 | 330 | 400 | 52 | 62 | 8 | 800 | 164 | 315 |  |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [128 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.4 | 21 | 20 | 15.3 | 117 | 205 | 15.7 | 0.485 |  | 6.06 | 11 | 0.099 | 6.05 | 11 |  | 6.02 | 10 | [8 empty] | 0.063 | [14 empty] | 0.035 | 1 | 0.44 |  | 0.058 | 0.012 | 2 | 0.46 |  | 0.048 | 1 | 0.57 | [76 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [128 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.049 | [9 empty] | 5.97 | 0.383 | 4 | 0.71 | 14.7 | 9.2 | 0.59013 |  | 5.91 | 0.322 | 5 | 0.74 | 15.2 | 9.3 | 0.41245 | 5.92 | 0.441 | 5 | 0.84 | 15.8 | 10.3 | 0.42519 |  |  |  | 0.016 |  |  |  |  | 0.024 |  |  |  | 0.013 | 7.16 | 0.053 | 1 | 4.1 | 14.4 | 20 | 38 | 0.023 | 7.19 | 0.056 | 1 | 3.8 | 17.4 | 21 | 36 | 0.016 | 4.5 | 4.3 | 4 | [56 empty] | 9:00 | 0.71 | 9.2 | 27.6522 | 19.633 | 5.97 | 14.7 | 13 | 1.5102 | 10 | 6 | 0.47013 | 9:00 | 0.74 | 9.3 | 27.3548 | 20.2426 | 5.91 | 15.2 | 8 | 2.5303 | 15 | 6 | 0.29245 | 9:00 | 0.84 | 10.3 | 26.2136 | 22.0194 | 5.92 | 15.8 | 8 | 2.7524 | 15 | 6 | 0.30519
10:00 | [128 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.57 | 16 | 17 | 15.9 | 119 | 203 | 15.6 | 0.479 |  | 5.88 | 6 | 0.087 | 5.87 | 6 |  | 5.74 | 6 | [8 empty] | 0.059 | [14 empty] | 0.026 | 2 | 0.45 |  | 0.058 | 0.012 | 2 | 0.54 |  | 0.042 | 2 | 0.53 | [76 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [128 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.337 | 4 | 0.7 | 15.1 | 9.2 | 0.40931 |  | 5.97 | 0.269 | 4 | 0.75 | 15.4 | 9.3 | 0.41245 | 5.96 | 0.295 | 4 | 0.87 | 15.9 | 10.3 | 0.42519 | [13 empty] | 7.12 | 0.044 | 2 | 4.3 | 14.4 |  |  |  | 7.14 | 0.054 | 2 | 3.5 | 17.7 |  |  |  | 4.5 | 4.2 | 3.2 | [56 empty] | 13:00 | 0.7 | 9.2 | 27.6522 | 19.3565 | 6 | 15.1 | 8 | 2.4196 | 15 | 6 | 0.28931 | 13:00 | 0.75 | 9.3 | 27.3548 | 20.5161 | 5.97 | 15.4 | 8 | 2.5645 | 15 | 6 | 0.29245 | 13:00 | 0.87 | 10.3 | 26.2136 | 22.8058 | 5.96 | 15.9 | 8 | 2.8507 | 15 | 6 | 0.30519
14:00 | [126 empty] | #REF! |  | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.48 | 17 | 18 | 15.4 | 117 | 193 | 15.7 | 0.481 |  | 6.18 | 9 | 0.091 | 6.16 | 9 |  | 6.13 | 9 | [8 empty] | 0.069 | [14 empty] | 0.037 | 2 | 0.31 |  | 0.066 | 0.018 | 2 | 0.42 |  | 0.052 | 2 | 0.41 | [76 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [128 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.55 | 0.046 | 2 | 3.9 | 14.5 |  |  |  | 7.45 | 0.05 | 2 | 3.7 | 17.8 |  |  |  | 4.6 | 4.2 | 3.3 | [56 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [128 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.49 | 16 | 18 | 14.8 | 112 | 205 | 15.6 | 0.478 |  | 6.16 | 9 | 0.084 | 6.12 | 9 |  | 6.12 | 9 | [8 empty] | 0.068 | [14 empty] | 0.035 | 2 | 0.24 |  | 0.066 | 0.015 | 2 | 0.39 |  | 0.05 | 2 | 0.37 | [76 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [128 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.061 | [9 empty] | 6.15 | 0.332 | 3 | 0.57 | 15 | 10.3 | 0.52487 |  | 6.18 | 0.298 | 3 | 0.78 | 14.9 | 10.3 | 0.72731 | 6.15 | 0.374 | 3 | 0.88 | 15.7 | 11.3 | 0.53852 |  |  |  | 0.014 | [9 empty] | 7.24 | 0.06 | 2 | 4.3 | 14.8 | 20 | 39 | 0.027 | 7.3 | 0.057 | 2 | 4.2 | 17.1 | 20 | 34 | 0.021 | 4.5 | 4.2 | 3.3 | [56 empty] | 21:00 | 0.57 | 10.3 | 24.699 | 14.0784 | 6.15 | 15 | 10 | 1.4078 | 15 | 6.5 | 0.40487 | 21:00 | 0.78 | 10.3 | 24.699 | 19.2652 | 6.18 | 14.9 | 15 | 1.2843 | 10 | 6.5 | 0.60731 | 21:00 | 0.88 | 11.3 | 23.8938 | 21.0265 | 6.15 | 15.7 | 10 | 2.1027 | 15 | 6.5 | 0.41852
22:00 | [72 empty] | DOSE |  | TOTAL | 28.9 | 28.9 | 31.9 | 89.7 | 27.4 | 27.4 | 30.4 | 85.2 | 0 | 34.9114 | 0 | 44.2742 | 79.1856 | 5.3381 | TOTAL | 239.4919 | 22873.3116 | 0 | 2426.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7816 | 4.6804 | 5.2158 | 0.85472 | 0.81792 | 0.85472 | 0.75658 | 0.87989 | 0.87989 | 3.9947 | 13 | 0.14959 | 0.15132 | 0.14996 | 3.3203 | 1.499 | 0.30023 | 12.2825 | 2.2325 | 17.5597 | 3.3588 | 1.5403 | 0.31344 | 11.3896 | 1.9868 | 24.8858 |  |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.4 | 19 | 18 | 16.1 | 117 | 204 | 15.2 | 0.497 |  | 5.97 | 9 | 0.082 | 5.96 | 9 |  | 5.94 | 9 | [8 empty] | 0.06 | [14 empty] | 0.028 | 1 | 0.29 |  | 0.059 | 0.01 | 1 | 0.38 |  | 0.042 | 1 | 0.37 | [22 empty] | AVERAGE | 9.6333 | 9.6333 | 10.6333 | 29.9 | 9.1333 | 9.1333 | 10.1333 | 28.4 |  | 11.6371 |  | 14.7581 | 26.3952 | 1.7794 | AVERAGE | 79.8306 | 7624.4372 |  | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5939 | 1.5601 | 1.7386 | 0.28491 | 0.27264 | 0.28491 | 0.25219 | 0.2933 | 0.2933 | 1.3316 | 4.3333 | 0.049862 | 0.050441 | 0.049986 | 1.1068 | 0.49967 | 0.10008 | 4.0942 | 0.74416 | 5.8532 | 1.1196 | 0.51343 | 0.10448 | 3.7965 | 0.66225 | 8.2953 |  |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.9 | 111 | 111 | 92.7 | 694 | 1208 | 93.8 | 2.86 | 0.11 | 36.25 | 56 | 0.531 | 36.17 | 56 | 0 | 35.94 | 55 | 0 | 24.2 | 1.498 | 15 | 2.53 | 59.8 | 38 | 2.0099 | 0.377 | 24.18 | 1.244 | 16 | 2.92 | 60.5 | 38.2 | 2.0378 | 24.16 | 1.58 | 16 | 3.34 | 62.9 | 42.2 | 1.8904 | 0.195 | 9 | 2.08 | 0.03 | 0.367 | 0.083 | 10 | 2.64 | 0.024 | 0.282 | 9 | 2.75 | 0.013 | 43.59 | 0.315 | 9 | 25.1 | 87.1 | 40 | 77 | 0.05 | 43.51 | 0.325 | 9 | 23.4 | 103 | 41 | 70 | 0.037 | 27.3 | 25.7 | 21 |  |  | MINIMUM | 9.3 | 9.3 | 10.3 | 28.9 | 8.8 | 8.8 | 9.8 | 27.4 |  | 10.9109 |  | 14.1667 | 25.0776 | 1.7294 | MINIMUM | 79.5256 | 7009.5632 |  | 808.8106 | [6 empty] | 1.5175 | 1.5175 | 1.5443 | 0.26585 | 0.25763 | 0.26585 | 0.22083 | 0.288 | 0.288 | 1.3316 | 3.5 | 0.049161 | 0.05036 | 0.049528 | 1.0972 | 0.49499 | 0.098514 | 4.0889 | 0.71277 | 5.8025 | 1.1069 | 0.49728 | 0.088461 | 3.7891 | 0.60513 | 8.1878 |  |  | MIN | 0.57 | 10.3 | 24.699 | 14.0784 | 6.15 | 15 | 10 | 1.4078 |  |  |  | MIN | 0.78 | 10.3 | 24.699 | 19.2652 | 6.18 | 14.9 | 15 | 1.2843 |  |  |  | MIN | 0.75 | 10.3 | 26.2136 | 19.6602 | 6.13 | 15.5 | 10 | 1.966 |  |  |  | 1.2843
AVERAGE | 6.4833 | 18.5 | 18.5 | 15.45 | 115.6667 | 201.3333 | 15.6333 | 0.47667 | 0.055 | 6.0417 | 9.3333 | 0.0885 | 6.0283 | 9.3333 |  | 5.99 | 9.1667 |  | 6.05 | 0.3745 | 3.75 | 0.6325 | 14.95 | 9.5 | 0.50247 | 0.062833 | 6.045 | 0.311 | 4 | 0.73 | 15.125 | 9.55 | 0.50945 | 6.04 | 0.395 | 4 | 0.835 | 15.725 | 10.55 | 0.47259 | 0.0325 | 1.5 | 0.34667 | 0.015 | 0.061167 | 0.013833 | 1.6667 | 0.44 | 0.024 | 0.047 | 1.5 | 0.45833 | 0.013 | 7.265 | 0.0525 | 1.5 | 4.1833 | 14.5167 | 20 | 38.5 | 0.025 | 7.2517 | 0.054167 | 1.5 | 3.9 | 17.1667 | 20.5 | 35 | 0.0185 | 4.55 | 4.2833 | 3.5 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 13.0896 |  | 15.9408 | 29.0304 | 1.8792 | MAXIMUM | 80.0178 | 8239.3112 |  | 808.8106 | [6 empty] | 1.7198 | 1.6186 | 1.8547 | 0.29444 | 0.29444 | 0.31897 | 0.2699 | 0.29908 | 0.29908 | 1.3316 | 5 | 0.05036 | 0.050604 | 0.050604 | 1.126 | 0.50202 | 0.1032 | 4.1005 | 0.76805 | 5.9547 | 1.126 | 0.53034 | 0.11795 | 3.8015 | 0.69271 | 8.5103
MINIMUM | 6.4 | 16 | 17 | 14.8 | 112 | 193 | 15.2 | 0.44 | 0.049 | 5.88 | 6 | 0.082 | 5.87 | 6 |  | 5.74 | 6 |  | 5.97 | 0.332 | 3 | 0.55 | 14.7 | 9.2 | 0.40931 | 0.058 | 5.91 | 0.269 | 3 | 0.65 | 14.9 | 9.3 | 0.41245 | 5.92 | 0.295 | 3 | 0.75 | 15.5 | 10.3 | 0.42519 | 0.026 | 1 | 0.24 | 0.014 | 0.058 | 0.01 | 1 | 0.38 | 0.024 | 0.042 | 1 | 0.37 | 0.013 | 7.12 | 0.044 | 1 | 3.9 | 14.4 | 20 | 38 | 0.023 | 7.14 | 0.05 | 1 | 3.5 | 16.5 | 20 | 34 | 0.016 | 4.5 | 4.2 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 29290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 960 | 1190 | 1440 | 1380 | 1440 | 1280 | 1640 | 1640 | 2100 | 0 | 2590 | 2620 | 2880 | 264 | 316 | 38 | 4360 | 895 | 1100 | 148 | 180 | 22 | 2160 | 442 | 865
MAXIMUM | 6.57 | 22 | 20 | 16.1 | 119 | 205 | 16 | 0.497 | 0.061 | 6.18 | 12 | 0.099 | 6.16 | 12 |  | 6.13 | 12 |  | 6.15 | 0.446 | 4 | 0.71 | 15.1 | 10.3 | 0.59013 | 0.069 | 6.18 | 0.355 | 5 | 0.78 | 15.4 | 10.3 | 0.72731 | 6.15 | 0.47 | 5 | 0.88 | 15.9 | 11.3 | 0.53852 | 0.037 | 2 | 0.45 | 0.016 | 0.066 | 0.018 | 2 | 0.54 | 0.024 | 0.052 | 2 | 0.57 | 0.013 | 7.55 | 0.06 | 2 | 4.3 | 14.8 | 20 | 39 | 0.027 | 7.45 | 0.057 | 2 | 4.2 | 17.8 | 21 | 36 | 0.021 | 4.6 | 4.4 | 4 | [17 empty] | AVERAGE | 9763.3333 | [9 empty] | 326.6667 | 320 | 396.6667 | 480 | 460 | 480 | 426.6667 | 546.6667 | 546.6667 | 700 |  | 863.3333 | 873.3333 | 960 | 88 | 105.3333 | 12.6667 | 1453.3333 | 298.3333 | 366.6667 | 49.3333 | 60 | 7.3333 | 720 | 147.3333 | 288.3333
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.02 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.47 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.55 | [5 empty] | 6.045 |  |  |  |  | 0.052 |  |  |  |  | 0.55 | [6 empty] | 0.052 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 9400 | [9 empty] | 300 | 300 | 340 | 480 | 420 | 440 | 360 | 520 | 520 | 700 |  | 820 | 840 | 920 | 84 | 102 | 12 | 1340 | 275 | 350 | 48 | 58 | 6 | 640 | 130 | 275
[90 empty] | MAXIMUM | 10440 | [9 empty] | 340 | 340 | 450 | 480 | 480 | 520 | 480 | 580 | 580 | 700 |  | 930 | 940 | 1020 | 96 | 112 | 14 | 1600 | 330 | 400 | 52 | 62 | 8 | 800 | 164 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [51 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.216 |  | TOTAL MGD: |  | 0.005 |  |  | FINISHED SOUTH 1 |  | START: | 23770330 |  | END: | 23770335 |  |  | Alum | 9314 | 8250 | 8250 | 7345 | 7345 | 0.9 | [45 empty] | 0.78 | 10.3 | 24.699 | 19.2652 | 6.18 | 14.9 | 15 | 1.2843
[73 empty] | FINISHED 2 | 15.169 |  | TOTAL MGD: |  | 11.211 |  |  | FINISHED SOUTH 2 |  | START: | 43350300 |  | END: | 43361511 |  |  | Caustic | 4280 | 7983 | 7983
[73 empty] | TOTAL RAW | 29.153 |  | TOTAL MGD: |  | 4.468 |  |  | FINISHED CONWAY |  | START: | 10027170 |  | END: | 10031638 |  |  | Hypochlorite | 18 |  | 42
[76 empty] | TOTAL MGD: |  | 10.701 |  |  | FINISHED PERRY |  | START: | 33328280 |  | END: | 33338981 |  |  | Phosphate | 2054
[76 empty] | TOTAL MGD: |  | 9.311 |  |  | RAW PLANT 1 |  | START: | 30500775 |  | END: | 30510086 |  |  | Fluoride | 2500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.395 |  |  | RAW PLANT 2 |  | START: | 30462201 |  | END: | 30471596 |  |  | Cal~Flo | 12.5 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.447 |  |  | RAW PLANT 3 |  | START: | 6978153 |  | END: | 6988600 |  |  | Zinc | 1448
[76 empty] | TOTAL MGD: |  | 0.854 |  |  | DECANT |  | START: | 1814453 |  | END: | 1815307 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.1262 |  |  | BLOW DOWN |  | START: | 9062.0892 |  | END: | 9063.2154 |  |  | NH3 | 10 |  | BI-SUL | 750
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23770335
43361511
10031638
33338981
30510086
30471596
6988600
1815307
9063.2154
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 19
DATE: | 2018-11-19 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-19 | [23 empty] | DATE: | 2018-11-19
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-19 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43423.0042 | 1,2,3 | 50 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 10.9109 | 1,3 | 14.1667 | 25.0776 | 1.8792 | 43423.0042 | 80.0178 | 7009.5632 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5443 | 1.5443 | 1.8547 | 0.26585 | 0.26585 | 0.26585 | 0.26585 | 0.29281 | 0.29281 | 1.3316 | 4.5 | 0.050066 | 0.050604 | 0.049827 | 1.126 | 0.49499 | 0.1032 | 4.0889 | 0.76805 | 5.9547 | 1.1069 | 0.49728 | 0.10703 | 3.7891 | 0.69271 | 8.5103 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.344 | 3 | 0.58 | 15 | 10.3 | 0.52487 |  | 6 | 0.3 | 3 | 0.62 | 15 | 10.3 | 0.4439 | 6 | 0.328 | 3 | 0.74 | 16 | 11.3 | 0.45481 | [13 empty] | 7.21 | 0.061 | 2 | 4.2 | 14 |  |  |  | 7.25 | 0.064 | 2 | 4 | 16.5 |  |  |  | 4.4 | 4.2 | 3.6 | [18 empty] | 10440 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 450 | 480 | 480 | 480 | 480 | 580 | 580 | 700 |  | 930 | 940 | 1020 | 96 | 112 | 14 | 1600 | 330 | 400 | 52 | 62 | 8 | 800 | 164 | 315 |  | 1:00 | 0.58 | 10.3 | 24.699 | 14.3254 | 6.01 | 15 | 10 | 1.4325 | 15 | 6.5 | 0.40487 | 1:00 | 0.62 | 10.3 | 24.699 | 15.3134 | 6 | 15 | 8 | 1.9142 | 15 | 6 | 0.3239 | 1:00 | 0.74 | 11.3 | 23.8938 | 17.6814 | 6 | 16 | 8 | 2.2102 | 15 | 6 | 0.33481
2:00 | [72 empty] | 43423.3454 | 1,2,3,5 | 44 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,1,3 | 13.1386 | 1,3 | 15.6557 | 28.7942 | 1.8792 | 43423.3454 | 80.1711 | 8423.7734 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5443 | 1.5443 | 1.4013 | 0.26585 | 0.2437 | 0.22154 | 0.31016 | 0.26252 | 0.24232 | 1.3316 | 0 | 0.049528 | 0.050604 | 0.050315 | 1.0791 | 0.49941 | 0.1032 | 4.094 | 0.74477 | 5.9547 | 1.1069 | 0.52134 | 0.093649 | 3.8091 | 0.69693 | 8.5103 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.5 | 20 | 18 | 15 | 114 | 200 | 16 | 0.463 |  | 6 | 10 | 0.081 | 6.01 | 10 |  | 5.95 | 10 | [8 empty] | 0.058 | [14 empty] | 0.033 | 1 | 0.25 |  | 0.06 | 0.016 | 1 | 0.37 |  | 0.043 | 1 | 0.45 | [38 empty] | 10460 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 340 | 480 | 440 | 400 | 560 | 520 | 480 | 700 |  | 920 | 940 | 1030 | 92 | 113 | 14 | 1570 | 320 | 400 | 52 | 65 | 7 | 800 | 165 | 315 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43423.4104 | 1,2,3,5 | 44 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 13.1386 | 1,3 | 15.6557 | 28.7942 | 1.8792 | 43423.4104 | 80.2541 | 8239 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.645 | 1.5483 | 1.4838 | 0.28229 | 0.25877 | 0.20584 | 0.31758 | 0.27724 | 0.27724 | 1.2365 | 0 | 0.049891 | 0.049891 | 0.049654 | 1.1244 | 0.49902 | 0.10208 | 4.1092 | 0.74376 | 6.1845 | 1.1269 | 0.50955 | 0.099158 | 3.8289 | 0.69321 | 8.4388 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.24 | 0.058 | 2 | 4 | 14 |  |  |  | 7.28 | 0.06 | 2 | 3.8 | 16.5 |  |  |  | 4.3 | 4.2 | 3.5 | [18 empty] | 9880 | [6 empty] | 0 | 0 | 0 | 340 | 320 | 340 | 480 | 440 | 350 | 540 | 520 | 520 | 650 |  | 870 | 870 | 960 | 90 | 106 | 13 | 1480 | 300 | 390 | 50 | 60 | 7 | 760 | 155 | 295 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43423.8349 | 1,2,3 | 60 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 13.1386 | 1,3 | 15.6557 | 28.7942 | 1.8648 | 43423.8349 | 79.9292 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5483 | 1.5483 | 1.5274 | 0.32934 | 0.32934 | 0.32934 | 0.32934 | 0.26657 | 0.26657 | 1.2365 | 2 | 0.050464 | 0.050464 | 0.050172 | 1.1244 | 0.49902 | 0.09423 | 4.1092 | 0.74376 | 6.1845 | 1.1269 | 0.50955 | 0.11332 | 3.8289 | 0.68873 | 8.4388 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.49 | 18 | 20 | 15.6 | 121 | 205 | 15.8 | 0.487 |  | 5.93 | 8 | 0.085 | 5.91 | 8 |  | 5.88 | 8 | [8 empty] | 0.054 | [14 empty] | 0.031 | 2 | 0.31 |  | 0.053 | 0.026 | 2 | 0.57 |  | 0.043 | 2 | 0.43 | [38 empty] | 9840 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 350 | 560 | 560 | 560 | 560 | 500 | 500 | 650 |  | 880 | 880 | 970 | 90 | 106 | 12 | 1480 | 300 | 390 | 50 | 60 | 8 | 760 | 154 | 295 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.044 | [9 empty] | 6.03 | 0.396 | 5 | 0.58 | 15.1 | 9.6 | 0.49736 |  | 6.03 | 0.357 | 5 | 0.55 | 15.3 | 9.7 | 0.50129 | 6.05 | 0.342 | 4 | 0.66 | 15.9 | 10.7 | 0.5163 |  |  |  | 0.017 |  |  |  |  | 0.018 |  |  |  | 0.012 | 7.18 | 0.052 | 2 | 4.4 | 14.3 | 21 | 40 | 0.023 | 7.2 | 0.053 | 2 | 4.1 | 17.6 | 22 | 42 | 0.019 | 4.3 | 4.1 | 3.7 | [55 empty] | 9:00 | 0.58 | 9.6 | 26.5 | 15.37 | 6.03 | 15.1 | 10 | 1.537 | 15 | 6.5 | 0.37736 | 9:00 | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.03 | 15.3 | 10 | 1.4425 | 15 | 6.5 | 0.38129 | 9:00 | 0.66 | 10.7 | 25.2336 | 16.6542 | 6.05 | 15.9 | 10 | 1.6654 | 15 | 6.5 | 0.3963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.45 | 20 | 20 | 14.9 | 115 | 197 | 15.8 | 0.482 |  | 6.05 | 9 | 0.086 | 6.07 | 10 |  | 6.02 | 9 | [8 empty] | 0.066 | [14 empty] | 0.026 | 2 | 0.33 |  | 0.065 | 0.023 | 2 | 0.43 |  | 0.044 | 2 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.09 | 0.435 | 5 | 0.56 | 15.4 | 9.7 | 0.50129 |  | 6.1 | 0.403 | 5 | 0.55 | 15.2 | 9.7 | 0.50129 | 6.12 | 0.333 | 5 | 0.56 | 15.4 | 10.7 | 0.5163 | [13 empty] | 7.37 | 0.055 | 2 | 4.3 | 14.8 |  |  |  | 7.39 | 0.06 | 2 | 4 | 17.7 |  |  |  | 4.3 | 4.1 | 3 | [55 empty] | 13:00 | 0.56 | 9.7 | 26.2268 | 14.687 | 6.09 | 15.4 | 10 | 1.4687 | 15 | 6.5 | 0.38129 | 13:00 | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.1 | 15.2 | 10 | 1.4425 | 15 | 6.5 | 0.38129 | 13:00 | 0.56 | 10.7 | 25.2336 | 14.1308 | 6.12 | 15.4 | 10 | 1.4131 | 15 | 6.5 | 0.3963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.46 | 18 | 19 | 14.5 | 112 | 195 | 15.7 | 0.477 |  | 6.08 | 10 | 0.087 | 6.06 | 10 |  | 6.05 | 9 | [8 empty] | 0.065 | [14 empty] | 0.033 | 2 | 0.34 |  | 0.064 | 0.024 | 2 | 0.56 |  | 0.046 | 2 | 0.44 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.4 | 0.053 | 2 | 4.2 | 14.5 |  |  |  | 7.38 | 0.057 | 2 | 4.4 | 17.7 |  |  |  | 4.2 | 4.1 | 4.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.44 | 16 | 17 | 14.1 | 117 | 198 | 15.4 | 0.489 |  | 6.07 | 10 | 0.097 | 6.11 | 10 |  | 6.06 | 10 | [8 empty] | 0.065 | [14 empty] | 0.032 | 2 | 0.37 |  | 0.064 | 0.022 | 2 | 0.49 |  | 0.048 | 2 | 0.4 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.059 | [9 empty] | 6.15 | 0.491 | 5 | 0.59 | 15.1 | 9.7 | 0.50129 |  | 6.14 | 0.444 | 5 | 0.65 | 15.1 | 9.7 | 0.50129 | 6.12 | 0.394 | 5 | 0.71 | 15.6 | 10.7 | 0.5163 |  |  |  | 0.02 | [9 empty] | 7.25 | 0.071 | 2 | 4.3 | 14.4 | 21 | 40 | 0.026 | 7.29 | 0.064 | 2 | 4.4 | 16.8 | 20 | 40 | 0.022 | 4.2 | 4.1 | 3.9 | [55 empty] | 21:00 | 0.59 | 9.7 | 26.2268 | 15.4738 | 6.15 | 15.1 | 10 | 1.5474 | 15 | 6.5 | 0.38129 | 21:00 | 0.65 | 9.7 | 26.2268 | 17.0474 | 6.14 | 15.1 | 10 | 1.7047 | 15 | 6.5 | 0.38129 | 21:00 | 0.71 | 10.7 | 25.2336 | 17.9159 | 6.12 | 15.6 | 10 | 1.7916 | 15 | 6.5 | 0.3963
22:00 | [72 empty] | DOSE |  | TOTAL | 40 | 40 | 44 | 124 | 38 | 38 | 42 | 118 | 0 | 50.3266 | 0 | 61.1338 | 111.4603 | 7.5024 | TOTAL | 320.3721 | 31911.6478 | 0 | 3235.2423 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2819 | 6.1852 | 6.2672 | 1.1433 | 1.0977 | 1.0226 | 1.2229 | 1.0991 | 1.0789 | 5.1361 | 6.5 | 0.19995 | 0.20156 | 0.19997 | 4.4539 | 1.9924 | 0.40272 | 16.4014 | 3.0003 | 24.2785 | 4.4675 | 2.0377 | 0.41316 | 15.256 | 2.7716 | 33.8982 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.4 | 15 | 17 | 14.7 | 119 | 198 | 15.3 | 0.502 |  | 6 | 11 | 0.087 | 6 | 11 |  | 5.97 | 10 | [8 empty] | 0.065 | [14 empty] | 0.027 | 1 | 0.33 |  | 0.065 | 0.02 | 1 | 0.64 |  | 0.042 | 1 | 0.5 | [22 empty] | AVERAGE | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 12.5816 |  | 15.2834 | 27.8651 | 1.8756 | AVERAGE | 80.093 | 7977.9119 |  | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5705 | 1.5463 | 1.5668 | 0.28583 | 0.27441 | 0.25564 | 0.30573 | 0.27478 | 0.26974 | 1.284 | 1.625 | 0.049987 | 0.050391 | 0.049992 | 1.1135 | 0.49811 | 0.10068 | 4.1003 | 0.75009 | 6.0696 | 1.1169 | 0.50943 | 0.10329 | 3.814 | 0.6929 | 8.4745 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.74 | 107 | 111 | 88.8 | 698 | 1193 | 94 | 2.9 | 0.103 | 36.13 | 58 | 0.523 | 36.16 | 59 | 0 | 35.93 | 56 | 0 | 24.28 | 1.666 | 18 | 2.31 | 60.6 | 39.3 | 2.0248 | 0.373 | 24.27 | 1.504 | 18 | 2.37 | 60.6 | 39.4 | 1.9478 | 24.29 | 1.397 | 17 | 2.67 | 62.9 | 43.4 | 2.0037 | 0.182 | 10 | 1.93 | 0.037 | 0.371 | 0.131 | 10 | 3.06 | 0.018 | 0.266 | 10 | 2.72 | 0.012 | 43.65 | 0.35 | 12 | 25.4 | 86 | 42 | 80 | 0.049 | 43.79 | 0.358 | 12 | 24.7 | 102.8 | 42 | 82 | 0.041 | 25.7 | 24.8 | 21.8 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 10.9109 |  | 14.1667 | 25.0776 | 1.8648 | MINIMUM | 79.9292 | 7009.5632 |  | 808.8106 | [6 empty] | 1.5443 | 1.5443 | 1.4013 | 0.26585 | 0.2437 | 0.20584 | 0.26585 | 0.26252 | 0.24232 | 1.2365 | 0 | 0.049528 | 0.049891 | 0.049654 | 1.0791 | 0.49499 | 0.09423 | 4.0889 | 0.74376 | 5.9547 | 1.1069 | 0.49728 | 0.093649 | 3.7891 | 0.68873 | 8.4388 |  | MIN | 0.58 | 10.3 | 24.699 | 14.3254 | 6.01 | 15 | 10 | 1.4325 |  |  |  | MIN | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.03 | 15.3 | 10 | 1.4425 |  |  |  | MIN | 0.56 | 10.7 | 25.2336 | 14.1308 | 6.12 | 15.4 | 10 | 1.4131 |  |  |  | 1.4131
AVERAGE | 6.4567 | 17.8333 | 18.5 | 14.8 | 116.3333 | 198.8333 | 15.6667 | 0.48333 | 0.0515 | 6.0217 | 9.6667 | 0.087167 | 6.0267 | 9.8333 |  | 5.9883 | 9.3333 |  | 6.07 | 0.4165 | 4.5 | 0.5775 | 15.15 | 9.825 | 0.5062 | 0.062167 | 6.0675 | 0.376 | 4.5 | 0.5925 | 15.15 | 9.85 | 0.48694 | 6.0725 | 0.34925 | 4.25 | 0.6675 | 15.725 | 10.85 | 0.50093 | 0.030333 | 1.6667 | 0.32167 | 0.0185 | 0.061833 | 0.021833 | 1.6667 | 0.51 | 0.018 | 0.044333 | 1.6667 | 0.45333 | 0.012 | 7.275 | 0.058333 | 2 | 4.2333 | 14.3333 | 21 | 40 | 0.0245 | 7.2983 | 0.059667 | 2 | 4.1167 | 17.1333 | 21 | 41 | 0.0205 | 4.2833 | 4.1333 | 3.6333 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 13.1386 |  | 15.6557 | 28.7942 | 1.8792 | MAXIMUM | 80.2541 | 8423.7734 |  | 808.8106 | [6 empty] | 1.645 | 1.5483 | 1.8547 | 0.32934 | 0.32934 | 0.32934 | 0.32934 | 0.29281 | 0.29281 | 1.3316 | 4.5 | 0.050464 | 0.050604 | 0.050315 | 1.126 | 0.49941 | 0.1032 | 4.1092 | 0.76805 | 6.1845 | 1.1269 | 0.52134 | 0.11332 | 3.8289 | 0.69693 | 8.5103
MINIMUM | 6.4 | 15 | 17 | 14.1 | 112 | 195 | 15.3 | 0.463 | 0.044 | 5.93 | 8 | 0.081 | 5.91 | 8 |  | 5.88 | 8 |  | 6.01 | 0.344 | 3 | 0.56 | 15 | 9.6 | 0.49736 | 0.054 | 6 | 0.3 | 3 | 0.55 | 15 | 9.7 | 0.4439 | 6 | 0.328 | 3 | 0.56 | 15.4 | 10.7 | 0.45481 | 0.026 | 1 | 0.25 | 0.017 | 0.053 | 0.016 | 1 | 0.37 | 0.018 | 0.042 | 1 | 0.4 | 0.012 | 7.18 | 0.052 | 2 | 4 | 14 | 21 | 40 | 0.023 | 7.2 | 0.053 | 2 | 3.8 | 16.5 | 20 | 40 | 0.019 | 4.2 | 4.1 | 3 | [15 empty] | MIL/MIN |  | TOTAL | 40620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1340 | 1320 | 1480 | 2000 | 1920 | 1790 | 2140 | 2120 | 2080 | 2700 | 0 | 3600 | 3630 | 3980 | 368 | 437 | 53 | 6130 | 1250 | 1580 | 204 | 247 | 30 | 3120 | 638 | 1220
MAXIMUM | 6.5 | 20 | 20 | 15.6 | 121 | 205 | 16 | 0.502 | 0.059 | 6.08 | 11 | 0.097 | 6.11 | 11 |  | 6.06 | 10 |  | 6.15 | 0.491 | 5 | 0.59 | 15.4 | 10.3 | 0.52487 | 0.066 | 6.14 | 0.444 | 5 | 0.65 | 15.3 | 10.3 | 0.50129 | 6.12 | 0.394 | 5 | 0.74 | 16 | 11.3 | 0.5163 | 0.033 | 2 | 0.37 | 0.02 | 0.065 | 0.026 | 2 | 0.64 | 0.018 | 0.048 | 2 | 0.5 | 0.012 | 7.4 | 0.071 | 2 | 4.4 | 14.8 | 21 | 40 | 0.026 | 7.39 | 0.064 | 2 | 4.4 | 17.7 | 22 | 42 | 0.022 | 4.4 | 4.2 | 4.1 | [17 empty] | AVERAGE | 10155 | [9 empty] | 335 | 330 | 370 | 500 | 480 | 447.5 | 535 | 530 | 520 | 675 |  | 900 | 907.5 | 995 | 92 | 109.25 | 13.25 | 1532.5 | 312.5 | 395 | 51 | 61.75 | 7.5 | 780 | 159.5 | 305
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0122 |  | TOTAL AVG COAG ALK: |  |  |  | 9.6111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.491 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.55 | [5 empty] | 6.07 |  |  |  |  | 0.048 |  |  |  |  | 0.55 | [6 empty] | 0.048 | [16 empty] | Pump Station MIN |  | 3 | [17 empty] | MINIMUM | 9840 | [9 empty] | 320 | 320 | 340 | 480 | 440 | 350 | 480 | 500 | 480 | 650 |  | 870 | 870 | 960 | 90 | 106 | 12 | 1480 | 300 | 390 | 50 | 60 | 7 | 760 | 154 | 295
[90 empty] | MAXIMUM | 10460 | [9 empty] | 340 | 340 | 450 | 560 | 560 | 560 | 560 | 580 | 580 | 700 |  | 930 | 940 | 1030 | 96 | 113 | 14 | 1600 | 330 | 400 | 52 | 65 | 8 | 800 | 165 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.123 |  | TOTAL MGD: |  | 2.294 |  |  | FINISHED SOUTH 1 |  | START: | 23770335 |  | END: | 23772629 |  |  | Alum | 9249 | 9768 | 9768 | 9064 | 9064 | 0.9 | [44 empty] | 0.56 | 10.7 | 25.2336 | 14.1308 | 6.12 | 15.4 | 10 | 1.4131
[73 empty] | FINISHED 2 | 16.543 |  | TOTAL MGD: |  | 9.829 |  |  | FINISHED SOUTH 2 |  | START: | 43361511 |  | END: | 43371340 |  |  | Caustic | 4112 | 7980 | 7980
[73 empty] | TOTAL RAW | 31.493 |  | TOTAL MGD: |  | 4.787 |  |  | FINISHED CONWAY |  | START: | 10031638 |  | END: | 10036425 |  |  | Hypochlorite | 16 |  | 39
[76 empty] | TOTAL MGD: |  | 11.756 |  |  | FINISHED PERRY |  | START: | 33338981 |  | END: | 33350737 |  |  | Phosphate | 2010
[76 empty] | TOTAL MGD: |  | 10.074 |  |  | RAW PLANT 1 |  | START: | 30510086 |  | END: | 30520160 |  |  | Fluoride | 2400 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.164 |  |  | RAW PLANT 2 |  | START: | 30471596 |  | END: | 30481760 |  |  | Cal~Flo | 8.7 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.255 |  |  | RAW PLANT 3 |  | START: | 6988600 |  | END: | 6999855 |  |  | Zinc | 1460
[76 empty] | TOTAL MGD: |  | 0.846 |  |  | DECANT |  | START: | 1815307 |  | END: | 1816153 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.3773 |  |  | BLOW DOWN |  | START: | 9063.2154 |  | END: | 9064.5927 |  |  | NH3 | 10 |  | BI-SUL | 750
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23772629
43371340
10036425
33350737
30520160
30481760
6999855
1816153
9064.5927
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 20
DATE: | 2018-11-20 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-20 | [23 empty] | DATE: | 2018-11-20
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-20 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43424.0248 | 1,2,3 | 60 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,1,3 | 13.1386 | 1,3 | 15.6557 | 28.7942 | 1.8648 | 43424.0248 | 79.9292 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5483 | 1.5483 | 1.5274 | 0.32934 | 0.32934 | 0.32934 | 0.32934 | 0.26657 | 0.26657 | 1.2365 | 2 | 0.050464 | 0.050464 | 0.050172 | 1.1244 | 0.49902 | 0.09423 | 4.1092 | 0.74376 | 6.1845 | 1.1269 | 0.50955 | 0.11332 | 3.8289 | 0.68873 | 8.4388 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.05 | 0.376 | 4 | 0.6 | 15 | 9.3 | 0.48557 |  | 6.06 | 0.305 | 4 | 0.62 | 15 | 9.3 | 0.48557 | 6.06 | 0.355 | 4 | 0.68 | 16 | 10.3 | 0.50148 | [13 empty] | 7.32 | 0.062 | 2 | 4.2 | 14.5 |  |  |  | 7.28 | 0.06 | 2 | 4.2 | 17.5 |  |  |  | 4.4 | 4.3 | 3.5 | [18 empty] | 9840 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 350 | 560 | 560 | 560 | 560 | 500 | 500 | 650 |  | 880 | 880 | 970 | 90 | 106 | 12 | 1480 | 300 | 390 | 50 | 60 | 8 | 760 | 154 | 295 |  | 1:00 | 0.6 | 9.3 | 27.3548 | 16.4129 | 6.05 | 15 | 10 | 1.6413 | 15 | 6.5 | 0.36557 | 1:00 | 0.62 | 9.3 | 27.3548 | 16.96 | 6.06 | 15 | 10 | 1.696 | 15 | 6.5 | 0.36557 | 1:00 | 0.68 | 10.3 | 26.2136 | 17.8252 | 6.06 | 16 | 10 | 1.7825 | 15 | 6.5 | 0.38148
2:00 | [72 empty] | 8:15 | 1,2,3 | 55 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | ,3,8 | 14.197 | 1,3 | 11.6669 | 25.8638 | 1.8648 | 43424.4045 | 83.1783 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5483 | 1.645 | 1.3965 | 0.31758 | 0.32346 | 0.35875 | 0.32346 | 0.27724 | 0.29856 | 1.2365 | 3.5 | 0.050464 | 0.050751 | 0.050689 | 1.087 | 0.49902 | 0.10208 | 4.0984 | 0.76855 | 6.1845 | 1.1269 | 0.50955 | 0.11332 | 3.8189 | 0.69321 | 8.4388 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.51 | 20 | 18 | 14.2 | 115 | 194 | 16 | 0.477 |  | 5.99 | 12 | 0.087 | 6 | 12 |  | 5.95 | 12 | [8 empty] | 0.066 | [14 empty] | 0.032 | 1 | 0.32 |  | 0.07 | 0.016 | 1 | 0.65 |  | 0.042 | 1 | 0.48 | [38 empty] | 10240 | [6 empty] | 0 | 0 | 0 | 320 | 340 | 320 | 540 | 550 | 610 | 550 | 520 | 560 | 650 |  | 880 | 885 | 980 | 87 | 106 | 13 | 1520 | 310 | 390 | 50 | 60 | 8 | 760 | 155 | 295 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43424.6893 | 1,2,3 | 55 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,3,8 | 12.1421 | 1,3 | 16.1122 | 28.2542 | 1.8648 | 43424.6893 | 80.0178 | 8731 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4535 | 1.5443 | 1.4838 | 0.33231 | 0.33231 | 0.35447 | 0.33231 | 0.28271 | 0.26252 | 1.2365 | 3.5 | 0.050604 | 0.049528 | 0.050804 | 1.126 | 0.49941 | 0.1032 | 4.1004 | 0.76805 | 6.1036 | 1.1069 | 0.48124 | 0.093649 | 3.7991 | 0.69693 | 8.5103 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.3 | 0.06 | 2 | 4.2 | 14.5 |  |  |  | 7.31 | 0.058 | 2 | 4 | 17.5 |  |  |  | 4.4 | 4.3 | 3.5 | [18 empty] | 10440 | [6 empty] | 0 | 0 | 0 | 320 | 340 | 360 | 600 | 600 | 640 | 600 | 560 | 520 | 650 |  | 940 | 920 | 1040 | 96 | 113 | 14 | 1620 | 330 | 410 | 52 | 60 | 7 | 800 | 165 | 315 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 19:41 | 1,2,3,5 | 55 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,3,8 | 12.1421 | 1,3 | 16.1122 | 28.2542 | 1.9512 | 43424.9895 | 80.0178 | 8731.2104 | 0 | 808.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5897 | 1.5897 | 1.731 | 0.30462 | 0.30462 | 0.33231 | 0.33231 | 0.26252 | 0.26252 | 1.2365 | 4 | 0.049528 | 0.049528 | 0.049827 | 1.1142 | 0.50383 | 0.1032 | 4.1004 | 0.76805 | 6.1036 | 1.1069 | 0.49728 | 0.10703 | 3.8013 | 0.70116 | 8.5103 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.49 | 17 | 16 | 14.1 | 121 | 196 | 16.2 | 0.499 |  | 5.93 | 9 | 0.093 | 5.96 | 8 |  | 5.9 | 9 | [8 empty] | 0.064 | [14 empty] | 0.026 | 2 | 0.3 |  | 0.061 | 0.018 | 1 | 0.36 |  | 0.04 | 2 | 0.42 | [38 empty] | 10440 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 420 | 550 | 550 | 600 | 600 | 520 | 520 | 650 |  | 920 | 920 | 1020 | 95 | 114 | 14 | 1620 | 330 | 410 | 52 | 62 | 8 | 810 | 166 | 315 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.01 | 0.485 | 4 | 0.46 | 15.1 | 9.2 | 0.48164 |  | 6 | 0.499 | 3 | 0.49 | 15.3 | 9.3 | 0.41245 | 6.03 | 0.407 | 3 | 0.6 | 15.7 | 10.4 | 0.50519 |  |  |  | 0.063 |  |  |  |  | 0.014 |  |  |  | 0.007 | 7.51 | 0.059 | 1 | 4.1 | 14.4 | 21 | 42 | 0.028 | 7.48 | 0.061 | 1 | 4.4 | 17.6 | 21 | 45 | 0.012 | 4.5 | 4.2 | 3.2 | [55 empty] | 9:00 | 0.46 | 9.2 | 27.6522 | 12.72 | 6.01 | 15.1 | 10 | 1.272 | 15 | 6.5 | 0.36164 | 9:00 | 0.49 | 9.3 | 27.3548 | 13.4039 | 6 | 15.3 | 8 | 1.6755 | 15 | 6 | 0.29245 | 9:00 | 0.6 | 10.4 | 25.9615 | 15.5769 | 6.03 | 15.7 | 10 | 1.5577 | 15 | 6.5 | 0.38519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.4 | 16 | 16 | 14.7 | 122 | 199 | 15.9 | 0.509 |  | 5.89 | 9 | 0.095 | 5.92 | 10 |  | 5.9 | 7 | [8 empty] | 0.066 | [14 empty] | 0.024 | 1 | 0.21 |  | 0.063 | 0.02 | 1 | 0.26 |  | 0.041 | 1 | 0.45 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.99 | 0.344 | 3 | 0.59 | 14.6 | 9.7 | 0.61568 |  | 5.98 | 0.293 | 3 | 0.51 | 15 | 9.7 | 0.42503 | 6.01 | 0.392 | 3 | 0.48 | 17.9 | 10.7 | 0.5163 | [13 empty] | 7.63 | 0.057 | 1 | 4.4 | 14.4 |  |  |  | 7.67 | 0.055 | 1 | 4.2 | 17.9 |  |  |  | 4.5 | 4.2 | 3.2 | [55 empty] | 13:00 | 0.59 | 9.7 | 26.2268 | 15.4738 | 5.99 | 14.6 | 13 | 1.1903 | 10 | 6 | 0.49568 | 13:00 | 0.51 | 9.7 | 26.2268 | 13.3757 | 5.98 | 15 | 8 | 1.672 | 15 | 6 | 0.30503 | 13:00 | 0.48 | 10.7 | 25.2336 | 12.1121 | 6.01 | 17.9 | 10 | 1.2112 | 15 | 6.5 | 0.3963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.39 | 16 | 18 | 15.5 | 125 | 204 | 15.4 | 0.517 |  | 6 | 9 | 0.09 | 5.96 | 9 |  | 5.93 | 9 | [8 empty] | 0.063 | [14 empty] | 0.029 | 1 | 0.34 |  | 0.063 | 0.018 | 1 | 0.32 |  | 0.04 | 1 | 0.38 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.48 | 0.06 | 1 | 4.3 | 14.4 |  |  |  | 7.51 | 0.059 | 1 | 4.2 | 17.4 |  |  |  | 4.4 | 4.4 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.37 | 20 | 18 | 15 | 118 | 204 | 15.3 | 0.518 |  | 5.99 | 9 | 0.094 | 5.95 | 9 |  | 5.94 | 9 | [8 empty] | 0.066 | [14 empty] | 0.03 | 1 | 0.3 |  | 0.064 | 0.016 | 1 | 0.8 |  | 0.041 | 1 | 0.54 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.059 | [9 empty] | 6 | 0.408 | 4 | 0.63 | 13.8 | 10.3 | 0.64634 |  | 6 | 0.254 | 4 | 0.59 | 15.1 | 10.3 | 0.4439 | 5.99 | 0.321 | 3 | 0.66 | 15.3 | 11.3 | 0.45481 |  |  |  | 0.011 | [9 empty] | 7.29 | 0.082 | 1 | 4.6 | 14.4 | 20 | 40 | 0.033 | 7.37 | 0.071 | 1 | 4.2 | 16.6 | 21 | 42 | 0.019 | 4.6 | 4.6 | 3.4 | [55 empty] | 21:00 | 0.63 | 10.3 | 24.699 | 15.5604 | 6 | 13.8 | 13 | 1.197 | 10 | 6 | 0.52634 | 21:00 | 0.59 | 10.3 | 24.699 | 14.5724 | 6 | 15.1 | 8 | 1.8216 | 15 | 6 | 0.3239 | 21:00 | 0.66 | 11.3 | 23.8938 | 15.7699 | 5.99 | 15.3 | 8 | 1.9712 | 15 | 6 | 0.33481
22:00 | [72 empty] | DOSE |  | TOTAL | 40 | 40 | 44 | 124 | 38 | 38 | 42 | 118 | 0 | 51.6197 | 0 | 59.5469 | 111.1666 | 7.5456 | TOTAL | 323.1431 | 33940.8328 | 0 | 3235.2423 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1397 | 6.3273 | 6.1387 | 1.2839 | 1.2897 | 1.3749 | 1.3174 | 1.089 | 1.0902 | 4.9458 | 13 | 0.20106 | 0.20027 | 0.20149 | 4.4516 | 2.0013 | 0.40272 | 16.4085 | 3.0484 | 24.5762 | 4.4675 | 1.9976 | 0.42732 | 15.2483 | 2.78 | 33.8982 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.39 | 17 | 16 | 15.1 | 126 | 206 | 15.2 | 0.537 |  | 6.01 | 9 | 0.088 | 6 | 9 |  | 5.97 | 8 | [8 empty] | 0.067 | [14 empty] | 0.037 | 1 | 0.36 |  | 0.069 | 0.018 | 1 | 0.68 |  | 0.052 | 1 | 0.42 | [22 empty] | AVERAGE | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 12.9049 |  | 14.8867 | 27.7916 | 1.8864 | AVERAGE | 80.7858 | 8485.2082 |  | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5349 | 1.5818 | 1.5347 | 0.32096 | 0.32243 | 0.34372 | 0.32936 | 0.27226 | 0.27254 | 1.2365 | 3.25 | 0.050265 | 0.050068 | 0.050373 | 1.1129 | 0.50032 | 0.10068 | 4.1021 | 0.7621 | 6.1441 | 1.1169 | 0.4994 | 0.10683 | 3.8121 | 0.69501 | 8.4745 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.55 | 106 | 102 | 88.6 | 727 | 1203 | 94 | 3.057 | 0.1 | 35.81 | 57 | 0.547 | 35.79 | 57 | 0 | 35.59 | 54 | 0 | 24.05 | 1.613 | 15 | 2.28 | 58.5 | 38.5 | 2.2292 | 0.392 | 24.04 | 1.351 | 14 | 2.21 | 60.4 | 38.6 | 1.7669 | 24.09 | 1.475 | 13 | 2.42 | 64.9 | 42.7 | 1.9778 | 0.178 | 7 | 1.83 | 0.074 | 0.39 | 0.106 | 6 | 3.07 | 0.014 | 0.256 | 7 | 2.69 | 0.007 | 44.53 | 0.38 | 8 | 25.8 | 86.6 | 41 | 82 | 0.061 | 44.62 | 0.364 | 8 | 25.2 | 104.5 | 42 | 87 | 0.031 | 26.8 | 26 | 19.9 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 12.1421 |  | 11.6669 | 25.8638 | 1.8648 | MINIMUM | 79.9292 | 8239.3112 |  | 808.8106 | [6 empty] | 1.4535 | 1.5443 | 1.3965 | 0.30462 | 0.30462 | 0.32934 | 0.32346 | 0.26252 | 0.26252 | 1.2365 | 2 | 0.049528 | 0.049528 | 0.049827 | 1.087 | 0.49902 | 0.09423 | 4.0984 | 0.74376 | 6.1036 | 1.1069 | 0.48124 | 0.093649 | 3.7991 | 0.68873 | 8.4388 |  | MIN | 0.59 | 9.7 | 26.2268 | 15.4738 | 5.99 | 14.6 | 13 | 1.1903 |  |  |  | MIN | 0.51 | 9.7 | 26.2268 | 13.3757 | 5.98 | 15 | 8 | 1.672 |  |  |  | MIN | 0.48 | 10.7 | 25.2336 | 12.1121 | 6.01 | 17.9 | 10 | 1.2112 |  |  |  | 1.1903
AVERAGE | 6.425 | 17.6667 | 17 | 14.7667 | 121.1667 | 200.5 | 15.6667 | 0.5095 | 0.05 | 5.9683 | 9.5 | 0.091167 | 5.965 | 9.5 |  | 5.9317 | 9 |  | 6.0125 | 0.40325 | 3.75 | 0.57 | 14.625 | 9.625 | 0.5573 | 0.065333 | 6.01 | 0.33775 | 3.5 | 0.5525 | 15.1 | 9.65 | 0.44174 | 6.0225 | 0.36875 | 3.25 | 0.605 | 16.225 | 10.675 | 0.49444 | 0.029667 | 1.1667 | 0.305 | 0.037 | 0.065 | 0.017667 | 1 | 0.51167 | 0.014 | 0.042667 | 1.1667 | 0.44833 |  | 7.4217 | 0.063333 | 1.3333 | 4.3 | 14.4333 | 20.5 | 41 | 0.0305 | 7.4367 | 0.060667 | 1.3333 | 4.2 | 17.4167 | 21 | 43.5 | 0.0155 | 4.4667 | 4.3333 | 3.3167 |  |  | MAXIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 14.197 |  | 16.1122 | 28.7942 | 1.9512 | MAXIMUM | 83.1783 | 8731.2104 |  | 808.8106 | [6 empty] | 1.5897 | 1.645 | 1.731 | 0.33231 | 0.33231 | 0.35875 | 0.33231 | 0.28271 | 0.29856 | 1.2365 | 4 | 0.050604 | 0.050751 | 0.050804 | 1.126 | 0.50383 | 0.1032 | 4.1092 | 0.76855 | 6.1845 | 1.1269 | 0.50955 | 0.11332 | 3.8289 | 0.70116 | 8.5103
MINIMUM | 6.37 | 16 | 16 | 14.1 | 115 | 194 | 15.2 | 0.477 | 0.041 | 5.89 | 9 | 0.087 | 5.92 | 8 |  | 5.9 | 7 |  | 5.99 | 0.344 | 3 | 0.46 | 13.8 | 9.2 | 0.48164 | 0.063 | 5.98 | 0.254 | 3 | 0.49 | 15 | 9.3 | 0.41245 | 5.99 | 0.321 | 3 | 0.48 | 15.3 | 10.3 | 0.45481 | 0.024 | 1 | 0.21 | 0.011 | 0.061 | 0.016 | 1 | 0.26 | 0.014 | 0.04 | 1 | 0.38 |  | 7.29 | 0.057 | 1 | 4.1 | 14.4 | 20 | 40 | 0.028 | 7.28 | 0.055 | 1 | 4 | 16.6 | 21 | 42 | 0.012 | 4.4 | 4.2 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 40960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1310 | 1350 | 1450 | 2250 | 2260 | 2410 | 2310 | 2100 | 2100 | 2600 | 0 | 3620 | 3605 | 4010 | 368 | 439 | 53 | 6240 | 1270 | 1600 | 204 | 242 | 31 | 3130 | 640 | 1220
MAXIMUM | 6.51 | 20 | 18 | 15.5 | 126 | 206 | 16.2 | 0.537 | 0.059 | 6.01 | 12 | 0.095 | 6 | 12 |  | 5.97 | 12 |  | 6.05 | 0.485 | 4 | 0.63 | 15.1 | 10.3 | 0.64634 | 0.067 | 6.06 | 0.499 | 4 | 0.62 | 15.3 | 10.3 | 0.48557 | 6.06 | 0.407 | 4 | 0.68 | 17.9 | 11.3 | 0.5163 | 0.037 | 2 | 0.36 | 0.063 | 0.07 | 0.02 | 1 | 0.8 | 0.014 | 0.052 | 2 | 0.54 |  | 7.63 | 0.082 | 2 | 4.6 | 14.5 | 21 | 42 | 0.033 | 7.67 | 0.071 | 2 | 4.4 | 17.9 | 21 | 45 | 0.019 | 4.6 | 4.6 | 3.5 | [17 empty] | AVERAGE | 10240 | [9 empty] | 327.5 | 337.5 | 362.5 | 562.5 | 565 | 602.5 | 577.5 | 525 | 525 | 650 |  | 905 | 901.25 | 1002.5 | 92 | 109.75 | 13.25 | 1560 | 317.5 | 400 | 51 | 60.5 | 7.75 | 782.5 | 160 | 305
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.955 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.499 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.015 |  |  |  |  | 0.052 |  |  |  |  | 0.46 | [6 empty] | 0.052 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 9840 | [9 empty] | 320 | 320 | 320 | 540 | 550 | 560 | 550 | 500 | 500 | 650 |  | 880 | 880 | 970 | 87 | 106 | 12 | 1480 | 300 | 390 | 50 | 60 | 7 | 760 | 154 | 295
[90 empty] | MAXIMUM | 10440 | [9 empty] | 350 | 350 | 420 | 600 | 600 | 640 | 600 | 560 | 560 | 650 |  | 940 | 920 | 1040 | 96 | 114 | 14 | 1620 | 330 | 410 | 52 | 62 | 8 | 810 | 166 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.57 |  | TOTAL MGD: |  | 5.803 |  |  | FINISHED SOUTH 1 |  | START: | 23772629 |  | END: | 23778432 |  |  | Alum | 9242 | 8658 | 8658 | 8124 | 8124 | 0.9 | [44 empty] | 0.59 | 9.7 | 26.2268 | 15.4738 | 5.99 | 14.6 | 13 | 1.1903
[73 empty] | FINISHED 2 | 15.918 |  | TOTAL MGD: |  | 5.767 |  |  | FINISHED SOUTH 2 |  | START: | 43371340 |  | END: | 43377107 |  |  | Caustic | 7652 | 7930 | 7930
[73 empty] | TOTAL RAW | 30.66 |  | TOTAL MGD: |  | 5.505 |  |  | FINISHED CONWAY |  | START: | 10036425 |  | END: | 10041930 |  |  | Hypochlorite | 20 |  | 44
[76 empty] | TOTAL MGD: |  | 10.413 |  |  | FINISHED PERRY |  | START: | 33350737 |  | END: | 33361150 |  |  | Phosphate | 1939
[76 empty] | TOTAL MGD: |  | 9.8 |  |  | RAW PLANT 1 |  | START: | 30520160 |  | END: | 30529960 |  |  | Fluoride | 2400 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.89 |  |  | RAW PLANT 2 |  | START: | 30481760 |  | END: | 30491650 |  |  | Cal~Flo | 13.2 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.97 |  |  | RAW PLANT 3 |  | START: | 6999855 |  | END: | 7010825 |  |  | Zinc | 1065
[76 empty] | TOTAL MGD: |  | 0.83 |  |  | DECANT |  | START: | 1816153 |  | END: | 1816983 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 1.232 |  |  | BLOW DOWN |  | START: | 9064.5927 |  | END: | 9065.8247 |  |  | NH3 | 9.87 |  | BI-SUL | 750
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23778432
43377107
10041930
33361150
30529960
30491650
7010825
1816983
9065.8247
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 21
DATE: | 2018-11-21 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-21 | [23 empty] | DATE: | 2018-11-21
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-21 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43425.0074 | 1,2,3,5 | 55 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | ,3,8 | 12.1421 | 1,3 | 16.1122 | 28.2542 | 1.9512 | 43425.0074 | 85.0764 | 9469.0592 | 0 | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5897 | 1.5897 | 1.731 | 0.30462 | 0.30462 | 0.33231 | 0.33231 | 0.26252 | 0.26252 | 1.2365 | 4 | 0.049528 | 0.049528 | 0.049827 | 1.1142 | 0.50383 | 0.1032 | 4.1004 | 0.76805 | 6.1036 | 1.1069 | 0.49728 | 0.10703 | 3.8013 | 0.70116 | 8.5103 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.396 | 4 | 0.55 | 15 | 10.3 | 0.52487 |  | 6 | 0.3 | 4 | 0.62 | 15 | 10.3 | 0.4439 | 6.07 | 0.471 | 5 | 0.6 | 15 | 11.3 | 0.53852 | [13 empty] | 7.43 | 0.068 | 1 | 4.4 | 14 |  |  |  | 7.48 | 0.062 | 1 | 4.2 | 17 |  |  |  | 4.6 | 4.6 | 3.6 | [18 empty] | 11100 | [9 empty] | 350 | 350 | 420 | 550 | 550 | 600 | 600 | 520 | 520 | 650 |  | 920 | 920 | 1020 | 95 | 114 | 14 | 1620 | 330 | 410 | 52 | 62 | 8 | 810 | 166 | 315 |  | 1:00 | 0.55 | 10.3 | 24.699 | 13.5845 | 6.01 | 15 | 10 | 1.3584 | 15 | 6.5 | 0.40487 | 1:00 | 0.62 | 10.3 | 24.699 | 15.3134 | 6 | 15 | 8 | 1.9142 | 15 | 6 | 0.3239 | 1:00 | 0.6 | 11.3 | 23.8938 | 14.3363 | 6.07 | 15 | 10 | 1.4336 | 15 | 6.5 | 0.41852
2:00 | [72 empty] | 43425.3373 | 1,2,3,5 | 43 | 10.5 | 10.5 | 11.5 | 32.5 | 10 | 10 | 11 | 31 | 8,3 | 13.847 | 1,3 | 16.8826 | 30.7296 | 1.8965 | 43425.3373 | 84.6342 | 9592.034 | 0 | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5579 | 1.5579 | 1.4163 | 0.32598 | 0.33956 | 0.35315 | 0.35315 | 0.27283 | 0.29764 | 1.2365 | 6.5 | 0.05012 | 0.05012 | 0.05036 | 1.1034 | 0.49808 | 0.10114 | 4.1144 | 0.74128 | 5.9961 | 1.1076 | 0.49611 | 0.10508 | 3.7176 | 0.66353 | 7.9577 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.43 | 18 | 16 | 14 | 123 | 202 | 16 | 0.516 |  | 6.02 | 10 | 0.092 | 6 | 11 |  | 5.95 | 10 | [8 empty] | 0.069 | [14 empty] | 0.037 | 1 | 0.38 |  | 0.072 | 0.016 | 1 | 0.55 |  | 0.062 | 1 | 0.4 | [38 empty] | 11250 | [9 empty] | 350 | 350 | 350 | 600 | 625 | 650 | 650 | 550 | 600 | 650 |  | 950 | 950 | 1050 | 96 | 115 | 14 | 1600 | 325 | 411 | 53 | 63 | 8 | 800 | 160 | 300 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43425.4219 | 1,2,3,5 | 43 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | 8,3 | 13.847 | 1,3 | 16.8826 | 30.7296 | 1.8965 | 43425.4219 | 83.8601 | 9592.034 | 0 | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5425 | 1.5425 | 1.4035 | 0.32291 | 0.33636 | 0.34982 | 0.34982 | 0.27048 | 0.29507 | 1.2365 | 6.5 | 0.049624 | 0.049624 | 0.049906 | 1.0925 | 0.49315 | 0.10014 | 3.8524 | 0.67749 | 5.9367 | 1.0976 | 0.49164 | 0.10413 | 3.6055 | 0.61645 | 7.886 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.36 | 0.065 | 1 | 4.4 | 14 |  |  |  | 7.3 | 0.06 | 1 | 4.3 | 17 |  |  |  | 4.6 | 4.8 | 3.6 | [18 empty] | 11250 | [9 empty] | 350 | 350 | 350 | 600 | 625 | 650 | 650 | 550 | 600 | 650 |  | 950 | 950 | 1050 | 96 | 115 | 14 | 1500 | 300 | 411 | 53 | 63 | 8 | 780 | 150 | 300 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43425.5396 | 1,2,3,5 | 43 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | 8,3 | 13.847 | 1,3 | 16.8826 | 30.7296 | 1.8965 | 43425.5396 | 87.5872 | 10206.908 | 0 | 808.8106 | 0 | 0 | 0 |  |  |  | 1.5425 | 1.5425 | 1.4035 | 0.32291 | 0.33636 | 0.34982 | 0.34982 | 0.27048 | 0.29507 | 1.2365 | 6.5 | 0.049624 | 0.049624 | 0.049906 | 1.0925 | 0.49315 | 0.10014 | 3.8524 | 0.67749 | 5.9367 | 1.0976 | 0.49164 | 0.10413 | 3.6055 | 0.61645 | 7.886 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.42 | 16 | 16 | 13.5 | 128 | 220 | 15 | 0.563 |  | 6.1 | 10 | 0.08 | 6.01 | 10 |  | 5.98 | 10 | [8 empty] | 0.067 | [14 empty] | 0.05 | 2 | 0.36 |  | 0.067 | 0.018 | 2 | 0.5 |  | 0.069 | 2 | 0.4 | [38 empty] | 11750 | [9 empty] | 350 | 350 | 350 | 600 | 625 | 650 | 650 | 550 | 600 | 650 |  | 950 | 950 | 1050 | 96 | 115 | 14 | 1500 | 300 | 411 | 53 | 63 | 8 | 780 | 150 | 300 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43425.8221 | 1,2,3,5 | 43 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | ,3 | 13.2854 | 1,3 | 17.5579 | 30.8434 | 1.8965 | 43425.8221 | 95.7123 | 7747.412 | 0 | 808.8106 | 0 | 0 | 0 | 2.2021 | 2.2021 | 2.0123 | 1.5866 | 1.5866 | 1.4437 | 0.33367 | 0.32291 | 0.34443 | 0.33905 | 0.25819 | 0.25769 | 1.4267 | 6 | 0.051191 | 0.050668 | 0.049906 | 1.0925 | 0.50173 | 0.092986 | 3.6766 | 0.6549 | 5.9223 | 1.0769 | 0.48384 | 0.10413 | 3.8555 | 0.57535 | 7.886 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.053 | [9 empty] | 6.09 | 0.639 | 5 | 0.67 | 15 | 10.6 | 0.53667 |  | 6.06 | 0.435 | 5 | 0.63 | 15.3 | 10.5 | 0.53274 | 6.09 | 0.504 | 5 | 0.6 | 15.5 | 11.8 | 0.55704 |  |  |  | 0.016 | [9 empty] | 7.74 | 0.067 | 2 | 4.5 | 14.2 | 25 | 58 | 0.023 | 7.66 | 0.081 | 2 | 4.5 | 17.1 | 25 | 59 | 0.023 | 4.5 | 4.5 | 3.8 | [18 empty] | 12840 | [6 empty] | 80 | 80 | 80 | 360 | 360 | 360 | 620 | 600 | 640 | 630 | 525 | 524 | 750 |  | 980 | 970 | 1050 | 96 | 117 | 13 | 1400 | 290 | 410 | 52 | 62 | 8 | 780 | 140 | 300 |  | 9:00 | 0.67 | 10.6 | 24 | 16.08 | 6.09 | 15 | 10 | 1.608 | 15 | 6.5 | 0.41667 | 9:00 | 0.63 | 10.5 | 24.2286 | 15.264 | 6.06 | 15.3 | 10 | 1.5264 | 15 | 6.5 | 0.41274 | 9:00 | 0.6 | 11.8 | 22.8814 | 13.7288 | 6.09 | 15.5 | 10 | 1.3729 | 15 | 6.5 | 0.43704
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.39 | 16 | 16 | 13 | 138 | 202 | 14.7 | 0.57 |  | 6.03 | 10 | 0.097 | 5.98 | 10 |  | 5.98 | 10 | [8 empty] | 0.076 | [14 empty] | 0.083 | 2 | 0.38 |  | 0.078 | 0.03 | 2 | 0.49 |  | 0.064 | 2 | 0.43 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.08 | 0.423 | 7 | 0.75 | 14.2 | 10.6 | 0.745 |  | 6.08 | 0.323 | 5 | 0.61 | 16 | 10.3 | 0.52487 | 6.1 | 0.63 | 6 | 0.61 | 15.3 | 11.8 | 0.55704 | [13 empty] | 7.9 | 0.069 | 2 | 4 | 14.1 |  |  |  | 7.82 | 0.083 | 2 | 4 | 17 |  |  |  | 4.5 | 4.5 | 3.8 | [55 empty] | 13:00 | 0.75 | 10.6 | 24 | 18 | 6.08 | 14.2 | 15 | 1.2 | 10 | 6.5 | 0.625 | 13:00 | 0.61 | 10.3 | 24.699 | 15.0664 | 6.08 | 16 | 10 | 1.5066 | 15 | 6.5 | 0.40487 | 13:00 | 0.61 | 11.8 | 22.8814 | 13.9576 | 6.1 | 15.3 | 10 | 1.3958 | 15 | 6.5 | 0.43704
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.41 | 16 | 16 | 13.7 | 140 | 208 | 14.9 | 0.576 |  | 6.17 | 10 | 0.089 | 6.06 | 10 |  | 6.05 | 10 | [8 empty] | 0.073 | [14 empty] | 0.066 | 2 | 0.39 |  | 0.072 | 0.03 | 2 | 0.43 |  | 0.066 | 2 | 0.46 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17;00 | [53 empty] | 7.86 | 0.069 | 2 | 4.1 | 14.2 |  |  |  | 7.69 | 0.08 | 2 | 4.2 | 16.6 |  |  |  | 4.4 | 4.4 | 3.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.36 | 15 | 14 | 13 | 130 | 200 | 15 | 0.555 |  | 6.14 | 8 | 0.083 | 6.09 | 9 |  | 6.02 | 8 | [8 empty] | 0.074 | [14 empty] | 0.059 | 2 | 0.32 |  | 0.079 | 0.029 | 2 | 0.65 |  | 0.064 | 2 | 0.65 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.048 | [9 empty] | 6.14 | 0.721 | 8 | 0.69 | 13.8 | 10.5 | 0.7391 |  | 6.18 | 0.514 | 7 | 0.74 | 15.2 | 10.5 | 0.53274 | 6.18 | 0.601 | 7 | 0.61 | 15.6 | 11.7 | 0.55333 |  |  |  | 0.014 | [9 empty] | 7.65 | 0.076 | 3 | 4.3 | 14.3 | 20 | 44 | 0.018 | 7.6 | 0.071 | 2 | 4.1 | 16.2 | 21 | 44 | 0.017 | 4.3 | 4.3 | 4 | [55 empty] | 21:00 | 0.69 | 10.5 | 24.2286 | 16.7177 | 6.14 | 13.8 | 15 | 1.1145 | 10 | 6.5 | 0.6191 | 21:00 | 0.74 | 10.5 | 24.2286 | 17.9291 | 6.18 | 15.2 | 10 | 1.7929 | 15 | 6.5 | 0.41274 | 21:00 | 0.61 | 11.7 | 23.0769 | 14.0769 | 6.18 | 15.6 | 10 | 1.4077 | 15 | 6.5 | 0.43333
22:00 | [72 empty] | DOSE |  | TOTAL | 52.6 | 52.6 | 57.6 | 162.8 | 50.1 | 50.1 | 55.1 | 155.3 | 0 | 66.9686 | 0 | 84.3178 | 151.2864 | 9.5371 | TOTAL | 436.8702 | 46607.4472 | 0 | 4044.0529 | 0 | 0 | 0 | 2.2021 | 2.2021 | 2.0123 | 7.8193 | 7.8193 | 7.3981 | 1.6101 | 1.6398 | 1.7295 | 1.7241 | 1.3345 | 1.408 | 6.3725 | 29.5 | 0.25009 | 0.24956 | 0.2499 | 5.4953 | 2.4899 | 0.49761 | 19.5963 | 3.5192 | 29.8955 | 5.4867 | 2.4605 | 0.52451 | 18.5856 | 3.1729 | 40.126 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.39 | 13 | 14 | 13.3 | 129 | 201 | 14.9 | 0.539 |  | 6 | 7 | 0.068 | 5.95 | 7 |  | 5.9 | 7 | [8 empty] | 0.058 | [14 empty] | 0.024 | 2 | 0.44 |  | 0.061 | 0.017 | 2 | 0.61 |  | 0.036 | 2 | 0.5 | [22 empty] | AVERAGE | 10.52 | 10.52 | 11.52 | 32.56 | 10.02 | 10.02 | 11.02 | 31.06 |  | 13.3937 |  | 16.8636 | 30.2573 | 1.9074 | AVERAGE | 87.374 | 9321.4894 |  | 808.8106 | 0 | 0 | 0 | 2.2021 | 2.2021 | 2.0123 | 1.5639 | 1.5639 | 1.4796 | 0.32202 | 0.32796 | 0.3459 | 0.34483 | 0.2669 | 0.2816 | 1.2745 | 5.9 | 0.050017 | 0.049913 | 0.049981 | 1.0991 | 0.49799 | 0.099522 | 3.9193 | 0.70384 | 5.9791 | 1.0973 | 0.4921 | 0.1049 | 3.7171 | 0.63459 | 8.0252 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.4 | 94 | 92 | 80.5 | 788 | 1233 | 90.5 | 3.319 | 0.101 | 36.46 | 55 | 0.509 | 36.09 | 57 | 0 | 35.88 | 55 | 0 | 24.32 | 2.179 | 24 | 2.66 | 58 | 42 | 2.5456 | 0.417 | 24.32 | 1.572 | 21 | 2.6 | 61.5 | 41.6 | 2.0342 | 24.44 | 2.206 | 23 | 2.42 | 61.4 | 46.6 | 2.2059 | 0.319 | 11 | 2.27 | 0.03 | 0.429 | 0.14 | 11 |  | 0 | 0.361 | 11 | 2.84 | 0 | 45.94 | 0.414 | 11 | 25.7 | 84.8 | 45 | 102 | 0.041 | 45.55 | 0.437 | 10 | 25.3 | 100.9 | 46 | 103 | 0.04 | 26.9 | 27.1 | 22.3 |  |  | MINIMUM | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 12.1421 |  | 16.1122 | 28.2542 | 1.8965 | MINIMUM | 83.8601 | 7747.412 |  | 808.8106 |  |  |  | 2.2021 | 2.2021 | 2.0123 | 1.5425 | 1.5425 | 1.4035 | 0.30462 | 0.30462 | 0.33231 | 0.33231 | 0.25819 | 0.25769 | 1.2365 | 4 | 0.049528 | 0.049528 | 0.049827 | 1.0925 | 0.49315 | 0.092986 | 3.6766 | 0.6549 | 5.9223 | 1.0769 | 0.48384 | 0.10413 | 3.6055 | 0.57535 | 7.886 |  | MIN | 0.69 | 10.5 | 24.2286 | 16.7177 | 6.14 | 13.8 | 15 | 1.1145 |  |  |  | MIN | 0.61 | 10.3 | 24.699 | 15.0664 | 6.08 | 16 | 10 | 1.5066 |  |  |  | MIN | 0.6 | 11.8 | 22.8814 | 13.7288 | 6.09 | 15.5 | 10 | 1.3729 |  |  |  | 1.1145
AVERAGE | 6.4 | 15.6667 | 15.3333 | 13.4167 | 131.3333 | 205.5 | 15.0833 | 0.55317 | 0.0505 | 6.0767 | 9.1667 | 0.084833 | 6.015 | 9.5 |  | 5.98 | 9.1667 |  | 6.08 | 0.54475 | 6 | 0.665 | 14.5 | 10.5 | 0.63641 | 0.0695 | 6.08 | 0.393 | 5.25 | 0.65 | 15.375 | 10.4 | 0.50856 | 6.11 | 0.5515 | 5.75 | 0.605 | 15.35 | 11.65 | 0.55148 | 0.053167 | 1.8333 | 0.37833 | 0.015 | 0.0715 | 0.023333 | 1.8333 |  |  | 0.060167 | 1.8333 | 0.47333 |  | 7.6567 | 0.069 | 1.8333 | 4.2833 | 14.1333 | 22.5 | 51 | 0.0205 | 7.5917 | 0.072833 | 1.6667 | 4.2167 | 16.8167 | 23 | 51.5 | 0.02 | 4.4833 | 4.5167 | 3.7167 |  |  | MAXIMUM | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 |  | 13.847 |  | 17.5579 | 30.8434 | 1.9512 | MAXIMUM | 95.7123 | 10206.908 |  | 808.8106 |  |  |  | 2.2021 | 2.2021 | 2.0123 | 1.5897 | 1.5897 | 1.731 | 0.33367 | 0.33956 | 0.35315 | 0.35315 | 0.27283 | 0.29764 | 1.4267 | 6.5 | 0.051191 | 0.050668 | 0.05036 | 1.1142 | 0.50383 | 0.1032 | 4.1144 | 0.76805 | 6.1036 | 1.1076 | 0.49728 | 0.10703 | 3.8555 | 0.70116 | 8.5103
MINIMUM | 6.36 | 13 | 14 | 13 | 123 | 200 | 14.7 | 0.516 | 0.048 | 6 | 7 | 0.068 | 5.95 | 7 |  | 5.9 | 7 |  | 6.01 | 0.396 | 4 | 0.55 | 13.8 | 10.3 | 0.52487 | 0.058 | 6 | 0.3 | 4 | 0.61 | 15 | 10.3 | 0.4439 | 6.07 | 0.471 | 5 | 0.6 | 15 | 11.3 | 0.53852 | 0.024 | 1 | 0.32 | 0.014 | 0.061 | 0.016 | 1 |  |  | 0.036 | 1 | 0.4 |  | 7.36 | 0.065 | 1 | 4 | 14 | 20 | 44 | 0.018 | 7.3 | 0.06 | 1 | 4 | 16.2 | 21 | 44 | 0.017 | 4.3 | 4.3 | 3.5 | [15 empty] | MIL/MIN |  | TOTAL | 58190 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 1760 | 1760 | 1830 | 2970 | 3025 | 3190 | 3180 | 2695 | 2844 | 3350 | 0 | 4750 | 4740 | 5220 | 479 | 576 | 69 | 7620 | 1545 | 2053 | 263 | 313 | 40 | 3950 | 766 | 1515
MAXIMUM | 6.43 | 18 | 16 | 14 | 140 | 220 | 16 | 0.576 | 0.053 | 6.17 | 10 | 0.097 | 6.09 | 11 |  | 6.05 | 10 |  | 6.14 | 0.721 | 8 | 0.75 | 15 | 10.6 | 0.745 | 0.076 | 6.18 | 0.514 | 7 | 0.74 | 16 | 10.5 | 0.53274 | 6.18 | 0.63 | 7 | 0.61 | 15.6 | 11.8 | 0.55704 | 0.083 | 2 | 0.44 | 0.016 | 0.079 | 0.03 | 2 |  |  | 0.069 | 2 | 0.65 |  | 7.9 | 0.076 | 3 | 4.5 | 14.3 | 25 | 58 | 0.023 | 7.82 | 0.083 | 2 | 4.5 | 17.1 | 25 | 59 | 0.023 | 4.6 | 4.8 | 4 | [17 empty] | AVERAGE | 11638 | [6 empty] | 80 | 80 | 80 | 352 | 352 | 366 | 594 | 605 | 638 | 636 | 539 | 568.8 | 670 |  | 950 | 948 | 1044 | 95.8 | 115.2 | 13.8 | 1524 | 309 | 410.6 | 52.6 | 62.6 | 8 | 790 | 153.2 | 303
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0239 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.721 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.55 | [5 empty] | 6.09 |  |  |  |  | 0.083 |  |  |  |  | 0.55 | [6 empty] | 0.083 | [16 empty] | Pump Station MIN |  | 3.5 | [17 empty] | MINIMUM | 11100 | [6 empty] | 80 | 80 | 80 | 350 | 350 | 350 | 550 | 550 | 600 | 600 | 520 | 520 | 650 |  | 920 | 920 | 1020 | 95 | 114 | 13 | 1400 | 290 | 410 | 52 | 62 | 8 | 780 | 140 | 300
[90 empty] | MAXIMUM | 12840 | [6 empty] | 80 | 80 | 80 | 360 | 360 | 420 | 620 | 625 | 650 | 650 | 550 | 600 | 750 |  | 980 | 970 | 1050 | 96 | 117 | 14 | 1620 | 330 | 411 | 53 | 63 | 8 | 810 | 166 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.144 |  | TOTAL MGD: |  | 7.034 |  |  | FINISHED SOUTH 1 |  | START: | 23778432 |  | END: | 23785466 |  |  | Alum | 9308 | 7597 | 7597 | 9585 | 9585 | 0.9 | [44 empty] | 0.69 | 10.5 | 24.2286 | 16.7177 | 6.14 | 13.8 | 15 | 1.1145
[73 empty] | FINISHED 2 | 16.71 |  | TOTAL MGD: |  | 7.11 |  |  | FINISHED SOUTH 2 |  | START: | 43377107 |  | END: | 43384217 |  |  | Caustic | 7569 | 7867 | 7867
[73 empty] | TOTAL RAW | 34.381 |  | TOTAL MGD: |  | 5.178 |  |  | FINISHED CONWAY |  | START: | 10041930 |  | END: | 10047108 |  |  | Hypochlorite | 17 |  | 41
[76 empty] | TOTAL MGD: |  | 11.532 |  |  | FINISHED PERRY |  | START: | 33361150 |  | END: | 33372682 |  |  | Phosphate | 1889
[76 empty] | TOTAL MGD: |  | 11 |  |  | RAW PLANT 1 |  | START: | 30529960 |  | END: | 30540960 |  |  | Fluoride | 2400 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.079 |  |  | RAW PLANT 2 |  | START: | 30491650 |  | END: | 30502729 |  |  | Cal~Flo | 8.97 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.302 |  |  | RAW PLANT 3 |  | START: | 7010825 |  | END: | 7023127 |  |  | Zinc | 1198
[76 empty] | TOTAL MGD: |  | 0.953 |  |  | DECANT |  | START: | 1816983 |  | END: | 1817936 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 1.2657 |  |  | BLOW DOWN |  | START: | 9065.8247 |  | END: | 9067.0905 |  |  | NH3 | 9.65 |  | BI-SUL | 700
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23785466
43384217
10047108
33372682
30540960
30502729
7023127
1817936
9067.0905
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 22
DATE: | 2018-11-22 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-22 | [23 empty] | DATE: | 2018-11-22
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-22 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43426.0337 | 1,2,3,5 | 43 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | ,3 | 13.2854 | 1,3 | 17.5579 | 30.8434 | 2.3315 | 43426.0337 | 95.7123 | 7747.412 | 0 | 808.8106 | 0 | 0 | 0 | 9.6343 | 9.9096 | 9.0553 | 1.5866 | 1.5866 | 1.4437 | 0.37672 | 0.34443 | 0.34443 | 0.33905 | 0.31966 | 0.31966 | 1.4267 | 6 | 0.051191 | 0.050668 | 0.049906 | 1.0925 | 0.50173 | 0.092986 | 3.7669 | 0.6549 | 5.9223 | 1.0769 | 0.48384 | 0.10413 | 3.8555 | 0.57535 | 8.4117 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.95 | 0.782 | 9 | 0.6 | 13.4 | 10.5 | 0.65656 |  | 5.87 | 0.398 | 7 | 0.67 | 14.6 | 10.6 | 0.66167 | 5.91 | 0.742 | 8 | 0.66 | 15.3 | 11.7 | 0.46667 | [13 empty] | 7.12 | 0.059 | 1 | 4.1 | 14 |  |  |  | 7.02 | 0.055 | 1 | 4.1 | 16.3 |  |  |  | 4.2 | 4.2 | 4.1 | [18 empty] | 12840 | [6 empty] | 350 | 360 | 360 | 360 | 360 | 360 | 700 | 640 | 640 | 630 | 650 | 650 | 750 |  | 980 | 970 | 1050 | 96 | 117 | 13 | 1440 | 290 | 410 | 52 | 62 | 8 | 780 | 140 | 320 |  | 1:00 | 0.6 | 10.5 | 24.2286 | 14.5371 | 5.95 | 13.4 | 13 | 1.1182 | 10 | 6 | 0.53656 | 1:00 | 0.67 | 10.6 | 24 | 16.08 | 5.87 | 14.6 | 13 | 1.2369 | 10 | 6 | 0.54167 | 1:00 | 0.66 | 11.7 | 23.0769 | 15.2308 | 5.91 | 15.3 | 8 | 1.9038 | 15 | 6 | 0.34667
2:00 | [72 empty] | 43426.377 | 1,2,3,5 | 41 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | 8,3 | 11.6626 | 1,3 | 16.5758 | 28.2384 | 2.4264 | 43426.377 | 102.123 | 7993.3616 | 0 | 808.8106 | 0 | 0 | 0 | 10.1848 | 10.3775 | 10.313 | 1.5866 | 1.5866 | 1.4035 | 0.38211 | 0.36596 | 0.36596 | 0.34982 | 0.35408 | 0.34425 | 1.4267 | 6 | 0.049624 | 0.049624 | 0.049906 | 1.1039 | 0.50173 | 0.10014 | 3.8245 | 0.6549 | 5.9945 | 1.0976 | 0.49945 | 0.10413 | 3.6455 | 0.61645 | 8.4117 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.41 | 14 | 14 | 12.7 | 130 | 197 | 14.9 | 0.552 |  | 6.22 | 10 | 0.073 | 6.25 | 11 |  | 6.22 | 10 | [8 empty] | 0.066 | [14 empty] | 0.022 | 1 | 0.61 |  | 0.063 | 0.017 | 1 | 0.49 |  | 0.034 | 1 | 0.44 | [38 empty] | 13700 | [6 empty] | 370 | 377 | 410 | 360 | 360 | 350 | 710 | 680 | 680 | 650 | 720 | 700 | 750 |  | 950 | 950 | 1050 | 97 | 117 | 14 | 1450 | 290 | 415 | 53 | 64 | 8 | 780 | 150 | 320 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43426.6287 | 1,3,5 | 65 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | 8,3 | 14.8061 | 1,3 | 10.9915 | 25.7976 | 2.4264 | 43426.6287 | 101.743 | 9100.1348 | 0 | 808.8106 | 0 | 0 | 0 | 10.7959 | 11.0002 | 10.8755 | 1.6868 | 1.6868 | 1.4838 | 0.40503 | 0.38792 | 0.38792 | 0.3708 | 0.3734 | 0.36303 | 1.4267 | 6 | 0.052758 | 0.052758 | 0.052758 | 1.101 | 0.5015 | 0.098859 | 4.0313 | 0.69627 | 5.6821 | 1.0947 | 0.50324 | 0.096324 | 3.8287 | 0.65168 | 7.7808 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.27 | 0.064 | 1 | 4.1 | 13.8 |  |  |  | 7.34 | 0.061 | 1 | 4 | 16 |  |  |  | 4.1 | 4.1 | 4.2 | [18 empty] | 12900 | [6 empty] | 370 | 377 | 410 | 360 | 360 | 350 | 710 | 680 | 680 | 650 | 720 | 700 | 750 |  | 950 | 950 | 1050 | 91 | 110 | 13 | 1450 | 290 | 370 | 50 | 61 | 7 | 780 | 150 | 280 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43426.8761 | 1,3,5 | 65 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | 8,3 | 12.4114 | 1,3 | 15.503 | 27.9144 | 2.4264 | 43426.8761 | 100.7966 | 7747.412 | 0 | 808.8106 | 0 | 0 | 0 | 10.7959 | 11.0002 | 10.8755 | 1.6868 | 1.5931 | 1.4414 | 0.47919 | 0.46778 | 0.39933 | 0.41074 | 0.3734 | 0.3734 | 1.9022 | 11 | 0.051092 | 0.049981 | 0.049994 | 1.0889 | 0.5015 | 0.098859 | 3.9213 | 0.64825 | 5.3749 | 1.1385 | 0.49499 | 0.096324 | 3.7918 | 0.56479 | 7.2251 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.46 | 14 | 14 | 12.9 | 123 | 196 | 14.8 | 0.559 |  | 6.09 | 10 | 0.079 | 6 | 10 |  | 6 | 10 | [8 empty] | 0.069 | [14 empty] | 0.033 | 2 | 0.56 |  | 0.07 | 0.03 | 2 | 0.49 |  | 0.036 | 2 | 0.46 | [38 empty] | 12780 | [6 empty] | 370 | 377 | 410 | 360 | 340 | 340 | 840 | 820 | 700 | 720 | 720 | 720 | 1000 |  | 920 | 900 | 995 | 90 | 110 | 13 | 1400 | 270 | 350 | 52 | 60 | 7 | 760 | 130 | 260 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.05 | [9 empty] | 6.07 | 0.53 | 7 | 0.86 | 14 | 10.5 | 0.7391 |  | 6.06 | 0.369 | 5 | 0.78 | 15.5 | 10.6 | 0.53667 | 6.08 | 0.603 | 6 | 0.76 | 15.5 | 11.7 | 0.55333 |  |  |  | 0.011 | [9 empty] | 7.4 | 0.063 | 2 | 4 | 13.6 | 22 | 44 | 0.018 | 7.52 | 0.066 | 2 | 4 | 15.8 | 22 | 44 | 0.01 | 4.1 | 3.9 | 4.3 | [55 empty] | 9:00 | 0.86 | 10.5 | 24.2286 | 20.8366 | 6.07 | 14 | 15 | 1.3891 | 10 | 6.5 | 0.6191 | 9:00 | 0.78 | 10.6 | 24 | 18.72 | 6.06 | 15.5 | 10 | 1.872 | 15 | 6.5 | 0.41667 | 9:00 | 0.76 | 11.7 | 23.0769 | 17.5385 | 6.08 | 15.5 | 10 | 1.7538 | 15 | 6.5 | 0.43333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.49 | 14 | 14 | 12.8 | 129 | 200 | 14.8 | 0.554 |  | 6.1 | 10 | 0.069 | 6.06 | 10 |  | 6.07 | 10 | [8 empty] | 0.057 | [14 empty] | 0.026 | 2 | 0.58 |  | 0.06 | 0.028 | 2 | 0.48 |  | 0.036 | 2 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.465 | 7 | 0.83 | 14 | 10.5 | 0.7391 |  | 6.09 | 0.308 | 5 | 0.65 | 15.5 | 10.5 | 0.53274 | 6.11 | 0.56 | 6 | 0.63 | 15.7 | 11.4 | 0.54222 | [13 empty] | 7.76 | 0.069 | 2 | 4.3 | 13.6 |  |  |  | 7.73 | 0.069 | 2 | 3.9 | 16.7 |  |  |  | 4.1 | 3.8 | 3.4 | [55 empty] | 13:00 | 0.83 | 10.5 | 24.2286 | 20.1097 | 6.1 | 14 | 15 | 1.3406 | 10 | 6.5 | 0.6191 | 13:00 | 0.65 | 10.5 | 24.2286 | 15.7486 | 6.09 | 15.5 | 10 | 1.5749 | 15 | 6.5 | 0.41274 | 13:00 | 0.63 | 11.4 | 23.6842 | 14.9211 | 6.11 | 15.7 | 10 | 1.4921 | 15 | 6.5 | 0.42222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.39 | 14 | 14 | 12.5 | 132 | 195 | 14.8 | 0.56 |  | 6.06 | 10 | 0.074 | 6.03 | 10 |  | 6.03 | 10 | [8 empty] | 0.058 | [14 empty] | 0.021 | 2 | 0.44 |  | 0.059 | 0.027 | 2 | 0.47 |  | 0.037 | 2 | 0.36 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.63 | 0.063 | 1 | 4.4 | 13.5 |  |  |  | 7.63 | 0.069 | 1 | 3.9 | 16.3 |  |  |  | 4.1 | 3.7 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.46 | 12 | 12 | 12.7 | 130 | 197 | 14.9 | 0.535 |  | 6.07 | 7 | 0.069 | 6.04 | 8 |  | 6.08 | 8 | [8 empty] | 0.062 | [14 empty] | 0.022 | 2 | 0.53 |  | 0.061 | 0.023 | 2 | 0.59 |  | 0.039 | 2 | 0.41 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.16 | 0.742 | 9 | 0.71 | 13.3 | 10 | 0.70962 |  | 6.16 | 0.553 | 7 | 0.64 | 14.5 | 10 | 0.70962 | 6.18 | 0.616 | 8 | 0.57 | 15.7 | 11 | 0.52741 |  |  |  | 0.016 |  |  |  |  | 0.016 |  |  |  | 0.018 | 7.77 | 0.053 | 3 | 4.7 | 13.7 | 20 | 42 | 0.017 | 7.74 | 0.057 | 2 | 4.4 | 16 | 21 | 43 | 0.012 | 4.2 | 3.8 | 3.5 | [55 empty] | 21:00 | 0.71 | 10 | 25.44 | 18.0624 | 6.16 | 13.3 | 15 | 1.2042 | 10 | 6.5 | 0.58962 | 21:00 | 0.64 | 10 | 25.44 | 16.2816 | 6.16 | 14.5 | 15 | 1.0854 | 10 | 6.5 | 0.58962 | 21:00 | 0.57 | 11 | 24.5455 | 13.9909 | 6.18 | 15.7 | 10 | 1.3991 | 15 | 6.5 | 0.40741
22:00 | [72 empty] | DOSE |  | TOTAL | 41.2 | 41.2 | 45.2 | 127.6 | 39.2 | 39.2 | 43.2 | 121.6 | 0 | 52.1654 | 0 | 60.6283 | 112.7938 | 9.6107 | TOTAL | 400.3749 | 32588.3204 | 0 | 3235.2423 | 0 | 0 | 0 | 41.411 | 42.2874 | 41.1193 | 6.5468 | 6.453 | 5.7723 | 1.6431 | 1.5661 | 1.4976 | 1.4704 | 1.4205 | 1.4003 | 6.1823 | 29 | 0.20466 | 0.20303 | 0.20256 | 4.3864 | 2.0065 | 0.39084 | 15.5441 | 2.6543 | 22.9738 | 4.4078 | 1.9815 | 0.40092 | 15.1216 | 2.4083 | 31.8294 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.37 | 12 | 13 | 12.4 | 116 | 195 | 14.6 | 0.512 |  | 6.04 | 8 | 0.074 | 5.96 | 7 |  | 6.03 | 8 | [8 empty] | 0.063 | [14 empty] | 0.023 | 2 | 0.4 |  | 0.071 | 0.02 | 2 | 0.48 |  | 0.035 | 2 | 0.49 | [22 empty] | AVERAGE | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 |  | 13.0414 |  | 15.1571 | 28.1984 | 2.4027 | AVERAGE | 100.0937 | 8147.0801 |  | 808.8106 | 0 | 0 | 0 | 10.3527 | 10.5719 | 10.2798 | 1.6367 | 1.6133 | 1.4431 | 0.41076 | 0.39152 | 0.37441 | 0.3676 | 0.35513 | 0.35008 | 1.5456 | 7.25 | 0.051166 | 0.050758 | 0.050641 | 1.0966 | 0.50161 | 0.097711 | 3.886 | 0.66358 | 5.7435 | 1.1019 | 0.49538 | 0.10023 | 3.7804 | 0.60207 | 7.9573 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.58 | 80 | 81 | 76 | 760 | 1180 | 88.8 | 3.272 | 0.093 | 36.58 | 55 | 0.438 | 36.34 | 56 | 0 | 36.43 | 56 | 0 | 24.28 | 2.519 | 32 | 3 | 54.7 | 41.5 | 2.8444 | 0.375 | 24.18 | 1.628 | 24 | 2.74 | 60.1 | 41.7 | 2.4407 | 24.28 | 2.521 | 28 | 2.62 | 62.2 | 45.8 | 2.0896 | 0.147 | 11 | 3.12 | 0.027 | 0.384 | 0.145 | 11 | 3 | 0.016 | 0.217 | 11 | 2.66 | 0.018 | 44.95 | 0.371 | 10 | 25.6 | 82.2 | 42 | 86 | 0.035 | 44.98 | 0.377 | 9 | 24.3 | 97.1 | 43 | 87 | 0.022 | 24.8 | 23.5 | 22.8 |  |  | MINIMUM | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 11.6626 |  | 10.9915 | 25.7976 | 2.3315 | MINIMUM | 95.7123 | 7747.412 |  | 808.8106 |  |  |  | 9.6343 | 9.9096 | 9.0553 | 1.5866 | 1.5866 | 1.4035 | 0.37672 | 0.34443 | 0.34443 | 0.33905 | 0.31966 | 0.31966 | 1.4267 | 6 | 0.049624 | 0.049624 | 0.049906 | 1.0889 | 0.5015 | 0.092986 | 3.7669 | 0.64825 | 5.3749 | 1.0769 | 0.48384 | 0.096324 | 3.6455 | 0.56479 | 7.2251 |  | MIN | 0.6 | 10.5 | 24.2286 | 14.5371 | 5.95 | 13.4 | 13 | 1.1182 |  |  |  | MIN | 0.64 | 10 | 25.44 | 16.2816 | 6.16 | 14.5 | 15 | 1.0854 |  |  |  | MIN | 0.57 | 11 | 24.5455 | 13.9909 | 6.18 | 15.7 | 10 | 1.3991 |  |  |  | 1.0854
AVERAGE | 6.43 | 13.3333 | 13.5 | 12.6667 | 126.6667 | 196.6667 | 14.8 | 0.54533 | 0.0465 | 6.0967 | 9.1667 | 0.073 | 6.0567 | 9.3333 |  | 6.0717 | 9.3333 |  | 6.07 | 0.62975 | 8 | 0.75 | 13.675 | 10.375 | 0.7111 | 0.0625 | 6.045 | 0.407 | 6 | 0.685 | 15.025 | 10.425 | 0.61017 | 6.07 | 0.63025 | 7 | 0.655 | 15.55 | 11.45 | 0.52241 | 0.0245 | 1.8333 | 0.52 | 0.0135 | 0.064 | 0.024167 | 1.8333 | 0.5 | 0.016 | 0.036167 | 1.8333 | 0.44333 | 0.018 | 7.4917 | 0.061833 | 1.6667 | 4.2667 | 13.7 | 21 | 43 | 0.0175 | 7.4967 | 0.062833 | 1.5 | 4.05 | 16.1833 | 21.5 | 43.5 | 0.011 | 4.1333 | 3.9167 | 3.8 |  |  | MAXIMUM | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 |  | 14.8061 |  | 17.5579 | 30.8434 | 2.4264 | MAXIMUM | 102.123 | 9100.1348 |  | 808.8106 |  |  |  | 10.7959 | 11.0002 | 10.8755 | 1.6868 | 1.6868 | 1.4838 | 0.47919 | 0.46778 | 0.39933 | 0.41074 | 0.3734 | 0.3734 | 1.9022 | 11 | 0.052758 | 0.052758 | 0.052758 | 1.1039 | 0.50173 | 0.10014 | 4.0313 | 0.69627 | 5.9945 | 1.1385 | 0.50324 | 0.10413 | 3.8555 | 0.65168 | 8.4117
MINIMUM | 6.37 | 12 | 12 | 12.4 | 116 | 195 | 14.6 | 0.512 | 0.043 | 6.04 | 7 | 0.069 | 5.96 | 7 |  | 6 | 8 |  | 5.95 | 0.465 | 7 | 0.6 | 13.3 | 10 | 0.65656 | 0.057 | 5.87 | 0.308 | 5 | 0.64 | 14.5 | 10 | 0.53274 | 5.91 | 0.56 | 6 | 0.57 | 15.3 | 11 | 0.46667 | 0.021 | 1 | 0.4 | 0.011 | 0.059 | 0.017 | 1 | 0.47 | 0.016 | 0.034 | 1 | 0.36 | 0.018 | 7.12 | 0.053 | 1 | 4 | 13.5 | 20 | 42 | 0.017 | 7.02 | 0.055 | 1 | 3.9 | 15.8 | 21 | 43 | 0.01 | 4.1 | 3.7 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 52220 | 0 | 0 | 0 | 0 | 0 | 0 | 1460 | 1491 | 1590 | 1440 | 1420 | 1400 | 2960 | 2820 | 2700 | 2650 | 2810 | 2770 | 3250 | 0 | 3800 | 3770 | 4145 | 374 | 454 | 53 | 5740 | 1140 | 1545 | 207 | 247 | 30 | 3100 | 570 | 1180
MAXIMUM | 6.49 | 14 | 14 | 12.9 | 132 | 200 | 14.9 | 0.56 | 0.05 | 6.22 | 10 | 0.079 | 6.25 | 11 |  | 6.22 | 10 |  | 6.16 | 0.782 | 9 | 0.86 | 14 | 10.5 | 0.7391 | 0.069 | 6.16 | 0.553 | 7 | 0.78 | 15.5 | 10.6 | 0.70962 | 6.18 | 0.742 | 8 | 0.76 | 15.7 | 11.7 | 0.55333 | 0.033 | 2 | 0.61 | 0.016 | 0.071 | 0.03 | 2 | 0.59 | 0.016 | 0.039 | 2 | 0.5 | 0.018 | 7.77 | 0.069 | 3 | 4.7 | 14 | 22 | 44 | 0.018 | 7.74 | 0.069 | 2 | 4.4 | 16.7 | 22 | 44 | 0.012 | 4.2 | 4.2 | 4.3 | [17 empty] | AVERAGE | 13055 | [6 empty] | 365 | 372.75 | 397.5 | 360 | 355 | 350 | 740 | 705 | 675 | 662.5 | 702.5 | 692.5 | 812.5 |  | 950 | 942.5 | 1036.25 | 93.5 | 113.5 | 13.25 | 1435 | 285 | 386.25 | 51.75 | 61.75 | 7.5 | 775 | 142.5 | 295
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.075 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.782 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.57 | [5 empty] | 6.0617 |  |  |  |  | 0.039 |  |  |  |  | 0.57 | [6 empty] | 0.039 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 12780 | [6 empty] | 350 | 360 | 360 | 360 | 340 | 340 | 700 | 640 | 640 | 630 | 650 | 650 | 750 |  | 920 | 900 | 995 | 90 | 110 | 13 | 1400 | 270 | 350 | 50 | 60 | 7 | 760 | 130 | 260
[90 empty] | MAXIMUM | 13700 | [6 empty] | 370 | 377 | 410 | 360 | 360 | 360 | 840 | 820 | 700 | 720 | 720 | 720 | 1000 |  | 980 | 970 | 1050 | 97 | 117 | 14 | 1450 | 290 | 415 | 53 | 64 | 8 | 780 | 150 | 320
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.822 |  | TOTAL MGD: |  | 6.498 |  |  | FINISHED SOUTH 1 |  | START: | 23785466 |  | END: | 23791964 |  |  | Alum | 9304 | 8627 | 8627 | 10170 | 10170 | 0.9 | [44 empty] | 0.64 | 10 | 25.44 | 16.2816 | 6.16 | 14.5 | 15 | 1.0854
[73 empty] | FINISHED 2 | 14.839 |  | TOTAL MGD: |  | 6.324 |  |  | FINISHED SOUTH 2 |  | START: | 43384217 |  | END: | 43390541 |  |  | Caustic | 7093 | 7770 | 7770
[73 empty] | TOTAL RAW | 31.693 |  | TOTAL MGD: |  | 4.049 |  |  | FINISHED CONWAY |  | START: | 10047108 |  | END: | 10051157 |  |  | Hypochlorite | 16 |  | 40
[76 empty] | TOTAL MGD: |  | 10.79 |  |  | FINISHED PERRY |  | START: | 33372682 |  | END: | 33383472 |  |  | Phosphate | 1851
[76 empty] | TOTAL MGD: |  | 10.133 |  |  | RAW PLANT 1 |  | START: | 30540960 |  | END: | 30551093 |  |  | Fluoride | 2200 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.227 |  |  | RAW PLANT 2 |  | START: | 30502729 |  | END: | 30512956 |  |  | Cal~Flo | 5.44 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.333 |  |  | RAW PLANT 3 |  | START: | 7023127 |  | END: | 7034460 |  |  | Zinc | 1184
[76 empty] | TOTAL MGD: |  | 1.102 |  |  | DECANT |  | START: | 1817936 |  | END: | 1819038 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 1.4644 |  |  | BLOW DOWN |  | START: | 9067.0905 |  | END: | 9068.5548 |  |  | NH3 | 9.44 |  | BI-SUL | 650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23791964
43390541
10051157
33383472
30551093
30512956
7034460
1819038
9068.5548
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 23
DATE: | 2018-11-23 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-23 | [23 empty] | DATE: | 2018-11-23
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-23 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43427.0308 | 1,3,5 | 65 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | 8,3 | 12.4114 | 1,3 | 14.495 | 26.9064 | 2.3109 | 43427.0308 | 100.7966 | 7747.412 | 0 | 808.8106 | 0 | 0 | 0 | 10.7959 | 11.0002 | 10.8755 | 1.6868 | 1.5931 | 1.4414 | 0.50201 | 0.4849 | 0.41644 | 0.42215 | 0.38896 | 0.38896 | 2.2827 | 10 | 0.051092 | 0.049981 | 0.049994 | 1.0889 | 0.5015 | 0.098859 | 3.9213 | 0.64825 | 5.3749 | 1.1385 | 0.49499 | 0.096324 | 3.7918 | 0.56479 | 7.2251 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.741 | 9 | 0.61 | 13.1 | 10 | 0.70962 |  | 6.06 | 0.631 | 8 | 0.61 | 14.4 | 10 | 0.70962 | 6.15 | 0.639 | 8 | 0.62 | 15.7 | 11 | 0.52741 | [13 empty] | 7.34 | 0.055 | 2 | 4.2 | 13.7 |  |  |  | 7.39 | 0.059 | 1 | 4.1 | 15.7 |  |  |  | 4.2 | 3.9 | 3.6 | [18 empty] | 12780 | [6 empty] | 370 | 377 | 410 | 360 | 340 | 340 | 880 | 850 | 730 | 740 | 750 | 750 | 1200 |  | 920 | 900 | 995 | 90 | 110 | 13 | 1400 | 270 | 350 | 52 | 60 | 7 | 760 | 130 | 260 |  | 1:00 | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 13.1 | 15 | 1.0346 | 10 | 6.5 | 0.58962 | 1:00 | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 14.4 | 15 | 1.0346 | 10 | 6.5 | 0.58962 | 1:00 | 0.62 | 11 | 24.5455 | 15.2182 | 6.15 | 15.7 | 10 | 1.5218 | 15 | 6.5 | 0.40741
2:00 | [72 empty] | 43427.3013 | 1,3,5 | 70 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | 8,3 | 10.849 | 1,3 | 16.5499 | 27.3989 | 2.7058 | 43427.3013 | 102.5317 | 8116.3364 | 0 | 808.8106 | 0 | 0 | 0 | 11.5254 | 11.6421 | 12.0426 | 1.6868 | 1.6399 | 1.4414 | 0.4849 | 0.4849 | 0.42785 | 0.42785 | 0.42526 | 0.42007 | 2.2827 | 8 | 0.049981 | 0.049981 | 0.050246 | 1.101 | 0.5015 | 0.098859 | 3.8263 | 0.64825 | 5.2214 | 1.0947 | 0.49499 | 0.096324 | 3.7684 | 0.65168 | 7.2251 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.26 | 12 | 12 | 12.5 | 128 | 194 | 14.6 | 0.533 |  | 5.91 | 8 | 0.076 | 5.94 | 8 |  | 6.04 | 8 | [8 empty] | 0.067 | [14 empty] | 0.029 | 2 | 0.43 |  | 0.06 | 0.02 | 2 | 0.5 |  | 0.035 | 2 | 0.51 | [38 empty] | 13000 | [6 empty] | 395 | 399 | 454 | 360 | 350 | 340 | 850 | 850 | 750 | 750 | 820 | 810 | 1200 |  | 900 | 900 | 1000 | 91 | 110 | 13 | 1400 | 270 | 340 | 50 | 60 | 7 | 750 | 150 | 260 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43427.6266 | 1,3,5 | 70 | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 | 8,3 | 12.9355 | 1,3 | 12.6994 | 25.6349 | 2.7058 | 43427.6266 | 102.5317 | 7378.4876 | 0 | 808.8106 | 0 | 0 | 0 | 17.5069 | 17.7987 | 16.9764 | 1.6868 | 1.6399 | 1.4414 | 0.4849 | 0.4849 | 0.42785 | 0.42785 | 0.42526 | 0.42007 | 2.2827 | 8 | 0.049981 | 0.049981 | 0.050246 | 1.101 | 0.5015 | 0.098859 | 3.8263 | 0.64825 | 5.4517 | 1.0947 | 0.49499 | 0.096324 | 3.7684 | 0.65168 | 7.2251 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.46 | 0.057 | 2 | 4.7 | 13.3 |  |  |  | 7.51 | 0.061 | 2 | 4.5 | 15.3 |  |  |  | 4.2 | 4 | 4.5 | [18 empty] | 13000 | [6 empty] | 600 | 610 | 640 | 360 | 350 | 340 | 850 | 850 | 750 | 750 | 820 | 810 | 1200 |  | 900 | 900 | 1000 | 91 | 110 | 13 | 1400 | 270 | 355 | 50 | 60 | 7 | 750 | 150 | 260 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43427.8122 | 1,2,3,6 | 44 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 13.1198 | 1,3 | 18.0216 | 31.1414 | 2.7058 | 43427.8122 | 101.1974 | 7378.4876 | 0 | 808.8106 | 0 | 0 | 0 | 17.4524 | 17.4524 | 17.0081 | 1.702 | 1.6583 | 1.4308 | 0.51182 | 0.4905 | 0.42652 | 0.44784 | 0.39006 | 0.39006 | 1.8262 | 4 | 0.050172 | 0.049137 | 0.049931 | 1.1043 | 0.50105 | 0.099158 | 3.9239 | 0.64848 | 5.5067 | 1.1084 | 0.50272 | 0.1032 | 3.8169 | 0.59058 | 7.1903 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.36 | 14 | 14 | 12.7 | 130 | 196 | 14.4 | 0.56 |  | 5.8 | 8 | 0.109 | 5.8 | 8 |  | 5.8 | 8 | [8 empty] | 0.055 | [14 empty] | 0.029 | 2 | 0.43 |  | 0.063 | 0.028 | 2 | 0.46 |  | 0.036 | 2 | 0.46 | [38 empty] | 13700 | [6 empty] | 640 | 640 | 682 | 390 | 380 | 360 | 960 | 920 | 800 | 840 | 800 | 800 | 960 |  | 970 | 950 | 1060 | 98 | 118 | 14 | 1520 | 290 | 385 | 54 | 65 | 8 | 780 | 145 | 276 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.046 | [9 empty] | 5.95 | 0.569 | 8 | 0.83 | 13.5 | 10 | 0.63101 |  | 5.95 | 0.513 | 8 | 0.66 | 14.8 | 10 | 0.63101 | 6.05 | 0.52 | 7 | 0.63 | 15.8 | 11 | 0.52741 |  |  |  | 0.015 | [9 empty] | 7.76 | 0.063 | 2 | 4.4 | 13.2 | 22 | 40 | 0.014 | 7.77 | 0.063 | 2 | 4.1 | 15.2 | 23 | 40 | 0.011 | 4.2 | 4 | 4.4 | [55 empty] | 9:00 | 0.83 | 10 | 25.44 | 21.1152 | 5.95 | 13.5 | 13 | 1.6242 | 10 | 6 | 0.51101 | 9:00 | 0.66 | 10 | 25.44 | 16.7904 | 5.95 | 14.8 | 13 | 1.2916 | 10 | 6 | 0.51101 | 9:00 | 0.63 | 11 | 24.5455 | 15.4636 | 6.05 | 15.8 | 10 | 1.5464 | 15 | 6.5 | 0.40741
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.31 | 12 | 12 | 12.8 | 132 | 199 | 14.3 | 0.557 |  | 6.03 | 8 | 0.083 | 5.98 | 8 |  | 5.96 | 8 | [8 empty] | 0.063 | [14 empty] | 0.039 | 2 | 0.43 |  | 0.066 | 0.02 | 2 | 0.46 |  | 0.039 | 2 | 0.4 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6 | 0.469 | 8 | 0.8 | 13.7 | 10 | 0.63101 |  | 6.09 | 0.5 | 7 | 0.66 | 15.3 | 10 | 0.51308 | 6.1 | 0.539 | 7 | 0.65 | 15.8 | 11 | 0.52741 | [13 empty] | 7.3 | 0.061 | 1 | 4.2 | 13.5 |  |  |  | 7.47 | 0.066 | 1 | 4.5 | 16.3 |  |  |  | 4.2 | 4 | 4.3 | [55 empty] | 13:00 | 0.8 | 10 | 25.44 | 20.352 | 6 | 13.7 | 13 | 1.5655 | 10 | 6 | 0.51101 | 13:00 | 0.66 | 10 | 25.44 | 16.7904 | 6.09 | 15.3 | 10 | 1.679 | 15 | 6.5 | 0.39308 | 13:00 | 0.65 | 11 | 24.5455 | 15.9545 | 6.1 | 15.8 | 10 | 1.5955 | 15 | 6.5 | 0.40741
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.29 | 13 | 12 | 13.1 | 136 | 200 | 14 | 0.563 |  | 6.1 | 8 | 0.093 | 6.13 | 8 |  | 6.12 | 8 | [8 empty] | 0.065 | [14 empty] | 0.038 | 1 | 0.46 |  | 0.067 | 0.022 | 1 | 0.49 |  | 0.036 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.36 | 0.063 | 1 | 4.4 | 13.3 |  |  |  | 7.32 | 0.063 | 1 | 4.2 | 16 |  |  |  | 4.4 | 4.1 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.34 | 12 | 12 | 12.7 | 117 | 190 | 14.3 | 0.507 |  | 6.03 | 8 | 0.088 | 6.01 | 8 |  | 6.06 | 8 | [8 empty] | 0.06 | [14 empty] | 0.037 | 2 | 0.62 |  | 0.062 | 0.017 | 1 | 0.46 |  | 0.042 | 1 | 0.64 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.19 | 0.7 | 9 | 0.86 | 12.9 | 10.7 | 0.7509 |  | 6.11 | 0.526 | 7 | 0.75 | 14.2 | 10.7 | 0.7509 | 6.18 | 0.58 | 7 | 0.75 | 14.8 | 11.7 | 0.77 |  |  |  | 0.009 |  |  |  |  | 0.012 |  |  |  | 0.009 | 7.27 | 0.055 | 2 | 4.2 | 13.2 | 20 | 37 | 0.013 | 7.82 | 0.064 | 2 | 4.2 | 15.4 | 21 | 39 | 0.011 | 4.4 | 4 | 3.6 | [55 empty] | 21:00 | 0.86 | 10.7 | 23.7757 | 20.4471 | 6.19 | 12.9 | 15 | 1.3631 | 10 | 6.5 | 0.6309 | 21:00 | 0.75 | 10.7 | 23.7757 | 17.8318 | 6.11 | 14.2 | 15 | 1.1888 | 10 | 6.5 | 0.6309 | 21:00 | 0.75 | 11.7 | 23.0769 | 17.3077 | 6.18 | 14.8 | 15 | 1.1538 | 10 | 6.5 | 0.65
22:00 | [72 empty] | DOSE |  | TOTAL | 40.7 | 40.7 | 44.7 | 126.1 | 38.7 | 38.7 | 42.7 | 120.1 | 0 | 49.3157 | 0 | 61.7659 | 111.0816 | 10.4282 | TOTAL | 407.0575 | 30620.7236 | 0 | 3235.2423 | 0 | 0 | 0 | 57.2806 | 57.8933 | 56.9027 | 6.7623 | 6.5313 | 5.7548 | 1.9836 | 1.9452 | 1.6987 | 1.7257 | 1.6295 | 1.6192 | 8.6742 | 30 | 0.20123 | 0.19908 | 0.20042 | 4.3953 | 2.0056 | 0.39574 | 15.4978 | 2.5932 | 21.5547 | 4.4362 | 1.9877 | 0.39218 | 15.1455 | 2.4587 | 28.8656 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.36 | 12 | 12 | 12.8 | 112 | 191 | 14.2 | 0.509 |  | 5.94 | 8 | 0.076 | 5.88 | 7 |  | 5.92 | 8 | [8 empty] | 0.064 | [14 empty] | 0.021 | 1 | 0.81 |  | 0.064 | 0.017 | 2 | 0.58 |  | 0.037 | 1 | 0.07 | [22 empty] | AVERAGE | 10.175 | 10.175 | 11.175 | 31.525 | 9.675 | 9.675 | 10.675 | 30.025 |  | 12.3289 |  | 15.4415 | 27.7704 | 2.607 | AVERAGE | 101.7644 | 7655.1809 |  | 808.8106 | 0 | 0 | 0 | 14.3201 | 14.4733 | 14.2257 | 1.6906 | 1.6328 | 1.4387 | 0.49591 | 0.4863 | 0.42467 | 0.43142 | 0.40738 | 0.40479 | 2.1686 | 7.5 | 0.050306 | 0.04977 | 0.050104 | 1.0988 | 0.50139 | 0.098934 | 3.8744 | 0.64831 | 5.3887 | 1.1091 | 0.49692 | 0.098045 | 3.7864 | 0.61468 | 7.2164 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.92 | 75 | 74 | 76.6 | 755 | 1170 | 85.8 | 3.229 | 0.089 | 35.81 | 48 | 0.525 | 35.74 | 47 | 0 | 35.9 | 48 | 0 | 24.2 | 2.479 | 34 | 3.1 | 53.2 | 40.7 | 2.7225 | 0.374 | 24.21 | 2.17 | 30 | 2.68 | 58.7 | 40.7 | 2.6046 | 24.48 | 2.278 | 29 | 2.65 | 62.1 | 44.7 | 2.3522 | 0.193 | 10 | 3.18 | 0.024 | 0.382 | 0.124 | 10 | 2.95 | 0.012 | 0.225 | 9 | 2.48 | 0.009 | 44.49 | 0.354 | 10 | 26.1 | 80.2 | 42 | 77 | 0.027 | 45.28 | 0.376 | 9 | 25.6 | 93.9 | 44 | 79 | 0.022 | 25.6 | 24 | 23.8 |  |  | MINIMUM | 10 | 10 | 11 | 31 | 9.5 | 9.5 | 10.5 | 29.5 |  | 10.849 |  | 12.6994 | 25.6349 | 2.3109 | MINIMUM | 100.7966 | 7378.4876 |  | 808.8106 |  |  |  | 10.7959 | 11.0002 | 10.8755 | 1.6868 | 1.5931 | 1.4308 | 0.4849 | 0.4849 | 0.41644 | 0.42215 | 0.38896 | 0.38896 | 1.8262 | 4 | 0.049981 | 0.049137 | 0.049931 | 1.0889 | 0.50105 | 0.098859 | 3.8263 | 0.64825 | 5.2214 | 1.0947 | 0.49499 | 0.096324 | 3.7684 | 0.56479 | 7.1903 |  | MIN | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 13.1 | 15 | 1.0346 |  |  |  | MIN | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 14.4 | 15 | 1.0346 |  |  |  | MIN | 0.75 | 11.7 | 23.0769 | 17.3077 | 6.18 | 14.8 | 15 | 1.1538 |  |  |  | 1.0346
AVERAGE | 6.32 | 12.5 | 12.3333 | 12.7667 | 125.8333 | 195 | 14.3 | 0.53817 | 0.0445 | 5.9683 | 8 | 0.0875 | 5.9567 | 7.8333 |  | 5.9833 | 8 |  | 6.05 | 0.61975 | 8.5 | 0.775 | 13.3 | 10.175 | 0.68063 | 0.062333 | 6.0525 | 0.5425 | 7.5 | 0.67 | 14.675 | 10.175 | 0.65115 | 6.12 | 0.5695 | 7.25 | 0.6625 | 15.525 | 11.175 | 0.58806 | 0.032167 | 1.6667 | 0.53 | 0.012 | 0.063667 | 0.020667 | 1.6667 | 0.49167 | 0.012 | 0.0375 | 1.5 | 0.41333 |  | 7.415 | 0.059 | 1.6667 | 4.35 | 13.3667 | 21 | 38.5 | 0.0135 | 7.5467 | 0.062667 | 1.5 | 4.2667 | 15.65 | 22 | 39.5 | 0.011 | 4.2667 | 4 | 3.9667 |  |  | MAXIMUM | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 13.1198 |  | 18.0216 | 31.1414 | 2.7058 | MAXIMUM | 102.5317 | 8116.3364 |  | 808.8106 |  |  |  | 17.5069 | 17.7987 | 17.0081 | 1.702 | 1.6583 | 1.4414 | 0.51182 | 0.4905 | 0.42785 | 0.44784 | 0.42526 | 0.42007 | 2.2827 | 10 | 0.051092 | 0.049981 | 0.050246 | 1.1043 | 0.5015 | 0.099158 | 3.9239 | 0.64848 | 5.5067 | 1.1385 | 0.50272 | 0.1032 | 3.8169 | 0.65168 | 7.2251
MINIMUM | 6.26 | 12 | 12 | 12.5 | 112 | 190 | 14 | 0.507 | 0.043 | 5.8 | 8 | 0.076 | 5.8 | 7 |  | 5.8 | 8 |  | 5.95 | 0.469 | 8 | 0.61 | 12.9 | 10 | 0.63101 | 0.055 | 5.95 | 0.5 | 7 | 0.61 | 14.2 | 10 | 0.51308 | 6.05 | 0.52 | 7 | 0.62 | 14.8 | 11 | 0.52741 | 0.021 | 1 | 0.43 | 0.009 | 0.06 | 0.017 | 1 | 0.46 | 0.012 | 0.035 | 1 | 0.07 |  | 7.27 | 0.055 | 1 | 4.2 | 13.2 | 20 | 37 | 0.013 | 7.32 | 0.059 | 1 | 4.1 | 15.2 | 21 | 39 | 0.011 | 4.2 | 3.9 | 3.4 | [15 empty] | MIL/MIN |  | TOTAL | 52480 | 0 | 0 | 0 | 0 | 0 | 0 | 2005 | 2026 | 2186 | 1470 | 1420 | 1380 | 3540 | 3470 | 3030 | 3080 | 3190 | 3170 | 4560 | 0 | 3690 | 3650 | 4055 | 370 | 448 | 53 | 5720 | 1100 | 1430 | 206 | 245 | 29 | 3040 | 575 | 1056
MAXIMUM | 6.36 | 14 | 14 | 13.1 | 136 | 200 | 14.6 | 0.563 | 0.046 | 6.1 | 8 | 0.109 | 6.13 | 8 |  | 6.12 | 8 |  | 6.19 | 0.741 | 9 | 0.86 | 13.7 | 10.7 | 0.7509 | 0.067 | 6.11 | 0.631 | 8 | 0.75 | 15.3 | 10.7 | 0.7509 | 6.18 | 0.639 | 8 | 0.75 | 15.8 | 11.7 | 0.77 | 0.039 | 2 | 0.81 | 0.015 | 0.067 | 0.028 | 2 | 0.58 | 0.012 | 0.042 | 2 | 0.64 |  | 7.76 | 0.063 | 2 | 4.7 | 13.7 | 22 | 40 | 0.014 | 7.82 | 0.066 | 2 | 4.5 | 16.3 | 23 | 40 | 0.011 | 4.4 | 4.1 | 4.5 | [17 empty] | AVERAGE | 13120 | [6 empty] | 501.25 | 506.5 | 546.5 | 367.5 | 355 | 345 | 885 | 867.5 | 757.5 | 770 | 797.5 | 792.5 | 1140 |  | 922.5 | 912.5 | 1013.75 | 92.5 | 112 | 13.25 | 1430 | 275 | 357.5 | 51.5 | 61.25 | 7.25 | 760 | 143.75 | 264
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9694 |  | TOTAL AVG COAG ALK: |  |  |  | 7.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.741 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.61 | [5 empty] | 6.0742 |  |  |  |  | 0.042 |  |  |  |  | 0.61 | [6 empty] | 0.042 | [16 empty] | Pump Station MIN |  | 3.4 | [17 empty] | MINIMUM | 12780 | [6 empty] | 370 | 377 | 410 | 360 | 340 | 340 | 850 | 850 | 730 | 740 | 750 | 750 | 960 |  | 900 | 900 | 995 | 90 | 110 | 13 | 1400 | 270 | 340 | 50 | 60 | 7 | 750 | 130 | 260
[90 empty] | MAXIMUM | 13700 | [6 empty] | 640 | 640 | 682 | 390 | 380 | 360 | 960 | 920 | 800 | 840 | 820 | 810 | 1200 |  | 970 | 950 | 1060 | 98 | 118 | 14 | 1520 | 290 | 385 | 54 | 65 | 8 | 780 | 150 | 276
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.027 |  | TOTAL MGD: |  | 6.161 |  |  | FINISHED SOUTH 1 |  | START: | 23791964 |  | END: | 23798125 |  |  | Alum | 9312 | 10180 | 10180 | 11200 | 11200 | 0.9 | [44 empty] | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 13.1 | 15 | 1.0346
[73 empty] | FINISHED 2 | 14.577 |  | TOTAL MGD: |  | 5.866 |  |  | FINISHED SOUTH 2 |  | START: | 43390541 |  | END: | 43396407 |  |  | Caustic | 6723 | 7653 | 7653
[73 empty] | TOTAL RAW | 30.618 |  | TOTAL MGD: |  | 4.307 |  |  | FINISHED CONWAY |  | START: | 10051157 |  | END: | 10055464 |  |  | Hypochlorite | 14 |  | 38
[76 empty] | TOTAL MGD: |  | 10.27 |  |  | FINISHED PERRY |  | START: | 33383472 |  | END: | 33393742 |  |  | Phosphate | 1820
[76 empty] | TOTAL MGD: |  | 9.768 |  |  | RAW PLANT 1 |  | START: | 30551093 |  | END: | 30560861 |  |  | Fluoride | 2200 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.893 |  |  | RAW PLANT 2 |  | START: | 30512956 |  | END: | 30522849 |  |  | Cal~Flo | 11.16 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.957 |  |  | RAW PLANT 3 |  | START: | 7034460 |  | END: | 7045417 |  |  | Zinc | 1063
[76 empty] | TOTAL MGD: |  | 1.061 |  |  | DECANT |  | START: | 1819038 |  | END: | 1820099 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 1.4217 |  |  | BLOW DOWN |  | START: | 9068.5548 |  | END: | 9069.9766 |  |  | NH3 | 9.23 |  | BI-SUL | 650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23798125
43396407
10055464
33393742
30560861
30522849
7045417
1820099
9069.9766
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 24
DATE: | 2018-11-24 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-24 | [23 empty] | DATE: | 2018-11-24
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-24 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43428.0207 | 1,2,3,6 | 44 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 12.8678 | 3112 | 15.6974 | 28.5653 | 2.8414 | 43428.0207 | 101.1974 | 7378.4876 | 0 | 808.8106 | 0 | 0 | 0 | 17.7251 | 18.5431 | 17.1328 | 1.702 | 1.6583 | 1.4308 | 0.51182 | 0.4905 | 0.42652 | 0.44784 | 0.39006 | 0.39006 | 1.8262 | 4 | 0.050172 | 0.049137 | 0.049931 | 1.1043 | 0.50105 | 0.099158 | 3.8569 | 0.64848 | 5.5067 | 1.1084 | 0.50272 | 0.1032 | 3.6947 | 0.59058 | 7.1903 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.09 | 0.651 | 7 | 0.83 | 13.1 | 10.7 | 0.7509 |  | 5.99 | 0.542 | 7 | 0.74 | 14 | 10.7 | 0.66678 | 6.09 | 0.748 | 9 | 0.83 | 14.7 | 11.7 | 0.77 | [13 empty] | 7.38 | 0.053 | 2 | 4.2 | 13.2 |  |  |  | 7.57 | 0.056 | 2 | 4.5 | 15.3 |  |  |  | 4.4 | 4.1 | 3.9 | [18 empty] | 13700 | [6 empty] | 650 | 680 | 687 | 390 | 380 | 360 | 960 | 920 | 800 | 840 | 800 | 800 | 960 |  | 970 | 950 | 1060 | 98 | 118 | 14 | 1490 | 290 | 385 | 54 | 65 | 8 | 750 | 145 | 276 |  | 1:00 | 0.83 | 10.7 | 23.7757 | 19.7338 | 6.09 | 13.1 | 15 | 1.3156 | 10 | 6.5 | 0.6309 | 1:00 | 0.74 | 10.7 | 23.7757 | 17.594 | 5.99 | 14 | 13 | 1.3534 | 10 | 6 | 0.54678 | 1:00 | 0.83 | 11.7 | 23.0769 | 19.1538 | 6.09 | 14.7 | 15 | 1.2769 | 10 | 6.5 | 0.65
2:00 | [72 empty] | 43428.3416 | 1,2,3,6 | 46 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 11.723 | 1,3 | 14.9702 | 26.6933 | 2.4725 | 43428.3416 | 101.936 | 7378.4876 | 0 | 808.8106 | 0 | 0 | 0 | 17.9978 | 18.8158 | 16.9583 | 1.6365 | 1.6583 | 1.391 | 0.50649 | 0.50649 | 0.45318 | 0.45318 | 0.43882 | 0.43882 | 1.8262 | 6 | 0.049137 | 0.049137 | 0.04946 | 1.1269 | 0.50105 | 0.099158 | 3.9069 | 0.62612 | 5.6497 | 1.1289 | 0.5 | 0.1032 | 3.8084 | 0.61095 | 6.1222 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.34 | 12 | 12 | 12.7 | 121 | 185 | 14.2 | 0.55 |  | 5.85 | 7 | 0.079 | 5.86 | 8 |  | 5.9 | 8 | [8 empty] | 0.067 | [14 empty] | 0.022 | 1 | 0.63 |  | 0.066 | 0.016 | 1 | 0.55 |  | 0.036 | 1 | 0.65 | [38 empty] | 13800 | [6 empty] | 660 | 690 | 680 | 375 | 380 | 350 | 950 | 950 | 850 | 850 | 900 | 900 | 960 |  | 950 | 950 | 1050 | 100 | 118 | 14 | 1490 | 280 | 395 | 55 | 65 | 8 | 800 | 150 | 235 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43428.7834 | 1,2,3,6 | 46 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 11.723 | 1,3 | 14.9702 | 26.6933 | 2.4725 | 43428.7834 | 101.936 | 7624.4372 | 0 | 808.8106 | 0 | 0 | 0 | 17.9978 | 18.8158 | 16.9583 | 1.6583 | 1.6583 | 1.391 | 0.50649 | 0.50649 | 0.45318 | 0.45318 | 0.5851 | 0.43882 | 1.8262 | 2.5 | 0.049137 | 0.049137 | 0.049931 | 1.1269 | 0.5 | 0.099158 | 3.9242 | 0.62612 | 5.6497 | 1.1289 | 0.5 | 0.1032 | 3.8069 | 0.69241 | 6.1222 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.2 | 0.057 | 2 | 4.3 | 13.1 |  |  |  | 7.51 | 0.054 | 2 | 4.2 | 15.4 |  |  |  | 4.4 | 4 | 4.2 | [18 empty] | 13800 | [6 empty] | 660 | 690 | 680 | 380 | 380 | 350 | 950 | 950 | 850 | 850 | 1200 | 900 | 960 |  | 950 | 950 | 1060 | 100 | 118 | 14 | 1500 | 280 | 395 | 55 | 65 | 8 | 780 | 170 | 235 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.31 | 12 | 12 | 12.3 | 128 | 188 | 14.2 | 0.542 |  | 5.96 | 8 | 0.071 | 5.97 | 8 |  | 5.92 | 8 | [8 empty] | 0.061 | [14 empty] | 0.021 | 1 | 0.61 |  | 0.076 | 0.017 | 2 | 0.56 |  | 0.035 | 1 | 0.66 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.042 | [9 empty] | 5.95 | 0.486 | 8 | 0.79 | 13.8 | 11 | 0.68211 |  | 6.03 | 0.454 | 9 | 0.78 | 15.1 | 11 | 0.55239 | 6.02 | 0.533 | 10 | 0.73 | 15.2 | 12 | 0.56444 |  |  |  | 0.01 | [9 empty] | 7.36 | 0.063 | 1 | 4.5 | 13.2 | 21 | 36 | 0.011 | 7.43 | 0.063 | 1 | 4.2 | 15.7 | 21 | 36 | 0.01 | 4.3 | 4.1 | 4.2 | [55 empty] | 9:00 | 0.79 | 11 | 23.1273 | 18.2705 | 5.95 | 13.8 | 13 | 1.4054 | 10 | 6 | 0.56211 | 9:00 | 0.78 | 11 | 23.1273 | 18.0393 | 6.03 | 15.1 | 10 | 1.8039 | 15 | 6.5 | 0.43239 | 9:00 | 0.73 | 12 | 22.5 | 16.425 | 6.02 | 15.2 | 10 | 1.6425 | 15 | 6.5 | 0.44444
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.33 | 12 | 12 | 11.9 | 126 | 189 | 14.3 | 0.536 |  | 6 | 8 | 0.075 | 6.09 | 8 |  | 6.05 | 8 | [8 empty] | 0.069 | [14 empty] | 0.023 | 1 | 0.63 |  | 0.073 | 0.021 | 1 | 0.54 |  | 0.039 | 2 | 0.61 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.439 | 8 | 0.79 | 12.9 | 11 | 0.76858 |  | 6.03 | 0.459 | 8 | 0.78 | 14 | 11 | 0.76858 | 6 | 0.693 | 10 | 0.73 | 14.6 | 12 | 0.69778 | [13 empty] | 7.73 | 0.066 | 1 | 4.2 | 13.2 |  |  |  | 7.69 | 0.063 | 1 | 4.1 | 16.4 |  |  |  | 4.3 | 4 | 3.2 | [55 empty] | 13:00 | 0.79 | 11 | 23.1273 | 18.2705 | 6.03 | 12.9 | 15 | 1.218 | 10 | 6.5 | 0.64858 | 13:00 | 0.78 | 11 | 23.1273 | 18.0393 | 6.03 | 14 | 15 | 1.2026 | 10 | 6.5 | 0.64858 | 13:00 | 0.73 | 12 | 22.5 | 16.425 | 6 | 14.6 | 13 | 1.2635 | 10 | 6 | 0.57778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.38 | 12 | 12 | 11.7 | 114 | 173 | 14.4 | 0.548 |  | 5.99 | 8 | 0.081 | 6.08 | 8 |  | 6.06 | 8 | [8 empty] | 0.07 | [14 empty] | 0.023 | 1 | 0.61 |  | 0.072 | 0.021 | 1 | 0.53 |  | 0.039 | 1 | 0.63 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.63 | 0.06 | 1 | 4 | 13.4 |  |  |  | 7.7 | 0.063 | 1 | 4.5 | 16.6 |  |  |  | 4.2 | 4 | 3.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.39 | 10 | 15 | 11.6 | 115 | 180 | 14.9 | 0.489 |  | 6.08 | 9 | 0.069 | 6.04 | 10 |  | 6.03 | 9 | [8 empty] | 0.056 | [14 empty] | 0.023 | 1 | 0.54 |  | 0.064 | 0.02 | 1 | 0.75 |  | 0.037 | 1 | 0.47 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.039 | [9 empty] | 6.15 | 0.518 | 5 | 0.87 | 15.5 | 10.7 | 0.5406 |  | 6.19 | 0.567 | 7 | 0.84 | 14.1 | 10.7 | 0.7509 | 6.1 | 0.68 | 7 | 0.71 | 15.4 | 11.7 | 0.55333 |  |  |  | 0.007 |  |  |  |  | 0.016 |  |  |  | 0.009 | 8 | 0.054 | 1 | 3.9 | 13.6 | 20 | 32 | 0.014 | 7.98 | 0.052 | 1 | 4 | 16.3 | 21 | 38 | 0.009 | 4 | 4 | 3.7 | [55 empty] | 21:00 | 0.87 | 10.7 | 23.7757 | 20.6849 | 6.15 | 15.5 | 10 | 2.0685 | 15 | 6.5 | 0.4206 | 21:00 | 0.84 | 10.7 | 23.7757 | 19.9716 | 6.19 | 14.1 | 15 | 1.3314 | 10 | 6.5 | 0.6309 | 21:00 | 0.71 | 11.7 | 23.0769 | 16.3846 | 6.1 | 15.4 | 10 | 1.6385 | 15 | 6.5 | 0.43333
22:00 | [72 empty] | DOSE |  | TOTAL | 32.1 | 32.1 | 35.1 | 99.3 | 30.6 | 30.6 | 33.6 | 94.8 | 0 | 36.3139 | 3112 | 45.6379 | 81.9518 | 7.7864 | TOTAL | 305.0695 | 22381.4124 | 0 | 2426.4317 | 0 | 0 | 0 | 53.7206 | 56.1748 | 51.0493 | 4.9968 | 4.9749 | 4.2128 | 1.5248 | 1.5035 | 1.3329 | 1.3542 | 1.414 | 1.2677 | 5.4785 | 12.5 | 0.14845 | 0.14741 | 0.14932 | 3.3581 | 1.5021 | 0.29747 | 11.6879 | 1.9007 | 16.8061 | 3.3662 | 1.5027 | 0.30961 | 11.31 | 1.8939 | 19.4348 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.36 | 11 | 14 | 10.8 | 116 | 182 | 14.7 | 0.505 |  | 6.01 | 8 | 0.086 | 5.99 | 9 |  | 5.92 | 9 | [8 empty] | 0.064 | [14 empty] | 0.021 | 1 | 0.6 |  | 0.064 | 0.021 | 1 | 0.86 |  | 0.034 | 1 | 0.52 | [22 empty] | AVERAGE | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 12.1046 | 3112 | 15.2126 | 27.3173 | 2.5955 | AVERAGE | 101.6898 | 7460.4708 |  | 808.8106 | 0 | 0 | 0 | 17.9069 | 18.7249 | 17.0164 | 1.6656 | 1.6583 | 1.4043 | 0.50827 | 0.50116 | 0.44429 | 0.4514 | 0.47133 | 0.42257 | 1.8262 | 4.1667 | 0.049482 | 0.049137 | 0.049774 | 1.1194 | 0.5007 | 0.099158 | 3.896 | 0.63358 | 5.602 | 1.1221 | 0.50091 | 0.1032 | 3.77 | 0.63131 | 6.4783 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.11 | 69 | 77 | 71 | 720 | 1097 | 86.7 | 3.17 | 0.081 | 35.89 | 48 | 0.461 | 36.03 | 51 | 0 | 35.88 | 50 | 0 | 24.22 | 2.094 | 28 | 3.28 | 55.3 | 43.4 | 2.7422 | 0.387 | 24.24 | 2.022 | 31 | 3.14 | 57.2 | 43.4 | 2.7386 | 24.21 | 2.654 | 36 | 3 | 59.9 | 47.4 | 2.5856 | 0.133 | 6 | 3.62 | 0.017 | 0.415 | 0.116 | 7 | 3.79 | 0.016 |  | 7 | 3.54 | 0.009 | 45.3 | 0.353 | 8 | 25.1 | 79.7 | 41 | 68 | 0.025 | 45.88 | 0.351 | 8 | 25.5 | 95.7 | 42 | 74 | 0.019 | 25.6 | 24.2 | 22.7 |  |  | MINIMUM | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 11.723 | 3112 | 14.9702 | 26.6933 | 2.4725 | MINIMUM | 101.1974 | 7378.4876 |  | 808.8106 |  |  |  | 17.7251 | 18.5431 | 16.9583 | 1.6365 | 1.6583 | 1.391 | 0.50649 | 0.4905 | 0.42652 | 0.44784 | 0.39006 | 0.39006 | 1.8262 | 2.5 | 0.049137 | 0.049137 | 0.04946 | 1.1043 | 0.5 | 0.099158 | 3.8569 | 0.62612 | 5.5067 | 1.1084 | 0.5 | 0.1032 | 3.6947 | 0.59058 | 6.1222 |  | MIN | 0.79 | 11 | 23.1273 | 18.2705 | 6.03 | 12.9 | 15 | 1.218 |  |  |  | MIN | 0.78 | 11 | 23.1273 | 18.0393 | 6.03 | 14 | 15 | 1.2026 |  |  |  | MIN | 0.73 | 12 | 22.5 | 16.425 | 6 | 14.6 | 13 | 1.2635 |  |  |  | 1.2026
AVERAGE | 6.3517 | 11.5 | 12.8333 | 11.8333 | 120 | 182.8333 | 14.45 | 0.52833 | 0.0405 | 5.9817 | 8 | 0.076833 | 6.005 | 8.5 |  | 5.98 | 8.3333 |  | 6.055 | 0.5235 | 7 | 0.82 | 13.825 | 10.85 | 0.68555 | 0.0645 | 6.06 | 0.5055 | 7.75 | 0.785 | 14.3 | 10.85 | 0.68466 | 6.0525 | 0.6635 | 9 | 0.75 | 14.975 | 11.85 | 0.64639 | 0.022167 | 1 | 0.60333 | 0.0085 | 0.069167 | 0.019333 | 1.1667 | 0.63167 | 0.016 |  | 1.1667 | 0.59 |  | 7.55 | 0.058833 | 1.3333 | 4.1833 | 13.2833 | 20.5 | 34 | 0.0125 | 7.6467 | 0.0585 | 1.3333 | 4.25 | 15.95 | 21 | 37 | 0.0095 | 4.2667 | 4.0333 | 3.7833 |  |  | MAXIMUM | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 12.8678 | 3112 | 15.6974 | 28.5653 | 2.8414 | MAXIMUM | 101.936 | 7624.4372 |  | 808.8106 |  |  |  | 17.9978 | 18.8158 | 17.1328 | 1.702 | 1.6583 | 1.4308 | 0.51182 | 0.50649 | 0.45318 | 0.45318 | 0.5851 | 0.43882 | 1.8262 | 6 | 0.050172 | 0.049137 | 0.049931 | 1.1269 | 0.50105 | 0.099158 | 3.9242 | 0.64848 | 5.6497 | 1.1289 | 0.50272 | 0.1032 | 3.8084 | 0.69241 | 7.1903
MINIMUM | 6.31 | 10 | 12 | 10.8 | 114 | 173 | 14.2 | 0.489 | 0.039 | 5.85 | 7 | 0.069 | 5.86 | 8 |  | 5.9 | 8 |  | 5.95 | 0.439 | 5 | 0.79 | 12.9 | 10.7 | 0.5406 | 0.056 | 5.99 | 0.454 | 7 | 0.74 | 14 | 10.7 | 0.55239 | 6 | 0.533 | 7 | 0.71 | 14.6 | 11.7 | 0.55333 | 0.021 | 1 | 0.54 | 0.007 | 0.064 | 0.016 | 1 | 0.53 | 0.016 |  | 1 | 0.47 |  | 7.2 | 0.053 | 1 | 3.9 | 13.1 | 20 | 32 | 0.011 | 7.43 | 0.052 | 1 | 4 | 15.3 | 21 | 36 | 0.009 | 4 | 4 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 41300 | 0 | 0 | 0 | 0 | 0 | 0 | 1970 | 2060 | 2047 | 1145 | 1140 | 1060 | 2860 | 2820 | 2500 | 2540 | 2900 | 2600 | 2880 | 0 | 2870 | 2850 | 3170 | 298 | 354 | 42 | 4480 | 850 | 1175 | 164 | 195 | 24 | 2330 | 465 | 746
MAXIMUM | 6.39 | 12 | 15 | 12.7 | 128 | 189 | 14.9 | 0.55 | 0.042 | 6.08 | 9 | 0.086 | 6.09 | 10 |  | 6.06 | 9 |  | 6.15 | 0.651 | 8 | 0.87 | 15.5 | 11 | 0.76858 | 0.07 | 6.19 | 0.567 | 9 | 0.84 | 15.1 | 11 | 0.76858 | 6.1 | 0.748 | 10 | 0.83 | 15.4 | 12 | 0.77 | 0.023 | 1 | 0.63 | 0.01 | 0.076 | 0.021 | 2 | 0.86 | 0.016 |  | 2 | 0.66 |  | 8 | 0.066 | 2 | 4.5 | 13.6 | 21 | 36 | 0.014 | 7.98 | 0.063 | 2 | 4.5 | 16.6 | 21 | 38 | 0.01 | 4.4 | 4.1 | 4.2 | [17 empty] | AVERAGE | 13766.6667 | [6 empty] | 656.6667 | 686.6667 | 682.3333 | 381.6667 | 380 | 353.3333 | 953.3333 | 940 | 833.3333 | 846.6667 | 966.6667 | 866.6667 | 960 |  | 956.6667 | 950 | 1056.6667 | 99.3333 | 118 | 14 | 1493.3333 | 283.3333 | 391.6667 | 54.6667 | 65 | 8 | 776.6667 | 155 | 248.6667
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9889 |  | TOTAL AVG COAG ALK: |  |  |  | 8.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.748 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.71 | [5 empty] | 6.0558 |  |  |  |  | 0.023 |  |  |  |  | 0.71 | [6 empty] | 0.023 | [16 empty] | Pump Station MIN |  | 3.2 | [17 empty] | MINIMUM | 13700 | [6 empty] | 650 | 680 | 680 | 375 | 380 | 350 | 950 | 920 | 800 | 840 | 800 | 800 | 960 |  | 950 | 950 | 1050 | 98 | 118 | 14 | 1490 | 280 | 385 | 54 | 65 | 8 | 750 | 145 | 235
[90 empty] | MAXIMUM | 13800 | [6 empty] | 660 | 690 | 687 | 390 | 380 | 360 | 960 | 950 | 850 | 850 | 1200 | 900 | 960 |  | 970 | 950 | 1060 | 100 | 118 | 14 | 1500 | 290 | 395 | 55 | 65 | 8 | 800 | 170 | 276
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.845 |  | TOTAL MGD: |  | 6.46 |  |  | FINISHED SOUTH 1 |  | START: | 23798125 |  | END: | 23804585 |  |  | Alum | 9307 | 8890 | 8890 | 9603 | 9603 | 0.9 | [44 empty] | 0.78 | 11 | 23.1273 | 18.0393 | 6.03 | 14 | 15 | 1.2026
[73 empty] | FINISHED 2 | 16.057 |  | TOTAL MGD: |  | 6.385 |  |  | FINISHED SOUTH 2 |  | START: | 43396407 |  | END: | 43402792 |  |  | Caustic | 5948 | 7515 | 7515
[73 empty] | TOTAL RAW | 32.732 |  | TOTAL MGD: |  | 4.644 |  |  | FINISHED CONWAY |  | START: | 10055464 |  | END: | 10060108 |  |  | Hypochlorite | 18 |  | 45
[76 empty] | TOTAL MGD: |  | 11.413 |  |  | FINISHED PERRY |  | START: | 33393742 |  | END: | 33405155 |  |  | Phosphate | 1762
[76 empty] | TOTAL MGD: |  | 10.438 |  |  | RAW PLANT 1 |  | START: | 30560861 |  | END: | 30571299 |  |  | Fluoride | 2200 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.568 |  |  | RAW PLANT 2 |  | START: | 30522849 |  | END: | 30533417 |  |  | Cal~Flo | 8.69 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.726 |  |  | RAW PLANT 3 |  | START: | 7045417 |  | END: | 7057143 |  |  | Zinc | 1068
[76 empty] | TOTAL MGD: |  | 1.088 |  |  | DECANT |  | START: | 1820099 |  | END: | 1821187 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 1.0234 |  |  | BLOW DOWN |  | START: | 9069.9766 |  | END: | 9071 |  |  | NH3 | 9 |  | BI-SUL | 650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23804585
43402792
10060108
33405155
30571299
30533417
7057143
1821187
9071
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 25
DATE: | 2018-11-25 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-25 | [23 empty] | DATE: | 2018-11-25
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-25 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43429.2054 | 1,2,3,6 | 46 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 11.723 | 1,3 | 14.9702 | 26.6933 | 2.4725 | 43429.2054 | 101.936 | 7624.4372 | 0 | 808.8106 | 0 | 0 | 0 | 17.9978 | 18.8158 | 16.9583 | 1.6583 | 1.6583 | 1.391 | 0.50649 | 0.50649 | 0.45318 | 0.45318 | 0.5851 | 0.43882 | 1.8262 | 2.5 | 0.049137 | 0.049137 | 0.049931 | 1.1269 | 0.5 | 0.099158 | 3.9242 | 0.62612 | 5.6497 | 1.1289 | 0.59 | 0.1032 | 3.8069 | 0.69241 | 6.1222 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.434 | 6 | 0.93 | 13.3 | 10.2 | 0.72142 |  | 6.12 | 0.503 | 7 | 0.99 | 14.9 | 10.3 | 0.72731 | 6.06 | 0.423 | 7 | 0.74 | 15.3 | 11.6 | 0.54963 | [13 empty] | 7.91 | 0.053 | 1 | 3.9 | 13.4 |  |  |  | 8.1 | 0.054 | 1 | 3.7 | 16.2 |  |  |  | 3.9 | 4.1 | 3.7 | [18 empty] | 13800 | [6 empty] | 660 | 690 | 680 | 380 | 380 | 350 | 950 | 950 | 850 | 850 | 1200 | 900 | 960 |  | 950 | 950 | 1060 | 100 | 118 | 14 | 1500 | 280 | 395 | 55 | 0.5 | 8 | 780 | 170 | 235 |  | 1:00 | 0.93 | 10.2 | 24.9412 | 23.1953 | 6.14 | 13.3 | 15 | 1.5464 | 10 | 6.5 | 0.60142 | 1:00 | 0.99 | 10.3 | 24.699 | 24.452 | 6.12 | 14.9 | 15 | 1.6301 | 10 | 6.5 | 0.60731 | 1:00 | 0.74 | 11.6 | 23.2759 | 17.2241 | 6.06 | 15.3 | 10 | 1.7224 | 15 | 6.5 | 0.42963
2:00 | [72 empty] | 43429.369 | 1,2,3,6 | 46 | 10.4 | 10.5 | 11.8 | 32.7 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 15.6931 | 1,3 | 15.2366 | 30.9298 | 2.4264 | 43429.369 | 94.5494 | 6517.664 | 0 | 808.8106 | 0 | 0 | 0 | 17.9978 | 18.8158 | 16.9583 | 1.6583 | 1.6147 | 1.391 | 0.50649 | 0.50649 | 0.42652 | 0.50649 | 0.51196 | 0.51196 | 1.712 | 3 | 0.049137 | 0.049137 | 0.04946 | 1.1269 | 0.50105 | 0.099158 | 4.1166 | 0.64848 | 5.5067 | 1.0673 | 0.6 | 0.1032 | 3.7369 | 0.61095 | 5.8617 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.57 | 13 | 15 | 10.8 | 114 | 183 | 14.8 | 0.509 |  | 6.01 | 8 | 0.082 | 5.96 | 9 |  | 5.91 | 8 | [8 empty] | 0.062 | [14 empty] | 0.02 | 1 | 0.59 |  | 0.06 | 0.021 | 1 | 0.89 |  | 0.033 | 2 | 0.56 | [38 empty] | 12800 | [6 empty] | 660 | 690 | 680 | 380 | 370 | 350 | 950 | 950 | 800 | 950 | 1050 | 1050 | 900 |  | 950 | 950 | 1050 | 100 | 118 | 14 | 1510 | 290 | 385 | 52 | 0.5 | 8 | 780 | 150 | 225 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43429.5839 | 1,2,3,6 | 46 | 9.6 | 9.6 | 10.6 | 29.8 | 9.1 | 9.1 | 10.1 | 28.3 | 8,3 | 11.8699 | 1,3 | 12.2213 | 24.0912 | 2.4264 | 43429.5839 | 95.174 | 6517.664 | 0 | 808.8106 | 0 | 0 | 0 | 18.3883 | 19.209 | 17.1215 | 1.6876 | 1.5408 | 1.4103 | 0.5051 | 0.5051 | 0.44568 | 0.5051 | 0.51127 | 0.51127 | 1.5789 | 3 | 0.049279 | 0.049279 | 0.052235 | 1.0989 | 0.49975 | 0.1032 | 4.074 | 0.68927 | 5.5952 | 1.0925 | 0.6 | 0.10014 | 3.7119 | 0.63232 | 6.0956 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.76 | 0.052 | 1 | 3.8 | 13.3 |  |  |  | 7.94 | 0.049 | 1 | 3.6 | 16.2 |  |  |  | 3.9 | 4 | 4.4 | [18 empty] | 11600 | [6 empty] | 605 | 632 | 622 | 345 | 315 | 320 | 850 | 850 | 750 | 850 | 950 | 950 | 830 |  | 850 | 850 | 1000 | 87 | 105 | 13 | 1400 | 275 | 349 | 48 | 0.5 | 7 | 720 | 140 | 211 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43429.8553 | 1,2,3,6 | 54 | 9.6 | 9.6 | 10.6 | 29.8 | 9.1 | 9.1 | 10.1 | 28.3 | 8,3 | 13.0162 | 1,3 | 15.6917 | 28.7078 | 2.4264 | 43429.8553 | 95.7483 | 6517.664 | 0 | 808.8106 | 0 | 0 | 0 | 18.3883 | 19.209 | 17.1215 | 1.6631 | 1.5653 | 1.4103 | 0.54076 | 0.52293 | 0.5051 | 0.49916 | 0.58984 | 0.44938 | 1.5789 | 3 | 0.052178 | 0.049859 | 0.050146 | 1.0863 | 0.49975 | 0.1032 | 3.8786 | 0.62661 | 5.5952 | 1.047 | 0.59 | 0.10014 | 3.7116 | 0.58715 | 5.7779 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.31 | 12 | 14 | 10.8 | 128 | 180 | 14.1 | 0.554 |  | 6.01 | 8 | 0.081 | 5.94 | 8 |  | 5.88 | 8 | [8 empty] | 0.06 | [14 empty] | 0.017 | 1 | 0.5 |  | 0.063 | 0.017 | 2 | 0.66 |  | 0.033 | 1 | 0.49 | [38 empty] | 11670 | [6 empty] | 605 | 632 | 622 | 340 | 320 | 320 | 910 | 880 | 850 | 840 | 1096 | 835 | 830 |  | 900 | 860 | 960 | 86 | 105 | 13 | 1340 | 250 | 349 | 46 | 0.5 | 7 | 700 | 130 | 200 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.049 | [9 empty] | 6.08 | 0.574 | 8 | 0.73 | 13.6 | 10.7 | 0.7509 |  | 6.08 | 0.567 | 8 | 0.73 | 15 | 10.7 | 0.5406 | 6.08 | 0.603 | 10 | 0.5 | 15 | 11.7 | 0.55333 |  |  |  | 0.007 | [9 empty] | 7.47 | 0.059 | 1 | 4 | 13.3 | 20 | 36 | 0.009 | 7.98 | 0.061 | 2 | 4 | 16.2 | 20 | 36 | 0.007 | 3.8 | 4 | 4.3 | [55 empty] | 9:00 | 0.73 | 10.7 | 23.7757 | 17.3563 | 6.08 | 13.6 | 15 | 1.1571 | 10 | 6.5 | 0.6309 | 9:00 | 0.73 | 10.7 | 23.7757 | 17.3563 | 6.08 | 15 | 10 | 1.7356 | 15 | 6.5 | 0.4206 | 9:00 | 0.5 | 11.7 | 23.0769 | 11.5385 | 6.08 | 15 | 10 | 1.1538 | 15 | 6.5 | 0.43333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.22 | 12 | 12 | 10.5 | 131 | 180 | 14.3 | 0.546 |  | 6 | 8 | 0.078 | 6 | 8 |  | 5.93 | 8 | [8 empty] | 0.06 | [14 empty] | 0.02 | 1 | 0.53 |  | 0.06 | 0.022 | 1 | 0.6 |  | 0.033 | 1 | 0.46 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.425 | 7 | 0.79 | 13.2 | 10.8 | 0.75679 |  | 6.06 | 0.474 | 8 | 0.7 | 15 | 10.7 | 0.5406 | 6.03 | 0.53 | 6 | 0.59 | 15.4 | 11.7 | 0.55333 | [13 empty] | 7.79 | 0.069 | 1 | 4.3 | 13.3 |  |  |  | 8.01 | 0.067 | 1 | 4.3 | 16.3 |  |  |  | 4.1 | 4 | 3.5 | [55 empty] | 13:00 | 0.79 | 10.8 | 23.5556 | 18.6089 | 6.03 | 13.2 | 15 | 1.2406 | 10 | 6.5 | 0.63679 | 13:00 | 0.7 | 10.7 | 23.7757 | 16.643 | 6.06 | 15 | 10 | 1.6643 | 15 | 6.5 | 0.4206 | 13:00 | 0.59 | 11.7 | 23.0769 | 13.6154 | 6.03 | 15.4 | 10 | 1.3615 | 15 | 6.5 | 0.43333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.25 | 12 | 12 | 10.6 | 126 | 180 | 14.5 | 0.56 |  | 6.1 | 8 | 0.082 | 6.01 | 8 |  | 6.08 | 8 | [8 empty] | 0.063 | [14 empty] | 0.02 | 1 | 0.43 |  | 0.064 | 0.02 | 1 | 0.56 |  | 0.041 | 1 | 0.41 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.8 | 0.066 | 1 | 4.2 | 13.4 |  |  |  | 7.85 | 0.069 | 1 | 4.1 | 16 |  |  |  | 4.1 | 4 | 3.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.26 | 11 | 14 | 9.71 | 125 | 177 | 14.6 | 0.543 |  | 6.1 | 8 | 0.072 | 6.06 | 8 |  | 5.97 | 8 | [8 empty] | 0.065 | [14 empty] | 0.022 | 1 | 0.52 |  | 0.061 | 0.018 | 2 | 0.52 |  | 0.037 | 2 | 0.55 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.04 | [9 empty] | 6.08 | 0.576 | 7 | 0.89 | 12.9 | 9.6 | 0.68604 |  | 6.12 | 0.514 | 7 | 0.75 | 14.4 | 9.6 | 0.68604 | 6.1 | 0.608 | 5 | 0.68 | 14.4 | 10.6 | 0.70889 |  |  |  | 0.007 |  |  |  |  | 0.02 |  |  |  | 0.009 | 7.46 | 0.059 | 1 | 4 | 13.2 | 20 | 34 | 0.013 | 7.86 | 0.063 | 1 | 4.3 | 15.6 | 20 | 36 | 0.015 | 4.2 | 4 | 3.5 | [55 empty] | 21:00 | 0.89 | 9.6 | 26.5 | 23.585 | 6.08 | 12.9 | 15 | 1.5723 | 10 | 6.5 | 0.56604 | 21:00 | 0.75 | 9.6 | 26.5 | 19.875 | 6.12 | 14.4 | 15 | 1.325 | 10 | 6.5 | 0.56604 | 21:00 | 0.68 | 10.6 | 25.4717 | 17.3208 | 6.1 | 14.4 | 15 | 1.1547 | 10 | 6.5 | 0.58889
22:00 | [72 empty] | DOSE |  | TOTAL | 40.3 | 40.4 | 44.7 | 125.4 | 38.6 | 38.6 | 42.6 | 119.8 | 0 | 52.3022 | 0 | 58.1198 | 110.4221 | 9.7517 | TOTAL | 387.4078 | 27177.4292 | 0 | 3235.2423 | 0 | 0 | 0 | 72.7722 | 76.0496 | 68.1596 | 6.6673 | 6.3791 | 5.6026 | 2.0588 | 2.041 | 1.8305 | 1.9639 | 2.1982 | 1.9114 | 6.6959 | 11.5 | 0.19973 | 0.19741 | 0.20177 | 4.4389 | 2.0005 | 0.40472 | 15.9935 | 2.5905 | 22.3467 | 4.3357 | 2.38 | 0.40669 | 14.9674 | 2.5228 | 23.8574 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.18 | 10 | 14 | 9.8 | 127 | 178 | 14.6 | 0.502 |  | 5.96 | 7 | 0.069 | 5.95 | 7 |  | 5.88 | 7 | [8 empty] | 0.065 | [14 empty] | 0.024 | 1 | 0.46 |  | 0.068 | 0.016 | 1 | 0.52 |  | 0.037 | 1 | 0.57 | [22 empty] | AVERAGE | 10.075 | 10.1 | 11.175 | 31.35 | 9.65 | 9.65 | 10.65 | 29.95 |  | 13.0756 |  | 14.53 | 27.6055 | 2.4379 | AVERAGE | 96.8519 | 6794.3573 |  | 808.8106 | 0 | 0 | 0 | 18.193 | 19.0124 | 17.0399 | 1.6668 | 1.5948 | 1.4007 | 0.51471 | 0.51025 | 0.45762 | 0.49098 | 0.54954 | 0.47786 | 1.674 | 2.875 | 0.049933 | 0.049353 | 0.050443 | 1.1097 | 0.50014 | 0.10118 | 3.9984 | 0.64762 | 5.5867 | 1.0839 | 0.595 | 0.10167 | 3.7418 | 0.63071 | 5.9643 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.79 | 70 | 81 | 62.21 | 751 | 1078 | 86.9 | 3.214 | 0.089 | 36.18 | 47 | 0.464 | 35.92 | 48 | 0 | 35.65 | 47 | 0 | 24.33 | 2.009 | 28 | 3.34 | 53 | 41.3 | 2.9151 | 0.375 | 24.38 | 2.058 | 30 | 3.17 | 59.3 | 41.3 | 2.4945 | 24.27 | 2.164 | 28 | 2.51 | 60.1 | 45.6 | 2.3652 | 0.123 | 6 | 3.03 | 0.014 | 0.376 | 0.114 | 8 | 3.75 | 0.02 | 0.214 | 8 | 3.04 | 0.009 | 46.19 | 0.358 | 6 | 24.2 | 79.9 | 40 | 70 | 0.022 | 47.74 | 0.363 | 7 | 24 | 96.5 | 40 | 72 | 0.022 | 24 | 24.1 | 22.9 |  |  | MINIMUM | 9.6 | 9.6 | 10.6 | 29.8 | 9.1 | 9.1 | 10.1 | 28.3 |  | 11.723 |  | 12.2213 | 24.0912 | 2.4264 | MINIMUM | 94.5494 | 6517.664 |  | 808.8106 |  |  |  | 17.9978 | 18.8158 | 16.9583 | 1.6583 | 1.5408 | 1.391 | 0.5051 | 0.5051 | 0.42652 | 0.45318 | 0.51127 | 0.43882 | 1.5789 | 2.5 | 0.049137 | 0.049137 | 0.04946 | 1.0863 | 0.49975 | 0.099158 | 3.8786 | 0.62612 | 5.5067 | 1.047 | 0.59 | 0.10014 | 3.7116 | 0.58715 | 5.7779 |  | MIN | 0.73 | 10.7 | 23.7757 | 17.3563 | 6.08 | 13.6 | 15 | 1.1571 |  |  |  | MIN | 0.75 | 9.6 | 26.5 | 19.875 | 6.12 | 14.4 | 15 | 1.325 |  |  |  | MIN | 0.5 | 11.7 | 23.0769 | 11.5385 | 6.08 | 15 | 10 | 1.1538 |  |  |  | 1.1538
AVERAGE | 6.2983 | 11.6667 | 13.5 | 10.3683 | 125.1667 | 179.6667 | 14.4833 | 0.53567 | 0.0445 | 6.03 | 7.8333 | 0.077333 | 5.9867 | 8 |  | 5.9417 | 7.8333 |  | 6.0825 | 0.50225 | 7 | 0.835 | 13.25 | 10.325 | 0.72879 | 0.0625 | 6.095 | 0.5145 | 7.5 | 0.7925 | 14.825 | 10.325 | 0.62364 | 6.0675 | 0.541 | 7 | 0.6275 | 15.025 | 11.4 | 0.5913 | 0.0205 | 1 | 0.505 | 0.007 | 0.062667 | 0.019 | 1.3333 | 0.625 | 0.02 | 0.035667 | 1.3333 | 0.50667 |  | 7.6983 | 0.059667 | 1 | 4.0333 | 13.3167 | 20 | 35 | 0.011 | 7.9567 | 0.0605 | 1.1667 | 4 | 16.0833 | 20 | 36 | 0.011 | 4 | 4.0167 | 3.8167 |  |  | MAXIMUM | 10.7 | 10.7 | 11.8 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 |  | 15.6931 |  | 15.6917 | 30.9298 | 2.4725 | MAXIMUM | 101.936 | 7624.4372 |  | 808.8106 |  |  |  | 18.3883 | 19.209 | 17.1215 | 1.6876 | 1.6583 | 1.4103 | 0.54076 | 0.52293 | 0.5051 | 0.50649 | 0.58984 | 0.51196 | 1.8262 | 3 | 0.052178 | 0.049859 | 0.052235 | 1.1269 | 0.50105 | 0.1032 | 4.1166 | 0.68927 | 5.6497 | 1.1289 | 0.6 | 0.1032 | 3.8069 | 0.69241 | 6.1222
MINIMUM | 6.18 | 10 | 12 | 9.71 | 114 | 177 | 14.1 | 0.502 | 0.04 | 5.96 | 7 | 0.069 | 5.94 | 7 |  | 5.88 | 7 |  | 6.03 | 0.425 | 6 | 0.73 | 12.9 | 9.6 | 0.68604 | 0.06 | 6.06 | 0.474 | 7 | 0.7 | 14.4 | 9.6 | 0.5406 | 6.03 | 0.423 | 5 | 0.5 | 14.4 | 10.6 | 0.54963 | 0.017 | 1 | 0.43 | 0.007 | 0.06 | 0.016 | 1 | 0.52 | 0.02 | 0.033 | 1 | 0.41 |  | 7.46 | 0.052 | 1 | 3.8 | 13.2 | 20 | 34 | 0.009 | 7.85 | 0.049 | 1 | 3.6 | 15.6 | 20 | 36 | 0.007 | 3.8 | 4 | 3.5 | [15 empty] | MIL/MIN |  | TOTAL | 49870 | 0 | 0 | 0 | 0 | 0 | 0 | 2530 | 2644 | 2604 | 1445 | 1385 | 1340 | 3660 | 3630 | 3250 | 3490 | 4296 | 3735 | 3520 | 0 | 3650 | 3610 | 4070 | 373 | 446 | 54 | 5750 | 1095 | 1478 | 201 | 2 | 30 | 2980 | 590 | 871
MAXIMUM | 6.57 | 13 | 15 | 10.8 | 131 | 183 | 14.8 | 0.56 | 0.049 | 6.1 | 8 | 0.082 | 6.06 | 9 |  | 6.08 | 8 |  | 6.14 | 0.576 | 8 | 0.93 | 13.6 | 10.8 | 0.75679 | 0.065 | 6.12 | 0.567 | 8 | 0.99 | 15 | 10.7 | 0.72731 | 6.1 | 0.608 | 10 | 0.74 | 15.4 | 11.7 | 0.70889 | 0.024 | 1 | 0.59 | 0.007 | 0.068 | 0.022 | 2 | 0.89 | 0.02 | 0.041 | 2 | 0.57 |  | 7.91 | 0.069 | 1 | 4.3 | 13.4 | 20 | 36 | 0.013 | 8.1 | 0.069 | 2 | 4.3 | 16.3 | 20 | 36 | 0.015 | 4.2 | 4.1 | 4.4 | [17 empty] | AVERAGE | 12467.5 | [6 empty] | 632.5 | 661 | 651 | 361.25 | 346.25 | 335 | 915 | 907.5 | 812.5 | 872.5 | 1074 | 933.75 | 880 |  | 912.5 | 902.5 | 1017.5 | 93.25 | 111.5 | 13.5 | 1437.5 | 273.75 | 369.5 | 50.25 | 0.5 | 7.5 | 745 | 147.5 | 217.75
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9861 |  | TOTAL AVG COAG ALK: |  |  |  | 7.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.608 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.5 | [5 empty] | 6.0817 |  |  |  |  | 0.041 |  |  |  |  | 0.5 | [6 empty] | 0.041 | [16 empty] | Pump Station MIN |  | 3.5 | [17 empty] | MINIMUM | 11600 | [6 empty] | 605 | 632 | 622 | 340 | 315 | 320 | 850 | 850 | 750 | 840 | 950 | 835 | 830 |  | 850 | 850 | 960 | 86 | 105 | 13 | 1340 | 250 | 349 | 46 | 0.5 | 7 | 700 | 130 | 200
[90 empty] | MAXIMUM | 13800 | [6 empty] | 660 | 690 | 680 | 380 | 380 | 350 | 950 | 950 | 850 | 950 | 1200 | 1050 | 960 |  | 950 | 950 | 1060 | 100 | 118 | 14 | 1510 | 290 | 395 | 55 | 0.5 | 8 | 780 | 170 | 235
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.866 |  | TOTAL MGD: |  | 6.539 |  |  | FINISHED SOUTH 1 |  | START: | 23804585 |  | END: | 23811124 |  |  | Alum | 9305 | 9794 | 9794 | 8297 | 8297 | 0.8 | [44 empty] | 0.5 | 11.7 | 23.0769 | 11.5385 | 6.08 | 15 | 10 | 1.1538
[73 empty] | FINISHED 2 | 15.75 |  | TOTAL MGD: |  | 6.327 |  |  | FINISHED SOUTH 2 |  | START: | 43402792 |  | END: | 43409119 |  |  | Caustic | 5316 | 7304 | 7304
[73 empty] | TOTAL RAW | 32.289 |  | TOTAL MGD: |  | 4.605 |  |  | FINISHED CONWAY |  | START: | 10060108 |  | END: | 10064713 |  |  | Hypochlorite | 15 |  | 41
[76 empty] | TOTAL MGD: |  | 11.145 |  |  | FINISHED PERRY |  | START: | 33405155 |  | END: | 33416300 |  |  | Phosphate | 1697
[76 empty] | TOTAL MGD: |  | 10.238 |  |  | RAW PLANT 1 |  | START: | 30571299 |  | END: | 30581537 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.4 |  |  | RAW PLANT 2 |  | START: | 30533417 |  | END: | 30543817 |  |  | Cal~Flo | 14.57 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.651 |  |  | RAW PLANT 3 |  | START: | 7057143 |  | END: | 7068794 |  |  | Zinc | 1154
[76 empty] | TOTAL MGD: |  | 1.182 |  |  | DECANT |  | START: | 1821187 |  | END: | 1822369 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 1.887 |  |  | BLOW DOWN |  | START: | 9071 |  | END: | 9072.887 |  |  | NH3 | 8.78 |  | BI-SUL | 650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 0
23811124
43409119
10064713
33416300
30581537
30543817
7068794
1822369
9072.887
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2BCOperator:
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. BuildingBCOperator:
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1BCOperator:
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 26
DATE: | 2018-11-26 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-26 | [23 empty] | DATE: | 2018-11-26
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-26 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43430.0252 | 1,2,3,6 | 54 | 9.6 | 9.6 | 10.6 | 29.8 | 9.1 | 9.1 | 10.1 | 28.3 | 8,3 | 11.8829 | 1,3 | 15.6917 | 27.5746 | 2.4903 | 43430.0252 | 95.7483 | 6517.664 | 0 | 808.8106 | 0 | 0 | 0 | 18.3883 | 19.209 | 17.2592 | 1.6631 | 1.4919 | 1.3442 | 0.54076 | 0.52293 | 0.5051 | 0.49916 | 0.58984 | 0.44938 | 1.5789 | 3 | 0.052178 | 0.049859 | 0.050146 | 1.0863 | 0.49975 | 0.1032 | 3.8786 | 0.62661 | 5.2905 | 1.047 | 0 | 0.10014 | 3.7116 | 0.58715 | 5.0556 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.487 | 8 | 0.59 | 12.9 | 9.5 | 0.68014 |  | 6.06 | 0.52 | 7 | 0.74 | 14.3 | 9.5 | 0.68014 | 6.01 | 0.609 | 7 | 0.79 | 15.1 | 10.8 | 0.52 | [13 empty] | 7.7 | 0.051 | 1 | 4 | 13.4 |  |  |  | 7.64 | 0.059 | 1 | 4.1 | 15.6 |  |  |  | 4.1 | 4.1 | 3.7 | [18 empty] | 11670 | [6 empty] | 605 | 632 | 627 | 340 | 305 | 305 | 910 | 880 | 850 | 840 | 1096 | 835 | 830 |  | 900 | 860 | 960 | 86 | 105 | 13 | 1340 | 250 | 330 | 46 | 59 | 7 | 700 | 130 | 175 |  | 1:00 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.01 | 12.9 | 15 | 1.0533 | 10 | 6.5 | 0.56014 | 1:00 | 0.74 | 9.5 | 26.7789 | 19.8164 | 6.06 | 14.3 | 15 | 1.3211 | 10 | 6.5 | 0.56014 | 1:00 | 0.79 | 10.8 | 25 | 19.75 | 6.01 | 15.1 | 10 | 1.975 | 15 | 6.5 | 0.4
2:00 | [72 empty] | 43430.4116 | 1,3,6 | 54 | 9.6 | 9.6 | 10.6 | 29.8 | 9.1 | 9.1 | 10.1 | 28.3 | 8,3 | 12.6158 | 1,3 | 12.1176 | 24.7334 | 2.3242 | 43430.4116 | 105.8401 | 7132.538 | 0 | 808.8106 | 0 | 0 | 0 | 21.5797 | 22.7955 | 20.232 | 1.4674 | 1.4674 | 1.3222 | 0.57463 | 0.55858 | 0.52293 | 0.52293 | 0.53818 | 0.592 | 1.5789 | 5 | 0.049279 | 0.049279 | 0.051191 | 1.0989 | 0.49975 | 0.1032 | 3.984 | 0.40103 | 4.8096 | 1.0925 | 0.49744 | 0.10014 | 3.7316 | 0.60974 | 5.0845 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.24 | 11 | 13 | 9.87 | 121 | 178 | 14.5 | 0.549 |  | 5.87 | 7 | 0.073 | 5.82 | 7 |  | 5.88 | 7 | [8 empty] | 0.067 | [14 empty] | 0.018 | 1 | 0.42 |  | 0.067 | 0.021 | 1 | 0.53 |  | 0.037 | 1 | 0.57 | [38 empty] | 12900 | [6 empty] | 710 | 750 | 735 | 300 | 300 | 300 | 967 | 940 | 880 | 880 | 1000 | 1100 | 830 |  | 850 | 850 | 980 | 87 | 105 | 13 | 1400 | 160 | 300 | 48 | 58 | 7 | 700 | 135 | 176 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43430.585 | 1,2,3,6 | 54 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | 8,3 | 12.6158 | 1,3 | 12.1176 | 24.7334 | 2.3242 | 43430.585 | 105.8501 | 7747.412 | 0 | 789.7797 | 0 | 0 | 0 | 20.0118 | 21.1955 | 18.9658 | 1.5425 | 1.5425 | 1.3634 | 0.55971 | 0.53818 | 0.50589 | 0.50589 | 0.52621 | 0.57785 | 1.712 | 5 | 0.049624 | 0.049624 | 0.049906 | 1.1039 | 0.50173 | 0.10014 | 3.8624 | 0.63232 | 5.0845 | 1.0976 | 0.49945 | 0.10413 | 3.6523 | 0.61645 | 4.9419 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.67 | 0.054 | 1 | 4.1 | 13.5 |  |  |  | 7.53 | 0.06 | 1 | 4.2 | 15.6 |  |  |  | 4 | 4 | 4.5 | [18 empty] | 14200 | [6 empty] | 727 | 770 | 754 | 350 | 350 | 340 | 1040 | 1000 | 940 | 940 | 1070 | 1175 | 900 |  | 950 | 950 | 1050 | 97 | 117 | 14 | 1500 | 280 | 352 | 53 | 64 | 8 | 750 | 150 | 188 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43430.6561 | 1,2,3,6 | 54 | 10.6 | 10.6 | 11.6 | 32.8 | 10.1 | 10.1 | 11.1 | 31.3 | 8,3 | 6.8482 | 1,3 | 13.7736 | 20.6218 | 2.3242 | 43430.6561 | 109.5772 | 7870.3868 | 0 | 808.8106 | 0 | 0 | 0 | 21.3882 | 22.4892 | 19.8713 | 1.5425 | 1.5425 | 1.3634 | 0.58069 | 0.55971 | 0.52526 | 0.52526 | 0.54588 | 0.59998 | 1.7786 | 5 | 0.049624 | 0.049624 | 0.049906 | 1.1039 | 0.50173 | 0.10014 | 3.8624 | 0.63232 | 5.3012 | 1.0976 | 0.49945 | 0.10413 | 3.6523 | 0.61645 | 5.0996 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.22 | 11 | 12 | 9.87 | 123 | 178 | 14.5 | 0.568 |  | 5.94 | 8 | 0.088 | 5.94 | 8 |  | 5.93 | 8 | [8 empty] | 0.073 | [14 empty] | 0.02 | 1 | 0.5 |  | 0.076 | 0.022 | 1 | 0.49 |  | 0.037 | 1 | 0.43 | [38 empty] | 14700 | [6 empty] | 777 | 817 | 790 | 350 | 350 | 340 | 1079 | 1040 | 976 | 976 | 1110 | 1220 | 935 |  | 950 | 950 | 1050 | 97 | 117 | 14 | 1500 | 280 | 367 | 53 | 64 | 8 | 750 | 150 | 194 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43430.8623 | 1,2,3,6 | 50 | 10.9 | 10.9 | 11.9 | 33.7 | 10.4 | 10.4 | 11.4 | 32.2 | 8,3 | 13.212 | 1,3 | 16.9315 | 30.1435 | 2.3242 | 43430.8623 | 110.8515 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 20.7995 | 21.8702 | 18.88 | 1.4552 | 1.4552 | 1.3276 | 0.56524 | 0.55477 | 0.52337 | 0.53383 | 0.65676 | 0.59012 | 1.7786 | 3.5 | 0.050475 | 0.049714 | 0.049981 | 1.0831 | 0.49975 | 0.097251 | 3.9724 | 0.65794 | 5.1202 | 1.1293 | 0.5167 | 0.10139 | 3.8013 | 0.60023 | 5.4005 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6 | 0.54 | 7 | 0.72 | 14 | 9.6 | 0.61057 |  | 6.03 | 0.551 | 7 | 0.66 | 15.3 | 9.6 | 0.49736 | 6 | 0.636 | 6 | 0.6 | 15.5 | 10.6 | 0.43407 |  |  |  | 0.012 | [9 empty] | 7.61 | 0.064 | 1 | 4.1 | 13.6 | 21 | 41 | 0.011 | 7.49 | 0.055 | 1 | 4.1 | 15.6 | 22 | 36 | 0.012 | 4.1 | 4 | 3.8 | [18 empty] | 15279 | [6 empty] | 777 | 817 | 770 | 340 | 340 | 340 | 1080 | 1060 | 1000 | 1020 | 1370 | 1231 | 935 |  | 995 | 980 | 1080 | 98 | 120 | 14 | 1540 | 300 | 365 | 56 | 68 | 8 | 870 | 150 | 211 |  | 9:00 | 0.72 | 9.6 | 26.5 | 19.08 | 6 | 14 | 13 | 1.4677 | 10 | 6 | 0.49057 | 9:00 | 0.66 | 9.6 | 26.5 | 17.49 | 6.03 | 15.3 | 10 | 1.749 | 15 | 6.5 | 0.37736 | 9:00 | 0.6 | 10.6 | 25.4717 | 15.283 | 6 | 15.5 | 8 | 1.9104 | 15 | 6 | 0.31407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.22 | 11 | 12 | 9.84 | 128 | 179 | 14.6 | 0.555 |  | 6.1 | 8 | 0.084 | 6.16 | 8 |  | 6.1 | 8 | [8 empty] | 0.061 | [14 empty] | 0.02 | 1 | 0.49 |  | 0.063 | 0.022 | 1 | 0.5 |  | 0.036 | 1 | 0.43 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.09 | 0.408 | 6 | 0.7 | 13.5 | 10.2 | 0.72142 |  | 6.13 | 0.484 | 6 | 0.69 | 14.9 | 10.3 | 0.72731 | 6.14 | 0.593 | 5 | 0.68 | 14.4 | 11.6 | 0.76444 | [13 empty] | 7.73 | 0.063 | 1 | 4.2 | 13.8 |  |  |  | 7.67 | 0.061 | 1 | 4.1 | 16.2 |  |  |  | 4 | 4 | 3.3 | [55 empty] | 13:00 | 0.7 | 10.2 | 24.9412 | 17.4588 | 6.09 | 13.5 | 15 | 1.1639 | 10 | 6.5 | 0.60142 | 13:00 | 0.69 | 10.3 | 24.699 | 17.0423 | 6.13 | 14.9 | 15 | 1.1362 | 10 | 6.5 | 0.60731 | 13:00 | 0.68 | 11.6 | 23.2759 | 15.8276 | 6.14 | 14.4 | 15 | 1.0552 | 10 | 6.5 | 0.64444
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.23 | 11 | 12 | 9.83 | 129 | 182 | 14.7 | 0.563 |  | 6.09 | 8 | 0.079 | 6.12 | 8 |  | 6.13 | 8 | [8 empty] | 0.06 | [14 empty] | 0.023 | 1 | 0.42 |  | 0.063 | 0.012 | 1 | 0.41 |  | 0.036 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.39 | 0.061 | 1 | 4.1 | 13.8 |  |  |  | 7.32 | 0.066 | 1 | 3.9 | 15.9 |  |  |  | 4 | 4 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.16 | 11 | 12 | 9.98 | 132 | 180 | 14.7 | 0.564 |  | 6.05 | 7 | 0.074 | 6.08 | 7 |  | 5.9 | 7 | [8 empty] | 0.071 | [14 empty] | 0.022 | 1 | 0.56 |  | 0.072 | 0.017 | 1 | 0.65 |  | 0.037 | 1 | 0.36 | [33 empty] | 0.5455 | [41 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [85 empty] | 0.4899 | [41 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.038 | [9 empty] | 6.01 | 0.518 | 7 | 0.83 | 13.1 | 10.9 | 0.76269 |  | 6.06 | 0.44 | 5 | 0.7 | 14.5 | 10.9 | 0.76269 | 6.05 | 0.568 | 4 | 0.71 | 14.4 | 11.9 | 0.78111 |  |  |  | 0.013 | [9 empty] | 7.98 | 0.072 | 1 | 4 | 13.7 | 20 | 38 | 0.016 | 7.54 | 0.074 | 1 | 3.9 | 15.8 | 20 | 36 | 0.012 | 4 | 4.1 | 3.5 | [13 empty] | 0.4919 | [41 empty] | 21:00 | 0.83 | 10.9 | 23.3394 | 19.3717 | 6.01 | 13.1 | 15 | 1.2914 | 10 | 6.5 | 0.64269 | 21:00 | 0.7 | 10.9 | 23.3394 | 16.3376 | 6.06 | 14.5 | 15 | 1.0892 | 10 | 6.5 | 0.64269 | 21:00 | 0.71 | 11.9 | 22.6891 | 16.1092 | 6.05 | 14.4 | 15 | 1.0739 | 10 | 6.5 | 0.66111
22:00 | [72 empty] | DOSE |  | TOTAL | 51.3 | 51.3 | 56.3 | 158.9 | 48.8 | 48.8 | 53.8 | 151.4 | 0 | 57.1748 | 0.4683 | 70.632 | 127.8068 | 11.787 | TOTAL | 527.8672 | 37507.312 | 0 | 4025.022 | 0 | 0 | 0 | 102.1675 | 107.5594 | 95.2084 | 7.6708 | 7.4996 | 6.7208 | 0.1568 | 2.7342 | 2.5825 | 2.5871 | 2.8569 | 2.8093 | 8.4269 | 21.5 | 0.25118 | 0.2481 | 0.25113 | 5.4761 | 2.5027 | 0.50394 | 19.56 | 2.9502 | 25.606 | 5.4641 | 2.013 | 0.50994 | 18.549 | 3.03 | 25.5822 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.13 | 10 | 13 | 9.97 | 123 | 179 | 14.5 | 0.545 |  | 6.03 | 8 | 0.076 | 6.06 | 8 |  | 5.85 | 7 | [8 empty] | 0.064 | [14 empty] | 0.02 | 1 | 0.5 |  | 0.066 | 0.013 | 1 | 0.58 |  | 0.035 | 2 | 0.42 | [22 empty] | AVERAGE | 10.26 | 7.6 | 13.6 | 2 | 0.064 | 21 | 41 | 3.9 |  | 11.435 | 0.5274 | 14.1264 | 25.5614 | 2.3574 | AVERAGE | 105.5734 | 7501.4624 |  | 805.0044 | 7.49 | 15.9 | 2 | 0.055 | 22 | 36 | 4 | 1.4999 | 1.3442 | 0.2249 | 0.54683 | 0.51651 | 0.51741 | 0.57137 | 0.56186 | 1.6854 | 4.3 | 0.050236 | 0.04962 | 0.050226 | 1.0952 | 0.50054 | 0.10079 | 3.912 | 0.59005 | 5.1212 | 1.0928 | 0.40261 | 0.10199 | 3.7098 | 0.606 | 5.1164 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.2 | 65 | 74 | 59.36 | 756 | 1076 | 87.5 | 3.344 | 0.075 | 36.08 | 46 | 0.474 | 36.18 | 46 | 0 | 35.79 | 45 | 0 | 24.11 | 1.953 | 28 | 2.84 | 53.5 | 40.2 | 2.7748 | 0.396 | 24.28 | 1.995 | 25 | 2.79 | 59 | 40.3 | 2.6675 | 24.2 | 2.406 | 22 | 2.78 | 59.4 | 44.9 | 2.4996 | 0.123 | 6 | 2.89 | 0.025 | 0.407 | 0.107 | 6 | 3.16 | 0 | 0.218 | 7 | 2.61 | 0 | 46.08 | 0.365 | 6 | 24.5 | 81.8 | 41 | 79 | 0.027 | 45.19 | 0.375 | 6 | 24.3 | 94.7 | 42 | 72 | 0.024 | 24.2 | 24.2 | 22.1 |  |  | MINIMUM | 9.6 | 9.6 | 10.6 | 29.8 | 9.1 | 9.1 | 10.1 | 28.3 |  | 6.8482 | 0.4899 | 12.1176 | 20.6218 | 2.3242 | MINIMUM | 95.7483 | 6517.664 |  | 789.7797 |  |  |  | 18.3883 | 19.209 | 17.2592 | 1.4552 | 1.4552 | 1.3222 | 0.54076 | 0.52293 | 0.5051 | 0.49916 | 0.52621 | 0.44938 | 1.5789 | 3 | 0.049279 | 0.049279 | 0.049906 | 1.0831 | 0.49975 | 0.097251 | 3.8624 | 0.40103 | 4.8096 | 1.047 | 0 | 0.10014 | 3.6523 | 0.58715 | 4.9419 |  | MIN | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.01 | 12.9 | 15 | 1.0533 |  |  |  | MIN | 0.7 | 10.9 | 23.3394 | 16.3376 | 6.06 | 14.5 | 15 | 1.0892 |  |  |  | MIN | 0.68 | 11.6 | 23.2759 | 15.8276 | 6.14 | 14.4 | 15 | 1.0552 |  |  |  | 1.0533
AVERAGE | 6.2 | 10.8333 | 12.3333 | 9.8933 | 126 | 179.3333 | 14.5833 | 0.55733 | 0.0375 | 6.0133 | 7.6667 | 0.079 | 6.03 | 7.6667 |  | 5.965 | 7.5 |  | 6.0275 | 0.48825 | 7 | 0.71 | 13.375 | 10.05 | 0.6937 | 0.066 | 6.07 | 0.49875 | 6.25 | 0.6975 | 14.75 | 10.075 | 0.66687 | 6.05 | 0.6015 | 5.5 | 0.695 | 14.85 | 11.225 | 0.62491 | 0.0205 | 1 | 0.48167 | 0.0125 | 0.067833 | 0.017833 | 1 | 0.52667 |  | 0.036333 | 1.1667 | 0.435 |  | 7.68 | 0.060833 | 1 | 4.0833 | 13.6333 | 20.5 | 39.5 | 0.0135 | 7.5317 | 0.0625 | 1 | 4.05 | 15.7833 | 21 | 36 | 0.012 | 4.0333 | 4.0333 | 3.6833 |  |  | MAXIMUM | 10.9 | 10.9 | 11.9 | 33.7 | 10.4 | 10.4 | 11.4 | 32.2 |  | 13.212 | 0.4899 | 16.9315 | 30.1435 | 2.4903 | MAXIMUM | 110.8515 | 8239.3112 |  | 808.8106 |  |  |  | 21.5797 | 22.7955 | 20.232 | 1.6631 | 1.5425 | 1.3634 | 0.58069 | 0.55971 | 0.52526 | 0.53383 | 0.65676 | 0.59998 | 1.7786 | 5 | 0.052178 | 0.049859 | 0.051191 | 1.1039 | 0.50173 | 0.1032 | 3.984 | 0.65794 | 5.3012 | 1.1293 | 0.5167 | 0.10413 | 3.8013 | 0.61645 | 5.4005
MINIMUM | 6.13 | 10 | 12 | 9.83 | 121 | 178 | 14.5 | 0.545 | 0.037 | 5.87 | 7 | 0.073 | 5.82 | 7 |  | 5.85 | 7 |  | 6 | 0.408 | 6 | 0.59 | 12.9 | 9.5 | 0.61057 | 0.06 | 6.03 | 0.44 | 5 | 0.66 | 14.3 | 9.5 | 0.49736 | 6 | 0.568 | 4 | 0.6 | 14.4 | 10.6 | 0.43407 | 0.018 | 1 | 0.42 | 0.012 | 0.063 | 0.012 | 1 | 0.41 |  | 0.035 | 1 | 0.36 |  | 7.39 | 0.051 | 1 | 4 | 13.4 | 20 | 38 | 0.011 | 7.32 | 0.055 | 1 | 3.9 | 15.6 | 20 | 36 | 0.012 | 4 | 4 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 68749 | 0 | 0 | 0 | 0 | 0 | 0 | 3596 | 3786 | 3676 | 1680 | 1645 | 1625 | 5076 | 4920 | 4646 | 4656 | 5646 | 5561 | 4430 | 0 | 4645 | 4590 | 5120 | 465 | 564 | 68 | 7280 | 1270 | 1714 | 256 | 313 | 38 | 3770 | 715 | 944
MAXIMUM | 6.24 | 11 | 13 | 9.98 | 132 | 182 | 14.7 | 0.568 | 0.038 | 6.1 | 8 | 0.088 | 6.16 | 8 |  | 6.13 | 8 |  | 6.09 | 0.54 | 8 | 0.83 | 14 | 10.9 | 0.76269 | 0.073 | 6.13 | 0.551 | 7 | 0.74 | 15.3 | 10.9 | 0.76269 | 6.14 | 0.636 | 7 | 0.79 | 15.5 | 11.9 | 0.78111 | 0.023 | 1 | 0.56 | 0.013 | 0.076 | 0.022 | 1 | 0.65 |  | 0.037 | 2 | 0.57 |  | 7.98 | 0.072 | 1 | 4.2 | 13.8 | 21 | 41 | 0.016 | 7.67 | 0.074 | 1 | 4.2 | 16.2 | 22 | 36 | 0.012 | 4.1 | 4.1 | 4.5 | [17 empty] | AVERAGE | 13749.8 | [6 empty] | 719.2 | 757.2 | 735.2 | 336 | 329 | 325 | 1015.2 | 984 | 929.2 | 931.2 | 1129.2 | 1112.2 | 886 |  | 929 | 918 | 1024 | 93 | 112.8 | 13.6 | 1456 | 254 | 342.8 | 51.2 | 62.6 | 7.6 | 754 | 143 | 188.8
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0028 |  | TOTAL AVG COAG ALK: |  |  |  | 7.6111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.636 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.59 | [5 empty] | 6.0492 |  |  |  |  | 0.037 |  |  |  |  | 0.59 | [6 empty] | 0.037 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 11670 | [6 empty] | 605 | 632 | 627 | 300 | 300 | 300 | 910 | 880 | 850 | 840 | 1000 | 835 | 830 |  | 850 | 850 | 960 | 86 | 105 | 13 | 1340 | 160 | 300 | 46 | 58 | 7 | 700 | 130 | 175
[90 empty] | MAXIMUM | 15279 | [6 empty] | 777 | 817 | 790 | 350 | 350 | 340 | 1080 | 1060 | 1000 | 1020 | 1370 | 1231 | 935 |  | 995 | 980 | 1080 | 98 | 120 | 14 | 1540 | 300 | 367 | 56 | 68 | 8 | 870 | 150 | 211
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.29 |  | TOTAL MGD: |  | 5.974 |  |  | FINISHED SOUTH 1 |  | START: | 23811124 |  | END: | 23817098 |  |  | Alum | 7226 | 8635 | 8635 | 7762 | 7762 | 0 | [44 empty] | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.01 | 12.9 | 15 | 1.0533
[73 empty] | FINISHED 2 | 16.02 |  | TOTAL MGD: |  | 6.316 |  |  | FINISHED SOUTH 2 |  | START: | 43409119 |  | END: | 43415435 |  |  | Caustic | 4631 | 7174 | 7174
[73 empty] | TOTAL RAW | 31.833 |  | TOTAL MGD: |  | 5.009 |  |  | FINISHED CONWAY |  | START: | 10064713 |  | END: | 10069722 |  |  | Hypochlorite | 14 |  | 41
[76 empty] | TOTAL MGD: |  | 11.011 |  |  | FINISHED PERRY |  | START: | 33416300 |  | END: | 33427311 |  |  | Phosphate | 1650
[76 empty] | TOTAL MGD: |  | 10.141 |  |  | RAW PLANT 1 |  | START: | 30581537 |  | END: | 30591678 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.285 |  |  | RAW PLANT 2 |  | START: | 30543817 |  | END: | 30554102 |  |  | Cal~Flo | 12.43 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.407 |  |  | RAW PLANT 3 |  | START: | 7068794 |  | END: | 7080201 |  |  | Zinc | 1093
[76 empty] | TOTAL MGD: |  | 1.005 |  |  | DECANT |  | START: | 1822369 |  | END: | 1823374 |  |  | Polymer | 25
[76 empty] | TOTAL MGD: |  | 1.4541 |  |  | BLOW DOWN |  | START: | 9072.887 |  | END: | 9074.3412 |  |  | NH3 | 8.59 |  | BI-SUL | 600
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 810
23817098
43415435
10069722
33427311
30591678
30554102
7080201
1823374
9074.3412
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 27
DATE: | 2018-11-27 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2018-11-27 | [23 empty] | DATE: | 2018-11-27
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-27 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43431.0273 | 1,2,3,6 | 55 | 11.3 | 11.3 | 12.5 |  | 10.8 | 10.8 | 12 | 33.6 | 8,3 | 12.4 | 1,3 | 18.0778 | 83.6424 | 2.4925 | 43431.0273 | 109.92 | 8362.286 | 0 | 808.8106 | 0 | 0 | 0 | 20.7862 | 21.8965 | 18.9075 | 1.4838 | 1.4838 | 1.3539 | 0.56542 | 0.55532 | 0.50989 | 0.50989 | 0.53852 | 0.58872 | 1.7786 | 3.5 | 0.049827 | 0.049827 | 0.049241 | 1.0962 | 0.50129 | 0.093649 | 4.0247 | 0.64413 | 4.7955 | 1.092 | 0.5053 | 0.096324 | 3.8033 | 0.62724 | 5.3007 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.594 | 6 | 0.78 | 13 | 10.9 | 0.76269 |  | 6.13 | 0.56 | 6 | 0.68 | 14.3 | 10.9 | 0.76269 | 6.02 | 0.694 | 7 | 0.72 | 14.4 | 12.5 | 0.81444 | [13 empty] | 7.65 | 0.059 | 1 | 3.9 | 13.5 |  |  |  | 7.56 | 0.054 | 2 | 4.1 | 15.4 |  |  |  | 4 | 4.3 | 3.6 | [18 empty] | 15780 | [6 empty] | 805 | 848 | 810 | 360 | 360 | 365 | 1120 | 1100 | 1010 | 1010 | 1180 | 1290 | 935 |  | 1020 | 1020 | 1120 | 103 | 125 | 14 | 1650 | 305 | 355 | 57 | 70 | 8 | 890 | 165 | 218 |  | 1:00 | 0.78 | 10.9 | 23.3394 | 18.2048 | 6.1 | 13 | 15 | 1.2137 | 10 | 6.5 | 0.64269 | 1:00 | 0.68 | 10.9 | 23.3394 | 15.8708 | 6.13 | 14.3 | 15 | 1.0581 | 10 | 6.5 | 0.64269 | 1:00 | 0.72 | 12.5 | 21.6 | 15.552 | 6.02 | 14.4 | 15 | 1.0368 | 10 | 6.5 | 0.69444
2:00 | [72 empty] | 43431.2211 | 1,2,3,6 | 55 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | 8,3 | 7.9934 | 1,3 | 20.0621 | 28.0555 | 2.4925 | 43431.2211 | 109.9848 | 8239.3112 | 0 | 808.8106 | 0 | 0 | 0 | 20.7895 | 20.911 | 18.8985 | 1.6257 | 1.6257 | 1.2998 | 0.57047 | 0.54195 | 0.52293 | 0.53244 | 0.43882 | 0.61435 | 1.8071 | 3.5 | 0.050005 | 0.050005 | 0.049803 | 1.0995 | 0.50091 | 0.10051 | 3.956 | 0.70608 | 4.8207 | 1.1034 | 1.0811 | 0.10403 | 3.8293 | 0.69338 | 5.2521 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.26 | 11 | 13 | 9.97 | 121 | 181 | 14.4 | 0.532 |  | 5.9 | 7 | 0.071 | 6.07 | 8 |  | 5.92 | 8 | [8 empty] | 0.067 | [14 empty] | 0.024 | 1 | 0.47 |  | 0.065 | 0.009 | 1 | 0.52 |  | 0.034 | 1 | 0.45 | [38 empty] | 16644 | [6 empty] | 855 | 860 | 842 | 420 | 420 | 365 | 1200 | 1140 | 1100 | 1120 | 1000 | 1400 | 950 |  | 1090 | 1090 | 1180 | 110 | 133 | 16 | 1745 | 356 | 380 | 60 | 156 | 9 | 926 | 190 | 225 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43431.3262 | 1,2,3,6 | 65 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | 8,3 | 10.7813 | 1,3 | 19.8504 | 30.6317 | 0.0019253 | 43431.3262 | 112.9981 | 8608.2356 | 0 | 808.8106 | 0 | 0 | 0 | 21.5432 | 22.3699 | 20.4247 | 1.4708 | 1.6257 | 1.3532 | 0.57047 | 0.54195 | 0.51342 | 0.5467 | 0.68456 | 0.66701 | 1.8071 | 7 | 0.050464 | 0.04817 | 0.048537 | 1.0995 | 0.50091 | 0.10051 | 3.8866 | 0.67434 | 4.8207 | 1.1034 | 0.49895 | 0.10403 | 3.7345 | 0.65689 | 4.6685 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 8.21 | 0.06 | 1 | 4.5 | 13.2 |  |  |  | 8.19 | 0.056 | 2 | 4.4 | 15.1 |  |  |  | 4.1 | 4.3 | 3.7 | [18 empty] | 17100 | [6 empty] | 886 | 920 | 910 | 380 | 420 | 380 | 1200 | 1140 | 1080 | 1150 | 1560 | 1520 | 950 |  | 1100 | 1050 | 1150 | 110 | 133 | 16 | 1710 | 340 | 380 | 60 | 72 | 9 | 900 | 180 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43431.4417 | 1,2,3,6 | 65 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | 8,3 | 10.7813 | 1,3 | 19.8504 | 30.6317 | 0.0019253 | 43431.4417 | 116.3021 | 9223.1096 | 0 | 808.8106 | 0 | 0 | 0 | 21.5432 | 22.3699 | 20.4247 | 1.4708 | 1.6257 | 1.3532 | 0.59662 | 0.56571 | 0.5776 | 0.5776 | 0.71528 | 0.70212 | 1.9118 | 7 | 0.050464 | 0.04817 | 0.048537 | 1.0995 | 0.50091 | 0.10051 | 3.8866 | 0.67434 | 4.8207 | 1.1034 | 0.49895 | 0.10403 | 3.7345 | 0.65689 | 4.6685 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.25 | 10 | 12 | 9.64 | 133 | 180 | 14.1 | 0.58 |  | 5.98 | 8 | 0.068 | 5.98 | 8 |  | 5.92 | 8 | [8 empty] | 0.058 | [14 empty] | 0.02 | 1 | 0.6 |  | 0.064 | 0.02 | 2 | 0.6 |  | 0.03 | 2 | 0.59 | [38 empty] | 17600 | [6 empty] | 886 | 920 | 910 | 380 | 420 | 380 | 1255 | 1190 | 1215 | 1215 | 1630 | 1600 | 1005 |  | 1100 | 1050 | 1150 | 110 | 133 | 16 | 1710 | 340 | 380 | 60 | 72 | 9 | 900 | 180 | 200 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43431.5935 | 1,2,3,6 | 65 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | 8,3 | 10.7813 | 1,3 | 19.8504 | 30.6317 | 0.0019253 | 43431.5935 | 120.9278 | 9223.1096 | 0 | 808.8106 | 0 | 0 | 0 | 21.3973 | 22.3699 | 20.2003 | 1.4708 | 1.6257 | 1.3532 | 0.62276 | 0.59424 | 0.6085 | 0.60612 | 0.746 | 0.73283 | 2.2827 | 7 | 0.050464 | 0.04817 | 0.048537 | 1.0995 | 0.50091 | 0.10051 | 3.8866 | 0.67434 | 4.8207 | 1.1034 | 0.49895 | 0.10403 | 3.7345 | 0.65689 | 4.6685 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.049 | [9 empty] | 5.98 | 0.562 | 8 | 0.88 | 13 | 12 | 0.73321 |  | 6 | 0.5 | 8 | 0.8 | 14.1 | 12 | 0.73321 | 6.01 | 0.685 | 9 | 0.8 | 14.4 | 13.5 | 0.87 |  |  |  | 0.009 | [9 empty] | 7.89 | 0.066 | 2 | 4 | 15.3 | 21 | 36 | 0.015 | 7.58 | 0.063 | 2 | 4.8 | 15 | 21 | 36 | 0.014 | 4 | 4.5 | 4.6 | [18 empty] | 18300 | [6 empty] | 880 | 920 | 900 | 380 | 420 | 380 | 1310 | 1250 | 1280 | 1275 | 1700 | 1670 | 1200 |  | 1100 | 1050 | 1150 | 110 | 133 | 16 | 1710 | 340 | 380 | 60 | 72 | 9 | 900 | 180 | 200 |  | 9:00 | 0.88 | 12 | 21.2 | 18.656 | 5.98 | 13 | 13 | 1.4351 | 10 | 6 | 0.61321 | 9:00 | 0.8 | 12 | 21.2 | 16.96 | 6 | 14.1 | 13 | 1.3046 | 10 | 6 | 0.61321 | 9:00 | 0.8 | 13.5 | 20 | 16 | 6.01 | 14.4 | 15 | 1.0667 | 10 | 6.5 | 0.75
10:00 | [72 empty] | 43431.6585 | 1,2,3,6 | 65 | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 | 8,3 | 10.7813 | 1,3 | 19.8504 | 30.6317 | 0.0019253 | 43431.6585 | 120.9278 | 9715.0088 | 0 | 808.8106 | 0 | 0 | 0 | 21.3973 | 22.3699 | 20.2003 | 1.4708 | 1.6257 | 1.3532 | 0.68314 | 0.65129 | 0.66745 | 0.66555 | 0.746 | 0.73283 | 2.2827 | 7 | 0.050464 | 0.04817 | 0.048537 | 1.0995 | 0.50091 | 0.10051 | 3.8866 | 0.67434 | 4.8207 | 1.1034 | 0.49895 | 0.10403 | 3.7345 | 0.65689 | 4.6685 |  | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.16 | 10 | 12 | 9.62 | 130 | 178 | 14.2 | 0.574 |  | 6.08 | 8 | 0.077 | 6.09 | 8 |  | 6.09 | 8 | [8 empty] | 0.063 | [14 empty] | 0.02 | 1 | 0.4 |  | 0.062 | 0.02 | 1 | 0.45 |  | 0.036 | 2 | 0.4 | [38 empty] | 18300 | [6 empty] | 880 | 920 | 900 | 380 | 420 | 380 | 1437 | 1370 | 1404 | 1400 | 1700 | 1670 | 1200 |  | 1100 | 1050 | 1150 | 110 | 133 | 16 | 1710 | 340 | 380 | 60 | 72 | 9 | 900 | 180 | 200 |  | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [72 empty] | 43431.8562 | 1,2,3,6 | 47 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 8,3 | 13.6368 | 1,3 | 16.9776 | 30.6144 | 0.0019253 | 43431.8562 | 120.8112 | 9346.0844 | 0 | 808.8106 | 0 | 0 | 0 | 18.8332 | 19.629 | 17.7501 | 1.5261 | 1.6109 | 1.3934 | 0.73642 | 0.71568 | 0.72605 | 0.72605 | 0.81007 | 0.64178 | 2.2827 | 10 | 0.050246 | 0.050246 | 0.050005 | 1.0947 | 0.49911 | 0.096324 | 3.9772 | 0.66254 | 3.821 | 1.1194 | 0.5122 | 0.10051 | 3.8134 | 0.57518 | 3.8058 |  | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.27 | 0.503 | 8 | 0.78 | 12.9 | 12 | 0.82755 |  | 6.32 | 0.526 | 6 | 0.76 | 14.4 | 12 | 0.82755 | 6.28 | 0.583 | 5 | 0.79 | 14.2 | 13 | 0.84222 | [13 empty] | 7.83 | 0.063 | 2 | 4.3 | 13.2 |  |  |  | 7.76 | 0.064 | 2 | 4.3 | 15 |  |  |  | 4.1 | 4.5 | 3.8 | [18 empty] | 16800 | [6 empty] | 710 | 740 | 730 | 360 | 380 | 360 | 1420 | 1380 | 1400 | 1400 | 1704 | 1350 | 1200 |  | 1000 | 1000 | 1090 | 100 | 121 | 14 | 1580 | 305 | 275 | 56 | 68 | 8 | 800 | 145 | 150 |  | 13:00 | 0.78 | 12 | 21.2 | 16.536 | 6.27 | 12.9 | 15 | 1.1024 | 10 | 6.5 | 0.70755 | 13:00 | 0.76 | 12 | 21.2 | 16.112 | 6.32 | 14.4 | 15 | 1.0741 | 10 | 6.5 | 0.70755 | 13:00 | 0.79 | 13 | 20.7692 | 16.4077 | 6.28 | 14.2 | 15 | 1.0938 | 10 | 6.5 | 0.72222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.35 | 10 | 12 | 9.84 | 132 | 174 | 14.3 | 0.574 |  | 6.25 | 9 | 0.081 | 6.22 | 8 |  | 6.18 | 10 | [8 empty] | 0.063 | [14 empty] | 0.02 | 2 | 0.43 |  | 0.074 | 0.02 | 2 | 0.4 |  | 0.042 | 2 | 0.36 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 8.03 | 0.07 | 2 | 4.5 | 13.1 |  |  |  | 7.73 | 0.063 | 2 | 4.2 | 15.6 |  |  |  | 4.1 | 4.5 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.27 | 11 | 15 | 9.7 | 126 | 175 | 13.9 | 0.559 |  | 6.18 | 8 | 0.08 | 6.19 | 9 |  | 6.14 | 8 | [8 empty] | 0.065 | [14 empty] | 0.021 | 1 | 0.5 |  | 0.075 | 0.012 | 1 | 0.69 |  | 0.041 | 1 | 0.64 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.036 | [9 empty] | 6.28 | 0.489 | 6 | 0.79 | 12.8 | 11 | 0.76858 |  | 6.3 | 0.46 | 5 | 0.7 | 13 | 11 | 0.76858 | 6.23 | 0.438 | 6 | 0.75 | 14.2 | 12 | 0.78667 |  |  |  | 0.01 | [9 empty] | 8.3 | 0.063 | 1 | 4.5 | 13.1 | 20 | 34 | 0.013 | 7.9 | 0.07 | 1 | 4.3 | 15.1 | 20 | 35 | 0.013 | 4.1 | 4.5 | 3.8 | [55 empty] | 21:00 | 0.79 | 11 | 23.1273 | 18.2705 | 6.28 | 12.8 | 15 | 1.218 | 10 | 6.5 | 0.64858 | 21:00 | 0.7 | 11 | 23.1273 | 16.1891 | 6.3 | 13 | 15 | 1.0793 | 10 | 6.5 | 0.64858 | 21:00 | 0.75 | 12 | 22.5 | 16.875 | 6.23 | 14.2 | 15 | 1.125 | 10 | 6.5 | 0.66667
22:00 | [72 empty] | DOSE |  | TOTAL | 82.3 | 82.3 | 89.5 | 219 | 78.8 | 78.8 | 86 | 243.6 | 0 | 77.1554 | 0 | 134.519 | 264.839 | 4.9946 | TOTAL | 811.8717 | 62717.1452 | 0 | 5661.674 | 0 | 0 | 0 | 146.29 | 151.9163 | 136.806 | 10.519 | 11.2231 | 9.4599 | 4.3453 | 4.1661 | 4.1258 | 4.1643 | 4.6792 | 4.6796 | 14.1527 | 45 | 0.35193 | 0.34276 | 0.3432 | 7.6882 | 3.5049 | 0.69254 | 27.504 | 4.7101 | 32.7202 | 7.7286 | 4.0943 | 0.71699 | 26.3838 | 4.5234 | 33.0327 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.32 | 10 | 15 | 8.98 | 117 | 174 | 14.1 | 0.519 |  | 6.23 | 9 | 0.073 | 6.24 | 9 |  | 6.16 | 10 | [8 empty] | 0.068 | [14 empty] | 0.018 | 1 | 0.4 |  | 0.072 | 0.011 | 1 | 0.49 |  | 0.035 | 1 | 0.56 | [22 empty] | AVERAGE | 11.7571 | 11.7571 | 12.7857 | 36.5 | 11.2571 | 11.2571 | 12.2857 | 34.8 |  | 11.0222 |  | 19.217 | 37.8341 | 0.71352 | AVERAGE | 115.9817 | 8959.5922 |  | 808.8106 | 0 | 0 | 0 | 20.8986 | 21.7023 | 19.5437 | 1.5027 | 1.6033 | 1.3514 | 0.62076 | 0.59516 | 0.58941 | 0.59491 | 0.66846 | 0.66852 | 2.0218 | 6.4286 | 0.050276 | 0.048965 | 0.049028 | 1.0983 | 0.5007 | 0.098934 | 3.9291 | 0.67288 | 4.6743 | 1.1041 | 0.58491 | 0.10243 | 3.7691 | 0.64619 | 4.719 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.61 | 62 | 79 | 57.75 | 759 | 1062 | 85 | 3.338 | 0.085 | 36.62 | 49 | 0.45 | 36.79 | 50 | 0 | 36.41 | 52 | 0 | 24.63 | 2.148 | 28 | 3.23 | 51.7 | 45.9 | 3.092 | 0.384 | 24.75 | 2.046 | 25 | 2.94 | 55.8 | 45.9 | 3.092 | 24.54 | 2.4 | 27 | 3.06 | 57.2 | 51 | 3.3133 | 0.123 | 7 | 2.8 | 0.019 | 0.412 | 0.092 | 8 | 3.15 | 0 | 0.218 | 9 | 3 | 0 | 47.91 | 0.381 | 9 | 25.7 | 81.4 | 41 | 70 | 0.028 | 46.72 | 0.37 | 11 | 26.1 | 91.2 | 41 | 71 | 0.027 | 24.4 | 26.6 | 23.3 |  |  | MINIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 7.9934 |  | 16.9776 | 28.0555 | 0.0019253 | MINIMUM | 109.92 | 8239.3112 |  | 808.8106 |  |  |  | 18.8332 | 19.629 | 17.7501 | 1.4708 | 1.4838 | 1.2998 | 0.56542 | 0.54195 | 0.50989 | 0.50989 | 0.43882 | 0.58872 | 1.7786 | 3.5 | 0.049827 | 0.04817 | 0.048537 | 1.0947 | 0.49911 | 0.093649 | 3.8866 | 0.64413 | 3.821 | 1.092 | 0.49895 | 0.096324 | 3.7345 | 0.57518 | 3.8058 |  | MIN | 0.78 | 12 | 21.2 | 16.536 | 6.27 | 12.9 | 15 | 1.1024 |  |  |  | MIN | 0.68 | 10.9 | 23.3394 | 15.8708 | 6.13 | 14.3 | 15 | 1.0581 |  |  |  | MIN | 0.72 | 12.5 | 21.6 | 15.552 | 6.02 | 14.4 | 15 | 1.0368 |  |  |  | 1.0368
AVERAGE | 6.2683 | 10.3333 | 13.1667 | 9.625 | 126.5 | 177 | 14.1667 | 0.55633 | 0.0425 | 6.1033 | 8.1667 | 0.075 | 6.1317 | 8.3333 |  | 6.0683 | 8.6667 |  | 6.1575 | 0.537 | 7 | 0.8075 | 12.925 | 11.475 | 0.77301 | 0.064 | 6.1875 | 0.5115 | 6.25 | 0.735 | 13.95 | 11.475 | 0.77301 | 6.135 | 0.6 | 6.75 | 0.765 | 14.3 | 12.75 | 0.82833 | 0.0205 | 1.1667 | 0.46667 | 0.0095 | 0.068667 | 0.015333 | 1.3333 | 0.525 |  | 0.036333 | 1.5 | 0.5 |  | 7.985 | 0.0635 | 1.5 | 4.2833 | 13.5667 | 20.5 | 35 | 0.014 | 7.7867 | 0.061667 | 1.8333 | 4.35 | 15.2 | 20.5 | 35.5 | 0.0135 | 4.0667 | 4.4333 | 3.8833 |  |  | MAXIMUM | 12 | 12 | 13 | 37 | 11.5 | 11.5 | 12.5 | 35.5 |  | 13.6368 |  | 20.0621 | 83.6424 | 2.4925 | MAXIMUM | 120.9278 | 9715.0088 |  | 808.8106 |  |  |  | 21.5432 | 22.3699 | 20.4247 | 1.6257 | 1.6257 | 1.3934 | 0.73642 | 0.71568 | 0.72605 | 0.72605 | 0.81007 | 0.73283 | 2.2827 | 10 | 0.050464 | 0.050246 | 0.050005 | 1.0995 | 0.50129 | 0.10051 | 4.0247 | 0.70608 | 4.8207 | 1.1194 | 1.0811 | 0.10403 | 3.8293 | 0.69338 | 5.3007
MINIMUM | 6.16 | 10 | 12 | 8.98 | 117 | 174 | 13.9 | 0.519 | 0.036 | 5.9 | 7 | 0.068 | 5.98 | 8 |  | 5.92 | 8 |  | 5.98 | 0.489 | 6 | 0.78 | 12.8 | 10.9 | 0.73321 | 0.058 | 6 | 0.46 | 5 | 0.68 | 13 | 10.9 | 0.73321 | 6.01 | 0.438 | 5 | 0.72 | 14.2 | 12 | 0.78667 | 0.018 | 1 | 0.4 | 0.009 | 0.062 | 0.009 | 1 | 0.4 |  | 0.03 | 1 | 0.36 |  | 7.65 | 0.059 | 1 | 3.9 | 13.1 | 20 | 34 | 0.013 | 7.56 | 0.054 | 1 | 4.1 | 15 | 20 | 35 | 0.013 | 4 | 4.3 | 3.6 | [15 empty] | MIL/MIN |  | TOTAL | 120524 | 0 | 0 | 0 | 0 | 0 | 0 | 5902 | 6128 | 6002 | 2660 | 2840 | 2610 | 8942 | 8570 | 8489 | 8570 | 10474 | 10500 | 7440 | 0 | 7510 | 7310 | 7990 | 753 | 911 | 108 | 11815 | 2326 | 2530 | 413 | 582 | 61 | 6216 | 1220 | 1393
MAXIMUM | 6.35 | 11 | 15 | 9.97 | 133 | 181 | 14.4 | 0.58 | 0.049 | 6.25 | 9 | 0.081 | 6.24 | 9 |  | 6.18 | 10 |  | 6.28 | 0.594 | 8 | 0.88 | 13 | 12 | 0.82755 | 0.068 | 6.32 | 0.56 | 8 | 0.8 | 14.4 | 12 | 0.82755 | 6.28 | 0.694 | 9 | 0.8 | 14.4 | 13.5 | 0.87 | 0.024 | 2 | 0.6 | 0.01 | 0.075 | 0.02 | 2 | 0.69 |  | 0.042 | 2 | 0.64 |  | 8.3 | 0.07 | 2 | 4.5 | 15.3 | 21 | 36 | 0.015 | 8.19 | 0.07 | 2 | 4.8 | 15.6 | 21 | 36 | 0.014 | 4.1 | 4.5 | 4.6 | [17 empty] | AVERAGE | 17217.7143 | [6 empty] | 843.1429 | 875.4286 | 857.4286 | 380 | 405.7143 | 372.8571 | 1277.4286 | 1224.2857 | 1212.7143 | 1224.2857 | 1496.2857 | 1500 | 1062.8571 |  | 1072.8571 | 1044.2857 | 1141.4286 | 107.5714 | 130.1429 | 15.4286 | 1687.8571 | 332.2857 | 361.4286 | 59 | 83.1429 | 8.7143 | 888 | 174.2857 | 199
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1011 |  | TOTAL AVG COAG ALK: |  |  |  | 8.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.694 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.68 | [5 empty] | 6.16 |  |  |  |  | 0.042 |  |  |  |  | 0.68 | [6 empty] | 0.042 | [16 empty] | Pump Station MIN |  | 3.6 | [17 empty] | MINIMUM | 15780 | [6 empty] | 710 | 740 | 730 | 360 | 360 | 360 | 1120 | 1100 | 1010 | 1010 | 1000 | 1290 | 935 |  | 1000 | 1000 | 1090 | 100 | 121 | 14 | 1580 | 305 | 275 | 56 | 68 | 8 | 800 | 145 | 150
[90 empty] | MAXIMUM | 18300 | [6 empty] | 886 | 920 | 910 | 420 | 420 | 380 | 1437 | 1380 | 1404 | 1400 | 1704 | 1670 | 1200 |  | 1100 | 1090 | 1180 | 110 | 133 | 16 | 1745 | 356 | 380 | 60 | 156 | 9 | 926 | 190 | 225
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.999 |  | TOTAL MGD: |  | 6.279 |  |  | FINISHED SOUTH 1 |  | START: | 23817098 |  | END: | 23823377 |  |  | Alum | 2268 | 11000 | 11000 | 7562 | 7562 | 0 | [44 empty] | 0.72 | 12.5 | 21.6 | 15.552 | 6.02 | 14.4 | 15 | 1.0368
[73 empty] | FINISHED 2 | 17.383 |  | TOTAL MGD: |  | 6.72 |  |  | FINISHED SOUTH 2 |  | START: | 43415435 |  | END: | 43422155 |  |  | Caustic | 3855 | 7014 | 7014
[73 empty] | TOTAL RAW | 35.89 |  | TOTAL MGD: |  | 5.423 |  |  | FINISHED CONWAY |  | START: | 10069722 |  | END: | 10075145 |  |  | Hypochlorite | 18.5 |  | 43
[76 empty] | TOTAL MGD: |  | 11.96 |  |  | FINISHED PERRY |  | START: | 33427311 |  | END: | 33439271 |  |  | Phosphate | 1621
[76 empty] | TOTAL MGD: |  | 11.386 |  |  | RAW PLANT 1 |  | START: | 30591678 |  | END: | 30603064 |  |  | Fluoride | 1750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.566 |  |  | RAW PLANT 2 |  | START: | 30554102 |  | END: | 30565668 |  |  | Cal~Flo | 9.23 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.938 |  |  | RAW PLANT 3 |  | START: | 7080201 |  | END: | 7093139 |  |  | Zinc | 1094
[76 empty] | TOTAL MGD: |  | 1.514 |  |  | DECANT |  | START: | 1823374 |  | END: | 1824888 |  |  | Polymer | 7
[76 empty] | TOTAL MGD: |  | 1.553 |  |  | BLOW DOWN |  | START: | 9074.3412 |  | END: | 9075.8941 |  |  | NH3 | 8.35 |  | BI-SUL | 600
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 817
23823377
43422155
10075145
33439271
30603064
30565668
7093139
1824888
9075.8941
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 28
DATE: | 2018-11-28 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2018-11-28 | [23 empty] | DATE: | 2018-11-28
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-28 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43432.0282 | 1,2,3,6 | 47 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 8,3 | 11.9016 | 1,3 | 18.4853 | 30.3869 | 3.0201 | 43432.0282 | 120.8112 | 9346.0844 | 0 | 808.8106 | 0 | 0 | 0 | 18.7006 | 19.3637 | 17.7501 | 1.5261 | 1.6109 | 1.3934 | 0.73642 | 0.71568 | 0.72605 | 0.72605 | 0.81007 | 0.64178 | 2.2827 | 9 | 0.050246 | 0.050246 | 0.050005 | 1.0947 | 0.49911 | 0.096324 | 3.8772 | 0.66254 | 3.821 | 1.1194 | 0.5122 | 0.10051 | 3.7334 | 0.57518 | 3.8058 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.3 | 0.551 | 6 | 0.72 | 12.5 | 11 | 0.76858 |  | 6.3 | 0.355 | 5 | 0.7 | 13 | 11 | 0.76858 | 6.32 | 0.616 | 6 | 0.79 | 13.9 | 12 | 0.78667 | [13 empty] | 7.43 | 0.051 | 1 | 4.2 | 12.9 |  |  |  | 7.32 | 0.056 | 1 | 4.3 | 15 |  |  |  | 4.3 | 4.5 | 4.1 | [18 empty] | 16800 | [6 empty] | 705 | 730 | 730 | 360 | 380 | 360 | 1420 | 1380 | 1400 | 1400 | 1704 | 1350 | 1200 |  | 1000 | 1000 | 1090 | 100 | 121 | 14 | 1580 | 305 | 275 | 56 | 68 | 8 | 800 | 145 | 150 |  | 1:00 | 0.72 | 11 | 23.1273 | 16.6516 | 6.3 | 12.5 | 15 | 1.1101 | 10 | 6.5 | 0.64858 | 1:00 | 0.7 | 11 | 23.1273 | 16.1891 | 6.3 | 13 | 15 | 1.0793 | 10 | 6.5 | 0.64858 | 1:00 | 0.79 | 12 | 22.5 | 17.775 | 6.32 | 13.9 | 15 | 1.185 | 10 | 6.5 | 0.66667
2:00 | [72 empty] | 43432.071 | 1,2,3,6 | 47 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 11.9016 | 1,3 | 18.4853 | 30.3869 | 3.0201 | 43432.071 | 121.2891 | 9346.0844 | 0 | 808.8106 | 0 | 0 | 0 | 18.2704 | 19.0885 | 17.3323 | 1.4838 | 1.571 | 1.391 | 0.74641 | 0.71442 | 0.73041 | 0.73574 | 0.81426 | 0.64848 | 2.2827 | 9 | 0.050172 | 0.050172 | 0.051345 | 1.1043 | 0.50105 | 0.099158 | 4.0228 | 0.67084 | 2.7891 | 1.1084 | 0.51 | 0.1032 | 3.8184 | 0.57022 | 2.7355 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.28 | 10 | 14 | 9.32 | 131 | 175 | 13.9 | 0.571 |  | 6.06 | 8 | 0.077 | 6.06 | 8 |  | 6.1 | 9 | [8 empty] | 0.071 | [14 empty] | 0.017 | 1 | 0.32 |  | 0.076 | 0.009 | 1 | 0.45 |  | 0.036 | 1 | 0.46 | [38 empty] | 16420 | [6 empty] | 670 | 700 | 695 | 340 | 360 | 350 | 1400 | 1340 | 1370 | 1380 | 1670 | 1330 | 1200 |  | 970 | 970 | 1090 | 98 | 118 | 14 | 1600 | 300 | 195 | 54 | 66 | 8 | 800 | 140 | 105 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43432.3493 | 1,2,3,6 | 47 | 10.7 | 10.7 | 11.7 | 33.1 | 10.2 | 10.2 | 11.2 | 31.6 | 8,3 | 11.9016 | 1,3 | 18.4853 | 30.3869 | 3.0201 | 43432.3493 | 119.8118 | 9346.0844 | 0 | 824.6696 | 0 | 0 | 0 | 17.8614 | 18.8158 | 17.083 | 1.5274 | 1.5274 | 1.5102 | 0.74641 | 0.68243 | 0.73574 | 0.74641 | 0.59485 | 0.74112 | 2.2827 | 6.5 | 0.050172 | 0.050689 | 0.050874 | 1.1269 | 0.50105 | 0.099158 | 3.9628 | 0.69321 | 2.7891 | 1.1084 | 0.51046 | 0.1032 | 3.8406 | 0.59058 | 2.7355 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.43 | 0.052 | 1 | 4.3 | 12.5 |  |  |  | 7.57 | 0.055 | 1 | 4.3 | 14.5 |  |  |  | 4.3 | 4.5 | 4.6 | [18 empty] | 16220 | [6 empty] | 655 | 690 | 685 | 350 | 350 | 380 | 1400 | 1280 | 1380 | 1400 | 1220 | 1520 | 1200 |  | 970 | 980 | 1080 | 100 | 118 | 14 | 1600 | 310 | 195 | 54 | 66 | 8 | 830 | 145 | 105 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43432.6083 | 1,2,3,6 | 47 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | 8,3 | 11.9016 | 1,3 | 18.4853 | 30.3869 | 3.0201 | 43432.6083 | 109.6589 | 8731.2104 | 0 | 824.6696 | 0 | 0 | 0 | 12.4834 | 12.6339 | 10.4987 | 1.6934 | 1.6934 | 1.6583 | 0.70573 | 0.67633 | 0.73514 | 0.73514 | 0.61312 | 0.69309 | 2.2827 | 0 | 0.051611 | 0.051611 | 0.049137 | 1.0995 | 0.49902 | 0.09423 | 4.0046 | 0.74376 | 3.0923 | 1.1043 | 0.50955 | 0.14165 | 3.8142 | 0.67084 | 3.0036 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.09 | 11 | 16 | 8.86 | 130 | 176 | 13.9 | 0.555 |  | 6.32 | 9 | 0.057 | 6.35 | 9 |  | 6.38 | 9 | [8 empty] | 0.058 | [14 empty] | 0.032 | 2 | 0.46 |  | 0.066 | 0.01 | 1 | 0.43 |  | 0.034 | 1 | 0.42 | [38 empty] | 13500 | [6 empty] | 415 | 420 | 385 | 350 | 350 | 380 | 1200 | 1150 | 1250 | 1250 | 1150 | 1300 | 1200 |  | 900 | 900 | 950 | 88 | 106 | 12 | 1460 | 300 | 195 | 49 | 60 | 10 | 750 | 150 | 105 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 20:30 | 1,2,6 | 50 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | 0,1,2 | 11.6064 | 1,3 | 16.2778 | 27.8842 | 3.0201 | 43432.8965 | 110.4712 | 8731.2104 | 0 | 824.6696 | 0 | 0 | 0 | 11.581 | 12.6339 | 11.3168 | 1.5483 | 1.645 | 1.4838 | 0.77631 | 0.75278 | 0.77631 | 0.79983 | 0.5758 | 0.74641 | 2.2827 | 5 | 0.049317 | 0.050464 | 0.049654 | 1.0995 | 0.49902 | 0.10208 | 3.9983 | 0.70657 | 3.0923 | 1.1269 | 0.50955 | 0.099158 | 3.7695 | 0.67084 | 3.0036 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.046 | [9 empty] | 6.01 | 0.178 | 3 | 0.68 | 12.1 | 10.7 | 0.7509 |  | 5.98 | 0.166 | 3 | 0.68 | 13.7 | 10.7 | 0.66678 | 5.99 | 0.243 | 3 | 0.84 | 13.7 | 11.7 | 0.68333 |  |  |  | 0.058 | [9 empty] | 7.09 | 0.051 | 1 | 4.3 | 12.5 | 20 | 50 | 0.021 | 7.02 | 0.059 | 2 | 4.2 | 14.5 | 20 | 50 | 0.024 | 4.3 | 4.3 | 3.7 | [18 empty] | 13600 | [6 empty] | 385 | 420 | 415 | 320 | 340 | 340 | 1320 | 1280 | 1320 | 1360 | 1080 | 1400 | 1200 |  | 860 | 880 | 960 | 88 | 106 | 13 | 1405 | 285 | 195 | 50 | 60 | 7 | 740 | 150 | 105 |  | 9:00 | 0.68 | 10.7 | 23.7757 | 16.1675 | 6.01 | 12.1 | 15 | 1.0778 | 10 | 6.5 | 0.6309 | 9:00 | 0.68 | 10.7 | 23.7757 | 16.1675 | 5.98 | 13.7 | 13 | 1.2437 | 10 | 6 | 0.54678 | 9:00 | 0.84 | 11.7 | 23.0769 | 19.3846 | 5.99 | 13.7 | 13 | 1.4911 | 10 | 6 | 0.56333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.22 | 14 | 15 | 8.62 | 125 | 177 | 13.7 | 0.552 |  | 6.18 | 10 | 0.087 | 6.2 | 10 |  | 6.14 | 10 | [8 empty] | 0.058 | [14 empty] | 0.026 | 1 | 0.41 |  | 0.061 | 0.01 | 1 | 0.7 |  | 0.035 | 1 | 0.53 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.172 | 3 | 0.7 | 13 | 10.7 | 0.7509 |  | 6.24 | 0.168 | 3 | 0.7 | 13.5 | 10.7 | 0.7509 | 6.19 | 0.285 | 3 | 0.72 | 14 | 11.7 | 0.77 | [13 empty] | 7.53 | 0.055 | 1 | 4.5 | 13 |  |  |  | 7.23 | 0.045 | 1 | 4.3 | 16 |  |  |  | 4.4 | 4.3 | 3.6 | [55 empty] | 13:00 | 0.7 | 10.7 | 23.7757 | 16.643 | 6.12 | 13 | 15 | 1.1095 | 10 | 6.5 | 0.6309 | 13:00 | 0.7 | 10.7 | 23.7757 | 16.643 | 6.24 | 13.5 | 15 | 1.1095 | 10 | 6.5 | 0.6309 | 13:00 | 0.72 | 11.7 | 23.0769 | 16.6154 | 6.19 | 14 | 15 | 1.1077 | 10 | 6.5 | 0.65
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.26 | 15 | 15 | 8.34 | 122 | 170 | 14.5 | 0.531 |  | 6.15 | 10 | 0.075 | 6.17 | 10 |  | 6.08 | 10 | [8 empty] | 0.052 | [14 empty] | 0.023 | 1 | 0.44 |  | 0.052 | 0.016 | 1 | 0.65 |  | 0.034 | 1 | 0.55 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.55 | 0.052 | 1 | 4.5 | 13 |  |  |  | 7.35 | 0.042 | 1 | 4.3 | 16 |  |  |  | 4.4 | 4.2 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.34 | 12 | 18 | 8.4 | 130 | 169 | 14.6 | 0.555 |  | 6.15 | 8 | 0.097 | 6.21 | 10 |  | 6.17 | 10 | [8 empty] | 0.058 | [14 empty] | 0.024 | 2 | 0.33 |  | 0.056 | 0.015 | 1 | 0.7 |  | 0.034 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.03 | [9 empty] | 6.23 | 0.2 | 3 | 0.74 | 12.5 | 9.3 | 0.66835 |  | 6.3 | 0.192 | 3 | 0.76 | 12.9 | 9.6 | 0.68604 | 6.27 | 0.303 | 4 | 0.72 | 13.7 | 10.7 | 0.71444 |  |  |  | 0.012 |  |  |  |  | 0.009 |  |  |  | 0.009 | 7.33 | 0.047 | 1 | 4.6 | 12.5 | 20 | 58 | 0.011 | 7.28 | 0.05 | 1 | 4.2 | 15.1 | 21 | 63 | 0.014 | 4.4 | 4.2 | 3.8 | [55 empty] | 21:00 | 0.74 | 9.3 | 27.3548 | 20.2426 | 6.23 | 12.5 | 15 | 1.3495 | 10 | 6.5 | 0.54835 | 21:00 | 0.76 | 9.6 | 26.5 | 20.14 | 6.3 | 12.9 | 15 | 1.3427 | 10 | 6.5 | 0.56604 | 21:00 | 0.72 | 10.7 | 25.2336 | 18.1682 | 6.27 | 13.7 | 15 | 1.2112 | 10 | 6.5 | 0.59444
22:00 | [72 empty] | DOSE |  | TOTAL | 51.8 | 51.8 | 56.8 | 160.4 | 49.3 | 49.3 | 54.3 | 152.9 | 0 | 59.2128 | 0 | 90.2189 | 149.4317 | 15.1006 | TOTAL | 582.0422 | 45500.674 | 0 | 4091.63 | 0 | 0 | 0 | 78.8969 | 82.5358 | 73.9808 | 7.779 | 8.0478 | 7.4368 | 3.7113 | 3.5416 | 3.7037 | 3.7432 | 3.4081 | 3.4709 | 11.4135 | 29.5 | 0.25152 | 0.25318 | 0.25101 | 5.5248 | 2.4993 | 0.49095 | 19.8658 | 3.4769 | 15.5836 | 5.5674 | 2.5517 | 0.54773 | 18.9761 | 3.0777 | 15.284 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.34 | 10 | 17 | 8.33 | 128 | 171 | 14.1 | 0.548 |  | 6.05 | 9 | 0.079 | 6.19 | 9 |  | 6.16 | 10 | [8 empty] | 0.061 | [14 empty] | 0.022 | 1 | 0.41 |  | 0.062 | 0.012 | 1 | 0.62 |  | 0.034 | 1 | 0.36 | [22 empty] | AVERAGE | 10.36 | 10.36 | 11.36 | 32.08 | 9.86 | 9.86 | 10.86 | 30.58 |  | 11.8426 |  | 18.0438 | 29.8863 | 3.0201 | AVERAGE | 116.4084 | 9100.1348 |  | 818.326 | 0 | 0 | 0 | 15.7794 | 16.5072 | 14.7962 | 1.5558 | 1.6096 | 1.4874 | 0.74226 | 0.70833 | 0.74073 | 0.74864 | 0.68162 | 0.69418 | 2.2827 | 5.9 | 0.050303 | 0.050636 | 0.050203 | 1.105 | 0.49985 | 0.098191 | 3.9732 | 0.69538 | 3.1167 | 1.1135 | 0.51035 | 0.10955 | 3.7952 | 0.61553 | 3.0568 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.53 | 72 | 95 | 51.87 | 766 | 1038 | 84.7 | 3.312 | 0.076 | 36.91 | 54 | 0.472 | 37.18 | 56 | 0 | 37.03 | 58 | 0 | 24.66 | 1.101 | 15 | 2.84 | 50.1 | 41.7 | 2.9387 | 0.358 | 24.82 | 0.881 | 14 | 2.84 | 53.1 | 42 | 2.8723 | 24.77 | 1.447 | 16 | 3.07 | 55.3 | 46.1 | 2.9544 | 0.144 | 8 | 2.37 | 0.07 | 0.373 | 0.072 | 6 | 3.55 | 0.009 | 0.207 | 6 | 2.78 | 0.009 | 44.36 | 0.308 | 6 | 26.4 | 76.4 | 40 | 108 | 0.032 | 43.77 | 0.307 | 7 | 25.6 | 91.1 | 41 | 113 | 0.038 | 26.1 | 26 | 23.6 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 11.6064 |  | 16.2778 | 27.8842 | 3.0201 | MINIMUM | 109.6589 | 8731.2104 |  | 808.8106 |  |  |  | 11.581 | 12.6339 | 10.4987 | 1.4838 | 1.5274 | 1.391 | 0.70573 | 0.67633 | 0.72605 | 0.72605 | 0.5758 | 0.64178 | 2.2827 | 0 | 0.049317 | 0.050172 | 0.049137 | 1.0947 | 0.49902 | 0.09423 | 3.8772 | 0.66254 | 2.7891 | 1.1043 | 0.50955 | 0.099158 | 3.7334 | 0.57022 | 2.7355 |  | MIN | 0.68 | 10.7 | 23.7757 | 16.1675 | 6.01 | 12.1 | 15 | 1.0778 |  |  |  | MIN | 0.7 | 11 | 23.1273 | 16.1891 | 6.3 | 13 | 15 | 1.0793 |  |  |  | MIN | 0.72 | 11.7 | 23.0769 | 16.6154 | 6.19 | 14 | 15 | 1.1077 |  |  |  | 1.0778
AVERAGE | 6.255 | 12 | 15.8333 | 8.645 | 127.6667 | 173 | 14.1167 | 0.552 | 0.038 | 6.1517 | 9 | 0.078667 | 6.1967 | 9.3333 |  | 6.1717 | 9.6667 |  | 6.165 | 0.27525 | 3.75 | 0.71 | 12.525 | 10.425 | 0.73468 | 0.059667 | 6.205 | 0.22025 | 3.5 | 0.71 | 13.275 | 10.5 | 0.71807 | 6.1925 | 0.36175 | 4 | 0.7675 | 13.825 | 11.525 | 0.73861 | 0.024 | 1.3333 | 0.395 | 0.035 | 0.062167 | 0.012 | 1 | 0.59167 |  | 0.0345 | 1 | 0.46333 |  | 7.3933 | 0.051333 | 1 | 4.4 | 12.7333 | 20 | 54 | 0.016 | 7.295 | 0.051167 | 1.1667 | 4.2667 | 15.1833 | 20.5 | 56.5 | 0.019 | 4.35 | 4.3333 | 3.9333 |  |  | MAXIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 11.9016 |  | 18.4853 | 30.3869 | 3.0201 | MAXIMUM | 121.2891 | 9346.0844 |  | 824.6696 |  |  |  | 18.7006 | 19.3637 | 17.7501 | 1.6934 | 1.6934 | 1.6583 | 0.77631 | 0.75278 | 0.77631 | 0.79983 | 0.81426 | 0.74641 | 2.2827 | 9 | 0.051611 | 0.051611 | 0.051345 | 1.1269 | 0.50105 | 0.10208 | 4.0228 | 0.74376 | 3.821 | 1.1269 | 0.5122 | 0.14165 | 3.8406 | 0.67084 | 3.8058
MINIMUM | 6.09 | 10 | 14 | 8.33 | 122 | 169 | 13.7 | 0.531 | 0.03 | 6.05 | 8 | 0.057 | 6.06 | 8 |  | 6.08 | 9 |  | 6.01 | 0.172 | 3 | 0.68 | 12.1 | 9.3 | 0.66835 | 0.052 | 5.98 | 0.166 | 3 | 0.68 | 12.9 | 9.6 | 0.66678 | 5.99 | 0.243 | 3 | 0.72 | 13.7 | 10.7 | 0.68333 | 0.017 | 1 | 0.32 | 0.012 | 0.052 | 0.009 | 1 | 0.43 |  | 0.034 | 1 | 0.36 |  | 7.09 | 0.047 | 1 | 4.2 | 12.5 | 20 | 50 | 0.011 | 7.02 | 0.042 | 1 | 4.2 | 14.5 | 20 | 50 | 0.014 | 4.3 | 4.2 | 3.6 | [15 empty] | MIL/MIN |  | TOTAL | 76540 | 0 | 0 | 0 | 0 | 0 | 0 | 2830 | 2960 | 2910 | 1720 | 1780 | 1810 | 6740 | 6430 | 6720 | 6790 | 6824 | 6900 | 6000 | 0 | 4700 | 4730 | 5170 | 474 | 569 | 67 | 7645 | 1500 | 1055 | 263 | 320 | 41 | 3920 | 730 | 570
MAXIMUM | 6.34 | 15 | 18 | 9.32 | 131 | 177 | 14.6 | 0.571 | 0.046 | 6.32 | 10 | 0.097 | 6.35 | 10 |  | 6.38 | 10 |  | 6.3 | 0.551 | 6 | 0.74 | 13 | 11 | 0.76858 | 0.071 | 6.3 | 0.355 | 5 | 0.76 | 13.7 | 11 | 0.76858 | 6.32 | 0.616 | 6 | 0.84 | 14 | 12 | 0.78667 | 0.032 | 2 | 0.46 | 0.058 | 0.076 | 0.016 | 1 | 0.7 |  | 0.036 | 1 | 0.55 |  | 7.55 | 0.055 | 1 | 4.6 | 13 | 20 | 58 | 0.021 | 7.57 | 0.059 | 2 | 4.3 | 16 | 21 | 63 | 0.024 | 4.4 | 4.5 | 4.6 | [17 empty] | AVERAGE | 15308 | [6 empty] | 566 | 592 | 582 | 344 | 356 | 362 | 1348 | 1286 | 1344 | 1358 | 1364.8 | 1380 | 1200 |  | 940 | 946 | 1034 | 94.8 | 113.8 | 13.4 | 1529 | 300 | 211 | 52.6 | 64 | 8.2 | 784 | 146 | 114
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1733 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.616 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.68 | [5 empty] | 6.1875 |  |  |  |  | 0.036 |  |  |  |  | 0.68 | [6 empty] | 0.036 | [16 empty] | Pump Station MIN |  | 3.6 | [17 empty] | MINIMUM | 13500 | [6 empty] | 385 | 420 | 385 | 320 | 340 | 340 | 1200 | 1150 | 1250 | 1250 | 1080 | 1300 | 1200 |  | 860 | 880 | 950 | 88 | 106 | 12 | 1405 | 285 | 195 | 49 | 60 | 7 | 740 | 140 | 105
[90 empty] | MAXIMUM | 16800 | [6 empty] | 705 | 730 | 730 | 360 | 380 | 380 | 1420 | 1380 | 1400 | 1400 | 1704 | 1520 | 1200 |  | 1000 | 1000 | 1090 | 100 | 121 | 14 | 1600 | 310 | 275 | 56 | 68 | 10 | 830 | 150 | 150
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.536 |  | TOTAL MGD: |  | 3.527 |  |  | FINISHED SOUTH 1 |  | START: | 23823377 |  | END: | 23826904 |  |  | Alum | 4929 | 9846 | 9846 | 9192 | 9192 | 0 | [44 empty] | 0.68 | 10.7 | 23.7757 | 16.1675 | 6.01 | 12.1 | 15 | 1.0778
[73 empty] | FINISHED 2 | 15.24 |  | TOTAL MGD: |  | 8.009 |  |  | FINISHED SOUTH 2 |  | START: | 43422155 |  | END: | 43430164 |  |  | Caustic | 7004 | 6850 | 6850
[73 empty] | TOTAL RAW | 29.571 |  | TOTAL MGD: |  | 4.191 |  |  | FINISHED CONWAY |  | START: | 10075145 |  | END: | 10079336 |  |  | Hypochlorite | 11.5 |  | 30
[76 empty] | TOTAL MGD: |  | 11.049 |  |  | FINISHED PERRY |  | START: | 33439271 |  | END: | 33450320 |  |  | Phosphate | 1515
[76 empty] | TOTAL MGD: |  | 9.396 |  |  | RAW PLANT 1 |  | START: | 30603064 |  | END: | 30612460 |  |  | Fluoride | 1750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.548 |  |  | RAW PLANT 2 |  | START: | 30565668 |  | END: | 30575216 |  |  | Cal~Flo | 13.54 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.627 |  |  | RAW PLANT 3 |  | START: | 7093139 |  | END: | 7103766 |  |  | Zinc | 1052
[76 empty] | TOTAL MGD: |  | 1.083 |  |  | DECANT |  | START: | 1824888 |  | END: | 1825971 |  |  | Polymer | 6
[76 empty] | TOTAL MGD: |  | 1.2869 |  |  | BLOW DOWN |  | START: | 9075.8941 |  | END: | 9077.181 |  |  | NH3 | 8.11 |  | BI-SUL | 1650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 825
23826904
43430164
10079336
33450320
30612460
30575216
7103766
1825971
9077.181
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 29
DATE: | 2018-11-29 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2018-11-29 | [23 empty] | DATE: | 2018-11-29
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-29 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43433.0067 | 1,2,6 | 50 | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 | 0,1,2 | 11.6064 | 1,3 | 16.2778 | 27.8842 | 2.2604 | 43433.0067 | 110.4712 | 8731.2104 | 0 | 824.6696 | 0 | 0 | 0 | 11.581 | 12.6339 | 11.3168 | 1.5483 | 1.645 | 1.4838 | 0.77631 | 0.75278 | 0.77631 | 0.79983 | 0.5758 | 0.74641 | 2.2827 | 5 | 0.049317 | 0.050464 | 0.049654 | 1.0995 | 0.49902 | 0.10208 | 3.9983 | 0.70657 | 3.0923 | 1.1269 | 0.50955 | 0.099158 | 3.7695 | 0.67084 | 3.0036 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.248 | 3 | 0.62 | 12.5 | 9.5 | 0.68014 |  | 6.21 | 0.234 | 3 | 0.65 | 12.5 | 9.6 | 0.68604 | 6.22 | 0.201 | 3 | 0.62 | 13.5 | 10.7 | 0.71444 | [13 empty] | 7.41 | 0.047 | 1 | 3.8 | 12.4 |  |  |  | 7.37 | 0.053 | 1 | 4.1 | 14.9 |  |  |  | 4.3 | 4.3 | 3.9 | [18 empty] | 13600 | [6 empty] | 385 | 420 | 415 | 320 | 340 | 340 | 1320 | 1280 | 1320 | 1360 | 1080 | 1400 | 1200 |  | 860 | 880 | 960 | 88 | 106 | 13 | 1405 | 285 | 195 | 50 | 60 | 7 | 740 | 150 | 105 |  | 1:00 | 0.62 | 9.5 | 26.7789 | 16.6029 | 6.14 | 12.5 | 15 | 1.1069 | 10 | 6.5 | 0.56014 | 1:00 | 0.65 | 9.6 | 26.5 | 17.225 | 6.21 | 12.5 | 15 | 1.1483 | 10 | 6.5 | 0.56604 | 1:00 | 0.62 | 10.7 | 25.2336 | 15.6449 | 6.22 | 13.5 | 15 | 1.043 | 10 | 6.5 | 0.59444
2:00 | [72 empty] | 43433.1022 | 1,2,3,6 | 50 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | 0,1,2 | 9.8712 | 1,3 | 18.7358 | 28.607 | 2.2604 | 43433.1022 | 109.7562 | 8731 | 0 | 824.6696 | 0 | 0 | 0 | 10.9064 | 11.8979 | 10.7159 | 1.5443 | 1.6352 | 1.5662 | 0.73662 | 0.72001 | 0.76432 | 0.77539 | 0.54523 | 0.74716 | 2.2827 | 5 | 0.05195 | 0.050066 | 0.049827 | 1.0908 | 0.49941 | 0.1032 | 4.0061 | 0.70986 | 3.2007 | 1.1069 | 0.48124 | 0.093649 | 3.7968 | 0.67581 | 3.3771 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.31 | 11 | 16 | 8.29 | 131 | 172 | 13.9 | 0.567 |  | 6 | 8 | 0.092 | 6.1 | 8 |  | 6.06 | 9 | [8 empty] | 0.062 | [14 empty] | 0.018 | 1 | 0.46 |  | 0.061 | 0.016 | 1 | 0.59 |  | 0.051 | 1 | 0.5 | [38 empty] | 14320 | [6 empty] | 385 | 420 | 415 | 340 | 360 | 380 | 1330 | 1300 | 1380 | 1400 | 1080 | 1480 | 1200 |  | 965 | 930 | 1020 | 93 | 113 | 14 | 1500 | 305 | 215 | 52 | 60 | 7 | 790 | 160 | 125 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43433.3357 | 1,2,3,6 | 43 | 10.3 | 10.3 | 11.3 | 31.9 | 9.8 | 9.8 | 10.8 | 30.4 | 0,1,2 | 9.8712 | 1,3 | 18.7358 | 28.607 | 2.2604 | 43433.3357 | 104.6976 | 9038.6474 | 0 | 808.8106 | 0 | 0 | 0 | 9.49 | 10.1982 | 9.1666 | 1.5897 | 1.5897 | 1.525 | 0.72001 | 0.69232 | 0.72001 | 0.7477 | 0.53008 | 0.70678 | 2.2827 | 5.5 | 0.050066 | 0.050066 | 0.050804 | 1.1142 | 0.49499 | 0.1032 | 3.9748 | 0.69823 | 3.3495 | 1.1069 | 0.49728 | 0.10703 | 3.7946 | 0.67581 | 3.3771 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.31 | 0.048 | 1 | 4.2 | 12.3 |  |  |  | 7.25 | 0.052 | 1 | 4.4 | 14.8 |  |  |  | 4.1 | 4.3 | 4.5 | [18 empty] | 13660 | [6 empty] | 335 | 360 | 355 | 350 | 350 | 370 | 1300 | 1250 | 1300 | 1350 | 1050 | 1400 | 1200 |  | 930 | 930 | 1040 | 95 | 112 | 14 | 1450 | 300 | 225 | 52 | 62 | 8 | 780 | 160 | 125 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43433.8472 | 1,2,3,6 | 43 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 0,1,2 | 15.2554 | 1,3 | 16.9618 | 32.2171 | 2.2604 | 43433.8472 | 104.703 | 8854.1852 | 0 | 808.8106 | 0 | 0 | 0 | 8.8861 | 9.5492 | 8.6319 | 1.5261 | 1.6109 | 1.4708 | 0.68456 | 0.68456 | 0.70531 | 0.7468 | 0.47539 | 0.66555 | 2.2827 | 7 | 0.050246 | 0.050246 | 0.049546 | 1.0947 | 0.49911 | 0.096324 | 3.9991 | 0.71684 | 3.4041 | 1.1194 | 0.5 | 0.10051 | 3.7527 | 0.65451 | 3.7297 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.26 | 15 | 16 | 8.33 | 127 | 174 | 13.1 | 0.56 |  | 6.11 | 10 | 0.098 | 6.15 | 10 |  | 6.12 | 10 | [8 empty] | 0.062 | [14 empty] | 0.034 | 1 | 0.47 |  | 0.063 | 0.01 | 1 | 0.62 |  | 0.041 | 1 | 0.58 | [38 empty] | 14560 | [6 empty] | 335 | 360 | 355 | 360 | 380 | 380 | 1320 | 1320 | 1360 | 1440 | 1000 | 1400 | 1200 |  | 1000 | 1000 | 1080 | 100 | 121 | 14 | 1620 | 330 | 245 | 56 | 62 | 8 | 820 | 165 | 147 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.039 | [9 empty] | 6.22 | 0.266 | 3 | 0.67 | 11.5 | 10.3 | 0.72731 |  | 6.28 | 0.264 | 3 | 0.73 | 11.9 | 10.3 | 0.72731 | 6.27 | 0.396 | 3 | 0.67 | 12.9 | 11.3 | 0.74778 |  |  |  | 0.016 | [9 empty] | 7.35 | 0.054 | 2 | 3.8 | 11.9 | 22 | 55 | 0.019 | 7.27 | 0.0456 | 2 | 4.1 | 14.8 | 20 | 50 | 0.014 | 4.1 | 4.3 | 3.7 | [55 empty] | 9:00 | 0.67 | 10.3 | 24.699 | 16.5483 | 6.22 | 11.5 | 15 | 1.1032 | 10 | 6.5 | 0.60731 | 9:00 | 0.73 | 10.3 | 24.699 | 18.0303 | 6.28 | 11.9 | 15 | 1.202 | 10 | 6.5 | 0.60731 | 9:00 | 0.67 | 11.3 | 23.8938 | 16.0088 | 6.27 | 12.9 | 15 | 1.0673 | 10 | 6.5 | 0.62778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.29 | 11 | 15 | 8.29 | 135 | 175 | 13.1 | 0.578 |  | 6.21 | 7 | 0.099 | 6.23 | 7 |  | 6.2 | 7 | [8 empty] | 0.061 | [14 empty] | 0.021 | 1 | 0.4 |  | 0.061 | 0.015 | 1 | 0.61 |  | 0.048 | 1 | 0.53 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.272 | 3 | 0.72 | 12 | 10.3 | 0.72731 |  | 6.21 | 0.27 | 3 | 0.74 | 13 | 10.3 | 0.72731 | 6.25 | 0.336 | 3 | 0.68 | 13.5 | 11.3 | 0.74778 | [13 empty] | 7.25 | 0.049 | 1 | 4 | 12 |  |  |  | 7.15 | 0.052 | 1 | 4.2 | 15.2 |  |  |  | 4 | 4.3 | 3.6 | [55 empty] | 13:00 | 0.72 | 10.3 | 24.699 | 17.7833 | 6.12 | 12 | 15 | 1.1856 | 10 | 6.5 | 0.60731 | 13:00 | 0.74 | 10.3 | 24.699 | 18.2773 | 6.21 | 13 | 15 | 1.2185 | 10 | 6.5 | 0.60731 | 13:00 | 0.68 | 11.3 | 23.8938 | 16.2478 | 6.25 | 13.5 | 15 | 1.0832 | 10 | 6.5 | 0.62778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.25 | 12 | 15 | 8.1 | 128 | 172 | 13.8 | 0.543 |  | 6.12 | 9 | 0.087 | 6.16 | 9 |  | 6.11 | 9 | [8 empty] | 0.066 | [14 empty] | 0.021 | 1 | 0.38 |  | 0.068 | 0.011 | 1 | 0.58 |  | 0.048 | 1 | 0.5 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.22 | 0.048 | 1 | 4 | 12 |  |  |  | 7.21 | 0.054 | 1 | 4.4 | 15.2 |  |  |  | 4 | 4.3 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.32 | 13 | 18 | 8.19 | 134 | 173 | 13.7 | 0.562 |  | 6.19 | 9 | 0.114 | 6.2 | 10 |  | 6.16 | 10 | [8 empty] | 0.065 | [14 empty] | 0.024 | 2 | 0.46 |  | 0.064 | 0.01 | 1 | 0.51 |  | 0.042 | 1 | 0.39 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.032 | [9 empty] | 6.11 | 0.337 | 4 | 0.69 | 12.2 | 10.8 | 0.75679 |  | 6.14 | 0.391 | 4 | 0.76 | 12.8 | 11.1 | 0.77448 | 6.18 | 0.462 | 5 | 0.71 | 13.6 | 12.2 | 0.79778 |  |  |  | 0.009 |  |  |  |  | 0.017 |  |  |  | 0.014 | 7.35 | 0.05 | 1 | 3.9 | 12.1 | 20 | 58 | 0.014 | 7.38 | 0.051 | 1 | 4.5 | 15.2 | 21 | 55 | 0.011 | 3.8 | 4.2 | 3.8 | [55 empty] | 21:00 | 0.69 | 10.8 | 23.5556 | 16.2533 | 6.11 | 12.2 | 15 | 1.0836 | 10 | 6.5 | 0.63679 | 21:00 | 0.76 | 11.1 | 22.9189 | 17.4184 | 6.14 | 12.8 | 15 | 1.1612 | 10 | 6.5 | 0.65448 | 21:00 | 0.71 | 12.2 | 22.1311 | 15.7131 | 6.18 | 13.6 | 15 | 1.0475 | 10 | 6.5 | 0.67778
22:00 | [72 empty] | DOSE |  | TOTAL | 41.3 | 41.3 | 45.3 | 127.9 | 39.3 | 39.3 | 43.3 | 121.9 | 0 | 46.6042 | 0 | 70.7112 | 117.3154 | 9.0415 | TOTAL | 429.628 | 35355.043 | 0 | 3266.9604 | 0 | 0 | 0 | 40.8635 | 44.2792 | 39.8311 | 6.2085 | 6.4808 | 6.0458 | 2.9175 | 2.8497 | 2.9659 | 3.0697 | 2.1265 | 2.8659 | 9.1308 | 22.5 | 0.20158 | 0.20084 | 0.19983 | 4.3992 | 1.9925 | 0.40482 | 15.9782 | 2.8315 | 13.0466 | 4.46 | 1.9881 | 0.40035 | 15.1136 | 2.677 | 13.4876 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.31 | 14 | 21 | 8.45 | 132 | 176 | 13.4 | 0.564 |  | 6.21 | 10 | 0.099 | 6.2 | 10 |  | 6.16 | 10 | [8 empty] | 0.066 | [14 empty] | 0.023 | 1 | 0.45 |  | 0.065 | 0.015 | 1 | 0.53 |  | 0.04 | 2 | 0.42 | [22 empty] | AVERAGE | 10.325 | 10.325 | 11.325 | 31.975 | 9.825 | 9.825 | 10.825 | 30.475 |  | 11.651 |  | 17.6778 | 29.3288 | 2.2604 | AVERAGE | 107.407 | 8838.7607 |  | 816.7401 | 0 | 0 | 0 | 10.2159 | 11.0698 | 9.9578 | 1.5521 | 1.6202 | 1.5114 | 0.72938 | 0.71242 | 0.74149 | 0.76743 | 0.53162 | 0.71647 | 2.2827 | 5.625 | 0.050395 | 0.05021 | 0.049958 | 1.0998 | 0.49813 | 0.1012 | 3.9946 | 0.70788 | 3.2616 | 1.115 | 0.49702 | 0.10009 | 3.7784 | 0.66925 | 3.3719 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.74 | 76 | 101 | 49.65 | 787 | 1042 | 81 | 3.374 | 0.071 | 36.84 | 53 | 0.589 | 37.04 | 54 | 0 | 36.81 | 55 | 0 | 24.59 | 1.123 | 13 | 2.7 | 48.2 | 40.9 | 2.8916 | 0.382 | 24.84 | 1.159 | 13 | 2.88 | 50.2 | 41.3 | 2.9151 | 24.92 | 1.395 | 14 | 2.68 | 53.5 | 45.5 | 3.0078 |  | 7 | 2.62 | 0.025 | 0.382 | 0.077 | 6 | 3.44 | 0.017 | 0.27 | 7 | 2.92 | 0.014 | 43.89 | 0.296 | 7 | 23.7 | 72.7 | 42 | 113 | 0.033 | 43.63 | 0.3076 | 7 | 25.7 | 90.1 | 41 | 105 | 0.025 | 24.3 | 25.7 | 23.3 |  |  | MINIMUM | 9.7 | 9.7 | 10.7 | 30.1 | 9.2 | 9.2 | 10.2 | 28.6 |  | 9.8712 |  | 16.2778 | 27.8842 | 2.2604 | MINIMUM | 104.6976 | 8731 |  | 808.8106 |  |  |  | 8.8861 | 9.5492 | 8.6319 | 1.5261 | 1.5897 | 1.4708 | 0.68456 | 0.68456 | 0.70531 | 0.7468 | 0.47539 | 0.66555 | 2.2827 | 5 | 0.049317 | 0.050066 | 0.049546 | 1.0908 | 0.49499 | 0.096324 | 3.9748 | 0.69823 | 3.0923 | 1.1069 | 0.48124 | 0.093649 | 3.7527 | 0.65451 | 3.0036 |  | MIN | 0.69 | 10.8 | 23.5556 | 16.2533 | 6.11 | 12.2 | 15 | 1.0836 |  |  |  | MIN | 0.65 | 9.6 | 26.5 | 17.225 | 6.21 | 12.5 | 15 | 1.1483 |  |  |  | MIN | 0.62 | 10.7 | 25.2336 | 15.6449 | 6.22 | 13.5 | 15 | 1.043 |  |  |  | 1.043
AVERAGE | 6.29 | 12.6667 | 16.8333 | 8.275 | 131.1667 | 173.6667 | 13.5 | 0.56233 | 0.0355 | 6.14 | 8.8333 | 0.098167 | 6.1733 | 9 |  | 6.135 | 9.1667 |  | 6.1475 | 0.28075 | 3.25 | 0.675 | 12.05 | 10.225 | 0.72289 | 0.063667 | 6.21 | 0.28975 | 3.25 | 0.72 | 12.55 | 10.325 | 0.72879 | 6.23 | 0.34875 | 3.5 | 0.67 | 13.375 | 11.375 | 0.75194 |  | 1.1667 | 0.43667 | 0.0125 | 0.063667 | 0.012833 | 1 | 0.57333 | 0.017 | 0.045 | 1.1667 | 0.48667 | 0.014 | 7.315 | 0.049333 | 1.1667 | 3.95 | 12.1167 | 21 | 56.5 | 0.0165 | 7.2717 | 0.051267 | 1.1667 | 4.2833 | 15.0167 | 20.5 | 52.5 | 0.0125 | 4.05 | 4.2833 | 3.8833 |  |  | MAXIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 15.2554 |  | 18.7358 | 32.2171 | 2.2604 | MAXIMUM | 110.4712 | 9038.6474 |  | 824.6696 |  |  |  | 11.581 | 12.6339 | 11.3168 | 1.5897 | 1.645 | 1.5662 | 0.77631 | 0.75278 | 0.77631 | 0.79983 | 0.5758 | 0.74716 | 2.2827 | 7 | 0.05195 | 0.050464 | 0.050804 | 1.1142 | 0.49941 | 0.1032 | 4.0061 | 0.71684 | 3.4041 | 1.1269 | 0.50955 | 0.10703 | 3.7968 | 0.67581 | 3.7297
MINIMUM | 6.25 | 11 | 15 | 8.1 | 127 | 172 | 13.1 | 0.543 | 0.032 | 6 | 7 | 0.087 | 6.1 | 7 |  | 6.06 | 7 |  | 6.11 | 0.248 | 3 | 0.62 | 11.5 | 9.5 | 0.68014 | 0.061 | 6.14 | 0.234 | 3 | 0.65 | 11.9 | 9.6 | 0.68604 | 6.18 | 0.201 | 3 | 0.62 | 12.9 | 10.7 | 0.71444 |  | 1 | 0.38 | 0.009 | 0.061 | 0.01 | 1 | 0.51 | 0.017 | 0.04 | 1 | 0.39 | 0.014 | 7.22 | 0.047 | 1 | 3.8 | 11.9 | 20 | 55 | 0.014 | 7.15 | 0.0456 | 1 | 4.1 | 14.8 | 20 | 50 | 0.011 | 3.8 | 4.2 | 3.6 | [15 empty] | MIL/MIN |  | TOTAL | 56140 | 0 | 0 | 0 | 0 | 0 | 0 | 1440 | 1560 | 1540 | 1370 | 1430 | 1470 | 5270 | 5150 | 5360 | 5550 | 4210 | 5680 | 4800 | 0 | 3755 | 3740 | 4100 | 376 | 452 | 55 | 5975 | 1220 | 880 | 210 | 244 | 30 | 3130 | 635 | 502
MAXIMUM | 6.32 | 15 | 21 | 8.45 | 135 | 176 | 13.9 | 0.578 | 0.039 | 6.21 | 10 | 0.114 | 6.23 | 10 |  | 6.2 | 10 |  | 6.22 | 0.337 | 4 | 0.72 | 12.5 | 10.8 | 0.75679 | 0.066 | 6.28 | 0.391 | 4 | 0.76 | 13 | 11.1 | 0.77448 | 6.27 | 0.462 | 5 | 0.71 | 13.6 | 12.2 | 0.79778 |  | 2 | 0.47 | 0.016 | 0.068 | 0.016 | 1 | 0.62 | 0.017 | 0.051 | 2 | 0.58 | 0.014 | 7.41 | 0.054 | 2 | 4.2 | 12.4 | 22 | 58 | 0.019 | 7.38 | 0.054 | 2 | 4.5 | 15.2 | 21 | 55 | 0.014 | 4.3 | 4.3 | 4.5 | [17 empty] | AVERAGE | 14035 | [6 empty] | 360 | 390 | 385 | 342.5 | 357.5 | 367.5 | 1317.5 | 1287.5 | 1340 | 1387.5 | 1052.5 | 1420 | 1200 |  | 938.75 | 935 | 1025 | 94 | 113 | 13.75 | 1493.75 | 305 | 220 | 52.5 | 61 | 7.5 | 782.5 | 158.75 | 125.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1494 |  | TOTAL AVG COAG ALK: |  |  |  | 9 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.462 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.62 | [5 empty] | 6.1958 |  |  |  |  | 0.051 |  |  |  |  | 0.62 | [23 empty] | Pump Station MIN |  | 3.6 | [17 empty] | MINIMUM | 13600 | [6 empty] | 335 | 360 | 355 | 320 | 340 | 340 | 1300 | 1250 | 1300 | 1350 | 1000 | 1400 | 1200 |  | 860 | 880 | 960 | 88 | 106 | 13 | 1405 | 285 | 195 | 50 | 60 | 7 | 740 | 150 | 105
[63 empty] | 0 | [26 empty] | MAXIMUM | 14560 | [6 empty] | 385 | 420 | 415 | 360 | 380 | 380 | 1330 | 1320 | 1380 | 1440 | 1080 | 1480 | 1200 |  | 1000 | 1000 | 1080 | 100 | 121 | 14 | 1620 | 330 | 245 | 56 | 62 | 8 | 820 | 165 | 147
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.551 |  | TOTAL MGD: |  | 0.01 |  |  | FINISHED SOUTH 1 |  | START: | 23826904 |  | END: | 23826914 |  |  | Alum | 345 | 8023 | 8023 | 7679 | 7679 | 0 | [44 empty] | 0.62 | 10.7 | 25.2336 | 15.6449 | 6.22 | 13.5 | 15 | 1.043
[73 empty] | FINISHED 2 | 16.71 |  | TOTAL MGD: |  | 12.541 |  |  | FINISHED SOUTH 2 |  | START: | 43430164 |  | END: | 43442705 |  |  | Caustic | 6630 | 6753 | 6753
[73 empty] | TOTAL RAW | 33.423 |  | TOTAL MGD: |  | 4.333 |  |  | FINISHED CONWAY |  | START: | 10079336 |  | END: | 10083669 |  |  | Hypochlorite | 12 |  | 24
[76 empty] | TOTAL MGD: |  | 12.377 |  |  | FINISHED PERRY |  | START: | 33450320 |  | END: | 33462697 |  |  | Phosphate | 1473
[76 empty] | TOTAL MGD: |  | 10.641 |  |  | RAW PLANT 1 |  | START: | 30612460 |  | END: | 30623101 |  |  | Fluoride | 1750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.778 |  |  | RAW PLANT 2 |  | START: | 30575216 |  | END: | 30585994 |  |  | Cal~Flo | 9.41 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.004 |  |  | RAW PLANT 3 |  | START: | 7103766 |  | END: | 7115770 |  |  | Zinc | 1058
[76 empty] | TOTAL MGD: |  | 1.128 |  |  | DECANT |  | START: | 1825971 |  | END: | 1827099 |  |  | Polymer | 7
[76 empty] | TOTAL MGD: |  | 1.1798 |  |  | BLOW DOWN |  | START: | 9077.181 |  | END: | 9078.3608 |  |  | NH3 | 7.88 |  | BI-SUL | 1650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 809
23826914
43442705
10083669
33462697
30623101
30585994
7115770
1827099
9078.3608
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 30
DATE: | 2018-11-30 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2018-11-30 | [23 empty] | DATE: | 2018-11-30
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-11-30 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43434.0161 | 1,2,3,6 | 43 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 0,1,2 | 15.2554 | 1,3 | 16.9618 | 32.2171 | 2.4651 | 43434.0161 | 104.703 | 8854.1852 | 0 | 808.8106 | 0 | 0 | 0 | 8.8861 | 9.5492 | 8.6319 | 1.5261 | 1.6109 | 1.4708 | 0.68456 | 0.68456 | 0.70531 | 0.7468 | 0.47539 | 0.66555 | 2.2827 | 7 | 0.050246 | 0.050246 | 0.049546 | 1.0947 | 0.49911 | 0.096324 | 3.9991 | 0.71684 | 3.4041 | 1.1194 | 0.5 | 0.10051 | 3.7527 | 0.65451 | 3.7297 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.15 | 0.403 | 4 | 0.7 | 11.9 | 11.1 | 0.77448 |  | 6.27 | 0.357 | 4 | 0.8 | 12.6 | 11.1 | 0.77448 | 6.23 | 0.352 | 4 | 0.78 | 13.3 | 12.5 | 0.81444 | [13 empty] | 7.55 | 0.051 | 1 | 4.2 | 12.1 |  |  |  | 7.63 | 0.05 | 1 | 4.3 | 15.1 |  |  |  | 3.7 | 4.1 | 3.8 | [18 empty] | 14560 | [6 empty] | 335 | 360 | 355 | 360 | 380 | 380 | 1320 | 1320 | 1360 | 1440 | 1000 | 1400 | 1200 |  | 1000 | 1000 | 1080 | 100 | 121 | 14 | 1620 | 330 | 245 | 56 | 70 | 8 | 820 | 165 | 147 |  | 1:00 | 0.7 | 11.1 | 22.9189 | 16.0432 | 6.15 | 11.9 | 15 | 1.0695 | 10 | 6.5 | 0.65448 | 1:00 | 0.8 | 11.1 | 22.9189 | 18.3351 | 6.27 | 12.6 | 15 | 1.2223 | 10 | 6.5 | 0.65448 | 1:00 | 0.78 | 12.5 | 21.6 | 16.848 | 6.23 | 13.3 | 15 | 1.1232 | 10 | 6.5 | 0.69444
2:00 | [72 empty] | 43434.3123 | 1,2,3,6 | 48 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 0,1,2 | 15.2554 | 1,3 | 16.9618 | 32.2171 | 2.4651 | 43434.3123 | 104.8468 | 9530.5466 | 0 | 840.5286 | 0 | 0 | 0 | 8.8861 | 9.5492 | 8.6319 | 1.5261 | 1.6957 | 1.3934 | 0.69493 | 0.67419 | 0.70531 | 0.68456 | 0.51342 | 0.59424 | 2.7392 | 8 | 0.050246 | 0.050246 | 0.052299 | 1.0947 | 0.49911 | 0.096324 | 3.9006 | 0.73857 | 3.4041 | 1.1194 | 0.5 | 0.10051 | 3.6421 | 0.63468 | 3.7297 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.28 | 10 | 20 | 8.17 | 137 | 180 | 13.5 | 0.569 |  | 6.13 | 9 | 0.096 | 6.14 | 9 |  | 6.13 | 10 | [8 empty] | 0.065 | [14 empty] | 0.02 | 1 | 0.36 |  | 0.066 | 0.01 | 1 | 0.49 |  | 0.039 | 1 | 0.31 | [38 empty] | 14580 | [6 empty] | 335 | 360 | 355 | 360 | 400 | 360 | 1340 | 1300 | 1360 | 1320 | 1080 | 1250 | 1440 |  | 1000 | 1000 | 1140 | 100 | 121 | 14 | 1600 | 340 | 245 | 56 | 0.7 | 8 | 840 | 160 | 147 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 13:10 | 1,2,3,6 | 48 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 0,1,2 | 15.2554 | 1,3 | 16.9618 | 32.2171 | 2.4651 | 43434.7102 | 119.9482 | 9223.1096 | 0 | 843.7004 | 0 | 0 | 0 | 14.1912 | 14.8543 | 13.4949 | 1.5261 | 1.6957 | 1.3934 | 0.69493 | 0.67419 | 0.70531 | 0.68456 | 0.51342 | 0.59424 | 2.7392 | 8 | 0.050246 | 0.050246 | 0.052299 | 1.0947 | 0.49911 | 0.096324 | 3.9006 | 0.73857 | 3.4041 | 1.1194 | 0.52 | 0.10051 | 3.6421 | 0.63468 | 3.7297 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.47 | 0.05 | 1 | 3.7 | 12.1 |  |  |  | 7.43 | 0.048 | 1 | 4.2 | 15 |  |  |  | 3.7 | 4.1 | 4.4 | [18 empty] | 16680 | [6 empty] | 535 | 560 | 555 | 360 | 400 | 360 | 1340 | 1300 | 1360 | 1320 | 1080 | 1250 | 1440 |  | 1000 | 1000 | 1140 | 100 | 121 | 14 | 1600 | 340 | 245 | 56 | 0.7 | 8 | 840 | 160 | 147 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43434.8424 | 1,2,3,6 | 44 | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 | 0,1,2 | 12.7325 | 1,3 | 18.8798 | 31.6123 | 2.4651 | 43434.8424 | 118.7976 | 9100.1348 | 0 | 843.7004 | 0 | 0 | 0 | 14.3238 | 14.987 | 13.7381 | 1.5261 | 1.6957 | 1.5483 | 0.62233 | 0.64307 | 0.66382 | 0.68456 | 0.45637 | 0.6085 | 2.0925 | 3 | 0.050246 | 0.050246 | 0.049546 | 1.0947 | 0.49911 | 0.096324 | 4.0139 | 0.69512 | 3.4041 | 1.1194 | 0.52727 | 0.10051 | 3.8137 | 0.63468 | 3.7297 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.21 | 12 | 17 | 8.44 | 129 | 176 | 12.7 | 0.562 |  | 6.14 | 10 | 0.092 | 6.16 | 10 |  | 6.12 | 10 | [8 empty] | 0.064 | [14 empty] | 0.022 | 1 | 0.34 |  | 0.063 | 0.011 | 1 | 0.78 |  | 0.038 | 1 | 0.48 | [38 empty] | 16520 | [6 empty] | 540 | 565 | 565 | 360 | 400 | 400 | 1200 | 1240 | 1280 | 1320 | 960 | 1280 | 1100 |  | 1000 | 1000 | 1080 | 100 | 121 | 14 | 1590 | 320 | 245 | 56 | 70 | 8 | 790 | 160 | 147 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.043 | [9 empty] | 6.18 | 0.406 | 4 | 0.72 | 11.8 | 11 | 0.76858 |  | 6.26 | 0.4 | 5 | 0.82 | 12.2 | 11 | 0.76858 | 6.2 | 0.366 | 5 | 0.69 | 13 | 12 | 0.78667 |  |  |  | 0.015 |  |  |  |  | 0.016 |  |  |  | 0.014 | 7.57 | 0.051 | 1 | 4.4 | 11.6 | 17 | 68 | 0.017 | 7.41 | 0.058 | 1 | 4.6 | 15.1 | 17 | 72 | 0.019 | 3.6 | 4.2 | 4.1 | [55 empty] | 9:00 | 0.72 | 11 | 23.1273 | 16.6516 | 6.18 | 11.8 | 15 | 1.1101 | 10 | 6.5 | 0.64858 | 9:00 | 0.82 | 11 | 23.1273 | 18.9644 | 6.26 | 12.2 | 15 | 1.2643 | 10 | 6.5 | 0.64858 | 9:00 | 0.69 | 12 | 22.5 | 15.525 | 6.2 | 13 | 15 | 1.035 | 10 | 6.5 | 0.66667
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.39 | 13 | 17 | 8.03 | 134 | 183 | 13.1 | 0.572 |  | 6.09 | 9 | 0.074 | 6.09 | 9 |  | 6.03 | 9 | [8 empty] | 0.064 | [14 empty] | 0.021 | 1 | 0.62 |  | 0.066 | 0.017 | 1 | 0.72 |  | 0.036 | 1 | 0.47 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.4 | 4 | 0.68 | 12.4 | 11 | 0.76858 |  | 6.25 | 0.345 | 5 | 0.81 | 12.7 | 11 | 0.76858 | 6.21 | 0.435 | 5 | 0.73 | 13.3 | 12 | 0.78667 | [13 empty] | 7.23 | 0.058 | 1 | 4.1 | 12.1 |  |  |  | 7.2 | 0.059 | 2 | 4.2 | 14.8 |  |  |  | 3.7 | 4 | 3.4 | [55 empty] | 13:00 | 0.68 | 11 | 23.1273 | 15.7265 | 6.12 | 12.4 | 15 | 1.0484 | 10 | 6.5 | 0.64858 | 13:00 | 0.81 | 11 | 23.1273 | 18.7331 | 6.25 | 12.7 | 15 | 1.2489 | 10 | 6.5 | 0.64858 | 13:00 | 0.73 | 12 | 22.5 | 16.425 | 6.21 | 13.3 | 15 | 1.095 | 10 | 6.5 | 0.66667
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.33 | 12 | 18 | 8.08 | 129 | 174 | 13.2 | 0.574 |  | 6.24 | 8 | 0.074 | 6.15 | 9 |  | 6.08 | 8 | [8 empty] | 0.068 | [14 empty] | 0.024 | 1 | 0.55 |  | 0.069 | 0.015 | 2 | 0.89 |  | 0.039 | 2 | 0.6 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.11 | 0.06 | 1 | 4.2 | 12.3 |  |  |  | 7.12 | 0.06 | 2 | 4.4 | 14.6 |  |  |  | 3.9 | 4 | 3.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.32 | 12 | 20 | 9.05 | 132 | 174 | 13.8 | 0.544 |  | 6.17 | 9 | 0.075 | 6.16 | 10 |  | 6.17 | 9 | [8 empty] | 0.05 | [14 empty] | 0.021 | 1 | 0.49 |  | 0.051 | 0.016 | 1 | 0.63 |  | 0.044 | 2 | 0.68 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.03 | [9 empty] | 6.15 | 0.276 | 4 | 0.74 | 12.2 | 10.5 | 0.7391 |  | 6.24 | 0.269 | 5 | 0.95 | 13.1 | 10.5 | 0.7391 | 6.23 | 0.25 | 5 | 0.82 | 13.8 | 11.9 | 0.78111 |  |  |  | 0.009 | [9 empty] | 7.44 | 0.049 | 1 | 4 | 12.1 | 20 | 45 | 0.012 | 7.31 | 0.052 | 1 | 4.4 | 12.1 | 20 | 45 | 0.012 | 4.1 | 4.3 | 4 | [55 empty] | 21:00 | 0.74 | 10.5 | 24.2286 | 17.9291 | 6.15 | 12.2 | 15 | 1.1953 | 10 | 6.5 | 0.6191 | 21:00 | 0.95 | 10.5 | 24.2286 | 23.0171 | 6.24 | 13.1 | 15 | 1.5345 | 10 | 6.5 | 0.6191 | 21:00 | 0.82 | 11.9 | 22.6891 | 18.605 | 6.23 | 13.8 | 15 | 1.2403 | 10 | 6.5 | 0.66111
22:00 | [72 empty] | DOSE |  | TOTAL | 44 | 44 | 48 | 136 | 42 | 42 | 46 | 130 | 0 | 58.4986 | 0 | 69.7651 | 128.2637 | 9.8605 | TOTAL | 448.2957 | 36707.9762 | 0 | 3336.7401 | 0 | 0 | 0 | 46.2872 | 48.9398 | 44.4967 | 6.1046 | 6.6981 | 5.806 | 2.6968 | 2.676 | 2.7797 | 2.8005 | 1.9586 | 2.4625 | 9.8536 | 26 | 0.20098 | 0.20098 | 0.20369 | 4.3788 | 1.9964 | 0.3853 | 15.8142 | 2.8891 | 13.6165 | 4.4778 | 2.0473 | 0.40205 | 14.8505 | 2.5585 | 14.9189 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.31 | 13 | 19 | 7.95 | 130 | 172 | 13.8 | 0.548 |  | 6.19 | 10 | 0.083 | 6.16 | 10 |  | 6.18 | 10 | [8 empty] | 0.063 | [14 empty] | 0.021 | 1 | 0.52 |  | 0.064 | 0.015 | 1 | 0.69 |  | 0.039 | 1 | 0.5 | [22 empty] | AVERAGE | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 14.6246 |  | 17.4413 | 32.0659 | 2.4651 | AVERAGE | 112.0739 | 9176.9941 |  | 834.185 | 0 | 0 | 0 | 11.5718 | 12.2349 | 11.1242 | 1.5261 | 1.6745 | 1.4515 | 0.67419 | 0.669 | 0.69493 | 0.70012 | 0.48965 | 0.61563 | 2.4634 | 6.5 | 0.050246 | 0.050246 | 0.050923 | 1.0947 | 0.49911 | 0.096324 | 3.9535 | 0.72228 | 3.4041 | 1.1194 | 0.51182 | 0.10051 | 3.7126 | 0.63964 | 3.7297 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.84 | 72 | 111 | 49.72 | 791 | 1059 | 80.1 | 3.369 | 0.073 | 36.96 | 55 | 0.494 | 36.86 | 57 | 0 | 36.71 | 56 | 0 | 24.6 | 1.485 | 16 | 2.84 | 48.3 | 43.6 | 3.0508 | 0.374 | 25.02 | 1.371 | 19 | 3.38 | 50.6 | 43.6 | 3.0508 | 24.87 | 1.403 | 19 | 3.02 | 53.4 | 48.4 | 3.1689 | 0.129 | 6 | 2.88 | 0.024 | 0.379 | 0.084 | 7 | 4.2 | 0.016 | 0.235 | 8 | 3.04 | 0.014 | 44.37 | 0.319 | 6 | 24.6 | 72.3 | 37 | 113 | 0.029 | 44.1 | 0.327 | 8 | 26.1 | 86.7 | 37 | 117 | 0.031 | 22.7 | 24.7 | 23.2 |  |  | MINIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 12.7325 |  | 16.9618 | 31.6123 | 2.4651 | MINIMUM | 104.703 | 8854.1852 |  | 808.8106 |  |  |  | 8.8861 | 9.5492 | 8.6319 | 1.5261 | 1.6109 | 1.3934 | 0.62233 | 0.64307 | 0.66382 | 0.68456 | 0.45637 | 0.59424 | 2.0925 | 3 | 0.050246 | 0.050246 | 0.049546 | 1.0947 | 0.49911 | 0.096324 | 3.9006 | 0.69512 | 3.4041 | 1.1194 | 0.5 | 0.10051 | 3.6421 | 0.63468 | 3.7297 |  | MIN | 0.68 | 11 | 23.1273 | 15.7265 | 6.12 | 12.4 | 15 | 1.0484 |  |  |  | MIN | 0.8 | 11.1 | 22.9189 | 18.3351 | 6.27 | 12.6 | 15 | 1.2223 |  |  |  | MIN | 0.69 | 12 | 22.5 | 15.525 | 6.2 | 13 | 15 | 1.035 |  |  |  | 1.035
AVERAGE | 6.3067 | 12 | 18.5 | 8.2867 | 131.8333 | 176.5 | 13.35 | 0.5615 | 0.0365 | 6.16 | 9.1667 | 0.082333 | 6.1433 | 9.5 |  | 6.1183 | 9.3333 |  | 6.15 | 0.37125 | 4 | 0.71 | 12.075 | 10.9 | 0.76269 | 0.062333 | 6.255 | 0.34275 | 4.75 | 0.845 | 12.65 | 10.9 | 0.76269 | 6.2175 | 0.35075 | 4.75 | 0.755 | 13.35 | 12.1 | 0.79222 | 0.0215 | 1 | 0.48 | 0.012 | 0.063167 | 0.014 | 1.1667 | 0.7 | 0.016 | 0.039167 | 1.3333 | 0.50667 | 0.014 | 7.395 | 0.053167 | 1 | 4.1 | 12.05 | 18.5 | 56.5 | 0.0145 | 7.35 | 0.0545 | 1.3333 | 4.35 | 14.45 | 18.5 | 58.5 | 0.0155 | 3.7833 | 4.1167 | 3.8667 |  |  | MAXIMUM | 11 | 11 | 12 | 34 | 10.5 | 10.5 | 11.5 | 32.5 |  | 15.2554 |  | 18.8798 | 32.2171 | 2.4651 | MAXIMUM | 119.9482 | 9530.5466 |  | 843.7004 |  |  |  | 14.3238 | 14.987 | 13.7381 | 1.5261 | 1.6957 | 1.5483 | 0.69493 | 0.68456 | 0.70531 | 0.7468 | 0.51342 | 0.66555 | 2.7392 | 8 | 0.050246 | 0.050246 | 0.052299 | 1.0947 | 0.49911 | 0.096324 | 4.0139 | 0.73857 | 3.4041 | 1.1194 | 0.52727 | 0.10051 | 3.8137 | 0.65451 | 3.7297
MINIMUM | 6.21 | 10 | 17 | 7.95 | 129 | 172 | 12.7 | 0.544 | 0.03 | 6.09 | 8 | 0.074 | 6.09 | 9 |  | 6.03 | 8 |  | 6.12 | 0.276 | 4 | 0.68 | 11.8 | 10.5 | 0.7391 | 0.05 | 6.24 | 0.269 | 4 | 0.8 | 12.2 | 10.5 | 0.7391 | 6.2 | 0.25 | 4 | 0.69 | 13 | 11.9 | 0.78111 | 0.02 | 1 | 0.34 | 0.009 | 0.051 | 0.01 | 1 | 0.49 | 0.016 | 0.036 | 1 | 0.31 | 0.014 | 7.11 | 0.049 | 1 | 3.7 | 11.6 | 17 | 45 | 0.012 | 7.12 | 0.048 | 1 | 4.2 | 12.1 | 17 | 45 | 0.012 | 3.6 | 4 | 3.4 | [15 empty] | MIL/MIN |  | TOTAL | 62340 | 0 | 0 | 0 | 0 | 0 | 0 | 1745 | 1845 | 1830 | 1440 | 1580 | 1500 | 5200 | 5160 | 5360 | 5400 | 4120 | 5180 | 5180 | 0 | 4000 | 4000 | 4440 | 400 | 484 | 56 | 6410 | 1330 | 980 | 224 | 141.4 | 32 | 3290 | 645 | 588
MAXIMUM | 6.39 | 13 | 20 | 9.05 | 137 | 183 | 13.8 | 0.574 | 0.043 | 6.24 | 10 | 0.096 | 6.16 | 10 |  | 6.18 | 10 |  | 6.18 | 0.406 | 4 | 0.74 | 12.4 | 11.1 | 0.77448 | 0.068 | 6.27 | 0.4 | 5 | 0.95 | 13.1 | 11.1 | 0.77448 | 6.23 | 0.435 | 5 | 0.82 | 13.8 | 12.5 | 0.81444 | 0.024 | 1 | 0.62 | 0.015 | 0.069 | 0.017 | 2 | 0.89 | 0.016 | 0.044 | 2 | 0.68 | 0.014 | 7.57 | 0.06 | 1 | 4.4 | 12.3 | 20 | 68 | 0.017 | 7.63 | 0.06 | 2 | 4.6 | 15.1 | 20 | 72 | 0.019 | 4.1 | 4.3 | 4.4 | [17 empty] | AVERAGE | 15585 | [6 empty] | 436.25 | 461.25 | 457.5 | 360 | 395 | 375 | 1300 | 1290 | 1340 | 1350 | 1030 | 1295 | 1295 |  | 1000 | 1000 | 1110 | 100 | 121 | 14 | 1602.5 | 332.5 | 245 | 56 | 35.35 | 8 | 822.5 | 161.25 | 147
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1406 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.435 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.68 | [5 empty] | 6.2075 |  |  |  |  | 0.044 |  |  |  |  | 0.68 | [6 empty] | 0.044 | [16 empty] | Pump Station MIN |  | 3.4 | [17 empty] | MINIMUM | 14560 | [6 empty] | 335 | 360 | 355 | 360 | 380 | 360 | 1200 | 1240 | 1280 | 1320 | 960 | 1250 | 1100 |  | 1000 | 1000 | 1080 | 100 | 121 | 14 | 1590 | 320 | 245 | 56 | 0.7 | 8 | 790 | 160 | 147
[90 empty] | MAXIMUM | 16680 | [6 empty] | 540 | 565 | 565 | 360 | 400 | 400 | 1340 | 1320 | 1360 | 1440 | 1080 | 1400 | 1440 |  | 1000 | 1000 | 1140 | 100 | 121 | 14 | 1620 | 340 | 245 | 56 | 70 | 8 | 840 | 165 | 147
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.408 |  | TOTAL MGD: |  | 0.005 |  |  | FINISHED SOUTH 1 |  | START: | 23826914 |  | END: | 23826919 |  |  | Alum | 4949 | 8612 | 8612 | 9161 | 9161 | 0 | [44 empty] | 0.69 | 12 | 22.5 | 15.525 | 6.2 | 13 | 15 | 1.035
[73 empty] | FINISHED 2 | 17.734 |  | TOTAL MGD: |  | 11.403 |  |  | FINISHED SOUTH 2 |  | START: | 43442705 |  | END: | 43454108 |  |  | Caustic | 6286 | 6666 | 6666
[73 empty] | TOTAL RAW | 33.203 |  | TOTAL MGD: |  | 4.072 |  |  | FINISHED CONWAY |  | START: | 10083669 |  | END: | 10087741 |  |  | Hypochlorite | 11.5 |  | 33
[76 empty] | TOTAL MGD: |  | 13.662 |  |  | FINISHED PERRY |  | START: | 33462697 |  | END: | 33476359 |  |  | Phosphate | 1439
[76 empty] | TOTAL MGD: |  | 10.582 |  |  | RAW PLANT 1 |  | START: | 30623101 |  | END: | 30633683 |  |  | Fluoride | 1500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.761 |  |  | RAW PLANT 2 |  | START: | 30585994 |  | END: | 30596755 |  |  | Cal~Flo | 13.4 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.86 |  |  | RAW PLANT 3 |  | START: | 7115770 |  | END: | 7127630 |  |  | Zinc | 1069
[76 empty] | TOTAL MGD: |  | 1.058 |  |  | DECANT |  | START: | 1827099 |  | END: | 1828157 |  |  | Polymer | 14
[76 empty] | TOTAL MGD: |  | 1.3379 |  |  | BLOW DOWN |  | START: | 9078.3608 |  | END: | 9079.6987 |  |  | NH3 | 7.63 |  | BI-SUL | 1650
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 2
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 844
23826919
43454108
10087741
33476359
30633683
30596755
7127630
1828157
9079.6987
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 31
DATE: | 2018-12-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 | [10 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 | [28 empty] | 6:00 - 18:00 |  | 0 |  | 0 | [37 empty] | 6:00 - 18:00 |  | 0 |  | 0
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 0 |  | 0 | [37 empty] | 18:00 - 6:00 |  | 0 |  | 0
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2018-12-01 | [23 empty] | DATE: | 2018-12-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2018-12-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [127 empty] | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [127 empty] | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
2:00 | [127 empty] | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | [127 empty] | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [127 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | [127 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [127 empty] | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | [127 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [127 empty] | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | [127 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [127 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | [127 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [127 empty] | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
22:00 | [72 empty] | DOSE |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | [74 empty] | AVERAGE | [14 empty] | AVERAGE |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [30 empty] | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MINIMUM | [14 empty] | MINIMUM | [37 empty] | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | 0
AVERAGE | [74 empty] | MAXIMUM | [14 empty] | MAXIMUM
MINIMUM | [87 empty] | MIL/MIN |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAXIMUM | [89 empty] | AVERAGE
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [7 empty] | TOTAL AVG COAG ALK: | [5 empty] | TOTAL MAX SETTLED NTU: | [6 empty] | TOTAL MIN SETTLED DISEN.: |  |  | 0 | [10 empty] | 0 | [28 empty] | Pump Station MIN |  | 0 | [17 empty] | MINIMUM
MAXIMUM
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.511 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23826919 |  | END: | 23826919 |  |  | Alum | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [51 empty] | 0
[73 empty] | FINISHED 2 | 18.903 |  | TOTAL MGD: |  | 10.511 |  |  | FINISHED SOUTH 2 |  | START: | 43454108 |  | END: | 43464619 |  |  | Caustic | #N/A | #N/A | #N/A
[73 empty] | TOTAL RAW | 33.423 |  | TOTAL MGD: |  | 4.218 |  |  | FINISHED CONWAY |  | START: | 10087741 |  | END: | 10091959 |  |  | Hypochlorite | #N/A |  | #N/A
[76 empty] | TOTAL MGD: |  | 14.685 |  |  | FINISHED PERRY |  | START: | 33476359 |  | END: | 33491044 |  |  | Phosphate | #N/A
[76 empty] | TOTAL MGD: |  | 10.561 |  |  | RAW PLANT 1 |  | START: | 30633683 |  | END: | 30644244 |  |  | Fluoride | #N/A |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.848 |  |  | RAW PLANT 2 |  | START: | 30596755 |  | END: | 30607603 |  |  | Cal~Flo | #N/A |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.014 |  |  | RAW PLANT 3 |  | START: | 7127630 |  | END: | 7139644 |  |  | Zinc | #N/A
[76 empty] | TOTAL MGD: |  | 1.18 |  |  | DECANT |  | START: | 1828157 |  | END: | 1829337 |  |  | Polymer | #N/A
[76 empty] | TOTAL MGD: |  | 1.2829 |  |  | BLOW DOWN |  | START: | 9079.6987 |  | END: | 9080.9816 |  |  | NH3 | #N/A |  | BI-SUL | #N/A
[87 empty] | 0 |  |  | Lime | #N/A |  | FILTER AIDE | #N/A
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | #N/A
23826919
43464619
10091959
33491044
30644244
30607603
7139644
1829337
9080.9816
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN MONTH
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## BULK TANK LEVEL
cal-flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday
| 2018-11-01 | 2018-11-02 | 2018-11-03 | 2018-11-04 | 2018-11-05 | 2018-11-06 | 2018-11-07 | 2018-11-08 | 2018-11-09 | 2018-11-10 | 2018-11-11 | 2018-11-12 | 2018-11-13 | 2018-11-14 | 2018-11-15 | 2018-11-16 | 2018-11-17 | 2018-11-18 | 2018-11-19 | 2018-11-20 | 2018-11-21 | 2018-11-22 | 2018-11-23 | 2018-11-24 | 2018-11-25 | 2018-11-26 | 2018-11-27 | 2018-11-28 | 2018-11-29 | 2018-11-30 | 2018-12-01
Alum1 | 9338 | 9336 | 9334 | 9333 | 9328 | 9322 | 9252 | 9329 | 9262 | 9266 | 9327 | 9324 | 9321 | 9321 | 9321 | 9249 | 9312 | 9314 | 9249 | 9242 | 9308 | 9304 | 9312 | 9307 | 9305 | 7226 | 2268 | 4929 | 345 | 4949 | #N/A
Alum2 | 9442 | 10140 | 9024 | 7929 | 8932 | 9963 | 8938 | 8806 | 8673 | 9389 | 8483 | 10476 | 9084 | 8279 | 9085 | 10679 | 9245 | 8250 | 9768 | 8658 | 7597 | 8627 | 10180 | 8890 | 9794 | 8635 | 11000 | 9846 | 8023 | 8612 | #N/A
Alum Tower | 841100% | 983800% | 888200% | 796000% | 915900% | 1044800% | 955500% | 909600% | 895400% | 948800% | 811300% | 980700% | 929000% | 858500% | 760000% | 940600% | 815000% | 734500% | 906400% | 812400% | 958500% | 1017000% | 1120000% | 960300% | 829700% | 776200% | 756200% | 919200% | 767900% | 916100% | #N/A
Caustic | 8743 | 8162 | 7983 | 7696 | 7381 | 7081 | 6761 | 6422 | 6058 | 5672 | 5418 | 5164 | 4959 | 4852 | 4746 | 4542 | 4411 | 4280 | 4112 | 7652 | 7569 | 7093 | 6723 | 5948 | 5316 | 4631 | 3855 | 7004 | 6630 | 6286 | #N/A
Caustic | 7220 | 7108 | 7012 | 6967 | 6859 | 6807 | 8628 | 8537 | 8447 | 8342 | 8380 | 8240 | 8190 | 8144 | 8092 | 8090 | 8034 | 7983 | 7980 | 7930 | 7867 | 7770 | 7653 | 7515 | 7304 | 7174 | 7014 | 6850 | 6753 | 6666 | #N/A
Hypochlorite | 13 | 12 | 9 | 8 | 11 | 10 | 14 | 15 | 19.5 | 16.8 | 15 | 13 | 18.5 | 17 | 16 | 21 | 19 | 18 | 16 | 20 | 17 | 16 | 14 | 18 | 15 | 14 | 18.5 | 11.5 | 12 | 11.5 | #N/A
Hypochlorite | 18 | 27 | 27 | 27 | 27 | 25.5 | 34 | 32 | 46 | 44.5 | 42 | 40.5 | 32 | 31 | 42 | 33 | 42 | 42 | 39 | 44 | 41 | 40 | 38 | 45 | 41 | 41 | 43 | 30 | 24 | 33 | #N/A
Phosphate | 2922 | 2877 | 2816 | 2817 | 2725 | 2636 | 2615 | 2564 | 2540 | 2493 | 2374 | 2339 | 2325 | 2227 | 2226 | 2137 | 2092 | 2054 | 2010 | 1939 | 1889 | 1851 | 1820 | 1762 | 1697 | 1650 | 1621 | 1515 | 1473 | 1439 | #N/A
Fluoride | 3750 | 3650 | 3650 | 3650 | 3250 | 3250 | 2931 | 3050 | 2936 | 2936 | 2835 | 3914 | 2500 | 2750 | 2750 | 2750 | 2750 | 2500 | 2400 | 2400 | 2400 | 2200 | 2200 | 2200 | 2000 | 2000 | 1750 | 1750 | 1750 | 1500 | #N/A
Cal~Flo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zinc | 1461 | 1474 | 1480 | 1484 | 1470 | 1440 | 1465 | 1482 | 1475 | 1482 | 1472 | 1460 | 1470 | 1464 | 1398 | 1398 | 1390 | 1448 | 1460 | 1065 | 1198 | 1184 | 1063 | 1068 | 1154 | 1093 | 1094 | 1052 | 1058 | 1069 | #N/A
Polymer | 23 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 7 | 6 | 7 | 14 | #N/A
NH3 | 8 | 7.63 | 7.39 | 7.13 | 6.89 | 6.7 | 6.49 | 12.68 | 12.45 | 12.22 | 11.97 | 11.73 | 11.51 | 11.32 | 11.1 | 11 | 11 | 10 | 10 | 9.87 | 9.65 | 9.44 | 9.23 | 9 | 8.78 | 8.59 | 8.35 | 8.11 | 7.88 | 7.63 | #N/A
Lime | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
Cabon | 888 | 841 | 841 | 841 | 841 | 841 | 841 | 940 | 980 | 856 | 970 | 831 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 817 | 825 | 809 | 844 | #N/A
filter aid | 2018-11-01: 2.8613

## AWOP 2018
2019-08-12 | Raw | Settled | Filter
Average | 12.544 | 0.53123 | 0.0526
Max | 18 | 0.804 | 0.092
Count |  | 0 | 0 | Average Raw
AWOP Count |  | 0 | 0 | Per day
2018-11-01 | 14.9 | 0.44 | 0.06
2018-11-02 | 14.6 | 0.396 | 0.087
2018-11-03 | 14.1 | 0.405 | 0.043
2018-11-04 | 13.8 | 0.393 | 0.038
2018-11-05 | 13.7 | 0.373 | 0.061
2018-11-06 | 12.8 | 0.385 | 0.045
2018-11-07 | 11.1 | 0.433 | 0.047
2018-11-08 | 10.4 | 0.531 | 0.044
2018-11-09 | 11.7 | 0.567 | 0.092
2018-11-10 | 11.7 | 0.804 | 0.056
2018-11-11 | 10.8 | 0.636 | 0.045
2018-11-12 | 10.6 | 0.587 | 0.076
2018-11-13 | 10.5 | 0.427 | 0.059
2018-11-14 | 18 | 0.43 | 0.066
2018-11-15 | 9.85 | 0.395 | 0.05
2018-11-16 | 14.2 | 0.364 | 0.061
2018-11-17 | 16.1 | 0.468 | 0.058
2018-11-18 | 16.1 | 0.47 | 0.052
2018-11-19 | 15.6 | 0.491 | 0.048
2018-11-20 | 15.5 | 0.499 | 0.052
2018-11-21 | 14 | 0.721 | 0.083
2018-11-22 | 12.9 | 0.782 | 0.039
2018-11-23 | 13.1 | 0.741 | 0.042
2018-11-24 | 12.7 | 0.748 | 0.023
2018-11-25 | 10.8 | 0.608 | 0.041
2018-11-26 | 9.98 | 0.636 | 0.037
2018-11-27 | 9.97 | 0.694 | 0.042
2018-11-28 | 9.32 | 0.616 | 0.036
2018-11-29 | 8.45 | 0.462 | 0.051
2018-11-30 | 9.05 | 0.435 | 0.044
2018-12-01

## REMOVAL
PLT1
2019-08-12 09:20 |  | DAILY AVG | RAW | RAW | RAW | RAW | RAW | RAW | RAW | RAW | avg last 12 | RAW | TREATED | TREATED | TREATED | Percent | Calculated Raw | Alum Dose: | Alum Dose | Treated pH | Settled UV | FILTER UV
Date | Time | ALUM DOSE | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | raw uv | MN | PH | ALKALINITY | Treated UV | Removal | TOC, mg/L | TOC Ratio | Divided By 100 | Divided By 10
2018-11-01 | 0:00 | 99.2276
| 1:00 | 99.2276 | [8 empty] | #DIV/0!
| 2:00 | 99.2276 | [8 empty] | #DIV/0!
| 3:00 | 99.2276 | 6.48 | 18 | 17 | 13.7 | 131 | 225 | 18.4 | 0.559 | 0.559 |  | 6.03 | 10 | 0.092 | 83.54% | 14.7105 | 6.7453 | 0.99228 | 0.603 | 0.066 | 0.064
| 4:00 | 99.2276 | [8 empty] | 0.559
| 5:00 | 99.2276 | [8 empty] | 0.559
| 6:00 | 99.2276 | [8 empty] | 0.559
| 7:00 | 99.2276 | 6.38 | 20 | 17 | 13.9 | 121 | 195 | 18 | 0.541 | 0.55 |  | 6 | 13 | 0.093 | 82.81% | 14.2368 | 6.9698 | 0.99228 | 0.6 | 0.061 | 0.067
| 8:00 | 99.2276 | [8 empty] | 0.55
| 9:00 | 99.2276 | [8 empty] | 0.55 | 0.051
| 10:00 | 99.2276 | [8 empty] | 0.55
| 11:00 | 99.2276 | 6.42 | 16 | 17 | 14.5 | 132 | 207 | 18.3 | 0.558 | 0.55267 |  | 6.01 | 12 | 0.075 | 86.56% | 14.6842 | 6.7574 | 0.99228 | 0.601 | 0.065 | 0.084
| 12:00 | 99.2276 | [8 empty] | 0.55267
| 13:00 | 99.2276 | [8 empty] | 0.55267
| 14:00 | 99.2276 | [8 empty] | 0.55267
| 15:00 | 99.2276 | 6.68 | 20 | 18 | 14.4 | 114 | 211 | 19.5 | 0.506 | 0.541 |  | 6.25 | 14 | 0.091 | 82.02% | 13.3158 | 7.4519 | 0.99228 | 0.625 | 0.058 | 0.058
| 16:00 | 99.2276 | [8 empty] | 0.535
| 17:00 | 99.2276 | [8 empty] | 0.535
| 18:00 | 99.2276 | [8 empty] | 0.535
| 19:00 | 99.2276 | 6.55 | 17 | 17 | 14.6 | 128 | 211 | 19.3 | 0.541 | 0.5365 |  | 6.09 | 14 | 0.091 | 83.18% | 14.2368 | 6.9698 | 0.99228 | 0.609 | 0.065 | 0.064
| 20:00 | 99.2276 | [8 empty] | 0.5365
| 21:00 | 99.2276 | [8 empty] | 0.535 | 0.049
| 22:00 | 99.2276 | [8 empty] | 0.535
| 23:00 | 99.2276 | 6.47 | 19 | 18 | 14.9 | 128 | 208 | 19.2 | 0.548 | 0.53825 |  | 6.03 | 13 | 0.101 | 81.57% | 14.4211 | 6.8807 | 0.99228 | 0.603 | 0.062 | 0.062
2018-11-02 | 0:00 | 92.1351 | [8 empty] | 0.53825
| 1:00 | 92.1351 | [8 empty] | 0.53167
| 2:00 | 92.1351 | [8 empty] | 0.53167
| 3:00 | 92.1351 | 6.47 | 19 | 18 | 14.6 | 128 | 207 | 18.4 | 0.561 | 0.539 |  | 6.05 | 10 | 0.093 | 83.42% | 14.7632 | 6.2409 | 0.92135 | 0.605 | 0.064 | 0.063
| 4:00 | 92.1351 | [8 empty] | 0.539
| 5:00 | 92.1351 | [8 empty] | 0.55
| 6:00 | 92.1351 | [8 empty] | 0.55
| 7:00 | 92.1351 | 6.46 | 20 | 18 | 14.6 | 123 | 205 | 18.6 | 0.54 | 0.5475 |  | 6.03 | 10 | 0.067 | 87.59% | 14.2105 | 6.4836 | 0.92135 | 0.603 | 0.061 | 0.061
| 8:00 | 92.1351 | [8 empty] | 0.5475
| 9:00 | 92.1351 | [8 empty] | 0.54967 | 0.078
| 10:00 | 92.1351 | [8 empty] | 0.54967
| 11:00 | 92.1351 | 6.48 | 21 | 18 | 14.6 | 115 | 200 | 19.8 | 0.489 | 0.5345 |  | 6.01 | 12 | 0.086 | 82.41% | 12.8684 | 7.1598 | 0.92135 | 0.601 | 0.061 | 0.061
| 12:00 | 92.1351 | [8 empty] | 0.5345
| 13:00 | 92.1351 | [8 empty] | 0.53
| 14:00 | 92.1351 | [8 empty] | 0.53
| 15:00 | 92.1351 | 6.48 | 22 | 18 | 14.2 | 120 | 200 | 19 | 0.528 | 0.5295 |  | 6.04 | 11 | 0.103 | 80.49% | 13.8947 | 6.6309 | 0.92135 | 0.604 | 0.06 | 0.061
| 16:00 | 92.1351 | [8 empty] | 0.5295
| 17:00 | 92.1351 | [8 empty] | 0.519
| 18:00 | 92.1351 | [8 empty] | 0.519
| 19:00 | 92.1351 | 6.49 | 21 | 19 | 14 | 122 | 195 | 19.7 | 0.509 | 0.5165 |  | 6.05 | 12 | 0.083 | 83.69% | 13.3947 | 6.8785 | 0.92135 | 0.605 | 0.066 | 0.067
| 20:00 | 92.1351 | [8 empty] | 0.5165
| 21:00 | 92.1351 | [8 empty] | 0.50867 | 0.048
| 22:00 | 92.1351 | [8 empty] | 0.50867
| 23:00 | 92.1351 | 6.42 | 20 | 20 | 14.1 | 121 | 194 | 19.7 | 0.513 | 0.50975 |  | 6.06 | 11 | 0.083 | 83.82% | 13.5 | 6.8248 | 0.92135 | 0.606 | 0.065 | 0.064
2018-11-03 | 24:00 | 87.126 | [8 empty] | 0.50975
| 25:00 | 87.126 | [8 empty] | 0.51667
| 26:00 | 87.126 | [8 empty] | 0.51667
| 27:00 | 87.126 | 6.45 | 18 | 17 | 13.9 | 122 | 198 | 18.9 | 0.519 | 0.51725 |  | 6.04 | 10 | 0.095 | 81.7% | 13.6579 | 6.3792 | 0.87126 | 0.604 | 0.068 | 0.065
| 28:00 | 87.126 | [8 empty] | 0.51725
| 29:00 | 87.126 | [8 empty] | 0.51367
| 30:00 | 87.126 | [8 empty] | 0.51367
| 31:00 | 87.126 | 6.42 | 22 | 19 | 13.4 | 121 | 195 | 18.8 | 0.528 | 0.51725 |  | 6.01 | 11 | 0.084 | 84.09% | 13.8947 | 6.2704 | 0.87126 | 0.601 | 0.064 | 0.063
| 32:00 | 87.126 | [8 empty] | 0.51725
| 33:00 | 87.126 | [8 empty] | 0.52 | 0.066
| 34:00 | 87.126 | [8 empty] | 0.52
| 35:00 | 87.126 | 6.38 | 21 | 19 | 13.2 | 93 | 193 | 18.9 | 0.446 | 0.5015 |  | 6.06 | 10 | 0.071 | 84.08% | 11.7368 | 7.4233 | 0.87126 | 0.606 | 0.062 | 0.069
| 36:00 | 87.126 | [8 empty] | 0.5015
| 37:00 | 87.126 | [8 empty] | 0.49767
| 38:00 | 87.126 | [8 empty] | 0.49767
| 39:00 | 87.126 | 6.45 | 22 | 20 | 13.6 | 100 | 193 | 19 | 0.486 | 0.49475 |  | 6.02 | 12 | 0.084 | 82.72% | 12.7895 | 6.8123 | 0.87126 | 0.602 | 0.061 | 0.064
| 40:00 | 87.126 | [8 empty] | 0.49475
| 41:00 | 87.126 | [8 empty] | 0.48667
| 42:00 | 87.126 | [8 empty] | 0.48667
| 43:00 | 87.126 | 6.46 | 20 | 18 | 13.7 | 123 | 191 | 19.6 | 0.542 | 0.5005 |  | 5.98 | 10 | 0.095 | 82.47% | 14.2632 | 6.1085 | 0.87126 | 0.598 | 0.059 | 0.06
| 44:00 | 87.126 | [8 empty] | 0.5005
| 45:00 | 87.126 | [8 empty] | 0.49133 | 0.054
| 46:00 | 87.126 | [8 empty] | 0.49133
| 47:00 | 87.126 | 6.42 | 21 | 17 | 14.1 | 118 | 186 | 19.6 | 0.494 | 0.492 |  | 6.01 | 11 | 0.094 | 80.97% | 13 | 6.702 | 0.87126 | 0.601 | 0.065 | 0.062
2018-11-04 | 48:00 | 84.1919 | [8 empty] | 0.492
| 49:00 | 84.1919 | [8 empty] | 0.50733
| 50:00 | 84.1919 | [8 empty] | 0.50733
| 51:00 | 84.1919 | 6.47 | 19 | 19 | 13.8 | 121 | 193 | 18.5 | 0.507 | 0.50725 |  | 6.1 | 10 | 0.095 | 81.26% | 13.3421 | 6.3102 | 0.84192 | 0.61 | 0.06 | 0.06
| 52:00 | 84.1919 | [8 empty] | 0.50725
| 53:00 | 84.1919 | [8 empty] | 0.51433
| 54:00 | 84.1919 | [8 empty] | 0.51433
| 55:00 | 84.1919 | 6.43 | 17 | 18 | 13.6 | 84 | 190 | 18.3 | 0.42 | 0.49075 |  | 6 | 9 | 0.07 | 83.33% | 11.0526 | 7.6174 | 0.84192 | 0.6 | 0.062 | 0.062
| 56:00 | 84.1919 | [8 empty] | 0.49075
| 57:00 | 84.1919 | [8 empty] | 0.47367 | 0.067
| 58:00 | 84.1919 | [8 empty] | 0.47367
| 59:00 | 84.1919 | 6.51 | 19 | 18 | 13.8 | 88 | 187 | 18.1 | 0.497 | 0.4795 |  | 6.01 | 10 | 0.077 | 84.51% | 13.0789 | 6.4372 | 0.84192 | 0.601 | 0.062 | 0.061
| 60:00 | 84.1919 | [8 empty] | 0.4795
| 61:00 | 84.1919 | [8 empty] | 0.47467
| 62:00 | 84.1919 | [8 empty] | 0.47467
| 63:00 | 84.1919 | 6.49 | 20 | 18 | 13 | 100 | 180 | 19 | 0.469 | 0.47325 |  | 6.04 | 11 | 0.089 | 81.02% | 12.3421 | 6.8215 | 0.84192 | 0.604 | 0.063 | 0.067
| 64:00 | 84.1919 | [8 empty] | 0.47325
| 65:00 | 84.1919 | [8 empty] | 0.462
| 66:00 | 84.1919 | [8 empty] | 0.462
| 67:00 | 84.1919 | 6.45 | 19 | 19 | 12.8 | 120 | 184 | 18.9 | 0.491 | 0.46925 |  | 6 | 12 | 0.075 | 84.73% | 12.9211 | 6.5159 | 0.84192 | 0.6 | 0.052 | 0.054
| 68:00 | 84.1919 | [8 empty] | 0.46925
| 69:00 | 84.1919 | [8 empty] | 0.48567 | 0.054
| 70:00 | 84.1919 | [8 empty] | 0.48567
| 71:00 | 84.1919 | 6.45 | 19.21 | 21 | 13.7 | 116 | 186 | 19 | 0.487 | 0.486 |  | 5.86 | 11 | 0.083 | 82.96% | 12.8158 | 6.5694 | 0.84192 | 0.586 | 0.057 | 0.056
2018-11-05 | 72:00 | 85.0246 | [8 empty] | 0.486
| 73:00 | 85.0246 | [8 empty] | 0.48233
| 74:00 | 85.0246 | [8 empty] | 0.48233
| 75:00 | 85.0246 | 6.35 | 18 | 16 | 13.7 | 119 | 197 | 18.5 | 0.498 | 0.48625 |  | 5.93 | 9 | 0.087 | 82.53% | 13.1053 | 6.4878 | 0.85025 | 0.593 | 0.061 | 0.062
| 76:00 | 85.0246 | [8 empty] | 0.48625
| 77:00 | 85.0246 | [8 empty] | 0.492
| 78:00 | 85.0246 | [8 empty] | 0.492
| 79:00 | 85.0246 | 6.43 | 20 | 17 | 13.1 | 112 | 185 | 18.5 | 0.494 | 0.4925 |  | 5.98 | 12 | 0.096 | 80.57% | 13 | 6.5404 | 0.85025 | 0.598 | 0.062 | 0.06
| 80:00 | 85.0246 | [8 empty] | 0.4925
| 81:00 | 85.0246 | [8 empty] | 0.493 | 0.094
| 82:00 | 85.0246 | [8 empty] | 0.493
| 83:00 | 85.0246 | 6.46 | 20 | 18 | 11.3 | 116 | 172 | 18.6 | 0.509 | 0.497 |  | 5.96 | 10 | 0.084 | 83.5% | 13.3947 | 6.3476 | 0.85025 | 0.596 | 0.066 | 0.066
| 84:00 | 85.0246 | [8 empty] | 0.497
| 85:00 | 85.0246 | [8 empty] | 0.50033
| 86:00 | 85.0246 | [8 empty] | 0.50033
| 87:00 | 85.0246 | 6.49 | 22 | 18 | 12 | 110 | 179 | 19.8 | 0.475 | 0.494 |  | 6.06 | 12 | 0.092 | 80.63% | 12.5 | 6.802 | 0.85025 | 0.606 | 0.061 | 0.062
| 88:00 | 85.0246 | [8 empty] | 0.494
| 89:00 | 85.0246 | [8 empty] | 0.49267
| 90:00 | 85.0246 | [8 empty] | 0.49267
| 91:00 | 85.0246 | 6.45 | 20 | 20 | 11.7 | 109 | 177 | 19.1 | 0.49 | 0.492 |  | 5.95 | 11 | 0.088 | 82.04% | 12.8947 | 6.5937 | 0.85025 | 0.595 | 0.066 | 0.066
| 92:00 | 85.0246 | [8 empty] | 0.492
| 93:00 | 85.0246 | [8 empty] | 0.49133 | 0.047
| 94:00 | 85.0246 | [8 empty] | 0.49133
| 95:00 | 85.0246 | 6.43 | 21 | 19 | 11.5 | 117 | 176 | 19.1 | 0.482 | 0.489 |  | 5.9 | 11 | 0.081 | 83.2% | 12.6842 | 6.7032 | 0.85025 | 0.59 | 0.06 | 0.06
2018-11-06 | 96:00 | 85.0246 | [8 empty] | 0.489
| 97:00 | 85.0246 | [8 empty] | 0.48233
| 98:00 | 85.0246 | [8 empty] | 0.48233
| 99:00 | 85.0246 | 6.4 | 18 | 17 | 12.8 | 118 | 177 | 19.3 | 0.491 | 0.4845 |  | 5.99 | 10 | 0.087 | 82.28% | 12.9211 | 6.5803 | 0.85025 | 0.599 | 0.06 | 0.06
| 100:00 | 85.0246 | [8 empty] | 0.4845
| 101:00 | 85.0246 | [8 empty] | 0.48767
| 102:00 | 85.0246 | [8 empty] | 0.48767
| 103:00 | 85.0246 | 6.46 | 20 | 17 | 11.5 | 117 | 176 | 19 | 0.513 | 0.494 |  | 6.01 | 13 | 0.102 | 80.12% | 13.5 | 6.2981 | 0.85025 | 0.601 | 0.068 | 0.067
| 104:00 | 85.0246 | [8 empty] | 0.494
| 105:00 | 85.0246 | [8 empty] | 0.49533 | 0.074
| 106:00 | 85.0246 | [8 empty] | 0.49533
| 107:00 | 85.0246 | 6.4 | 19 | 16 | 11.7 | 115 | 158 | 19.2 | 0.506 | 0.498 |  | 5.92 | 11 | 0.096 | 81.03% | 13.3158 | 6.3852 | 0.85025 | 0.592 | 0.074 | 0.076
| 108:00 | 85.0246 | [8 empty] | 0.498
| 109:00 | 85.0246 | [8 empty] | 0.50333
| 110:00 | 85.0246 | [8 empty] | 0.50333
| 111:00 | 85.0246 | 6.43 | 21 | 18 | 10.6 | 115 | 171 | 19.8 | 0.467 | 0.49425 |  | 5.99 | 12 | 0.089 | 80.94% | 12.2895 | 6.9185 | 0.85025 | 0.599 | 0.061 | 0.062
| 112:00 | 85.0246 | [8 empty] | 0.49425
| 113:00 | 85.0246 | [8 empty] | 0.49533
| 114:00 | 85.0246 | [8 empty] | 0.49533
| 115:00 | 85.0246 | 6.46 | 20 | 16 | 9.96 | 117 | 170 | 20.3 | 0.504 | 0.4975 |  | 5.98 | 11 | 0.092 | 81.75% | 13.2632 | 6.4106 | 0.85025 | 0.598 | 0.063 | 0.065
| 116:00 | 85.0246 | [8 empty] | 0.4975
| 117:00 | 85.0246 | [8 empty] | 0.49233 | 0.042
| 118:00 | 85.0246 | [8 empty] | 0.49233
| 119:00 | 85.0246 | 6.45 | 22 | 17 | 10.06 | 123 | 177 | 20.3 | 0.49 | 0.49175 |  | 5.92 | 10 | 0.075 | 84.69% | 12.8947 | 6.5937 | 0.85025 | 0.592 | 0.06 | 0.062
2018-11-07 | 120:00 | 82.9448 | [8 empty] | 0.49175
| 121:00 | 82.9448 | [8 empty] | 0.487
| 122:00 | 82.9448 | [8 empty] | 0.487
| 123:00 | 82.9448 | 6.4 | 22 | 18 | 11 | 117 | 174 | 20.5 | 0.507 | 0.492 |  | 5.78 | 9 | 0.092 | 81.85% | 13.3421 | 6.2168 | 0.82945 | 0.578 | 0.064 | 0.061
| 124:00 | 82.9448 | [8 empty] | 0.492
| 125:00 | 82.9448 | [8 empty] | 0.50033
| 126:00 | 82.9448 | [8 empty] | 0.50033
| 127:00 | 82.9448 | 6.37 | 17 | 15 | 11.1 | 121 | 174 | 19.6 | 0.533 | 0.5085 |  | 8 | 7 | 0.081 | 84.8% | 14.0263 | 5.9135 | 0.82945 | 0.8 | 0.071 | 0.07
| 128:00 | 82.9448 | [8 empty] | 0.5085
| 129:00 | 82.9448 | [8 empty] | 0.51 | 0.044
| 130:00 | 82.9448 | [8 empty] | 0.51
| 131:00 | 82.9448 | 6.32 | 17 | 16 | 10.5 | 122 | 172 | 19.5 | 0.529 | 0.51475 |  | 5.9 | 10 | 0.08 | 84.88% | 13.9211 | 5.9582 | 0.82945 | 0.59 | 0.07 | 0.069
| 132:00 | 82.9448 | [8 empty] | 0.51475
| 133:00 | 82.9448 | [8 empty] | 0.523
| 134:00 | 82.9448 | [8 empty] | 0.523
| 135:00 | 82.9448 | 6.4 | 18 | 15 | 10.6 | 121 | 171 | 19.7 | 0.527 | 0.524 |  | 5.89 | 9 | 0.08 | 84.82% | 13.8684 | 5.9808 | 0.82945 | 0.589 | 0.071 | 0.069
| 136:00 | 82.9448 | [8 empty] | 0.524
| 137:00 | 82.9448 | [8 empty] | 0.52967
| 138:00 | 82.9448 | [8 empty] | 0.52967
| 139:00 | 82.9448 | 6.45 | 16 | 16 | 9.63 | 122 | 167 | 19.7 | 0.528 | 0.52925 |  | 5.83 | 10 | 0.073 | 86.17% | 13.8947 | 5.9695 | 0.82945 | 0.583 | 0.065 | 0.067
| 140:00 | 82.9448 | [8 empty] | 0.52925
| 141:00 | 82.9448 | [8 empty] | 0.528 | 0.043
| 142:00 | 82.9448 | [8 empty] | 0.528
| 143:00 | 82.9448 | 6.49 | 16 | 16 | 10.7 | 126 | 173 | 19.5 | 0.538 | 0.5305 |  | 5.8 | 9 | 0.079 | 85.32% | 14.1579 | 5.8586 | 0.82945 | 0.58 | 0.068 | 0.068
2018-11-08 | 144:00 | 78.4351 | [8 empty] | 0.5305
| 145:00 | 78.4351 | [8 empty] | 0.531
| 146:00 | 78.4351 | [8 empty] | 0.531
| 147:00 | 78.4351 | 6.41 | 15 | 16 | 10.3 | 122 | 170 | 19.6 | 0.528 | 0.53025 |  | 5.9 | 10 | 0.083 | 84.28% | 13.8947 | 5.6449 | 0.78435 | 0.59 | 0.066 | 0.065
| 148:00 | 78.4351 | [8 empty] | 0.53025
| 149:00 | 78.4351 | [8 empty] | 0.53133
| 150:00 | 78.4351 | [8 empty] | 0.53133
| 151:00 | 78.4351 | 6.41 | 17 | 15 | 10 | 119 | 169 | 19.6 | 0.517 | 0.52775 |  | 6.06 | 8 | 0.087 | 83.17% | 13.6053 | 5.7651 | 0.78435 | 0.606 | 0.072 | 0.068
| 152:00 | 78.4351 | [8 empty] | 0.52775
| 153:00 | 78.4351 | [8 empty] | 0.52767 | 0.048
| 154:00 | 78.4351 | [8 empty] | 0.52767
| 155:00 | 78.4351 | 6.43 | 16 | 16 | 10.2 | 117 | 175 | 19.7 | 0.502 | 0.52125 |  | 5.98 | 8 | 0.079 | 84.26% | 13.2105 | 5.9373 | 0.78435 | 0.598 | 0.073 | 0.071
| 156:00 | 78.4351 | [8 empty] | 0.52125
| 157:00 | 78.4351 | [8 empty] | 0.51567
| 158:00 | 78.4351 | [8 empty] | 0.51567
| 159:00 | 78.4351 | 6.42 | 17 | 16 | 10.4 | 118 | 170 | 19.8 | 0.513 | 0.515 |  | 5.98 | 10 | 0.079 | 84.6% | 13.5 | 5.81 | 0.78435 | 0.598 | 0.071 | 0.069
| 160:00 | 78.4351 | [8 empty] | 0.515
| 161:00 | 78.4351 | [8 empty] | 0.51067
| 162:00 | 78.4351 | [8 empty] | 0.51067
| 163:00 | 78.4351 | 6.49 | 16 | 16 | 10.2 | 120 | 162 | 19.8 | 0.52 | 0.513 |  | 6 | 10 | 0.078 | 85% | 13.6842 | 5.7318 | 0.78435 | 0.6 | 0.067 | 0.073
| 164:00 | 78.4351 | [8 empty] | 0.513
| 165:00 | 78.4351 | [8 empty] | 0.51167 | 0.046
| 166:00 | 78.4351 | [8 empty] | 0.51167
| 167:00 | 78.4351 | 6.44 | 16 | 16 | 10.3 | 119 | 173 | 19.7 | 0.514 | 0.51225 |  | 6.05 | 10 | 0.08 | 84.44% | 13.5263 | 5.7987 | 0.78435 | 0.605 | 0.066 | 0.072
2018-11-09 | 168:00 | 76.4581 | [8 empty] | 0.51225
| 169:00 | 76.4581 | [8 empty] | 0.51567
| 170:00 | 76.4581 | [8 empty] | 0.51567
| 171:00 | 76.4581 | 6.44 | 16 | 16 | 10.2 | 120 | 170 | 19.8 | 0.512 | 0.51475 |  | 6.14 | 10 | 0.084 | 83.59% | 13.4737 | 5.6746 | 0.76458 | 0.614 | 0.08 | 0.07
| 172:00 | 76.4581 | [8 empty] | 0.51475
| 173:00 | 76.4581 | [8 empty] | 0.51533
| 174:00 | 76.4581 | [8 empty] | 0.51533
| 175:00 | 76.4581 | 6.44 | 17 | 15 | 10.5 | 114 | 172 | 19.5 | 0.492 | 0.5095 |  | 6.07 | 10 | 0.073 | 85.16% | 12.9474 | 5.9053 | 0.76458 | 0.607 | 0.068 | 0.069
| 176:00 | 76.4581 | [8 empty] | 0.5095
| 177:00 | 76.4581 | [8 empty] | 0.506 | 0.052
| 178:00 | 76.4581 | [8 empty] | 0.506
| 179:00 | 76.4581 | 6.51 | 17 | 16 | 11.4 | 108 | 175 | 19.5 | 0.476 | 0.4985 |  | 5.93 | 9 | 0.07 | 85.29% | 12.5263 | 6.1038 | 0.76458 | 0.593 | 0.066 | 0.067
| 180:00 | 76.4581 | [8 empty] | 0.4985
| 181:00 | 76.4581 | [8 empty] | 0.49333
| 182:00 | 76.4581 | [8 empty] | 0.49333
| 183:00 | 76.4581 | 6.42 | 16 | 16 | 11.2 | 106 | 173 | 19.6 | 0.482 | 0.4905 |  | 5.96 | 10 | 0.076 | 84.23% | 12.6842 | 6.0278 | 0.76458 | 0.596 | 0.072 | 0.068
| 184:00 | 76.4581 | [8 empty] | 0.4905
| 185:00 | 76.4581 | [8 empty] | 0.48333
| 186:00 | 76.4581 | [8 empty] | 0.48333
| 187:00 | 76.4581 | 6.41 | 16 | 16 | 11.6 | 110 | 180 | 19.8 | 0.493 | 0.48575 |  | 6 | 10 | 0.072 | 85.4% | 12.9737 | 5.8933 | 0.76458 | 0.6 | 0.065 | 0.066
| 188:00 | 76.4581 | [8 empty] | 0.48575
| 189:00 | 76.4581 | [8 empty] | 0.48367 | 0.054
| 190:00 | 76.4581 | [8 empty] | 0.48367
| 191:00 | 76.4581 | 6.42 | 16 | 16 | 11.7 | 108 | 175 | 19.6 | 0.488 | 0.48475 |  | 6 | 10 | 0.079 | 83.81% | 12.8421 | 5.9537 | 0.76458 | 0.6 | 0.069 | 0.066
2018-11-10 | 192:00 | 80.2436 | [8 empty] | 0.48475
| 193:00 | 80.2436 | [8 empty] | 0.48767
| 194:00 | 80.2436 | [8 empty] | 0.48767
| 195:00 | 80.2436 | 6.38 | 16 | 16 | 11.6 | 120 | 173 | 19.8 | 0.505 | 0.492 |  | 6.14 | 10 | 0.082 | 83.76% | 13.2895 | 6.0381 | 0.80244 | 0.614 | 0.07 | 0.076
| 196:00 | 80.2436 | [8 empty] | 0.492
| 197:00 | 80.2436 | [8 empty] | 0.49533
| 198:00 | 80.2436 | [8 empty] | 0.49533
| 199:00 | 80.2436 | 6.42 | 18 | 16 | 11.7 | 113 | 174 | 19.8 | 0.487 | 0.49325 |  | 6.02 | 12 | 0.073 | 85.01% | 12.8158 | 6.2613 | 0.80244 | 0.602 | 0.066 | 0.067
| 200:00 | 80.2436 | [8 empty] | 0.49325
| 201:00 | 80.2436 | [8 empty] | 0.49333 | 0.051
| 202:00 | 80.2436 | [8 empty] | 0.49333
| 203:00 | 80.2436 | 6.41 | 17 | 17 | 11 | 113 | 174 | 19.7 | 0.491 | 0.49275 |  | 5.99 | 11 | 0.076 | 84.52% | 12.9211 | 6.2103 | 0.80244 | 0.599 | 0.068 | 0.072
| 204:00 | 80.2436 | [8 empty] | 0.49275
| 205:00 | 80.2436 | [8 empty] | 0.49433
| 206:00 | 80.2436 | [8 empty] | 0.49433
| 207:00 | 80.2436 | 6.46 | 18 | 16 | 11 | 108 | 168 | 19.7 | 0.484 | 0.49175 |  | 6 | 10 | 0.071 | 85.33% | 12.7368 | 6.3001 | 0.80244 | 0.6 | 0.064 | 0.071
| 208:00 | 80.2436 | [8 empty] | 0.49175
| 209:00 | 80.2436 | [8 empty] | 0.48733
| 210:00 | 80.2436 | [8 empty] | 0.48733
| 211:00 | 80.2436 | 6.44 | 16 | 16 | 10.7 | 109 | 179 | 19.7 | 0.513 | 0.49375 |  | 6.1 | 10 | 0.074 | 85.58% | 13.5 | 5.944 | 0.80244 | 0.61 | 0.066 | 0.071
| 212:00 | 80.2436 | [8 empty] | 0.49375
| 213:00 | 80.2436 | [8 empty] | 0.496 | 0.049
| 214:00 | 80.2436 | [8 empty] | 0.496
| 215:00 | 80.2436 | 6.44 | 16 | 16 | 10.3 | 117 | 173 | 19.3 | 0.508 | 0.499 |  | 6 | 10 | 0.079 | 84.45% | 13.3684 | 6.0025 | 0.80244 | 0.6 | 0.069 | 0.074
2018-11-11 | 216:00 | 80.5856 | [8 empty] | 0.499
| 217:00 | 80.5856 | [8 empty] | 0.50167
| 218:00 | 80.5856 | [8 empty] | 0.50167
| 219:00 | 80.5856 | 6.46 | 17 | 16 | 10.8 | 122 | 169 | 19.2 | 0.517 | 0.5055 |  | 6.09 | 10 | 0.088 | 82.98% | 13.6053 | 5.9231 | 0.80586 | 0.609 | 0.073 | 0.075
| 220:00 | 80.5856 | [8 empty] | 0.5055
| 221:00 | 80.5856 | [8 empty] | 0.51267
| 222:00 | 80.5856 | [8 empty] | 0.51267
| 223:00 | 80.5856 | 6.32 | 18 | 16 | 10.2 | 114 | 174 | 18.8 | 0.501 | 0.50975 |  | 6.03 | 10 | 0.08 | 84.03% | 13.1842 | 6.1123 | 0.80586 | 0.603 | 0.072 | 0.073
| 224:00 | 80.5856 | [8 empty] | 0.50975
| 225:00 | 80.5856 | [8 empty] | 0.50867 | 0.051
| 226:00 | 80.5856 | [8 empty] | 0.50867
| 227:00 | 80.5856 | 6.41 | 18 | 16 | 10.2 | 119 | 187 | 18.5 | 0.512 | 0.5095 |  | 6.02 | 10 | 0.078 | 84.77% | 13.4737 | 5.981 | 0.80586 | 0.602 | 0.069 | 0.071
| 228:00 | 80.5856 | [8 empty] | 0.5095
| 229:00 | 80.5856 | [8 empty] | 0.51
| 230:00 | 80.5856 | [8 empty] | 0.51
| 231:00 | 80.5856 | 6.44 | 18 | 17 | 10.4 | 118 | 170 | 18.5 | 0.5 | 0.5075 |  | 6.05 | 11 | 0.075 | 85% | 13.1579 | 6.1245 | 0.80586 | 0.605 | 0.066 | 0.07
| 232:00 | 80.5856 | [8 empty] | 0.5075
| 233:00 | 80.5856 | [8 empty] | 0.50433
| 234:00 | 80.5856 | [8 empty] | 0.50433
| 235:00 | 80.5856 | 6.45 | 17 | 17 | 10.1 | 117 | 170 | 18.5 | 0.499 | 0.503 |  | 6.06 | 10 | 0.08 | 83.97% | 13.1316 | 6.1368 | 0.80586 | 0.606 | 0.07 | 0.074
| 236:00 | 80.5856 | [8 empty] | 0.503
| 237:00 | 80.5856 | [8 empty] | 0.50367 | 0.041
| 238:00 | 80.5856 | [8 empty] | 0.50367
| 239:00 | 80.5856 | 6.45 | 17 | 16 | 10.2 | 118 | 172 | 18.2 | 0.505 | 0.504 |  | 6.03 | 11 | 0.088 | 82.57% | 13.2895 | 6.0639 | 0.80586 | 0.603 | 0.072 | 0.076
2018-11-12 | 240:00 | 80.4678 | [8 empty] | 0.504
| 241:00 | 80.4678 | [8 empty] | 0.50133
| 242:00 | 80.4678 | [8 empty] | 0.50133
| 243:00 | 80.4678 | 6.47 | 18 | 17 | 10.6 | 120 | 170 | 18.2 | 0.514 | 0.5045 |  | 6 | 10 | 0.082 | 84.05% | 13.5263 | 5.949 | 0.80468 | 0.6 | 0.072 | 0.076
| 244:00 | 80.4678 | [8 empty] | 0.5045
| 245:00 | 80.4678 | [8 empty] | 0.506
| 246:00 | 80.4678 | [8 empty] | 0.506
| 247:00 | 80.4678 | 6.41 | 18 | 17 | 10.4 | 109 | 170 | 17.9 | 0.487 | 0.50125 |  | 6.05 | 10 | 0.084 | 82.75% | 12.8158 | 6.2788 | 0.80468 | 0.605 | 0.075 | 0.074
| 248:00 | 80.4678 | [8 empty] | 0.50125
| 249:00 | 80.4678 | [8 empty] | 0.502 | 0.051
| 250:00 | 80.4678 | [8 empty] | 0.502
| 251:00 | 80.4678 | 6.41 | 18 | 17 | 10.5 | 117 | 179 | 17.8 | 0.503 | 0.50225 |  | 6.09 | 10 | 0.081 | 83.9% | 13.2368 | 6.0791 | 0.80468 | 0.609 | 0.07 | 0.072
| 252:00 | 80.4678 | [8 empty] | 0.50225
| 253:00 | 80.4678 | [8 empty] | 0.50133
| 254:00 | 80.4678 | [8 empty] | 0.50133
| 255:00 | 80.4678 | 6.34 | 18 | 16 | 10.3 | 108 | 170 | 17.6 | 0.466 | 0.4925 |  | 6.16 | 10 | 0.082 | 82.4% | 12.2632 | 6.5617 | 0.80468 | 0.616 | 0.072 | 0.077
| 256:00 | 80.4678 | [8 empty] | 0.4925
| 257:00 | 80.4678 | [8 empty] | 0.48533
| 258:00 | 80.4678 | [8 empty] | 0.48533
| 259:00 | 80.4678 | 6.46 | 18 | 17 | 10.1 | 114 | 170 | 17.7 | 0.489 | 0.48625 |  | 6.1 | 10 | 0.075 | 84.66% | 12.8684 | 6.2531 | 0.80468 | 0.61 | 0.067 | 0.069
| 260:00 | 80.4678 | [8 empty] | 0.48625
| 261:00 | 80.4678 | [8 empty] | 0.486 | 0.041
| 262:00 | 80.4678 | [8 empty] | 0.486
| 263:00 | 80.4678 | 6.41 | 17 | 17 | 10.2 | 116 | 172 | 17.7 | 0.488 | 0.4865 |  | 6.06 | 11 | 0.081 | 83.4% | 12.8421 | 6.2659 | 0.80468 | 0.606 | 0.071 | 0.071
2018-11-13 | 264:00 | 80.9675 | [8 empty] | 0.4865
| 265:00 | 80.9675 | [8 empty] | 0.481
| 266:00 | 80.9675 | [8 empty] | 0.481
| 267:00 | 80.9675 | 6.41 | 18 | 17 | 9.83 | 112 | 158 | 17.6 | 0.497 | 0.485 |  | 6.01 | 11 | 0.081 | 83.7% | 13.0789 | 6.1907 | 0.80968 | 0.601 | 0.069 | 0.069
| 268:00 | 80.9675 | [8 empty] | 0.485
| 269:00 | 80.9675 | [8 empty] | 0.49133
| 270:00 | 80.9675 | [8 empty] | 0.49133
| 271:00 | 80.9675 | 6.44 | 18 | 18 | 10.5 | 111 | 167 | 17.6 | 0.473 | 0.48675 |  | 6.03 | 11 | 0.071 | 84.99% | 12.4474 | 6.5048 | 0.80968 | 0.603 | 0.067 | 0.069
| 272:00 | 80.9675 | [8 empty] | 0.48675
| 273:00 | 80.9675 | [8 empty] | 0.486 | 0.061
| 274:00 | 80.9675 | [8 empty] | 0.486
| 275:00 | 80.9675 | 6.31 | 16 | 18 | 9.73 | 98 | 169 | 17.7 | 0.464 | 0.4805 |  | 6 | 11 | 0.074 | 84.05% | 12.2105 | 6.631 | 0.80968 | 0.6 | 0.071 | 0.073
| 276:00 | 80.9675 | [8 empty] | 0.4805
| 277:00 | 80.9675 | [8 empty] | 0.478
| 278:00 | 80.9675 | [8 empty] | 0.478
| 279:00 | 80.9675 | 6.69 | 18 | 17 | 9.37 | 108 | 160 | 17.9 | 0.463 | 0.47425 |  | 5.92 | 11 | 0.062 | 86.61% | 12.1842 | 6.6453 | 0.80968 | 0.592 | 0.064 | 0.064
| 280:00 | 80.9675 | [8 empty] | 0.47425
| 281:00 | 80.9675 | [8 empty] | 0.46667
| 282:00 | 80.9675 | [8 empty] | 0.46667
| 283:00 | 80.9675 | 6.5 | 18 | 17 | 9.73 | 108 | 152 | 17.8 | 0.46 | 0.465 |  | 6.1 | 11 | 0.073 | 84.13% | 12.1053 | 6.6886 | 0.80968 | 0.61 | 0.068 | 0.064
| 284:00 | 80.9675 | [8 empty] | 0.465
| 285:00 | 80.9675 | [8 empty] | 0.46233 | 0.044
| 286:00 | 80.9675 | [8 empty] | 0.46233
| 287:00 | 80.9675 | 6.37 | 17 | 17 | 9.76 | 110 | 154 | 17.7 | 0.452 | 0.45975 |  | 6.03 | 11 | 0.074 | 83.63% | 11.8947 | 6.807 | 0.80968 | 0.603 | 0.063 | 0.066
2018-11-14 | 288:00 | 81.2865 | [8 empty] | 0.45975
| 289:00 | 81.2865 | [8 empty] | 0.45833
| 290:00 | 81.2865 | [8 empty] | 0.45833
| 291:00 | 81.2865 | 6.47 | 17 | 17 | 9.53 | 108 | 166 | 17.7 | 0.472 | 0.46175 |  | 6.06 | 11 | 0.09 | 80.93% | 12.4211 | 6.5443 | 0.81286 | 0.606 | 0.066 | 0.066
| 292:00 | 81.2865 | [8 empty] | 0.46175
| 293:00 | 81.2865 | [8 empty] | 0.46133
| 294:00 | 81.2865 | [8 empty] | 0.46133
| 295:00 | 81.2865 | 6.41 | 16 | 16 | 10.1 | 106 | 160 | 17.5 | 0.451 | 0.45875 |  | 6.01 | 10 | 0.09 | 80.04% | 11.8684 | 6.849 | 0.81286 | 0.601 | 0.067 | 0.065
| 296:00 | 81.2865 | [8 empty] | 0.45875
| 297:00 | 81.2865 | [8 empty] | 0.45833 | 0.047
| 298:00 | 81.2865 | [8 empty] | 0.45833
| 299:00 | 81.2865 | 6.43 | 16 | 16 | 9.5 | 116 | 164 | 17.3 | 0.496 | 0.46775 |  | 5.96 | 8 | 0.089 | 82.06% | 13.0526 | 6.2276 | 0.81286 | 0.596 | 0.069 | 0.068
| 300:00 | 81.2865 | [8 empty] | 0.46775
| 301:00 | 81.2865 | [8 empty] | 0.473
| 302:00 | 81.2865 | [8 empty] | 0.473
| 303:00 | 81.2865 | 6.36 | 16 | 16 | 13.6 | 112 | 174 | 17.3 | 0.465 | 0.471 |  | 6.17 | 8 | 0.086 | 81.51% | 12.2368 | 6.6428 | 0.81286 | 0.617 | 0.063 | 0.059
| 304:00 | 81.2865 | [8 empty] | 0.471
| 305:00 | 81.2865 | [8 empty] | 0.47067
| 306:00 | 81.2865 | [8 empty] | 0.47067
| 307:00 | 81.2865 | 6.33 | 17 | 16 | 18 | 109 | 154 | 17.1 | 0.464 | 0.469 |  | 6.19 | 11 | 0.082 | 82.33% | 12.2105 | 6.6571 | 0.81286 | 0.619 | 0.065 | 0.062
| 308:00 | 81.2865 | [8 empty] | 0.469
| 309:00 | 81.2865 | [8 empty] | 0.475 | 0.186
| 310:00 | 81.2865 | [8 empty] | 0.475
| 311:00 | 81.2865 | 6.27 | 16 | 16 | 8.95 | 110 | 156 | 17.1 | 0.461 | 0.4715 |  | 6 | 10 | 0.087 | 81.13% | 12.1316 | 6.7004 | 0.81286 | 0.6 | 0.064 | 0.062
2018-11-15 | 312:00 | 80.428 | [8 empty] | 0.4715
| 313:00 | 80.428 | [8 empty] | 0.46333
| 314:00 | 80.428 | [8 empty] | 0.46333
| 315:00 | 80.428 | 6.54 | 18 | 16 | 8.87 | 109 | 156 | 18 | 0.44 | 0.4575 |  | 6 | 10 | 0.086 | 80.45% | 11.5789 | 6.9461 | 0.80428 | 0.6 | 0.071 | 0.064
| 316:00 | 80.428 | [8 empty] | 0.4575
| 317:00 | 80.428 | [8 empty] | 0.455
| 318:00 | 80.428 | [8 empty] | 0.455
| 319:00 | 80.428 | 6.54 | 18 | 15 | 9.31 | 109 | 156 | 16.7 | 0.454 | 0.45475 |  | 6 | 10 | 0.09 | 80.18% | 11.9474 | 6.7319 | 0.80428 | 0.6 | 0.063 | 0.062
| 320:00 | 80.428 | [8 empty] | 0.45475
| 321:00 | 80.428 | [8 empty] | 0.45167 | 0.038
| 322:00 | 80.428 | [8 empty] | 0.45167
| 323:00 | 80.428 | 6.48 | 19 | 19 | 9.19 | 109 | 157 | 16.2 | 0.462 | 0.45425 |  | 6.06 | 9 | 0.095 | 79.44% | 12.1579 | 6.6153 | 0.80428 | 0.606 | 0.066 | 0.063
| 324:00 | 80.428 | [8 empty] | 0.45425
| 325:00 | 80.428 | [8 empty] | 0.452
| 326:00 | 80.428 | [8 empty] | 0.452
| 327:00 | 80.428 | 6.56 | 19 | 18 | 9.27 | 98 | 158 | 16.6 | 0.438 | 0.4485 |  | 6.19 | 10 | 0.082 | 81.28% | 11.5263 | 6.9778 | 0.80428 | 0.619 | 0.069 | 0.071
| 328:00 | 80.428 | [8 empty] | 0.4485
| 329:00 | 80.428 | [8 empty] | 0.45133
| 330:00 | 80.428 | [8 empty] | 0.45133
| 331:00 | 80.428 | 6.53 | 21 | 18 | 9.31 | 105 | 157 | 16.3 | 0.448 | 0.4505 |  | 6.17 | 11 | 0.105 | 76.56% | 11.7895 | 6.822 | 0.80428 | 0.617 | 0.064 | 0.069
| 332:00 | 80.428 | [8 empty] | 0.4505
| 333:00 | 80.428 | [8 empty] | 0.44933 | 0.084
| 334:00 | 80.428 | [8 empty] | 0.44933
| 335:00 | 80.428 | 6.55 | 18 | 17 | 9.85 | 105 | 162 | 16.1 | 0.452 | 0.45 |  | 6.11 | 9 | 0.084 | 81.42% | 11.8947 | 6.7616 | 0.80428 | 0.611 | 0.066 | 0.07
2018-11-16 | 336:00 | 80.1774 | [8 empty] | 0.45
| 337:00 | 80.1774 | [8 empty] | 0.446
| 338:00 | 80.1774 | [8 empty] | 0.446
| 339:00 | 80.1774 | 6.6 | 20 | 18 | 10.2 | 106 | 162 | 17 | 0.436 | 0.4435 |  | 6.02 | 10 | 0.079 | 81.88% | 11.4737 | 6.9879 | 0.80177 | 0.602 | 0.057 | 0.063
| 340:00 | 80.1774 | [8 empty] | 0.4435
| 341:00 | 80.1774 | [8 empty] | 0.44533
| 342:00 | 80.1774 | [8 empty] | 0.44533
| 343:00 | 80.1774 | 6.54 | 18 | 19 | 10.3 | 107 | 164 | 16.7 | 0.437 | 0.44325 |  | 6.06 | 11 | 0.089 | 79.63% | 11.5 | 6.9719 | 0.80177 | 0.606 | 0.059 | 0.06
| 344:00 | 80.1774 | [8 empty] | 0.44325
| 345:00 | 80.1774 | [8 empty] | 0.44167 | 0.037
| 346:00 | 80.1774 | [8 empty] | 0.44167
| 347:00 | 80.1774 | 6.53 | 18 | 19 | 11.9 | 112 | 176 | 16.3 | 0.449 | 0.4435 |  | 6.03 | 10 | 0.075 | 83.3% | 11.8158 | 6.7856 | 0.80177 | 0.603 | 0.055 | 0.05
| 348:00 | 80.1774 | [8 empty] | 0.4435
| 349:00 | 80.1774 | [8 empty] | 0.44067
| 350:00 | 80.1774 | [8 empty] | 0.44067
| 351:00 | 80.1774 | 6.54 | 19 | 21 | 12.5 | 109 | 183 | 16.7 | 0.462 | 0.446 |  | 6 | 10 | 0.079 | 82.9% | 12.1579 | 6.5947 | 0.80177 | 0.6 | 0.06 | 0.059
| 352:00 | 80.1774 | [8 empty] | 0.446
| 353:00 | 80.1774 | [8 empty] | 0.44933
| 354:00 | 80.1774 | [8 empty] | 0.44933
| 355:00 | 80.1774 | 6.42 | 20 | 19 | 13.2 | 107 | 184 | 15.9 | 0.455 | 0.45075 |  | 6.01 | 10 | 0.088 | 80.66% | 11.9737 | 6.6961 | 0.80177 | 0.601 | 0.057 | 0.058
| 356:00 | 80.1774 | [8 empty] | 0.45075
| 357:00 | 80.1774 | [8 empty] | 0.45533 | 0.049
| 358:00 | 80.1774 | [8 empty] | 0.45533
| 359:00 | 80.1774 | 6.63 | 16 | 18 | 14.2 | 110 | 179 | 15.7 | 0.47 | 0.459 |  | 6.04 | 9 | 0.082 | 82.55% | 12.3684 | 6.4824 | 0.80177 | 0.604 | 0.064 | 0.066
2018-11-17 | 360:00 | 80.0969 | [8 empty] | 0.459
| 361:00 | 80.0969 | [8 empty] | 0.46233
| 362:00 | 80.0969 | [8 empty] | 0.46233
| 363:00 | 80.0969 | 6.61 | 20 | 18 | 14.4 | 106 | 196 | 16.5 | 0.443 | 0.4575 |  | 6.01 | 10 | 0.08 | 81.94% | 11.6579 | 6.8706 | 0.80097 | 0.601 | 0.058 | 0.061
| 364:00 | 80.0969 | [8 empty] | 0.4575
| 365:00 | 80.0969 | [8 empty] | 0.456
| 366:00 | 80.0969 | [8 empty] | 0.456
| 367:00 | 80.0969 | 6.54 | 21 | 18 | 15.4 | 111 | 200 | 16.1 | 0.463 | 0.45775 |  | 6.04 | 9 | 0.09 | 80.56% | 12.1842 | 6.5738 | 0.80097 | 0.604 | 0.057 | 0.055
| 368:00 | 80.0969 | [8 empty] | 0.45775
| 369:00 | 80.0969 | [8 empty] | 0.45867 | 0.051
| 370:00 | 80.0969 | [8 empty] | 0.45867
| 371:00 | 80.0969 | 6.48 | 20 | 19 | 15.7 | 113 | 201 | 16.2 | 0.463 | 0.45975 |  | 6.05 | 11 | 0.09 | 80.56% | 12.1842 | 6.5738 | 0.80097 | 0.605 | 0.061 | 0.06
| 372:00 | 80.0969 | [8 empty] | 0.45975
| 373:00 | 80.0969 | [8 empty] | 0.45633
| 374:00 | 80.0969 | [8 empty] | 0.45633
| 375:00 | 80.0969 | 6.54 | 20 | 19 | 15.8 | 114 | 206 | 15.9 | 0.474 | 0.46075 |  | 6.04 | 10 | 0.085 | 82.07% | 12.4737 | 6.4213 | 0.80097 | 0.604 | 0.067 | 0.064
| 376:00 | 80.0969 | [8 empty] | 0.46075
| 377:00 | 80.0969 | [8 empty] | 0.46667
| 378:00 | 80.0969 | [8 empty] | 0.46667
| 379:00 | 80.0969 | 6.39 | 20 | 19 | 16.1 | 111 | 205 | 15.3 | 0.473 | 0.46825 |  | 6.07 | 12 | 0.087 | 81.61% | 12.4474 | 6.4348 | 0.80097 | 0.607 | 0.06 | 0.062
| 380:00 | 80.0969 | [8 empty] | 0.46825
| 381:00 | 80.0969 | [8 empty] | 0.47 | 0.066
| 382:00 | 80.0969 | [8 empty] | 0.47
| 383:00 | 80.0969 | 6.64 | 19 | 19 | 15.4 | 114 | 204 | 15.4 | 0.484 | 0.4735 |  | 6.13 | 13 | 0.084 | 82.64% | 12.7368 | 6.2886 | 0.80097 | 0.613 | 0.06 | 0.06
2018-11-18 | 384:00 | 79.8306 | [8 empty] | 0.4735
| 385:00 | 79.8306 | [8 empty] | 0.477
| 386:00 | 79.8306 | [8 empty] | 0.477
| 387:00 | 79.8306 | 6.56 | 22 | 20 | 15.2 | 112 | 198 | 16 | 0.44 | 0.46775 |  | 6 | 12 | 0.088 | 80% | 11.5789 | 6.8945 | 0.79831 | 0.6 | 0.058 | 0.06
| 388:00 | 79.8306 | [8 empty] | 0.46775
| 389:00 | 79.8306 | [8 empty] | 0.46567
| 390:00 | 79.8306 | [8 empty] | 0.46567
| 391:00 | 79.8306 | 6.4 | 21 | 20 | 15.3 | 117 | 205 | 15.7 | 0.485 | 0.4705 |  | 6.06 | 11 | 0.099 | 79.59% | 12.7632 | 6.2548 | 0.79831 | 0.606 | 0.063 | 0.058
| 392:00 | 79.8306 | [8 empty] | 0.4705
| 393:00 | 79.8306 | [8 empty] | 0.46967 | 0.049
| 394:00 | 79.8306 | [8 empty] | 0.46967
| 395:00 | 79.8306 | 6.57 | 16 | 17 | 15.9 | 119 | 203 | 15.6 | 0.479 | 0.472 |  | 5.88 | 6 | 0.087 | 81.84% | 12.6053 | 6.3331 | 0.79831 | 0.588 | 0.059 | 0.058
| 396:00 | 79.8306 | [8 empty] | 0.472
| 397:00 | 79.8306 | [8 empty] | 0.468
| 398:00 | 79.8306 | [8 empty] | 0.468
| 399:00 | 79.8306 | 6.48 | 17 | 18 | 15.4 | 117 | 193 | 15.7 | 0.481 | 0.47125 |  | 6.18 | 9 | 0.091 | 81.08% | 12.6579 | 6.3068 | 0.79831 | 0.618 | 0.069 | 0.066
| 400:00 | 79.8306 | [8 empty] | 0.47125
| 401:00 | 79.8306 | [8 empty] | 0.48167
| 402:00 | 79.8306 | [8 empty] | 0.48167
| 403:00 | 79.8306 | 6.49 | 16 | 18 | 14.8 | 112 | 205 | 15.6 | 0.478 | 0.48075 |  | 6.16 | 9 | 0.084 | 82.43% | 12.5789 | 6.3464 | 0.79831 | 0.616 | 0.068 | 0.066
| 404:00 | 79.8306 | [8 empty] | 0.48075
| 405:00 | 79.8306 | [8 empty] | 0.47933 | 0.061
| 406:00 | 79.8306 | [8 empty] | 0.47933
| 407:00 | 79.8306 | 6.4 | 19 | 18 | 16.1 | 117 | 204 | 15.2 | 0.497 | 0.48375 |  | 5.97 | 9 | 0.082 | 83.5% | 13.0789 | 6.1038 | 0.79831 | 0.597 | 0.06 | 0.059
2018-11-19 | 408:00 | 80.093 | [8 empty] | 0.48375
| 409:00 | 80.093 | [8 empty] | 0.48533
| 410:00 | 80.093 | [8 empty] | 0.48533
| 411:00 | 80.093 | 6.5 | 20 | 18 | 15 | 114 | 200 | 16 | 0.463 | 0.47975 |  | 6 | 10 | 0.081 | 82.51% | 12.1842 | 6.5735 | 0.80093 | 0.6 | 0.058 | 0.06
| 412:00 | 80.093 | [8 empty] | 0.47975
| 413:00 | 80.093 | [8 empty] | 0.47933
| 414:00 | 80.093 | [8 empty] | 0.47933
| 415:00 | 80.093 | 6.49 | 18 | 20 | 15.6 | 121 | 205 | 15.8 | 0.487 | 0.48125 |  | 5.93 | 8 | 0.085 | 82.55% | 12.8158 | 6.2496 | 0.80093 | 0.593 | 0.054 | 0.053
| 416:00 | 80.093 | [8 empty] | 0.48125
| 417:00 | 80.093 | [8 empty] | 0.48233 | 0.044
| 418:00 | 80.093 | [8 empty] | 0.48233
| 419:00 | 80.093 | 6.45 | 20 | 20 | 14.9 | 115 | 197 | 15.8 | 0.482 | 0.48225 |  | 6.05 | 9 | 0.086 | 82.16% | 12.6842 | 6.3144 | 0.80093 | 0.605 | 0.066 | 0.065
| 420:00 | 80.093 | [8 empty] | 0.48225
| 421:00 | 80.093 | [8 empty] | 0.47733
| 422:00 | 80.093 | [8 empty] | 0.47733
| 423:00 | 80.093 | 6.46 | 18 | 19 | 14.5 | 112 | 195 | 15.7 | 0.477 | 0.47725 |  | 6.08 | 10 | 0.087 | 81.76% | 12.5526 | 6.3806 | 0.80093 | 0.608 | 0.065 | 0.064
| 424:00 | 80.093 | [8 empty] | 0.47725
| 425:00 | 80.093 | [8 empty] | 0.482
| 426:00 | 80.093 | [8 empty] | 0.482
| 427:00 | 80.093 | 6.44 | 16 | 17 | 14.1 | 117 | 198 | 15.4 | 0.489 | 0.48375 |  | 6.07 | 10 | 0.097 | 80.16% | 12.8684 | 6.224 | 0.80093 | 0.607 | 0.065 | 0.064
| 428:00 | 80.093 | [8 empty] | 0.48375
| 429:00 | 80.093 | [8 empty] | 0.48267 | 0.059
| 430:00 | 80.093 | [8 empty] | 0.48267
| 431:00 | 80.093 | 6.4 | 15 | 17 | 14.7 | 119 | 198 | 15.3 | 0.502 | 0.4875 |  | 6 | 11 | 0.087 | 82.67% | 13.2105 | 6.0628 | 0.80093 | 0.6 | 0.065 | 0.065
2018-11-20 | 432:00 | 80.7858 | [8 empty] | 0.4875
| 433:00 | 80.7858 | [8 empty] | 0.48933
| 434:00 | 80.7858 | [8 empty] | 0.48933
| 435:00 | 80.7858 | 6.51 | 20 | 18 | 14.2 | 115 | 194 | 16 | 0.477 | 0.48625 |  | 5.99 | 12 | 0.087 | 81.76% | 12.5526 | 6.4358 | 0.80786 | 0.599 | 0.066 | 0.07
| 436:00 | 80.7858 | [8 empty] | 0.48625
| 437:00 | 80.7858 | [8 empty] | 0.48933
| 438:00 | 80.7858 | [8 empty] | 0.48933
| 439:00 | 80.7858 | 6.49 | 17 | 16 | 14.1 | 121 | 196 | 16.2 | 0.499 | 0.49175 |  | 5.93 | 9 | 0.093 | 81.36% | 13.1316 | 6.152 | 0.80786 | 0.593 | 0.064 | 0.061
| 440:00 | 80.7858 | [8 empty] | 0.49175
| 441:00 | 80.7858 | [8 empty] | 0.49267 | 0.041
| 442:00 | 80.7858 | [8 empty] | 0.49267
| 443:00 | 80.7858 | 6.4 | 16 | 16 | 14.7 | 122 | 199 | 15.9 | 0.509 | 0.49675 |  | 5.89 | 9 | 0.095 | 81.34% | 13.3947 | 6.0312 | 0.80786 | 0.589 | 0.066 | 0.063
| 444:00 | 80.7858 | [8 empty] | 0.49675
| 445:00 | 80.7858 | [8 empty] | 0.495
| 446:00 | 80.7858 | [8 empty] | 0.495
| 447:00 | 80.7858 | 6.39 | 16 | 18 | 15.5 | 125 | 204 | 15.4 | 0.517 | 0.5005 |  | 6 | 9 | 0.09 | 82.59% | 13.6053 | 5.9378 | 0.80786 | 0.6 | 0.063 | 0.063
| 448:00 | 80.7858 | [8 empty] | 0.5005
| 449:00 | 80.7858 | [8 empty] | 0.50833
| 450:00 | 80.7858 | [8 empty] | 0.50833
| 451:00 | 80.7858 | 6.37 | 20 | 18 | 15 | 118 | 204 | 15.3 | 0.518 | 0.51075 |  | 5.99 | 9 | 0.094 | 81.85% | 13.6316 | 5.9264 | 0.80786 | 0.599 | 0.066 | 0.064
| 452:00 | 80.7858 | [8 empty] | 0.51075
| 453:00 | 80.7858 | [8 empty] | 0.51467 | 0.059
| 454:00 | 80.7858 | [8 empty] | 0.51467
| 455:00 | 80.7858 | 6.39 | 17 | 16 | 15.1 | 126 | 206 | 15.2 | 0.537 | 0.52025 |  | 6.01 | 9 | 0.088 | 83.61% | 14.1316 | 5.7167 | 0.80786 | 0.601 | 0.067 | 0.069
2018-11-21 | 456:00 | 87.374 | [8 empty] | 0.52025
| 457:00 | 87.374 | [8 empty] | 0.524
| 458:00 | 87.374 | [8 empty] | 0.524
| 459:00 | 87.374 | 6.43 | 18 | 16 | 14 | 123 | 202 | 16 | 0.516 | 0.522 |  | 6.02 | 10 | 0.092 | 82.17% | 13.5789 | 6.4345 | 0.87374 | 0.602 | 0.069 | 0.072
| 460:00 | 87.374 | [8 empty] | 0.522
| 461:00 | 87.374 | [8 empty] | 0.52367
| 462:00 | 87.374 | [8 empty] | 0.52367
| 463:00 | 87.374 | 6.42 | 16 | 16 | 13.5 | 128 | 220 | 15 | 0.563 | 0.5335 |  | 6.1 | 10 | 0.08 | 85.79% | 14.8158 | 5.8974 | 0.87374 | 0.61 | 0.067 | 0.067
| 464:00 | 87.374 | [8 empty] | 0.5335
| 465:00 | 87.374 | [8 empty] | 0.53867 | 0.053
| 466:00 | 87.374 | [8 empty] | 0.53867
| 467:00 | 87.374 | 6.39 | 16 | 16 | 13 | 138 | 202 | 14.7 | 0.57 | 0.5465 |  | 6.03 | 10 | 0.097 | 82.98% | 15 | 5.8249 | 0.87374 | 0.603 | 0.076 | 0.078
| 468:00 | 87.374 | [8 empty] | 0.5465
| 469:00 | 87.374 | [8 empty] | 0.54967
| 470:00 | 87.374 | [8 empty] | 0.54967
| 471:00 | 87.374 | 6.41 | 16 | 16 | 13.7 | 140 | 208 | 14.9 | 0.576 | 0.55625 |  | 6.17 | 10 | 0.089 | 84.55% | 15.1579 | 5.7643 | 0.87374 | 0.617 | 0.073 | 0.072
| 472:00 | 87.374 | [8 empty] | 0.55625
| 473:00 | 87.374 | [8 empty] | 0.56967
| 474:00 | 87.374 | [8 empty] | 0.56967
| 475:00 | 87.374 | 6.36 | 15 | 14 | 13 | 130 | 200 | 15 | 0.555 | 0.566 |  | 6.14 | 8 | 0.083 | 85.05% | 14.6053 | 5.9824 | 0.87374 | 0.614 | 0.074 | 0.079
| 476:00 | 87.374 | [8 empty] | 0.566
| 477:00 | 87.374 | [8 empty] | 0.567 | 0.048
| 478:00 | 87.374 | [8 empty] | 0.567
| 479:00 | 87.374 | 6.39 | 13 | 14 | 13.3 | 129 | 201 | 14.9 | 0.539 | 0.56 |  | 6 | 7 | 0.068 | 87.38% | 14.1842 | 6.16 | 0.87374 | 0.6 | 0.058 | 0.061
2018-11-22 | 480:00 | 100.0937 | [8 empty] | 0.56
| 481:00 | 100.0937 | [8 empty] | 0.55667
| 482:00 | 100.0937 | [8 empty] | 0.55667
| 483:00 | 100.0937 | 6.41 | 14 | 14 | 12.7 | 130 | 197 | 14.9 | 0.552 | 0.5555 |  | 6.22 | 10 | 0.073 | 86.78% | 14.5263 | 6.8905 | 1.0009 | 0.622 | 0.066 | 0.063
| 484:00 | 100.0937 | [8 empty] | 0.5555
| 485:00 | 100.0937 | [8 empty] | 0.54867
| 486:00 | 100.0937 | [8 empty] | 0.54867
| 487:00 | 100.0937 | 6.46 | 14 | 14 | 12.9 | 123 | 196 | 14.8 | 0.559 | 0.55125 |  | 6.09 | 10 | 0.079 | 85.87% | 14.7105 | 6.8042 | 1.0009 | 0.609 | 0.069 | 0.07
| 488:00 | 100.0937 | [8 empty] | 0.55125
| 489:00 | 100.0937 | [8 empty] | 0.55 | 0.05
| 490:00 | 100.0937 | [8 empty] | 0.55
| 491:00 | 100.0937 | 6.49 | 14 | 14 | 12.8 | 129 | 200 | 14.8 | 0.554 | 0.551 |  | 6.1 | 10 | 0.069 | 87.55% | 14.5789 | 6.8656 | 1.0009 | 0.61 | 0.057 | 0.06
| 492:00 | 100.0937 | [8 empty] | 0.551
| 493:00 | 100.0937 | [8 empty] | 0.555
| 494:00 | 100.0937 | [8 empty] | 0.555
| 495:00 | 100.0937 | 6.39 | 14 | 14 | 12.5 | 132 | 195 | 14.8 | 0.56 | 0.55625 |  | 6.06 | 10 | 0.074 | 86.79% | 14.7368 | 6.7921 | 1.0009 | 0.606 | 0.058 | 0.059
| 496:00 | 100.0937 | [8 empty] | 0.55625
| 497:00 | 100.0937 | [8 empty] | 0.55767
| 498:00 | 100.0937 | [8 empty] | 0.55767
| 499:00 | 100.0937 | 6.46 | 12 | 12 | 12.7 | 130 | 197 | 14.9 | 0.535 | 0.552 |  | 6.07 | 7 | 0.069 | 87.1% | 14.0789 | 7.1095 | 1.0009 | 0.607 | 0.062 | 0.061
| 500:00 | 100.0937 | [8 empty] | 0.552
| 501:00 | 100.0937 | [8 empty] | 0.54967 | 0.043
| 502:00 | 100.0937 | [8 empty] | 0.54967
| 503:00 | 100.0937 | 6.37 | 12 | 13 | 12.4 | 116 | 195 | 14.6 | 0.512 | 0.54025 |  | 6.04 | 8 | 0.074 | 85.55% | 13.4737 | 7.4288 | 1.0009 | 0.604 | 0.063 | 0.071
2018-11-23 | 504:00 | 101.7644 | [8 empty] | 0.54025
| 505:00 | 101.7644 | [8 empty] | 0.53567
| 506:00 | 101.7644 | [8 empty] | 0.53567
| 507:00 | 101.7644 | 6.26 | 12 | 12 | 12.5 | 128 | 194 | 14.6 | 0.533 | 0.535 |  | 5.91 | 8 | 0.076 | 85.74% | 14.0263 | 7.2552 | 1.0176 | 0.591 | 0.067 | 0.06
| 508:00 | 101.7644 | [8 empty] | 0.535
| 509:00 | 101.7644 | [8 empty] | 0.52667
| 510:00 | 101.7644 | [8 empty] | 0.52667
| 511:00 | 101.7644 | 6.36 | 14 | 14 | 12.7 | 130 | 196 | 14.4 | 0.56 | 0.535 |  | 5.8 | 8 | 0.109 | 80.54% | 14.7368 | 6.9054 | 1.0176 | 0.58 | 0.055 | 0.063
| 512:00 | 101.7644 | [8 empty] | 0.535
| 513:00 | 101.7644 | [8 empty] | 0.535 | 0.046
| 514:00 | 101.7644 | [8 empty] | 0.535
| 515:00 | 101.7644 | 6.31 | 12 | 12 | 12.8 | 132 | 199 | 14.3 | 0.557 | 0.5405 |  | 6.03 | 8 | 0.083 | 85.1% | 14.6579 | 6.9426 | 1.0176 | 0.603 | 0.063 | 0.066
| 516:00 | 101.7644 | [8 empty] | 0.5405
| 517:00 | 101.7644 | [8 empty] | 0.55
| 518:00 | 101.7644 | [8 empty] | 0.55
| 519:00 | 101.7644 | 6.29 | 13 | 12 | 13.1 | 136 | 200 | 14 | 0.563 | 0.55325 |  | 6.1 | 8 | 0.093 | 83.48% | 14.8158 | 6.8686 | 1.0176 | 0.61 | 0.065 | 0.067
| 520:00 | 101.7644 | [8 empty] | 0.55325
| 521:00 | 101.7644 | [8 empty] | 0.56
| 522:00 | 101.7644 | [8 empty] | 0.56
| 523:00 | 101.7644 | 6.34 | 12 | 12 | 12.7 | 117 | 190 | 14.3 | 0.507 | 0.54675 |  | 6.03 | 8 | 0.088 | 82.64% | 13.3421 | 7.6273 | 1.0176 | 0.603 | 0.06 | 0.062
| 524:00 | 101.7644 | [8 empty] | 0.54675
| 525:00 | 101.7644 | [8 empty] | 0.54233 | 0.043
| 526:00 | 101.7644 | [8 empty] | 0.54233
| 527:00 | 101.7644 | 6.36 | 12 | 12 | 12.8 | 112 | 191 | 14.2 | 0.509 | 0.534 |  | 5.94 | 8 | 0.076 | 85.07% | 13.3947 | 7.5973 | 1.0176 | 0.594 | 0.064 | 0.064
2018-11-24 | 528:00 | 101.6898 | [8 empty] | 0.534
| 529:00 | 101.6898 | [8 empty] | 0.52633
| 530:00 | 101.6898 | [8 empty] | 0.52633
| 531:00 | 101.6898 | 6.34 | 12 | 12 | 12.7 | 121 | 185 | 14.2 | 0.55 | 0.53225 |  | 5.85 | 7 | 0.079 | 85.64% | 14.4737 | 7.0258 | 1.0169 | 0.585 | 0.067 | 0.066
| 532:00 | 101.6898 | [8 empty] | 0.53225
| 533:00 | 101.6898 | [8 empty] | 0.522
| 534:00 | 101.6898 | [8 empty] | 0.522
| 535:00 | 101.6898 | 6.31 | 12 | 12 | 12.3 | 128 | 188 | 14.2 | 0.542 | 0.527 |  | 5.96 | 8 | 0.071 | 86.9% | 14.2632 | 7.1295 | 1.0169 | 0.596 | 0.061 | 0.076
| 536:00 | 101.6898 | [8 empty] | 0.527
| 537:00 | 101.6898 | [8 empty] | 0.53367 | 0.042
| 538:00 | 101.6898 | [8 empty] | 0.53367
| 539:00 | 101.6898 | 6.33 | 12 | 12 | 11.9 | 126 | 189 | 14.3 | 0.536 | 0.53425 |  | 6 | 8 | 0.075 | 86.01% | 14.1053 | 7.2094 | 1.0169 | 0.6 | 0.069 | 0.073
| 540:00 | 101.6898 | [8 empty] | 0.53425
| 541:00 | 101.6898 | [8 empty] | 0.54267
| 542:00 | 101.6898 | [8 empty] | 0.54267
| 543:00 | 101.6898 | 6.38 | 12 | 12 | 11.7 | 114 | 173 | 14.4 | 0.548 | 0.544 |  | 5.99 | 8 | 0.081 | 85.22% | 14.4211 | 7.0515 | 1.0169 | 0.599 | 0.07 | 0.072
| 544:00 | 101.6898 | [8 empty] | 0.544
| 545:00 | 101.6898 | [8 empty] | 0.542
| 546:00 | 101.6898 | [8 empty] | 0.542
| 547:00 | 101.6898 | 6.39 | 10 | 15 | 11.6 | 115 | 180 | 14.9 | 0.489 | 0.52875 |  | 6.08 | 9 | 0.069 | 85.89% | 12.8684 | 7.9023 | 1.0169 | 0.608 | 0.056 | 0.064
| 548:00 | 101.6898 | [8 empty] | 0.52875
| 549:00 | 101.6898 | [8 empty] | 0.52433 | 0.039
| 550:00 | 101.6898 | [8 empty] | 0.52433
| 551:00 | 101.6898 | 6.36 | 11 | 14 | 10.8 | 116 | 182 | 14.7 | 0.505 | 0.5195 |  | 6.01 | 8 | 0.086 | 82.97% | 13.2895 | 7.6519 | 1.0169 | 0.601 | 0.064 | 0.064
2018-11-25 | 552:00 | 96.8519 | [8 empty] | 0.5195
| 553:00 | 96.8519 | [8 empty] | 0.514
| 554:00 | 96.8519 | [8 empty] | 0.514
| 555:00 | 96.8519 | 6.57 | 13 | 15 | 10.8 | 114 | 183 | 14.8 | 0.509 | 0.51275 |  | 6.01 | 8 | 0.082 | 83.89% | 13.3947 | 7.2306 | 0.96852 | 0.601 | 0.062 | 0.06
| 556:00 | 96.8519 | [8 empty] | 0.51275
| 557:00 | 96.8519 | [8 empty] | 0.501
| 558:00 | 96.8519 | [8 empty] | 0.501
| 559:00 | 96.8519 | 6.31 | 12 | 14 | 10.8 | 128 | 180 | 14.1 | 0.554 | 0.51425 |  | 6.01 | 8 | 0.081 | 85.38% | 14.5789 | 6.6433 | 0.96852 | 0.601 | 0.06 | 0.063
| 560:00 | 96.8519 | [8 empty] | 0.51425
| 561:00 | 96.8519 | [8 empty] | 0.52267 | 0.049
| 562:00 | 96.8519 | [8 empty] | 0.52267
| 563:00 | 96.8519 | 6.22 | 12 | 12 | 10.5 | 131 | 180 | 14.3 | 0.546 | 0.5285 |  | 6 | 8 | 0.078 | 85.71% | 14.3684 | 6.7406 | 0.96852 | 0.6 | 0.06 | 0.06
| 564:00 | 96.8519 | [8 empty] | 0.5285
| 565:00 | 96.8519 | [8 empty] | 0.53633
| 566:00 | 96.8519 | [8 empty] | 0.53633
| 567:00 | 96.8519 | 6.25 | 12 | 12 | 10.6 | 126 | 180 | 14.5 | 0.56 | 0.54225 |  | 6.1 | 8 | 0.082 | 85.36% | 14.7368 | 6.5721 | 0.96852 | 0.61 | 0.063 | 0.064
| 568:00 | 96.8519 | [8 empty] | 0.54225
| 569:00 | 96.8519 | [8 empty] | 0.55333
| 570:00 | 96.8519 | [8 empty] | 0.55333
| 571:00 | 96.8519 | 6.26 | 11 | 14 | 9.71 | 125 | 177 | 14.6 | 0.543 | 0.55075 |  | 6.1 | 8 | 0.072 | 86.74% | 14.2895 | 6.7779 | 0.96852 | 0.61 | 0.065 | 0.061
| 572:00 | 96.8519 | [8 empty] | 0.55075
| 573:00 | 96.8519 | [8 empty] | 0.54967 | 0.04
| 574:00 | 96.8519 | [8 empty] | 0.54967
| 575:00 | 96.8519 | 6.18 | 10 | 14 | 9.8 | 127 | 178 | 14.6 | 0.502 | 0.53775 |  | 5.96 | 7 | 0.069 | 86.25% | 13.2105 | 7.3314 | 0.96852 | 0.596 | 0.065 | 0.068
2018-11-26 | 576:00 | 105.5734 | [8 empty] | 0.53775
| 577:00 | 105.5734 | [8 empty] | 0.535
| 578:00 | 105.5734 | [8 empty] | 0.535
| 579:00 | 105.5734 | 6.24 | 11 | 13 | 9.87 | 121 | 178 | 14.5 | 0.549 | 0.5385 |  | 5.87 | 7 | 0.073 | 86.7% | 14.4474 | 7.3075 | 1.0557 | 0.587 | 0.067 | 0.067
| 580:00 | 105.5734 | [8 empty] | 0.5385
| 581:00 | 105.5734 | [8 empty] | 0.53133
| 582:00 | 105.5734 | [8 empty] | 0.53133
| 583:00 | 105.5734 | 6.22 | 11 | 12 | 9.87 | 123 | 178 | 14.5 | 0.568 | 0.5405 |  | 5.94 | 8 | 0.088 | 84.51% | 14.9474 | 7.063 | 1.0557 | 0.594 | 0.073 | 0.076
| 584:00 | 105.5734 | [8 empty] | 0.5405
| 585:00 | 105.5734 | [8 empty] | 0.53967 | 0.037
| 586:00 | 105.5734 | [8 empty] | 0.53967
| 587:00 | 105.5734 | 6.22 | 11 | 12 | 9.84 | 128 | 179 | 14.6 | 0.555 | 0.5435 |  | 6.1 | 8 | 0.084 | 84.86% | 14.6053 | 7.2285 | 1.0557 | 0.61 | 0.061 | 0.063
| 588:00 | 105.5734 | [8 empty] | 0.5435
| 589:00 | 105.5734 | [8 empty] | 0.55733
| 590:00 | 105.5734 | [8 empty] | 0.55733
| 591:00 | 105.5734 | 6.23 | 11 | 12 | 9.83 | 129 | 182 | 14.7 | 0.563 | 0.55875 |  | 6.09 | 8 | 0.079 | 85.97% | 14.8158 | 7.1257 | 1.0557 | 0.609 | 0.06 | 0.063
| 592:00 | 105.5734 | [8 empty] | 0.55875
| 593:00 | 105.5734 | [8 empty] | 0.562
| 594:00 | 105.5734 | [8 empty] | 0.562
| 595:00 | 105.5734 | 6.16 | 11 | 12 | 9.98 | 132 | 180 | 14.7 | 0.564 | 0.5625 |  | 6.05 | 7 | 0.074 | 86.88% | 14.8421 | 7.1131 | 1.0557 | 0.605 | 0.071 | 0.072
| 596:00 | 105.5734 | [8 empty] | 0.5625
| 597:00 | 105.5734 | [8 empty] | 0.56067 | 0.038
| 598:00 | 105.5734 | [8 empty] | 0.56067
| 599:00 | 105.5734 | 6.13 | 10 | 13 | 9.97 | 123 | 179 | 14.5 | 0.545 | 0.55675 |  | 6.03 | 8 | 0.076 | 86.06% | 14.3421 | 7.3611 | 1.0557 | 0.603 | 0.064 | 0.066
2018-11-27 | 600:00 | 115.9817 | [8 empty] | 0.55675
| 601:00 | 115.9817 | [8 empty] | 0.55733
| 602:00 | 115.9817 | [8 empty] | 0.55733
| 603:00 | 115.9817 | 6.26 | 11 | 13 | 9.97 | 121 | 181 | 14.4 | 0.532 | 0.551 |  | 5.9 | 7 | 0.071 | 86.65% | 14 | 8.2844 | 1.1598 | 0.59 | 0.067 | 0.065
| 604:00 | 115.9817 | [8 empty] | 0.551
| 605:00 | 115.9817 | [8 empty] | 0.547
| 606:00 | 115.9817 | [8 empty] | 0.547
| 607:00 | 115.9817 | 6.25 | 10 | 12 | 9.64 | 133 | 180 | 14.1 | 0.58 | 0.55525 |  | 5.98 | 8 | 0.068 | 88.28% | 15.2632 | 7.5988 | 1.1598 | 0.598 | 0.058 | 0.064
| 608:00 | 115.9817 | [8 empty] | 0.55525
| 609:00 | 115.9817 | [8 empty] | 0.55233 | 0.049
| 610:00 | 115.9817 | [8 empty] | 0.55233
| 611:00 | 115.9817 | 6.16 | 10 | 12 | 9.62 | 130 | 178 | 14.2 | 0.574 | 0.55775 |  | 6.08 | 8 | 0.077 | 86.59% | 15.1053 | 7.6782 | 1.1598 | 0.608 | 0.063 | 0.062
| 612:00 | 115.9817 | [8 empty] | 0.55775
| 613:00 | 115.9817 | [8 empty] | 0.562
| 614:00 | 115.9817 | [8 empty] | 0.562
| 615:00 | 115.9817 | 6.35 | 10 | 12 | 9.84 | 132 | 174 | 14.3 | 0.574 | 0.565 |  | 6.25 | 9 | 0.081 | 85.89% | 15.1053 | 7.6782 | 1.1598 | 0.625 | 0.063 | 0.074
| 616:00 | 115.9817 | [8 empty] | 0.565
| 617:00 | 115.9817 | [8 empty] | 0.576
| 618:00 | 115.9817 | [8 empty] | 0.576
| 619:00 | 115.9817 | 6.27 | 11 | 15 | 9.7 | 126 | 175 | 13.9 | 0.559 | 0.57175 |  | 6.18 | 8 | 0.08 | 85.69% | 14.7105 | 7.8843 | 1.1598 | 0.618 | 0.065 | 0.075
| 620:00 | 115.9817 | [8 empty] | 0.57175
| 621:00 | 115.9817 | [8 empty] | 0.569 | 0.036
| 622:00 | 115.9817 | [8 empty] | 0.569
| 623:00 | 115.9817 | 6.32 | 10 | 15 | 8.98 | 117 | 174 | 14.1 | 0.519 | 0.5565 |  | 6.23 | 9 | 0.073 | 85.93% | 13.6579 | 8.4919 | 1.1598 | 0.623 | 0.068 | 0.072
2018-11-28 | 624:00 | 116.4084 | [8 empty] | 0.5565
| 625:00 | 116.4084 | [8 empty] | 0.55067
| 626:00 | 116.4084 | [8 empty] | 0.55067
| 627:00 | 116.4084 | 6.28 | 10 | 14 | 9.32 | 131 | 175 | 13.9 | 0.571 | 0.55575 |  | 6.06 | 8 | 0.077 | 86.51% | 15.0263 | 7.747 | 1.1641 | 0.606 | 0.071 | 0.076
| 628:00 | 116.4084 | [8 empty] | 0.55575
| 629:00 | 116.4084 | [8 empty] | 0.54967
| 630:00 | 116.4084 | [8 empty] | 0.54967
| 631:00 | 116.4084 | 6.09 | 11 | 16 | 8.86 | 130 | 176 | 13.9 | 0.555 | 0.551 |  | 6.32 | 9 | 0.057 | 89.73% | 14.6053 | 7.9703 | 1.1641 | 0.632 | 0.058 | 0.066
| 632:00 | 116.4084 | [8 empty] | 0.551
| 633:00 | 116.4084 | [8 empty] | 0.54833 | 0.046
| 634:00 | 116.4084 | [8 empty] | 0.54833
| 635:00 | 116.4084 | 6.22 | 14 | 15 | 8.62 | 125 | 177 | 13.7 | 0.552 | 0.54925 |  | 6.18 | 10 | 0.087 | 84.24% | 14.5263 | 8.0136 | 1.1641 | 0.618 | 0.058 | 0.061
| 636:00 | 116.4084 | [8 empty] | 0.54925
| 637:00 | 116.4084 | [8 empty] | 0.55933
| 638:00 | 116.4084 | [8 empty] | 0.55933
| 639:00 | 116.4084 | 6.26 | 15 | 15 | 8.34 | 122 | 170 | 14.5 | 0.531 | 0.55225 |  | 6.15 | 10 | 0.075 | 85.88% | 13.9737 | 8.3305 | 1.1641 | 0.615 | 0.052 | 0.052
| 640:00 | 116.4084 | [8 empty] | 0.55225
| 641:00 | 116.4084 | [8 empty] | 0.546
| 642:00 | 116.4084 | [8 empty] | 0.546
| 643:00 | 116.4084 | 6.34 | 12 | 18 | 8.4 | 130 | 169 | 14.6 | 0.555 | 0.54825 |  | 6.15 | 8 | 0.097 | 82.52% | 14.6053 | 7.9703 | 1.1641 | 0.615 | 0.058 | 0.056
| 644:00 | 116.4084 | [8 empty] | 0.54825
| 645:00 | 116.4084 | [8 empty] | 0.546 | 0.03
| 646:00 | 116.4084 | [8 empty] | 0.546
| 647:00 | 116.4084 | 6.34 | 10 | 17 | 8.33 | 128 | 171 | 14.1 | 0.548 | 0.5465 |  | 6.05 | 9 | 0.079 | 85.58% | 14.4211 | 8.0721 | 1.1641 | 0.605 | 0.061 | 0.062
2018-11-29 | 648:00 | 107.407 | [8 empty] | 0.5465
| 649:00 | 107.407 | [8 empty] | 0.54467
| 650:00 | 107.407 | [8 empty] | 0.54467
| 651:00 | 107.407 | 6.31 | 11 | 16 | 8.29 | 131 | 172 | 13.9 | 0.567 | 0.55025 |  | 6 | 8 | 0.092 | 83.77% | 14.9211 | 7.1984 | 1.0741 | 0.6 | 0.062 | 0.061
| 652:00 | 107.407 | [8 empty] | 0.55025
| 653:00 | 107.407 | [8 empty] | 0.55667
| 654:00 | 107.407 | [8 empty] | 0.55667
| 655:00 | 107.407 | 6.26 | 15 | 16 | 8.33 | 127 | 174 | 13.1 | 0.56 | 0.5575 |  | 6.11 | 10 | 0.098 | 82.5% | 14.7368 | 7.2883 | 1.0741 | 0.611 | 0.062 | 0.063
| 656:00 | 107.407 | [8 empty] | 0.5575
| 657:00 | 107.407 | [8 empty] | 0.55833 | 0.039
| 658:00 | 107.407 | [8 empty] | 0.55833
| 659:00 | 107.407 | 6.29 | 11 | 15 | 8.29 | 135 | 175 | 13.1 | 0.578 | 0.56325 |  | 6.21 | 7 | 0.099 | 82.87% | 15.2105 | 7.0614 | 1.0741 | 0.621 | 0.061 | 0.061
| 660:00 | 107.407 | [8 empty] | 0.56325
| 661:00 | 107.407 | [8 empty] | 0.56833
| 662:00 | 107.407 | [8 empty] | 0.56833
| 663:00 | 107.407 | 6.25 | 12 | 15 | 8.1 | 128 | 172 | 13.8 | 0.543 | 0.562 |  | 6.12 | 9 | 0.087 | 83.98% | 14.2895 | 7.5165 | 1.0741 | 0.612 | 0.066 | 0.068
| 664:00 | 107.407 | [8 empty] | 0.562
| 665:00 | 107.407 | [8 empty] | 0.56033
| 666:00 | 107.407 | [8 empty] | 0.56033
| 667:00 | 107.407 | 6.32 | 13 | 18 | 8.19 | 134 | 173 | 13.7 | 0.562 | 0.56075 |  | 6.19 | 9 | 0.114 | 79.72% | 14.7895 | 7.2624 | 1.0741 | 0.619 | 0.065 | 0.064
| 668:00 | 107.407 | [8 empty] | 0.56075
| 669:00 | 107.407 | [8 empty] | 0.561 | 0.032
| 670:00 | 107.407 | [8 empty] | 0.561
| 671:00 | 107.407 | 6.31 | 14 | 21 | 8.45 | 132 | 176 | 13.4 | 0.564 | 0.56175 |  | 6.21 | 10 | 0.099 | 82.45% | 14.8421 | 7.2366 | 1.0741 | 0.621 | 0.066 | 0.065
2018-11-30 | 672:00 | 112.0739 | [8 empty] | 0.56175
| 673:00 | 112.0739 | [8 empty] | 0.55633
| 674:00 | 112.0739 | [8 empty] | 0.55633
| 675:00 | 112.0739 | 6.28 | 10 | 20 | 8.17 | 137 | 180 | 13.5 | 0.569 | 0.5595 |  | 6.13 | 9 | 0.096 | 83.13% | 14.9737 | 7.4847 | 1.1207 | 0.613 | 0.065 | 0.066
| 676:00 | 112.0739 | [8 empty] | 0.5595
| 677:00 | 112.0739 | [8 empty] | 0.565
| 678:00 | 112.0739 | [8 empty] | 0.565
| 679:00 | 112.0739 | 6.21 | 12 | 17 | 8.44 | 129 | 176 | 12.7 | 0.562 | 0.56425 |  | 6.14 | 10 | 0.092 | 83.63% | 14.7895 | 7.578 | 1.1207 | 0.614 | 0.064 | 0.063
| 680:00 | 112.0739 | [8 empty] | 0.56425
| 681:00 | 112.0739 | [8 empty] | 0.565 | 0.043
| 682:00 | 112.0739 | [8 empty] | 0.565
| 683:00 | 112.0739 | 6.39 | 13 | 17 | 8.03 | 134 | 183 | 13.1 | 0.572 | 0.56675 |  | 6.09 | 9 | 0.074 | 87.06% | 15.0526 | 7.4455 | 1.1207 | 0.609 | 0.064 | 0.066
| 684:00 | 112.0739 | [8 empty] | 0.56675
| 685:00 | 112.0739 | [8 empty] | 0.56767
| 686:00 | 112.0739 | [8 empty] | 0.56767
| 687:00 | 112.0739 | 6.33 | 12 | 18 | 8.08 | 129 | 174 | 13.2 | 0.574 | 0.56925 |  | 6.24 | 8 | 0.074 | 87.11% | 15.1053 | 7.4195 | 1.1207 | 0.624 | 0.068 | 0.069
| 688:00 | 112.0739 | [8 empty] | 0.56925
| 689:00 | 112.0739 | [8 empty] | 0.56933
| 690:00 | 112.0739 | [8 empty] | 0.56933
| 691:00 | 112.0739 | 6.32 | 12 | 20 | 9.05 | 132 | 174 | 13.8 | 0.544 | 0.563 |  | 6.17 | 9 | 0.075 | 86.21% | 14.3158 | 7.8287 | 1.1207 | 0.617 | 0.05 | 0.051
| 692:00 | 112.0739 | [8 empty] | 0.563
| 693:00 | 112.0739 | [8 empty] | 0.56333 | 0.03
| 694:00 | 112.0739 | [8 empty] | 0.56333
| 695:00 | 112.0739 | 6.31 | 13 | 19 | 7.95 | 130 | 172 | 13.8 | 0.548 | 0.5595 |  | 6.19 | 10 | 0.083 | 84.85% | 14.4211 | 7.7715 | 1.1207 | 0.619 | 0.063 | 0.064
2018-12-01 | 696:00 | 0 | [8 empty] | 0.5595
. | 697:00 | 0 | [8 empty] | 0.55533
| 698:00 | 0 | [8 empty] | 0.55533
| 699:00 | 0 | [8 empty] | 0.55533
| 700:00 | 0 | [8 empty] | 0.55533
| 701:00 | 0 | [8 empty] | 0.546
| 702:00 | 0 | [8 empty] | 0.546
| 703:00 | 0 | [8 empty] | 0.546
| 704:00 | 0 | [8 empty] | 0.546
| 705:00 | 0 | [8 empty] | 0.548
| 706:00 | 0 | [8 empty] | 0.548
| 707:00 | 0 | [8 empty] | 0.548
| 708:00 | 0 | [8 empty] | 0.548
| 709:00 | 0 | [8 empty] | #DIV/0!
| 710:00 | 0 | [8 empty] | #DIV/0!
| 711:00 | 0 | [8 empty] | #DIV/0!
| 712:00 | 0 | [8 empty] | #DIV/0!
| 713:00 | 0 | [8 empty] | #DIV/0!
| 714:00 | 0 | [8 empty] | #DIV/0!
| 715:00 | 0 | [8 empty] | #DIV/0!
| 716:00 | 0 | [8 empty] | #DIV/0!
| 717:00 | 0 | [8 empty] | #DIV/0!
| 718:00 | 0 | [8 empty] | #DIV/0!
| 719:00 | 0 | [8 empty] | #DIV/0!
TOTAL |  | 64817.9732 | 1153.18 | 2931.21 | 2948 | 2110.71 | 21374 | 32837 | 3019.8 | 91.945 |  | 3.104 | 1088.66 | 1745 | 14.979 | 150.5175 | 2419.6053 | 1203.5469 | 162.0449 | 108.866 | 11.621 | 11.795
AVERAGE |  | 87.1046 | 6.4066 | 16.2845 | 16.3778 | 11.7262 | 118.7444 | 182.4278 | 16.7767 | 0.51081 |  | 0.051733 | 6.0481 | 9.6944 | 0.083217 | 0.83621 | 13.4423 | 6.6864 | 0.90025 | 0.60481 | 0.064561 | 0.065528
MINIMUM |  | 0 | 6.09 | 10 | 12 | 7.95 | 84 | 152 | 12.7 | 0.42 |  | 0.03 | 5.78 | 6 | 0.057 | 0.76562 | 11.0526 | 5.6449 | 0.76458 | 0.578 | 0.05 | 0.05
MAXIMUM |  | 116.4084 | 6.69 | 22 | 21 | 18 | 140 | 225 | 20.5 | 0.58 |  | 0.186 | 8 | 14 | 0.114 | 0.8973 | 15.2632 | 8.4919 | 1.1641 | 0.8 | 0.08 | 0.084
09:19 |  | 09:19 | [13 empty] | HIGHLIGHT BETWEEN LIME |  | 5
08/12/19 |  | 08/13/19 | [12 empty] | TOTAL # IN THIS RANGE |  | 0 | 5.5
| 09:19 |  | TRUE | [11 empty] | TOTAL SAMPLES |  | 180
FALSE
WHAT
2019-08-12 09:20
1901-12-21
Formulas:
Date = MATCH([Date, row above],A4:A747,1)

## BW 1
|  | Surface Water System Monthly Operation Report | [10 empty] | DATE | TIME
|  | Operation of Filters | [9 empty] | LAST WASH | 1900-01-27 | 4:00 | 1900-01-27 04:00
|  | Bureau of Water | [9 empty] | THIS WASH | 1900-01-29 | 6:00 | 1900-01-29 06:00
TOTAL HOURS
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 1 |  |  |  |  | 2018-11-01 | [8 empty] | 50
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED
2018-11-01
2018-11-02 | 3:00 | 20 | 30 | 27 | 117200 | 55729.1667 | 10.7 | 6581.4653 | GE | L O H | 172929.1667
2018-11-03
2018-11-04
2018-11-05 | 16:00 | 20 | 30 | 85 | 117200 | 57291.6667 | 11 | 21300.3463 | DH |  | 174491.6667
2018-11-06
2018-11-07
2018-11-08
2018-11-09 | 12:30 | 20 | 30 | 92.5 | 117200 | 57291.6667 | 11 | 23179.7886 | SN | HEAD | 174491.6667
2018-11-10
2018-11-11
2018-11-12 | 16:30 | 20 | 30 | 76 | 117200 | 53645.8333 | 10.3 | 17833.06 | SN | HEAD | 170845.8333
2018-11-13
2018-11-14
2018-11-15
2018-11-16 | 23:30 | 20 | 30 | 103 | 117200 | 53645.8333 | 10.3 | 24168.4892 | DH |  | 170845.8333
2018-11-17
2018-11-18
2018-11-19
2018-11-20
2018-11-21 | 4:30 | 20 | 30 | 101 | 117200 | 53645.8333 | 10.3 | 23699.1981 | DH |  | 170845.8333
2018-11-22
2018-11-23 | 15:30 | 20 | 30 | 59 | 117200 | 52083.3333 | 10 | 13440.8602 | JMM |  | 169283.3333
2018-11-24
2018-11-25
2018-11-26 | 2:00 | 20 | 30 | 59.5 | 117200 | 50000 | 9.6 | 13012.5752 | R.H. | H.L. | 167200
2018-11-27
2018-11-28 | 4:00 | 20 | 30 | 46 | 117200 | 55729.1667 | 10.7 | 11212.8668 | R.H. | H.L. | 172929.1667
2018-11-29
2018-11-30 | 7:00 | 20 | 30 | 51 | 117200 | 57291.6667 | 11 | 12780.2078 | DH |  | 174491.6667
2018-12-01
Total |  | 200 | 300 | 700 | 1172000
Average |  | 20 | 30 | 70 | 117200
Maximum |  | 20 | 30 | 103 | 117200
Minimum |  | 20 | 30 | 27 | 117200
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Formulas:
Day = [Day, row above]+1
Note on F8: BCOperator: 5860 = water wash / min

## BW 2
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 2 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-22 | 23:00 | 1900-01-22 23:00
2 | 8:00 | 20 | 30 | 56 | 117200 | 55729.1667 | 10.7 | 11405.5124 | DH |  | 172929.1667 | THIS WASH | 1900-01-25 | 8:30 | 1900-01-25 08:30
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 57.5
6 | 8:00 | 20 | 30 | 96 | 117200 | 53645.8333 | 10.3 | 18821.3796 | DH |  | 170845.8333
7
8
9
10 | 8:00 | 20 | 30 | 96 | 117200 | 57291.6667 | 11 | 20100.5025 | MN | HEAD | 174491.6667
11
12
13 | 12:30 | 20 | 30 | 76.5 | 117200 | 48437.5 | 9.3 | 13542.1425 | S.N. |  | 165637.5
14
15
16
17 | 13:00 | 20 | 30 | 96.5 | 117200 | 54166.6667 | 10.4 | 19103.0912 | GHE | HEAD | 171366.6667
18
19
20
21 | 12:30 | 20 | 30 | 95.5 | 117200 | 55208.3333 | 10.6 | 19268.6919 | JMM |  | 172408.3333
22
23 | 23:00 | 20 | 30 | 58.5 | 117200 | 55729.1667 | 10.7 | 11914.6871 | SN | HEAD | 172929.1667
24
25
26 | 8:30 | 20 | 35 | 57.5 | 117200 | 58333.3333 | 9.6 | 10507.0809 | CBW |  | 175533.3333
27
28 | 8:30 | 20 | 30 | 48 | 117200 | 55729.1667 | 10.7 | 9776.1535 | DH |  | 172929.1667
29
30 | 8:30 | 20 | 30 | 48 | 117200 | 57291.6667 | 11 | 10050.2513 | SN | HEAD | 174491.6667
31
Total |  | 200 | 305 | 728.5 | 1172000
Average |  | 20 | 30.5 | 72.85 | 117200
Maximum |  | 20 | 35 | 96.5 | 117200
Minimum |  | 20 | 30 | 48 | 117200
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash /min

## BW 3
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 3 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 15:00 | 20 | 30 | 15 | 117200 | 55729.1667 | 10.7 | 3656.3696 | DH |  | 172929.1667 | LAST WASH | 1900-01-24 | 9:30 | 1900-01-24 09:30
2 | [11 empty] | THIS WASH | 1900-01-26 | 11:00 | 1900-01-26 11:00
3 | [12 empty] | TOTAL HOURS
4 | 15:00 | 20 | 30 | 72 | 117200 | 55729.1667 | 10.7 | 17550.5741 | DH |  | 172929.1667
5 | [13 empty] | 49.5
6
7
8 | 10:00 | 20 | 30 | 91 | 117200 | 50520.8333 | 9.7 | 20108.8937 | SN | HEAD | 167720.8333
9
10
11 | 1:00 | 20 | 30 | 63 | 117200 | 53645.8333 | 10.3 | 14782.6681 | JMM |  | 170845.8333
12
13
14
15 | 9:00 | 20 | 30 | 104 | 117200 | 48437.5 | 9.3 | 22033.8983 | DB | L O H | 165637.5
16
17
18 | 21:00 | 20 | 30 | 84 | 117200 | 53645.8333 | 10.3 | 19710.2242 | DH |  | 170845.8333
19
20
21 | 20:30 | 20 | 30 | 71.5 | 117200 | 55208.3333 | 10.6 | 17265.8101 | SN | LOH | 172408.3333
22
23 | 9:30 | 20 | 30 | 36.5 | 117200 | 52083.3333 | 10 | 8315.1084 | JMM |  | 169283.3333
24
25 | 9:30 | 20 | 30 | 48 | 117200 | 55729.1667 | 10.7 | 11700.3827 | CBW |  | 172929.1667
26
27 | 11:00 | 25 | 30 | 49.5 | 146500 | 57291.6667 | 11 | 12404.3193 | WL |  | 203791.6667
28
29 | 9:00 | 20 | 30 | 46 | 117200 | 53645.8333 | 10.3 | 10793.6942 | MN | HEAD | 170845.8333
30
31
Total |  | 225 | 330 | 680.5 | 1318500
Average |  | 20.4545 | 30 | 61.8636 | 119863.6364
Maximum |  | 25 | 30 | 104 | 146500
Minimum |  | 20 | 30 | 15 | 117200
|  | 11 | 11 | 11 | 11
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 4
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 4 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-22 | 4:00 | 1900-01-22 04:00
2 | 6:00 | 20 | 30 | 54 | 117200 | 55729.1667 | 10.7 | 13162.9306 | MN |  | 172929.1667 | THIS WASH | 1900-01-24 | 6:30 | 1900-01-24 06:30
3 | [12 empty] | TOTAL HOURS
4
5 | 6:30 | 20 | 30 | 72.5 | 117200 | 62500 | 12 | 19819.5735 | DH |  | 179700 |  |  | 50.5
6
7
8
9 | 1:00 | 20 | 30 | 90.5 | 117200 | 52083.3333 | 10 | 20616.9127 | JMM |  | 169283.3333
10
11
12 | 0:30 | 20 | 30 | 71.5 | 117200 | 52083.3333 | 10 | 16288.5001 | JMM |  | 169283.3333
13
14
15
16 | 11:30 | 20 | 30 | 107 | 117200 | 49479.1667 | 9.5 | 23157.0075 | GHE | HEAD | 166679.1667
17
18
19
20 | 14:00 | 20 | 30 | 98.5 | 117200 | 50520.8333 | 9.7 | 21766.2202 | GE | L O H | 167720.8333
21
22
23 | 4:00 | 20 | 30 | 62 | 117200 | 52083.3333 | 10 | 14124.2938 | R.H. |  | 169283.3333
24
25 | 6:30 | 20 | 30 | 50.5 | 117200 | 55729.1667 | 10.7 | 12309.7777 | JMM |  | 172929.1667
26
27 | 15:30 | 25 | 30 | 54 | 146500 | 57291.6667 | 11 | 13531.9847 | JMM |  | 203791.6667
28
29 | 15:30 | 20 | 30 | 48 | 117200 | 55729.1667 | 10.7 | 11700.3827 | DH |  | 172929.1667
30
31
Total |  | 205 | 300 | 708.5 | 1201300
Average |  | 20.5 | 30 | 70.85 | 120130
Maximum |  | 25 | 30 | 107 | 146500
Minimum |  | 20 | 30 | 48 | 117200
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 5
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 5 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-23 | 8:00 | 1900-01-23 08:00
2 | 15:00 | 25 | 45 | 63 | 146500 | 75781.25 | 9.7 | 13921.5418 | DH |  | 222281.25 | THIS WASH | 1900-01-25 | 16:00 | 1900-01-25 16:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 56
6
7 | 9:30 | 20 | 30 | 114 | 117200 | 52083.3333 | 10 | 25970.4757 | SN | HEAD | 169283.3333
8
9
10
11 | 8:30 | 20 | 30 | 95 | 117200 | 52083.3333 | 10 | 21642.0631 | SN | HEAD | 169283.3333
12
13
14
15 | 13:00 | 20 | 30 | 100.5 | 117200 | 48437.5 | 9.3 | 21292.3729 | DB | L O H | 165637.5
16
17
18
19 | 2:00 | 20 | 30 | 92 | 117200 | 53645.8333 | 10.3 | 21587.3884 | DH |  | 170845.8333
20
21
22 | 5:00 | 20 | 30 | 76 | 117200 | 55208.3333 | 10.6 | 18352.4695 | RH |  | 172408.3333
23
24 | 8:00 | 20 | 30 | 51 | 117200 | 55729.1667 | 10.7 | 12431.6566 | JMM |  | 172929.1667
25
26 | 16:00 | 30 | 30 | 56 | 175800 | 55208.3333 | 10.6 | 13522.8722 | CBW |  | 231008.3333
27
28 | 10:00 | 20 | 30 | 40 | 117200 | 53125 | 10.2 | 9294.6966 | MN | HEAD | 170325
29
30 | 12:00 | 20 | 30 | 50 | 117200 | 57291.6667 | 11 | 12529.6155 | DH |  | 174491.6667
31
Total |  | 215 | 315 | 737.5 | 1259900
Average |  | 21.5 | 31.5 | 73.75 | 125990
Maximum |  | 30 | 45 | 114 | 175800
Minimum |  | 20 | 30 | 40 | 117200
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 6
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 6 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-23 | 19:00 | 1900-01-23 19:00
2 | 10:30 | 20 | 30 | 34.5 | 117200 | 55729.1667 | 10.7 | 8409.6501 | MN | HEAD | 172929.1667 | THIS WASH | 1900-01-24 | 17:00 | 1900-01-24 17:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 22
6 | 11:30 | 20 | 30 | 97 | 117200 | 53645.8333 | 10.3 | 22760.616 | DH |  | 170845.8333
7
8
9
10 | 11:30 | 20 | 30 | 96 | 117200 | 57291.6667 | 11 | 24056.8617 | MN | HEAD | 174491.6667
11
12
13
14
15 | 6:00 | 20 | 30 | 114.5 | 117200 | 48437.5 | 9.3 | 24258.4746 | SN | LOH | 165637.5
16
17
18
19 | 1:00 | 20 | 30 | 91 | 117200 | 53645.8333 | 10.3 | 21352.7428 | DH |  | 170845.8333
20
21
22 | 11:30 | 20 | 30 | 82.5 | 117200 | 55208.3333 | 10.6 | 19922.0886 | JMM | LOH | 172408.3333
23
24 | 19:00 | 20 | 30 | 55.5 | 117200 | 55729.1667 | 10.7 | 13528.5675 | RH | H.L. | 172929.1667
25
26
27 | 3:30 | 20 | 30 | 56.5 | 117200 | 58854.1667 | 11.3 | 14544.6054 | R.H. | H.L.
28
29 | 10:30 | 20 | 30 | 43 | 117200 | 53645.8333 | 10.3 | 10089.7576 | DH | HEAD | 170845.8333
30
31
Total |  | 180 | 270 | 670.5 | 1054800
Average |  | 20 | 30 | 74.5 | 117200
Maximum |  | 20 | 30 | 114.5 | 117200
Minimum |  | 20 | 30 | 34.5 | 117200
|  | 9 | 9 | 9 | 9
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 7
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 7 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 18:00 | 20 | 30 | 18 | 117200 | 55729.1667 | 10.7 | 4387.6435 | GE | L O H | 172929.1667 | LAST WASH | 1900-01-27 | 2:30 | 1900-01-27 02:30
2 | [11 empty] | THIS WASH | 1900-01-29 | 20:30 | 1900-01-29 20:30
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 66
6 | 3:00 | 20 | 30 | 105 | 117200 | 53645.8333 | 10.3 | 24637.7802 | GE | L O H | 170845.8333
7
8
9
10 | 4:00 | 20 | 30 | 97 | 117200 | 57291.6667 | 11 | 24307.454 | CBW |  | 174491.6667
11
12
13
14 | 2:30 | 20 | 30 | 97 | 117200 | 45312.5 | 8.7 | 19224.9863 | JMM |  | 162512.5
15
16
17
18 | 7:00 | 20 | 30 | 100.5 | 117200 | 48437.5 | 9.3 | 21292.3729 | DB | L O H | 165637.5
19
20
21 | 16:30 | 20 | 30 | 81.5 | 117200 | 55208.3333 | 10.6 | 19680.6087 | JMM |  | 172408.3333
22
23 | 14:30 | 20 | 30 | 46 | 117200 | 52083.3333 | 10 | 10479.3147 | JMM |  | 169283.3333
24
25 | 11:30 | 20 | 30 | 43 | 117200 | 55729.1667 | 10.7 | 10481.5929 | JMM |  | 172929.1667
26
27 | 8:00 | 30 | 30 | 44.5 | 175800 | 57291.6667 | 11 | 11151.3578 | JMM |  | 233091.6667
28 | 2:30 | 20 | 30 | 18.5 | 117200 | 53645.8333 | 10.3 | 4340.9422 | GHE | LOH | 170845.8333
29
30 | 20:30 | 20 | 30 | 66 | 117200 | 57812.5 | 11.1 | 16689.4478 | GHE | HIT PROB | 175012.5
31
Total |  | 230 | 330 | 717 | 1347800
Average |  | 20.9091 | 30 | 65.1818 | 122527.2727
Maximum |  | 30 | 30 | 105 | 175800
Minimum |  | 20 | 30 | 18 | 117200
|  | 11 | 11 | 11 | 11
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 8
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 8 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-23 | 9:00 | 1900-01-23 09:00
2 | [11 empty] | THIS WASH | 1900-01-26 | 1:00 | 1900-01-26 01:00
3 | [12 empty] | TOTAL HOURS
4 | 4:00 | 20 | 30 | 76 | 117200 | 50520.8333 | 9.7 | 16794.2409 | DB | L O H | 167720.8333
5 | [13 empty] | 64
6
7
8 | 13:00 | 20 | 30 | 105 | 117200 | 50520.8333 | 9.7 | 23202.5697 | SN | HEAD | 167720.8333
9
10
11 | 13:30 | 20 | 30 | 72.5 | 117200 | 51562.5 | 9.9 | 16351.1482 | SN | HEAD | 168762.5
12
13
14
15
16 | 1:00 | 20 | 30 | 107.5 | 117200 | 48437.5 | 9.3 | 22775.4237 | DH |  | 165637.5
17
18
19 | 5:00 | 20 | 30 | 76 | 117200 | 53645.8333 | 10.3 | 17833.06 | DH |  | 170845.8333
20
21
22 | 8:00 | 20 | 30 | 75 | 117200 | 55208.3333 | 10.6 | 18110.9896 | CBW |  | 172408.3333
23
24 | 9:00 | 20 | 30 | 49 | 117200 | 55729.1667 | 10.7 | 11944.1407 | JMM |  | 172929.1667
25
26 | 19:00 | 30 | 30 | 58 | 175800 | 56770.8333 | 10.9 | 14402.2234 | SN | AUTO | 232570.8333
27
28 | 12:00 | 20 | 30 | 39 | 117200 | 53125 | 10.2 | 9062.3291 | MN | HEAD | 170325
29
30 | 16:00 | 20 | 30 | 52 | 117200 | 57291.6667 | 11 | 13030.8001 | DH |  | 174491.6667
31
Total |  | 210 | 300 | 710 | 1230600
Average |  | 21 | 30 | 71 | 123060
Maximum |  | 30 | 30 | 107.5 | 175800
Minimum |  | 20 | 30 | 39 | 117200
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 9
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 9 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 11:00 | 20 | 30 | 11 | 125000 | 60937.5 | 11.7 | 2543.8805 | DH | HEAD | 185937.5 | LAST WASH | 1900-01-23 | 15:30 | 1900-01-23 15:30
2 | [11 empty] | THIS WASH | 1900-01-26 | 1:00 | 1900-01-26 01:00
3 | [12 empty] | TOTAL HOURS
4
5 | 11:00 | 20 | 30 | 96 | 125000 | 67708.3333 | 13 | 24667.9317 | MN |  | 192708.3333 |  |  | 57.5
6
7
8
9
10 | 2:00 | 20 | 30 | 111 | 125000 | 62500 | 12 | 26328.2732 | CBW |  | 187500
11
12
13
14 | 12:30 | 20 | 30 | 106.5 | 125000 | 53645.8333 | 10.3 | 21682.2818 | SN | LOH / MAINTENANCE | 178645.8333
15
16
17
18 | 10:30 | 20 | 30 | 94 | 125000 | 53645.8333 | 10.3 | 19137.413 | GE | L O H | 178645.8333
19
20
21
22 | 10:30 | 20 | 30 | 96 | 125000 | 60416.6667 | 11.6 | 22011.3852 | JMM |  | 185416.6667
23
24 | 15:30 | 20 | 30 | 53 | 125000 | 60937.5 | 11.7 | 12256.8786 | CBW |  | 185937.5
25
26
27 | 1:00 | 20 | 30 | 57.5 | 125000 | 66145.8333 | 12.7 | 14434.1003 | SN | LOH | 191145.8333
28
29 | 8:00 | 20 | 30 | 55 | 125000 | 58854.1667 | 11.3 | 12284.5509 | DH | HEAD | 183854.1667
30
31
Total |  | 180 | 270 | 680 | 1125000
Average |  | 20 | 30 | 75.5556 | 125000
Maximum |  | 20 | 30 | 111 | 125000
Minimum |  | 20 | 30 | 11 | 125000
|  | 9 | 9 | 9 | 9
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 10
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 10 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 13:00 | 20 | 30 | 13 | 125000 | 60937.5 | 11.7 | 3006.4042 | DH |  | 185937.5 | LAST WASH | 1900-01-26 | 21:00 | 1900-01-26 21:00
2 | [11 empty] | THIS WASH | 1900-01-28 | 23:30 | 1900-01-28 23:30
3 | [12 empty] | TOTAL HOURS
4
5 | 15:00 | 20 | 30 | 98 | 125000 | 57291.6667 | 11 | 21307.7166 | DH |  | 182291.6667 |  |  | 50.5
6
7
8
9 | 23:00 | 20 | 30 | 104 | 125000 | 62500 | 12 | 24667.9317 | CBW |  | 187500
10
11
12
13 | 10:00 | 30 | 30 | 83 | 187500 | 53645.8333 | 10.3 | 16897.9285 | SN | HEAD | 241145.8333
14
15
16
17 | 7:00 | 20 | 30 | 93 | 125000 | 58854.1667 | 11.3 | 20772.0588 | DB | L O H | 183854.1667
18
19
20
21 | 10:30 | 20 | 30 | 99.5 | 125000 | 60416.6667 | 11.6 | 22813.8836 | CBW |  | 185416.6667
22
23 | 21:30 | 20 | 30 | 59 | 125000 | 60937.5 | 11.7 | 13644.4497 | SN | TURB | 185937.5
24
25 | 20:00 | 20 | 30 | 46.5 | 125000 | 50000 | 9.6 | 8823.5294 | SN | TURB | 175000
26
27 | 21:00 | 20 | 30 | 49 | 125000 | 62500 | 12 | 11622.3909 | SN | LOH | 187500
28
29 | 23:30 | 20 | 30 | 55.5 | 125000 | 62500 | 12 | 13164.1366 | GE | L O H | 187500
30
31
Total |  | 210 | 300 | 700.5 | 1312500
Average |  | 21 | 30 | 70.05 | 131250
Maximum |  | 30 | 30 | 104 | 187500
Minimum |  | 20 | 30 | 13 | 125000
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 11
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 11 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 9:00 | 20 | 30 | 9 | 125000 | 60937.5 | 11.7 | 2081.3567 | MN | HEAD | 185937.5 | LAST WASH | 1900-01-24 | 10:30 | 1900-01-24 10:30
2 | [11 empty] | THIS WASH | 1900-01-26 | 7:30 | 1900-01-26 07:30
3 | [12 empty] | TOTAL HOURS
4
5 | 9:00 | 20 | 30 | 96 | 125000 | 67708.3333 | 13 | 24667.9317 | DH |  | 192708.3333 |  |  | 45
6
7
8
9 | 9:30 | 20 | 30 | 96.5 | 125000 | 62500 | 12 | 22888.9943 | SN | HEAD | 187500
10
11
12 | 15:30 | 30 | 30 | 78 | 187500 | 58854.1667 | 11.3 | 17421.7268 | SN | HEAD | 246354.1667
13
14
15
16 | 12:30 | 20 | 30 | 93 | 125000 | 54687.5 | 10.5 | 19301.4706 | BC | HEAD HIT | 179687.5
17
18
19
20 | 10:30 | 20 | 30 | 94 | 125000 | 55729.1667 | 10.7 | 19880.6135 | GE | L O H | 180729.1667
21
22
23 | 2:30 | 20 | 30 | 64 | 125000 | 54687.5 | 10.5 | 13282.7324 | R.H. | L.O.H. | 179687.5
24
25 | 4:30 | 20 | 30 | 50 | 125000 | 60937.5 | 11.7 | 11563.093 | R.H. | L.O.H. | 185937.5
26
27 | 7:30 | 30 | 30 | 45 | 187500 | 62500 | 12 | 10673.6243 | CBW |  | 250000
28 | 14:30 | 20 | 30 | 31 | 125000 | 58854.1667 | 11.3 | 6924.0196 | DH |  | 183854.1667
29
30 | 10:30 | 20 | 30 | 44 | 125000 | 62500 | 12 | 10436.4326 | SN |  | 187500
31
Total |  | 240 | 330 | 700.5 | 1500000
Average |  | 21.8182 | 30 | 63.6818 | 136363.6364
Maximum |  | 30 | 30 | 96.5 | 187500
Minimum |  | 20 | 30 | 9 | 125000
|  | 11 | 11 | 11 | 11
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 12
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 12 |  |  |  |  | 2018-11-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 7:00 | 20 | 30 | 7 | 125000 | 60937.5 | 11.7 | 1618.833 | MN | HEAD | 185937.5 | LAST WASH | 1900-01-26 | 11:00 | 1900-01-26 11:00
2 | [11 empty] | THIS WASH | 1900-01-27 | 23:00 | 1900-01-27 23:00
3 | [12 empty] | TOTAL HOURS
4
5 | 7:00 | 20 | 30 | 96 | 125000 | 67708.3333 | 13 | 24667.9317 | MN |  | 192708.3333 |  |  | 36
6
7
8
9 | 3:30 | 20 | 30 | 92.5 | 125000 | 62500 | 12 | 21940.2277 | CBW |  | 187500
10
11
12 | 9:30 | 20 | 30 | 77 | 125000 | 58854.1667 | 11.3 | 17198.3713 | SN | HEAD | 183854.1667
13
14
15
16 | 18:30 | 20 | 30 | 105 | 125000 | 53645.8333 | 10.3 | 21376.8975 | MN | HEAD | 178645.8333
17
18
19
20 | 19:30 | 20 | 30 | 97 | 125000 | 58854.1667 | 11.3 | 21665.4807 | MN |  | 183854.1667
21
22
23 | 12:00 | 20 | 30 | 64.5 | 125000 | 57291.6667 | 11 | 14023.9564 | CBW |  | 182291.6667
24
25 | 11:00 | 20 | 30 | 47 | 125000 | 60937.5 | 11.7 | 10869.3074 | CBW |  | 185937.5
26
27 | 11:00 | 20 | 30 | 48 | 125000 | 62500 | 12 | 11385.1992 | CBW |  | 187500
28 | 23:00 | 20 | 30 | 36 | 125000 | 55729.1667 | 10.7 | 7613.852 | DB | L O H | 180729.1667
29
30 | 14:00 | 20 | 30 | 40 | 125000 | 62500 | 12 | 9487.666 | DH |  | 187500
31
Total |  | 220 | 330 | 710 | 1375000
Average |  | 20 | 30 | 64.5455 | 125000
Maximum |  | 20 | 30 | 105 | 125000
Minimum |  | 20 | 30 | 7 | 125000
|  | 11 | 11 | 11 | 11
Prepared by: _________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## FILTER PERFORMANCE (hidden)
Filter Performance Test
[18 empty] | Filter 1 |  | Filter 2 |  | Filter 3 |  | Filter 4 |  | Filter 5 |  | Filter 6 |  | Filter 7 |  | Filter 8 |  | Filter 9 |  | Filter 10 |  | Filter 11 |  | Filter 12
Date | OPER | Time | Filter # washed | Flow to Filter Cluster, MGD | Raw Uv 254 | Calculated Alum Dose, mg/L | Alum Dose, mg/L | Filter Washed headloss, ft | Filter washed Time in service, hrs | Filter # Affected with turbidity spike | Filter affected by turbidity spike Headloss, ft | Filter affected by turbidity spike time in service, hrs | Reason for filter washed (time or Headloss) | Settled water turbidity avg. for plant that filter was washed on. 24 hr avg., ntu | Filter affected max turbidity, ntu | Filtration rate, gpm'sq.ft | Solids Loading onto Filters, lbs/day/filter | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs |  | DATE | TIME
[42 empty] | LAST WASH | 2015-05-29 | 1:00
2015-05-28 | CBW | 1800 | 9 | 11.4 | 0.294 | 38.6842 | 40 | 4.25 | 92 | 10 | 3.91 | 82 | TIME | 0.5 | 0.19 | 5.492 | 35.6535 | [18 empty] | 1.59 | 82 | 2.3 | 5 | 5.29 | 73.5 | THIS WASH | 2015-05-31 | 0:00
2015-05-28 | JM | 2100 | 7 | 10.6 | 0.357 | 46.9737 | 40 | 3.91 | 65 | NONE |  |  | HEAD | 0.47 |  | 5.1066 | 31.1624 | [8 empty] | 5.87 | 106 | 3.61 | 11 |  |  | 3.33 | 25 | [9 empty] | TOTAL HOURS
2015-05-29 | CBW | 100 | 10 | 11.3 | 0.292 | 38.4211 | 40 | 1.9 | 89 | 12 | 6.35 | 101.5 | TURB | 0.5 | 0.11 | 5.4438 | 35.3407 | [16 empty] | 2.45 | 7 |  |  | 2.8 | 12 | 6.35 | 102.5 |  | 2015-05-29 | 48
2015-05-29 | GE | 600 | 3 | 10.4 | 0.276 | 36.3158 | 40 | 4.11 | 87 | NONE |  |  | HEAD | 0.45 |  | 5.0102 | 29.2734 | 5.21 | 86 | 4.23 | 22 |  |  | 4.22 | 89 | [17 empty] | 2015-05-31
2015-05-29 | MN | 700 | 5 | 10.5 | 0.276 | 36.3158 | 40 | 4.74 | 116 | NONE |  |  | TIME/HEAD | 0.29 |  | 5.0584 | 19.0465 | [10 empty] | 3.47 | 21 | 2.29 | 10 | 2.66 | 35
[16 empty] | 0 | 0
2015-05-29 | CBW | 2300 | 12 | 11.2 | 0.312 | 41.0526 | 44 | 5.28 | 123.5 | NONE |  |  | NTU/TIME | 0.591 |  | 5.3956 | 41.4031 | [16 empty] | 1.91 | 29 | 2.4 | 22 | 2.76 | 34 | 5.28 | 132.5
2015-05-30 | GE | 600 | 4 | 10.4 | 0.229 | 30.1316 | 40 | 3.66 | 120 | NONE |  |  | TIME/HEAD | 0.46 |  | 5.0102 | 29.9239 | 4.1 | 110.5 | 3.69 | 75 | 1.98 | 24
2015-05-30 | GE | 1030 | 1 | 10.4 | 0.235 | 30.9211 | 40 | 3.54 | 115 | NONE |  |  | TIME/HEAD | 0.52 |  | 5.0102 | 33.827 |  |  | 3.13 | 79.5 | 1.86 | 29 | 1.01 | 4.5
2015-05-31 | MN | 1000 | 2 | 11.2 | 0.226 | 29.7368 | 40 | 3.25 | 103 | NONE |  |  | TIME/HEAD | 0.41 |  | 5.3956 | 28.723 | 0.083 | 23.5 |  |  | 1.25 | 52.5 | 0.47 | 28
NEW MONTH | [15 empty] | 0 | 0
2015-06-02 | CBW | 4:30 | 8 | 34.1 | 0.241 | 31.7105 | 35 | 4.57 | 127.5/28.5 | NONE |  |  | HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 4.93 | 66/28.5 | 5.78 | 28.5 | 4.24 | 105/28.5
2015-06-02 | MN | 600 | 6 | 34.1 | 0.176 | 23.1579 | 35 | 3.71 | 115 / 30 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.33 | 94 / 30 |  |  | 2.43 | 104 / 30 | 1.03 | 129/30
2015-06-02 | GE | 1000 | 7 | 34.1 | 0.195 | 25.6579 | 32 | 2.42 | 104/34 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.86 | 99/34 | 0.09 | 4 |  |  | 0.45 | 5.5
2015-06-02 | GE | 1330 | 11 | 34.1 | 0.217 | 28.5526 | 32 | 5.37 | 120.5/37.5 | NONE |  |  | TIME/HEAD | 0.272 |  | 4.4803 | 58.0164 | [16 empty] | 5.45 | 115.5 | 1.9 | 67.5 |  |  | 3.83 | 86.5
2015-06-02 | CBW | 1930 | 3 | 34.1 | 0.181 | 23.8158 | 35 | 2.57 | 65.5/43.5 | NONE |  |  | TIME/HEAD | 0.281 |  | 4.4803 | 59.936 | 1.07 | 43.5 | 1.23 | 43.5 | 1.55 | 43.5 | 0.77 | 43.5
2015-06-03 | HE | 700 | 10 | 26.1 | 0.247 | 32.5 | 35 | 1.4 | 55 | NONE |  |  | TIME/HEAD | 0.25 |  | 3.4292 | 40.8139 | [16 empty] | 4.9 | 55 | 1.4 | 55 | 1.49 | 17 | 3.82 | 55
2015-06-10 | CBW | 1130 | 2 | 33.2 | 0.251 | 33.0263 | 35 | 0.19 | 116.5 | NONE |  |  | TIME/HEAD | 0.3 |  | 4.362 | 62.2998 | 0.01 | 29.5 | 0.91 | 116.5 | 0.48 | 26 | 0.27 | 92.5
2015-06-10 | CBW | 1330 | 5 | 33.2 | 0.251 | 33.0263 | 35 | 1.77 | 117.5 | NONE |  |  | TIME/HEAD | 0.21 |  | 4.362 | 43.6099 | [8 empty] | 1.77 | 117.5 | 0.49 | 69 | 0.06 | 45 | 0.05 | 48
2015-06-10 | GHE | 1900 | 12 | 33.2 | 0.239 | 31.4474 | 35 | 4.72 | 156 | NONE |  |  | TIME/HEAD | 0.2 |  | 4.362 | 41.5332 | [16 empty] | 0.05 | 32.5 | 0.06 | 35 | 0.05 | 36
2015-06-11 | GHE | 2:00 | 4 | 33.1 | 0.239 | 31.4474 | 35 | 3.81 | 107 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.3489 | 64.1826 | 3.54 | 44 | 3.48 | 14.5 | 3.51 | 40.5
2015-06-11 | CBW | 6:00 | 7 | 33.1 | 0.283 | 37.2368 | 35 | 3.75 | 67 | NONE |  |  | HEAD/CLEAR | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 3.99 | 16.5 | 5.53 | 85.5 | 3.75 | 61.5 | 0.05 | 64.5
2015-06-11 | CBW | 8:00 | 6 | 33.1 | 0.283 | 37.2368 | 35 | 3.41 | 87.5 | NONE |  |  | TIME/HEAD | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 2.92 | 18.5 |  |  | 1.56 | 62.5 | 2.1 | 66.5
2015-06-12 | CBW | 9:00 | 11 | 35.7 | 0.291 | 38.2895 | 35 | 3.91 | 98 | NONE |  |  | TIME/HEAD | 0.228 |  | 4.6905 | 50.9132
2015-06-12 | CBW | 14:00 | 8 | 35.7 | 0.232 | 30.5263 | 35 | 1.53 | 96.5 | NONE |  |  | TIME/HEAD | 0.278 |  | 4.6905 | 62.0784 | [8 empty] | 2.67 | 48.5 | 2.35 | 30 | 2.66 | 32 | 1.53 | 96.5 | 2.98 | 70.5 | 2.21 | 75 | 3.91 | 98 | 2.28 | 38
2015-06-13 | CBW | 600 | 1 | 38.6 | 0.224 | 29.4737 | 35 | 3.91 | 96 | NONE |  |  | TIME/HEAD | 0.3 |  | 5.0715 | 72.4329 |  |  | 3.82 | 75.5 | 3.62 | 69.5 | 2.49 | 52
2015-06-13 | CBW | 800 | 10 | 38.6 | 0.224 | 29.4737 | 35 | 3.02 | 98 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [16 empty] | 4.78 | 94.5 |  |  | 2.36 | 23 | 3.36 | 61
2015-06-13 | CBW | 900 | 3 | 38.6 | 0.224 | 29.4737 | 35 | 3.54 | 95.5 | NONE |  |  | TIME/HEAD | 0.35 |  | 5.0715 | 84.505 | 1.91 | 3 | 3.66 | 78.5 |  |  | 2.4 | 55
2015-06-13 | CBW | 1100 | 9 | 38.6 | 0.224 | 29.4737 | 35 | 4.78 | 96.5 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [18 empty] | 2.49 | 3 | 2.36 | 26 | 3.36 | 64
2015-06-14 | CBW | 600 | 7 | 42 | 0.26 | 34.2105 | 35 | 3.27 | 72 | NONE |  |  | HEAD/CLEAR WELL | 0.208 |  | 5.5182 | 54.6437 | [8 empty] | 5.21 | 88.5 | 4.31 | 70 |  |  | 2.97 | 40
2015-06-14 | CBW | 800 | 2 | 42 | 0.26 | 34.2105 | 35 | 3.59 | 92.5 | NONE |  |  | TIME | 0.257 |  | 5.5182 | 67.5165 | 3.37 | 26 |  |  | 2.96 | 23 | 3.74 | 78
2015-06-14 | CBW | 900 | 5 | 42 | 0.26 | 34.2105 | 35 | 5.09 | 91.5 | NONE |  |  | TIME | 0.208 |  | 5.5182 | 54.6437 | [10 empty] | 3.86 | 73 | 2.16 | 3 | 2.4 | 43
2015-06-14 | CBW | 1430 | 4 | 42 | 0.24 | 31.5789 | 35 | 4.68 | 84.5 | NONE |  |  | HEAD/CLEAR WELL | 0.257 |  | 5.5182 | 67.5165 | 4.04 | 32.5 | 3.96 | 6.5 | 3.54 | 29.5 | [10 empty] | 2.47 |  | 2.49 |  | 3.36 |  | 4.67
2015-06-14 | GE | 1800 | 8 | 42 | 0.218 | 28.6842 | 35 | 3.61 | 22 | NONE |  |  | HEAD | 0.31 |  | 5.5182 | 81.4401 | [8 empty] | 4.08 | 9 | 5.65 | 82 | 3.52 | 12
2015-06-15 | GE | 500 | 6 | 41.4 | 0.22 | 28.9474 | 35 | 3.88 | 23 | NONE |  |  | HEAD | 0.32 |  | 5.4394 | 82.8662 | [8 empty] | 4.52 | 20 |  |  | 3.88 | 23 | 3.15 | 11
2015-06-15 | CBW | 10:00 | 12 | 41.4 | 0.254 | 33.4211 | 35 | 5.15 | 111 | NONE |  |  | TIME | 0.202 |  | 5.4394 | 52.3093
2015-06-16 | CBW | 13:30 | 11 | 40.4 | 0.229 | 30.1316 | 35 | 5.36 | 100.5 | NONE |  |  | TIME | 0.216 |  | 5.308 | 54.5836
2015-06-17 | DMH | 1500 | 10 | 40.2 | 0.251 | 33.0263 | 40 | 1.49 | 103 | None |  |  | TIME | 0.225 |  | 5.2817 | 56.5765 | [16 empty] | 5.1 | 100 |  |  | 2.8 | 25.5 | 3.6 | 53
2015-06-18 | WL | 6:00 | 1 | 36.8 | 0.262 | 34.4737 | 40 | 2.2 | 120 | None |  |  | Time | 0.316 |  | 4.835 | 72.7381 |  |  | 1.54 | 93.4 | 2.23 | 84 | 0.79 | 81.5
2015-06-18 | WL | 9:00 | 3 | 36.8 | 0.262 | 34.4737 | 40 | 1.55 | 120 | NONE |  |  | Time | 0.316 |  | 4.835 | 72.7381 | 0.23 | 0.75 | 1.55 | 95.4 |  |  | 1.31 | 83.5
2015-06-18 | DMH | 1300 | 4 | 36.8 | 0.262 | 34.4737 | 40 | 1.31 | 94.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 5.79 | 1.56 | 100.45 | 0 | 3.78
2015-06-18 | DMH | 1530 | 2 | 36.8 | 0.262 | 34.4737 | 40 | 1.57 | 103.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 8.17 |  |  | 0 | 6.16 | 0.31 | 0.64
2015-06-19 | WL | 9:00 | 7 | 33.7 | 0.274 | 36.0526 | 40 | 3.5 | 123 | NONE |  |  | Time/HEAD | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 3.7 | 118.54 | 2.4 | 98.21 |  |  | 2.7 | 109.62
2015-06-19 | DMH | 11:00 | 5 | 33.7 | 0.274 | 36.0526 | 40 | 3.88 | 122 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [10 empty] | 2.33 | 100.25 | 0.33 | 0.072 | 2.73 | 111.65
2015-06-19 | DMH | 13:00 | 6 | 33.7 | 0.274 | 36.0526 | 40 | 2.32 | 104 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 0.36 | 1.03 |  |  | 0.33 | 3.01 | 2.72 | 113.94
2015-06-20 | WL | 8:30 | 8 | 31.4 | 0.289 | 38.0263 | 45 | 2.72 | 134.5 | NONE |  |  | TIME | 0.243 |  | 4.1255 | 47.7269 | [8 empty] | 0.36 | 20.71 | 0.02 | 18.65 | 0.33 | 22.68
2015-06-20 | WL | 12:00 | 12 | 31.4 | 0.31 | 40.7895 | 45 | 5.32 | 122 | NONE | 9,11 |  | TIME | 0.374 | 0.06 | 4.1255 | 73.4562 | [16 empty] | 2.23 |  | 2.25 |  | 4.41
2015-06-22 | DMH | 13:30 | 11 | 33.5 | 0.327 | 43.0263 | 50 | 6.42 | 144 | 9,10 | 9 |  | TIME/HEAD | 0.466 | .09,.5 | 4.4015 | 97.6468 | [16 empty] | 4.28 | 114.5 | 1.75 | 118.5 |  |  | 2.4 | 49.5
2015-06-23 | WL | 6:00 | 10 | 42.1 | 0.305 | 40.1316 | 50 | 1.25 | 135 | 9 |  |  | TIME | 0.419 | 0.13 | 5.5314 | 110.3376 | [16 empty] | 5.28 |  |  |  | 2.21 |  | 3.47
2015-06-23 | WL | 9:00 | 9 | 42.1 | 0.305 | 40.1316 | 50 | 5.28 | 134 | None | 11,12 |  | TIME | 0.419 |  | 5.5314 | 110.3376 | [18 empty] | 2.26 |  | 2.72 |  | 3.98
2015-06-24 | MN | 1200 | 3 | 42.1 | 0.294 | 38.6842 | 40 | 3.54 | 147 | NONE |  |  | TIME/HEAD | 0.335 |  | 5.5314 | 88.2174 | 2.75 | 150 | 2.2 | 139 |  |  | 2.34 | 142
2015-06-24 | MN | 1600 | 7 | 37.1 | 0.297 | 39.0789 | 40 | 3.87 | 127 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.8744 | 71.9388 | [8 empty] | 3.89 | 125 | 3.05 | 119 |  |  | 2.9 | 104.5
2015-06-25 | GHE | 2:00 | 4 | 37.1 | 0.372 | 48.9474 | 50 | 3.83 | 157 | None |  |  | Time | 0.4 |  | 4.8744 | 92.8242 | 4.76 | 164 | 4.26 | 154.5 | 0.46 | 161
2015-06-25 | MN | 830 | 8 | 37.1 | 0.306 | 40.2632 | 40 | 3.96 | 120 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 | [8 empty] | 5.83 | 141.5 | 4.63 | 138.5 | 0.44 | 18.5
2015-06-25 | MN | 1000 | 1 | 37.1 | 0.306 | 40.2632 | 40 | 4.78 | 172 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 |  |  | 4.21 | 162.5 | 0.46 | 22 | 0.26 | 3 |  |  | 4.61 | 142.5 | 0.97 | 23 | 0.47 | 4.5
2015-06-25 | MN | 1300 | 5 | 37.1 | 0.306 | 40.2632 | 40 | 5.73 | 148 |  |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906
2015-06-25 | CBW | 1900 | 12 | 37.1 | 0.304 | 40 | 40 | 6.62 | 127 | NONE |  |  | TIME | 0.46 |  | 4.8744 | 106.7478 | [16 empty] | 4.39 | 58 | 1.26 | 61 | 5.75 | 77.5
2015-06-25 | CBW | 2300 | 11 | 37.1 | 0.304 | 40 | 40 | 5.75 | 81.5 | NONE |  |  | TIME | 0.68 |  | 4.8744 | 157.8011 | [16 empty] | 4.39 | 62 | 1.25 | 65 |  |  | 0.76 | 6
2015-06-26 | CBW | 1300 | 2 | 37.1 | 0.304 | 40 | 40 | 4.17 | 178.5 | NONE |  |  | TIME | 0.58 |  | 4.8744 | 134.5951 | 0.27 | 15 |  |  | 0.97 | 37 | 0.05 | 18 | 0.44 | 18 |  |  | 0.97 | 41 | 0.47 | 24.5
2015-06-26 | MN | 900 | 6 | 37.1 | 0.304 | 40 | 40 | 4.55 | 164 | NONE |  |  | TIME/HEAD | 0.52 |  | 4.8744 | 120.6715
2015-06-27 | CBW | 4:30 | 10 | 37.1 | 0.311 | 40.9211 | 40 | 2.81 | 94.5 | 9 | 6.4 | 91.5 | Turb. | 0.48 |  | 4.8744 | 111.389 | [16 empty] | 6.4 | 91.5 |  |  | 2.32 | 29.5 | 2.97 | 33.5
2015-06-27 | CBW | 19:00 | 9 | 37.1 | 0.338 | 44.4737 | 40 | 5.89 | 106 | NONE |  |  | TIME | 0.54 |  | 4.8744 | 125.3127 | [18 empty] | 2.89 | 14.5 | 3.4 | 44 | 3.37 | 48
2015-06-28 | GHE | 19:00 | 7 | 38.3 | 0.226 | 29.7368 | 35 | 2.94 | 101 | NONE |  |  | TIME/AUTO | 0.38 |  | 5.0321 | 91.0353 | [8 empty] | 2.46 | 78 | 1.4 | 58 |  |  | 1.81 | 82.5
2015-06-29 | CBW | 600 | 3 | 38.3 | 0.226 | 29.7368 | 35 | 4 | 114 | NONE |  |  | HEAD | 0.62 |  | 5.0321 | 148.5312 | 2.29 | 102 | 1.01 | 76 |  |  | 2.03 | 100
2015-06-29 | MN | 1030 | 8 | 42 | 0.226 | 29.7368 | 35 | 3.01 | 98 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [8 empty] | 3.47 | 93 | 2.42 | 73.5 | 0.18 | 15.5
2015-06-29 | MN | 1400 | 4 | 42 | 0.232 | 30.5263 | 35 | 2.03 | 103 | NONE |  |  | TIME | 0.31 |  | 5.5182 | 81.4401 | 3.31 | 100 | 2.06 | 61 | 0.11 | 8
2015-06-29 | CBW | 2000 | 12 | 42 | 0.251 | 33.0263 | 35 | 5.39 | 97 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [16 empty] | 3.31 | 49 | 2.31 | 63.5 | 5.42 | 93
2015-06-29 | CBW | 2200 | 1 | 42 | 0.251 | 33.0263 | 35 | 4.37 | 118 | NONE |  |  | TIME | 0.51 |  | 5.5182 | 133.9821 |  |  | 3.06 | 92 | 0.11 | 16 | 0.11 | 8
2015-06-30 | MN | 700 | 5 | 42 | 0.244 | 32.1053 | 35 | 4.47 | 114 | NONE |  |  | TIME | 0.45 |  | 5.5182 | 118.2195 | [10 empty] | 3.95 | 94 | 1.98 | 36 | 0.85 | 21.5
2015-07-01 | CBW | 1:30 | 6 | 40 | 0.252 | 33.1579 | 35 | 4.97 | 111 | NONE |  |  | TIME | 0.4 |  | 5.2555 | 100.08 | [8 empty] | 0.11 | 18.5 |  |  | 2.74 | 54.5 | 1.87 | 27
2015-07-02 | wl | 1:30 | 8 | 13.3 | 0.226 | 29.7368 | 45 | 3.3 | 63 | none |  |  | head | 0.327 |  | 1.7474 | 27.2036 | [8 empty] | 1.8 | 41.5 | 0.6 | 22.5 | 0 | 15.5
2015-07-02 | wl | 4:00 | 3 | 13.6 | 0.239 | 31.4474 | 45 | 2.8 | 70 | none |  |  | head | 0.306 |  | 1.7869 | 26.0308 | 1.7 | 54 | 0.7 | 38 |  |  | 2 | 61
2015-07-07 | wl | 18:00 | 1 | 11.6 | 0.217 | 28.5526 | 45 | 1.2 | 103 | none |  |  | time | 0.262 |  | 1.5241 | 19.0102 |  |  | 0.2 | 54 | 0 | 30.5 | 1.7 | 128
2015-07-07 | DMH | 20:00 | 4 | 11.6 | 0.217 | 28.5526 | 45 | 1.51 | 131 |  |  |  | time | 0.275 |  | 1.5241 | 19.9535 | 0.35 | 0.79 | 0.25 | 56.12 | 0.03 | 0.06
2015-07-09 | JM | 900 | 12 | 13.7 | 0.253 | 33.2895 | 40 | 6.27 | 147 | NONE |  |  | TIME | 0.372 |  | 1.8 | 31.878 | [16 empty] | 4.09 | 93 | 2.18 | 74 | 5.95 | 123
2015-07-09 | MN | 1100 | 5 | 13.2 | 0.253 | 33.2895 | 40 | 2.86 | 98 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | [10 empty] | 2.27 | 93.5 | 1.61 | 69.5 | 0.54 | 49
2015-07-09 | MN | 1530 | 2 | 13.2 | 0.253 | 33.2895 | 40 | 1.78 | 96 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | 0.3 | 44.5 |  |  | 1.05 | 67 | 0 | 43.5
2015-07-10 | JM | 800 | 11 | 13.8 | 0.252 | 33.1579 | 40 | 6.96 | 146 | NONE |  |  | TIME/TURB | 0.39 |  | 1.8131 | 33.6644 | [16 empty] | 5.09 | 116 | 1.68 | 97 |  |  | 2.17 | 23
2015-07-10 | MN | 1030 | 3 | 13.2 | 0.252 | 33.1579 | 40 | 2.05 | 96 | NONE |  |  | TIME | 0.42 |  | 1.7343 | 34.6777 | 0.86 | 66 | 0.07 | 19 |  |  | 1.01 | 62
2015-07-10 | MN | 1330 | 6 | 13.2 | 0.252 | 33.1579 | 40 | 3.29 | 120 | NONE |  |  | TIME | 0.38 |  | 1.7343 | 31.3751 | [8 empty] | 0.7 | 26.5 |  |  | 3.12 | 102 | 2.07 | 76
2015-07-10 | CBW | 2230 | 9 | 14.4 | 0.272 | 35.7895 | 40 | 6.1 | 130.5 | NONE |  |  | TIME/TURB | 0.52 |  | 1.892 | 46.8374 | [18 empty] | 1.68 | 111.5 | 2.18 | 14.5 | 3.26 | 37.5
2015-07-11 | CBW | 3:30 | 10 | 14.7 | 0.272 | 35.7895 | 40 | 3.01 | 116 | NONE |  |  | TIME/TURB | 0.56 |  | 1.9314 | 51.4912 | [16 empty] | 1.67 | 5 |  |  | 2.68 | 19.5 | 3.26 | 42.5
2015-07-11 | MN | 630 | 7 | 14.5 | 0.281 | 36.9737 | 40 | 4.61 | 118 | NONE |  |  | TIME/HEAD | 0.42 |  | 1.9051 | 38.093 | [8 empty] | 2.21 | 19.5 | 0.15 | 17 |  |  | 3.59 | 92.5
2015-07-11 | MN | 1100 | 4 | 14.4 | 0.281 | 36.9737 | 45 | 2.53 | 86 | NONE |  |  | TIME | 0.28 |  | 1.892 | 25.2202 | 2.4 | 89 | 1.07 | 44 | 0.5 | 24.5
2015-07-11 | MN | 1400 | 8 | 14.5 | 0.281 | 36.9737 | 45 | 4.12 | 100 | NONE |  |  | HEAD | 0.35 |  | 1.9051 | 31.7441 | [8 empty] | 2.71 | 27 | 0.7 | 24.5 | 0.06 | 7.5
2015-07-12 | MN | 900 | 1 | 13.4 | 0.305 | 40.1316 | 45 | 3.4 | 111 | NONE |  |  | TIME | 0.34 |  | 1.7606 | 28.4978 |  |  | 2.08 | 66.5 | 1.5 | 22.5 | 0.46 | 22
2015-07-13 | CBW | 4:00 | 12 | 12.7 | 0.319 | 41.9737 | 45 | 5.75 | 91 | NONE |  |  | TIME | 0.355 |  | 1.6686 | 28.2007 | [16 empty] | 3.68 | 53.5 | 2 | 48.5 | 5.19 | 67.5
2015-07-14 | MN | 600 | 5 | 12 | 0.345 | 45.3947 | 50 | 5.82 | 115 | NONE |  |  | TIME/HEAD | 0.25 |  | 1.5766 | 18.765 | [10 empty] | 3.25 | 91.5 | 2.6 | 71.5 | 2.51 | 62
2015-07-14 | MN | 830 | 2 | 12 | 0.345 | 45.3947 | 50 | 3.55 | 113 | NONE |  |  | TIME | 0.29 |  | 1.5766 | 21.7674 | 0.41 | 23.5 |  |  | 3.3 | 97 | 1 | 69.5
2015-07-15 | DMH | 830 | 3 | 12.1 | 0.388 | 51.0526 | 50 | 4 | 118 | NONE |  |  | TIME/HEAD | 0.23 |  | 1.5898 | 17.4077 | 0.91 | 70.02 | 0.26 | 0.079 |  |  | 1.5 | 91.16
2015-07-15 | DMH | 1130 | 11 | 13.7 | 0.388 | 51.0526 | 50 | 7.25 | 123.5 | 9,10 | 6.03,1.29 | 109104 | TIME/HEAD | 0.369 | 0.215 | 1.8 | 31.6209 | [16 empty] | 6.03 | 109 | 1.29 | 104 |  |  | 3.02 | 55.5
2015-07-15 | DMH | 1300 | 7 | 13.4 | 0.388 | 51.0526 | 50 | 4.14 | 102.5 | NONE |  |  | HEAD | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.26 | 29.63 | 4.25 | 118.24 |  |  | 3.52 | 93.34
2015-07-15 | DMH | 1430 | 6 | 13.4 | 0.388 | 51.0526 | 50 | 4.26 | 121 | NONE |  |  | TIME | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.77 | 30.97 |  |  | 0.49 | 0.27 | 3.52 | 94.69
2015-07-15 | DMH | 1630 | 9 | 13.7 | 0.346 | 45.5263 | 50 | 6.03 | 114 | NONE |  |  | TIME | 0.417 |  | 1.8 | 35.7342 | [18 empty] | 1.29 | 109 | 1.98 | 5 | 3.04 | 60.5
2015-07-16 | DMH | 1000 | 4 | 13 | 0.381 | 50.1316 | 55 | 3.02 | 119 | NONE |  |  | TIME/HEAD | 0.239 |  | 1.708 | 19.4343 | 2.47 | 95.77 | 0.76 | 48.68 | 0.49 | 24.61
2015-07-16 | DMH | 1130 | 1 | 10.8 | 0.381 | 50.1316 | 55 | 1.96 | 107.5 | NONE |  |  | TIME | 0.419 |  | 1.419 | 28.3051 |  |  | 0.76 | 50.32 | 0.49 | 26.25 | 0.47 | 0.86
2015-07-18 | DMH | 1300 | 12 | 10.3 | 0.391 | 51.4474 | 60 | 4.98 | 129 | NONE |  |  | TIME | 0.359 |  | 1.3533 | 23.1291 | [16 empty] | 3.24 | 69 | 1.99 | 65.5 | 4.01 | 74
2015-07-19 | R.H. | 400 | 8 | 10.8 | 0.365 | 48.0263 | 60 | 2.31 | 82 | NONE |  |  | TIME/HEAD | 0.22 |  | 1.419 | 14.8619 | [14 empty] | 2.33 | 82
2015-07-19 | DMH | 900 | 2 | 11.1 | 0.378 | 49.7368 | 60 | 1.77 | 120.5 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 67.03 |  |  | 2.02 | 95.23 | 0.47 | 69.84
2015-07-19 | DMH | 1030 | 7 | 11.2 | 0.378 | 49.7368 | 60 | 3.06 | 93.5 | NONE |  |  | TIME/HEAD | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 12.43 | 2.41 | 91.16 |  |  | 1.62 | 92.45
2015-07-19 | DMH | 1430 | 3 | 11.1 | 0.378 | 49.7368 | 60 | 2.02 | 102 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 72.28 | 0 | 4 |  |  | 0.47 | 75.1
2015-07-19 | DMH | 1600 | 6 | 11.2 | 0.331 | 43.5526 | 60 | 2.39 | 97.5 | NONE |  |  | TIME | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 18.01 |  |  | 0.48 | 4.33 | 0.01 | 10.56
2015-07-20 | DMH | 1300 | 10 | 13 | 0.341 | 44.8684 | 55 | 3.24 | 113 | NONE |  |  | TIME | 0.398 |  | 1.708 | 32.3634 | [16 empty] | 2.12 | 43 |  |  | 6.05 | 98 | 2.76 | 48
2015-07-21 | DMH | 1130 | 4 | 11 | 0.358 | 47.1053 | 55 | 1.47 | 121.5 | NONE |  |  | TIME | 0.204 |  | 1.4453 | 14.0362 | 1.02 | 117.42 | 0 | 49.14 | 0.33 | 43.89
2015-07-21 | DMH | 1400 | 1 | 10.7 | 0.358 | 47.1053 | 55 | 1.02 | 122.5 |  |  |  | TIME | 0.204 |  | 1.4058 | 13.6534 |  |  | 0 | 51.75 | 0.33 | 46.5 | 0.46 | 1.31
2015-07-23 | GE | 900 | 2 | 10.9 | 0.267 | 35.1316 | 45 | 0.53 | 96 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | 0.11 | 19 |  |  | 0.85 | 92.5 | 0.46 | 21.5
2015-07-23 | MN | 1200 | 5 | 10.9 | 0.267 | 35.1316 | 40 | 3.07 | 111 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | [10 empty] | 1.52 | 92 | 1.48 | 97.5 | 2.03 | 102
2015-07-24 | GE | 900 | 12 | 10.1 | 0.214 | 28.1579 | 40 | 4.78 | 140 | NONE |  |  | TIME | 0.35 |  | 1.327 | 22.1114 | [16 empty] | 4.16 | 110.5 | 2.21 | 86 | 3.37 | 92
2015-07-24 | MN | 1230 | 4 | 9.6 | 0.214 | 28.1579 | 35 | 0.46 | 73 | NONE |  |  | TIME | 0.3 |  | 1.2613 | 18.0144 | 0.12 | 68.5 | 0.24 | 51.5 | 0.84 | 118
2015-07-25 | GHE | 730 | 7 | 9.1 | 0.188 | 24.7368 | 35 | 2.01 | 141 | NONE |  |  | TIME | 0.24 |  | 1.1956 | 13.6609 | [8 empty] | 0.44 | 19.5 | 2.03 | 111.5 |  |  | 2.52 | 123.5
2015-07-25 | GE | 930 | 9 | 9.4 | 0.181 | 23.8158 | 35 | 4.64 | 160 | NONE |  |  | TIME | 0.31 |  | 1.235 | 18.2271 | [18 empty] | 2.21 | 116.5 | 3.36 | 110.5 | 1.3 | 11.5
2015-07-26 | CBW | 5:00 | 8 | 9.1 | 0.181 | 23.8158 | 35 | 3.75 | 169 | NONE |  |  | HEAD | 0.27 |  | 1.1956 | 15.3685 | [8 empty] | 1.45 | 65 | 3.57 | 157 | 0.02 | 21.5
2015-07-26 | MN | 730 | 3 | 9.1 | 0.163 | 21.4474 | 32 | 2.37 | 157 | NONE |  |  | TIME | 0.28 |  | 1.1956 | 15.9377 | 1.29 | 113 | 0.24 | 69.5 |  |  | 0.46 | 43
2015-07-26 | MN | 900 | 6 | 9.1 | 0.163 | 21.4474 | 32 | 3.05 | 161 | NONE |  |  | TIME | 0.26 |  | 1.1956 | 14.7993 | [8 empty] | 1.45 | 69 |  |  | 0.02 | 25.5 | 0.46 | 4
2015-07-27 | GE | 800 | 10 | 10.9 | 0.169 | 22.2368 | 30 | 1.71 | 163 | NONE |  |  | TIME | 0.29 |  | 1.4321 | 19.7721 | [16 empty] | 4.68 | 23.5 |  |  | 4.93 | 157 | 2.67 | 71
2015-07-27 | MN | 1500 | 1 | 11 | 0.172 | 22.6316 | 30 | 2.82 | 145 | NONE |  |  | TIME | 0.28 |  | 1.4453 | 19.2654 |  |  | 1.79 | 102 | 0 | 31.5 | 0.96 | 74.5
2015-07-28 | GE | 800 | 11 | 9.9 | 0.19 | 25 | 30 | 5.48 | 161 | NONE |  |  | TIME | 0.29 |  | 1.3007 | 17.9581 | [16 empty] | 3.2 | 47 | 2.14 | 24 |  |  | 4.39 | 95
2015-07-28 | MN | 1400 | 5 | 9.9 | 0.19 | 25 | 30 | 4.47 | 122 | NONE |  |  | TIME | 0.25 |  | 1.3007 | 15.4811 | [10 empty] | 0.72 | 52 | 2.06 | 78.5 | 1.47 | 57
2015-08-02 | dh | 2000 | 8 | 10.4 | 0.186 | 24.4737 | 38 | 1.84 | 44 | none |  |  | head | 0.228 |  | 1.3664 | 14.8319 | [8 empty] | 0.26 | 11.21 | 0.01 | 36.7 | 3.06 | 106.11
2015-08-04 | wl | 1800 | 2 | 7.2 | 0.156 | 20.5263 | 38 | 2.07 | 140 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 59 |  |  | 0.04 | 106 | 0 | 31.5
2015-08-04 | dh | 2000 | 3 | 7.2 | 0.156 | 20.5263 | 38 | 1.48 | 92 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 60.89 | 0 | 0.76 |  |  | 0 | 33.23
2015-08-05 | CBW | 13:30 | 9 | 9.1 | 0.151 | 19.8684 | 30 | 4.84 | 109.5 | NONE |  |  | TIME | 0.19 |  | 1.1956 | 10.8149 | [16 empty] | 4.84 | 109.5 | 109.5 | 1.65 | 4.14 | 102 | 2.18 | 53.5
2015-08-06 | CBW | 7:00 | 10 | 9.6 | 0.163 | 21.4474 | 30 | 2.83 | 127 | NONE |  |  | TIME | 0.391 |  | 1.2613 | 23.4788 | [16 empty] | 1.29 | 17.5 | 2.83 | 127 | 5.68 | 119 | 3.24 | 71
2015-08-06 | CBW | 1400 | 6 | 9.2 | 0.171 | 22.5 | 30 | 1.52 | 134 | NONE |  |  | TIME | 0.39 |  | 1.2088 | 22.4429 | [8 empty] | 1.27 | 102.5 | 1.52 | 134 | 0 | 78.5 | 0.81 | 90
2015-08-06 | CBW | 1600 | 11 | 9.6 | 0.174 | 22.8947 | 30 | 5.69 | 128.5 | NONE |  |  | TIME | 0.31 |  | 1.2613 | 18.6149 | [16 empty] | 1.29 | 26.5 | 2.32 | 9 |  |  | 3.24 | 80
2015-08-07 | CBW | 8:00 | 1 | 8.6 | 0.178 | 23.4211 | 37 | 1.02 | 128 | NONE |  |  | TIME | 0.5 |  | 1.1299 | 26.8965 | 1.02 | 128 | 0.39 | 62 | 0 | 60 | 0.5 | 95.5
2015-08-07 | CBW | 13:00 | 5 | 8.6 | 0.178 | 23.4211 | 37 | 2.27 | 125.5 | NONE |  |  | TIME | 0.32 |  | 1.1299 | 17.2138 | [8 empty] | 2.27 | 125.5 | 0 | 23 | 1.01 | 101.5 | 1.81 | 113
2015-08-08 | CBW | 6:00 | 8 | 8.5 | 0.235 | 30.9211 | 35 | 2.8 | 130 | NONE |  |  | TIME | 0.47 |  | 1.1168 | 24.9887 | [8 empty] | 0 | 17 | 0.5 | 40 | 2.52 | 118.5 | 2.8 | 130
2015-08-08 | CBW | 8:00 | 7 | 8.5 | 0.165 | 21.7105 | 35 | 2.52 | 120 | NONE |  |  | TIME | 0.46 |  | 1.1168 | 24.4571 | [8 empty] | 0 | 19 | 0.5 | 42 | 2.52 | 120 | 0 | 2
2015-08-09 | CBW | 6:30 | 12 | 9.2 | 0.169 | 22.2368 | 35 | 6.05 | 142.5 | NONE |  |  | TIME | 0.58 |  | 1.2088 | 33.3767 | [16 empty] | 3.81 | 89 | 2.34 | 71.5 | 3.42 | 62.5 | 6.05 | 142.5
2015-08-09 | CBW | 9:00 | 4 | 8.9 | 0.169 | 22.2368 | 35 | 2.18 | 144.5 | NONE |  |  | TIME | 0.43 |  | 1.1693 | 23.9379 | 0.46 | 49 | 0.78 | 111 | 2 | 109 | 2.18 | 144.5
2015-08-10 | CBW | 6:00 | 2 | 9.3 | 0.181 | 23.8158 | 35 | 2.37 | 132 | NONE |  |  | TIME | 0.66 |  | 1.2219 | 38.3932 | 0.46 | 70 | 2.37 | 132 | 3.52 | 130 | 0 | 21
2015-08-10 | CBW | 10:00 | 3 | 10 | 0.181 | 23.8158 | 35 | 3.52 | 134 | NONE |  |  | TIME | 0.33 |  | 1.3139 | 20.6415 | 0.96 | 74 | 0.06 | 136 | 3.52 | 134 | 0 | 25
2015-08-11 | CBW | 6:30 | 9 | 9.8 | 0.177 | 23.2895 | 34 | 6.84 | 137 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [18 empty] | 1.32 | 119.5 | 6.97 | 110.5 | 3.74 | 48
2015-08-11 | CBW | 8:00 | 10 | 9.8 | 0.177 | 23.2895 | 34 | 0.8 | 121 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 1.5 |  |  | 6.97 | 112 | 3.76 | 49.5
2015-08-11 | CBW | 13:30 | 11 | 9.8 | 0.177 | 23.2895 | 34 | 6.47 | 117.5 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 7 | 2.58 | 5.5 |  |  | 3.74 | 55
2015-08-11 | CBW | 1500 | 6 | 9.4 | 0.177 | 23.2895 | 34 | 5.01 | 121 | NONE |  |  | TIME | 0.27 |  | 1.235 | 15.8752 | [8 empty] | 4.56 | 98 | 5.01 | 121 | 0 | 79 | 3.53 | 81
2015-08-11 | GHE | 18:00 | 1 | 7.4 | 0.138 | 18.1579 | 35 | 1.45 | 106 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 |  |  | 0.06 | 37 | 0 | 32 | 0.51 | 57
2015-08-11 | GHE | 20:00 | 5 | 7.4 | 0.138 | 18.1579 | 35 | 2.5 | 103 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 | [10 empty] | 0 | 5 | 0 | 84 | 3.03 | 86
2015-08-12 | MN | 600 | 8 | 7.5 | 0.152 | 20 | 35 | 2.54 | 96 | NONE |  |  | TIME | 0.42 |  | 0.9854 | 19.7032 | [8 empty] | 0.12 | 9 | 0 | 14 | 0.2 | 93
2015-08-12 | DMH | 11:30 | 7 | 7.8 | 0.133 | 17.5 | 35 | 0.02 | 99.5 | NONE |  |  | TIME | 0.282 |  | 1.0248 | 13.7585 | [8 empty] | 0.09 | 14.45 | 0.06 | 19.07 |  |  | 0 | 4.64
2015-08-13 | wl | 10:00 | 12 | 9.3 | 0.149 | 19.6053 | 40 | 4.94 | 99.5 | none |  |  | time | 0.39 |  | 1.2219 | 22.6869 | [16 empty] | 1.37 | 51.5 | 2.57 | 50 | 2.05 | 44.5
2015-08-13 | wl | 16:00 | 4 | 8.8 | 0.15 | 19.7368 | 40 | 1.1 | 103 | none |  |  | time | 0.267 |  | 1.1562 | 14.6967 | 0 | 44.6 | 0.2 | 80.6 | 0.2 | 76
2015-08-14 | dmh | 11:00 | 2 | 10.4 | 0.15 | 19.7368 | 40 | 0.51 | 101 | none |  |  | time | 0.289 |  | 1.3664 | 18.8 | 0 | 63.34 |  |  | 1 | 95.12 | 0 | 17.27
2015-08-14 | dmh | 15:30 | 3 | 10.6 | 0.15 | 19.7368 | 40 | 0.1 | 99.5 | none |  |  | time | 0.289 |  | 1.3927 | 19.1616 | 0 | 3.56 | 0.45 | 68.11 |  |  | 0.06 | 22.04
2015-08-15 | wl | 9:30 | 1 | 9.9 | 0.149 | 19.6053 | 40 | 0 | 84 | none |  |  | time | 0.399 |  | 1.3007 | 24.7079 |  |  | 0 | 22 | 0 | 17 | 0 | 40.5
2015-08-15 | CBW | 11:30 | 9 | 10.4 | 0.149 | 19.6053 | 40 | 3.2 | 101 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [18 empty] | 2 | 99.5 | 3.5 | 94.5 | 2.6 | 49.5
2015-08-15 | CBW | 1400 | 10 | 10.4 | 0.149 | 19.6053 | 40 | 2.9 | 102 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [16 empty] | 1.1 |  |  |  | 3.6 |  | 2.8
2015-08-15 | wl | 1600 | 6 | 9.2 | 0.149 | 19.6053 | 40 | 0.5 | 96 | none |  |  | time | 0.448 |  | 1.2088 | 25.7806 | [8 empty] | 0.5 | 91 |  |  | 0.4 | 75 | 0.2 | 80
2015-08-15 | he | 1800 | 11 |  |  | 0 | 45 | 3.62 | 99.5 | none |  |  | time | 0.487 |  | 0 | 0
2015-08-16 | wl | 8:30 | 5 | 9.4 | 0.147 | 19.3421 | 45 | 1 | 110.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [10 empty] | 0 | 15.5 | 0.8 | 92 | 0.7 | 97
2015-08-16 | wl | 10:30 | 8 | 9.4 | 0.147 | 19.3421 | 45 | 0.7 | 100.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 1 | 0 | 17.5 | 0.8 | 94
2015-08-16 | wl | 13:30 | 7 | 9.4 | 0.147 | 19.3421 | 45 | 0.8 | 98 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 4 | 0 | 20.5 |  |  | 0 | 2
2015-08-17 | wl | 11:00 | 12 | 10.3 | 0.149 | 19.6053 | 45 | 3.63 | 97 | none |  |  | time | 0.348 |  | 1.3533 | 22.4204 | [16 empty] | 1.7 | 47.5 | 2.82 | 45 | 1.89 | 41
2015-08-17 | wl | 1600 | 4 | 9.7 | 0.149 | 19.6053 | 45 | 0.1 | 96 | none |  |  | time | 0.367 |  | 1.2745 | 22.2672 | 0 | 52.5 | 0 | 76 | 0 | 71.5
2015-08-18 | wl | 7:30 | 2 | 9.6 | 0.149 | 19.6053 | 45 | 0.3 | 91.6 | none |  |  | time | 0.354 |  | 1.2613 | 21.257 | 0 | 68.3 |  |  | 0.2 | 86.8 | 0 | 14.1
2015-08-18 | dh | 10:00 | 3 | 9.6 | 0.149 | 19.6053 | 45 | 0.04 | 89 | none |  |  | time | 0.403 |  | 1.2613 | 24.1993 | 0 | 70.53 | 0 | 1.01 |  |  | 0 | 16.39
2015-08-19 | GE | 9:30 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0.45 | 10 | 0.05 | 11.5 | 0 | 17.5
2015-08-19 | GE | 13:30 | 9 | 8.9 |  | 0 | 40 | 2.21 | 98 | NONE |  |  | TIME | 0.32 |  | 1.1693 | 17.8142 | [18 empty] | 2.32 | 93.5 | 2.43 | 91.5 | 1.59 | 51.5
2015-08-19 | GE | 16:00 | 6 | 8.3 |  | 0 | 40 | 0.22 | 96 | NONE |  |  | TIME | 0.3 |  | 1.0905 | 15.575 | [8 empty] | 0.31 | 79.5 |  |  | 0.34 | 74.5 | 0.23 | 77.5
2015-08-19 | CBW | 19:00 | 10 | 8.8 |  | 0 | 39 | 2.91 | 101 | NONE |  |  | TIME | 0.231 |  | 1.1562 | 12.7152 | [16 empty] | 1.26 | 5.5 |  |  | 2.43 | 99 | 1.6 | 56
2015-08-19 | CBW | 23:00 | 11 | 8.8 |  | 0 | 39 | 2.43 | 100.5 | NONE |  |  | TIME | 0.227 |  | 1.1562 | 12.495 | [16 empty] | 1.26 | 9.5 | 2.91 | 4 |  |  | 2.1 | 60
2015-08-20 | MN | 830 | 5 | 8.3 |  | 0 | 38 | 0.81 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [10 empty] | 0.21 | 16 | 0.34 | 91 | 0.23 | 94
2015-08-20 | MN | 1030 | 8 | 8.3 |  | 0 | 38 | 0.21 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [8 empty] | 0 | 2 | 0.21 | 18 | 0.34 | 93
2015-08-20 | MN | 1330 | 7 | 8.3 |  | 0 | 38 | 0.34 | 96 | NONE |  |  | TIME | 0.2 |  | 1.0905 | 10.3833 | [8 empty] | 0 | 5 | 0.21 | 21 |  |  | 0.13 | 3 | 1.29 | 45.5 | 2.51 | 28 | 1.36 | 38
2015-08-21 | MN | 1100 | 12 | 8.8 |  | 0 | 35 | 2.1 | 96 | NONE |  |  | TIME | 0.22 |  | 1.1562 | 12.1097
2015-08-21 | MN | 1600 | 4 | 8.3 | 0.176 | 23.1579 | 35 | 0 | 96 | NONE |  |  | TIME | 0.22 |  | 1.0905 | 11.4216 | 0 | 54.5 | 0 | 80.5 | 0 | 78
2015-08-22 | CBW | 4:00 | 2 | 8.3 | 0.176 | 23.1579 | 35 | N/A | 92.5 | NONE |  |  | TIME | 0.34 |  | 1.0905 | 17.6516 | N/A | 66.5 |  |  | N/A | 90 | N/A | 12
2015-08-22 | MN | 1000 | 3 | 8.3 |  | 0 | 35 | 0 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | 0 | 72.5 | 0 | 6 |  |  | 0 | 18
2015-08-23 | MN | 930 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0 | 29.5 | 0.44 | 23.5 | 0 | 42.5
2015-08-23 | MN | 1600 | 6 | 8.3 |  | 0 | 45 | 0 | 96 | NONE |  |  | TIME | 0.28 |  | 1.0905 | 14.5366 | [8 empty] | 0 | 78 |  |  | 0 | 73 | 0 | 76 |  |  | 2.51 | 110.5 | 1.86 | 105.5 | 1.47 | 69.5
2015-08-24 | MN | 830 | 9 | 9.5 |  | 0 | 45 | 2.3 | 115 | NONE |  |  | TIME | 0.25 |  | 1.2482 | 14.8556
2015-08-24 | MN | 1030 | 5 | 9 |  | 0 | 45 | 1.02 | 98 | NONE |  |  | TIME | 0.23 |  | 1.1825 | 12.9478 | [10 empty] | 0 | 16 | 0 | 92 | 0.52 | 95
2015-08-24 | CBW | 21:00 | 10 | 10.3 | 0.14 | 18.4211 | 35 | 3.03 | 124 | NONE |  |  | TIME | 0.25 |  | 1.3533 | 16.1066 | [16 empty] | 1.19 | 12.5 |  |  | 2.87 | 118 | 2.5 | 82
2015-08-25 | CBW | 2:00 | 11 | 10.2 | 0.14 | 18.4211 | 35 | 2.36 | 123 | NONE |  |  | TIME | 0.2 |  | 1.3401 | 12.7602 | [16 empty] | 1.19 | 17.5 | 2.5 | 5 |  |  | 1.99 | 87
2015-09-02 | CBW | 13:00 | 3 | 7.3 | 0.263 | 34.6053 | 45 | N/A | 37 | NONE |  |  | TIME | 0.26 |  | 0.95912 | 11.872 | N/A | 28 | N/A | 29 |  |  | N/A | 37
2015-09-02 | CBW | 15:00 | 1 | 7.7 | 0.263 | 34.6053 | 45 | N/A | 39 | NONE |  |  | TIME | 0.21 |  | 1.0117 | 10.1143 |  |  | N/A | 31 | N/A | 2 | N/A | 39
2015-09-03 | CBW | 6:00 | 6 | 8.5 | 0.256 | 33.6842 | 45 | 1 | 54 | NONE |  |  | TIME | 0.3 |  | 1.1168 | 15.9503 | [8 empty] | 0.5 | 54 | 1.01 | 54 | 0 | 54 | 0.01 | 54
2015-09-03 | CBW | 9:00 | 9 | 9.2 | 0.256 | 33.6842 | 45 | 2.24 | 57 | NONE |  |  | TIME | 0.276 |  | 1.2088 | 15.8827 | [18 empty] | 2.58 | 57 | 1.92 | 57 | 1.67 | 48
2015-09-03 | CBW | 12:00 | 5 | 7.3 | 0.256 | 33.6842 | 45 | 1 | 60 | NONE |  |  | TIME | 0.22 |  | 0.95912 | 10.0455 | [10 empty] | 0.29 | 6 | 0 | 60 | 0.01 | 60
2015-09-04 | CBW | 7:00 | 10 | 7 | 0.256 | 33.6842 | 45 | 2.08 | 79 | NONE |  |  | TIME | 0.58 |  | 0.91971 | 25.3953 | [16 empty] | 0.67 | 22 |  |  | 1.91 | 79 | 0.67 | 79
2015-09-04 | CBW | 9:30 | 11 | 8.5 | 0.256 | 33.6842 | 45 | 1.92 | 81.5 | NONE |  |  | TIME | 0.4 |  | 1.1168 | 21.267 | [16 empty] | 0.67 | 24.5 | 2.71 | 2.5 |  |  | 1.68 | 81.5
2015-09-04 | CBW | 13:00 | 8 | 8.5 | 0.256 | 33.6842 | 45 | N/A | 85 | NONE |  |  | TIME | 0.32 |  | 1.1168 | 17.0136 | [8 empty] | 4.7 | 25 | 0.29 | 31 | 0 | 85
2015-09-05 | CBW | 7:00 | 12 | 9.1 | 0.256 | 33.6842 | 45 | 1.38 | 103 | NONE |  |  | TIME | 0.6 |  | 1.1956 | 34.1523 | [16 empty] | 1.22 | 46 | 2.62 | 24 | 1.16 | 21.5
2015-09-05 | CBW | 9:00 | 7 | 8.3 | 0.304 | 40 | 45 | 0.31 | 105 | NONE |  |  | TIME | 0.27 |  | 1.0905 | 14.0175 | [8 empty] | N/A | 45 | N/A | 51 |  |  | N/A | 20
2015-09-05 | CBW | 1500 | 4 | 7.1 | 0.304 | 40 | 45 | N/A | 111 | NONE |  |  | TIME | 0.25 |  | 0.93285 | 11.1026 | N/A | 72 | N/A | 103 | N/A | 74
2015-09-06 | CBW | 7:00 | 2 | 7.1 | 0.295 | 38.8158 | 40 | N/A | 119 | NONE |  |  | TIME | 0.56 |  | 0.93285 | 24.8699 | N/A | 88 |  |  | N/A | 90 | N/A | 16
2015-09-07 | CBW | 9:00 | 3 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 116 | NONE |  |  | TIME | 0.49 |  | 1.0117 | 23.6001 | N/A | 114 | N/A | 26 |  |  | N/A | 4
2015-09-07 | CBW | 14:00 | 1 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 119 | NONE |  |  | TIME | 0.38 |  | 1.0117 | 18.3021 |  |  | N/A | 31 | N/A | 5 | N/A | 47
2015-09-08 | CBW | 6:00 | 6 | 8.1 | 0.233 | 30.6579 | 45 | 2.51 | 120 | NONE |  |  | TIME | 0.4 |  | 1.0642 | 20.2662 | [8 empty] | 2.02 | 114 |  |  | 1.72 | 69 | 2.53 | 89
2015-09-08 | CBW | 8:00 | 9 | 8.9 | 0.233 | 30.6579 | 45 | 3.74 | 119 | NONE |  |  | TIME | 0.5 |  | 1.1693 | 27.8347 | [18 empty] | 2.11 | 97 | 3.24 | 94 | 2.43 | 73
2015-09-08 | CBW | 12:00 | 5 | 0.31 | 0.233 | 30.6579 | 45 | 2.56 | 120 | NONE |  |  | TIME | 0.32 |  | 0.04073 | 0.6205 | [10 empty] | 0 | 6 | 2.24 | 7.5 | 3.05 | 95
2015-09-09 | wl | 8:00 | 8 | 7.2 | 0.335 | 44.0789 | 45 | 3.8 | 115 | NONE |  |  | time | 0.367 |  | 0.94598 | 16.5282 | [8 empty] | 0 | 18 | 0 | 25.5 | 2.9 | 93.5
2015-09-10 | wl | 8:30 | 4 | 6.6 | 0.345 | 45.3947 | 50 | 1.3 | 113.5 | NONE |  |  | time | 0.317 |  | 0.86715 | 13.0867 | 0 | 66 | 0.4 | 96 | 0 | 71
2015-09-10 | dh | 10:30 | 12 | 7.5 | 0.345 | 45.3947 | 50 | 3.05 | 123.5 | NONE |  |  | time | 0.381 |  | 0.9854 | 17.8737 | [16 empty] | 1.04 |  | 0.06 |  | 1.06
2015-09-11 | wl | 14:30 | 2 | 7.2 | 0.309 | 40.6579 | 50 | 0.8 | 127.5 | NONE |  |  | time | 0.301 |  | 0.94598 | 13.5558 | 0 | 95.5 |  |  | 0.3 | 101 | 7.4 | 28.5
2015-09-12 | DH | 10:00 | 1 | 7.2 | 0.31 | 40.7895 | 50 | 0.035 | 116 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 |  |  | 0.059 | 18.02 | 0.04 | 120.31 | 0.06 | 47.81
2015-09-12 | DH | 14:00 | 3 | 7.2 | 0.31 | 40.7895 | 50 | 0.04 | 125 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 | 0.069 | 2.97 | 0.063 | 22.42 |  |  | 0.06 | 52.21
2015-09-13 | wl | 10:00 | 6 | 6.6 | 0.31 | 40.7895 | 50 | 0.9 | 124 | none |  |  | Time | 0.285 |  | 0.86715 | 11.7657 | [8 empty] | 0.8 | 115.5 |  |  | 0 | 96 | 0 | 98
2015-09-13 | DH | 12:00 | 5 | 6.5 | 0.31 | 40.7895 | 50 | 0.06 | 120 | NONE |  |  | TIME | 0.285 |  | 0.85401 | 11.5874 | [10 empty] | 0.08 | 0.71 | 0.06 | 97.48 | 0.04 | 99.49
2015-09-14 | DH | 9:00 | 10 | 8.5 | 0.306 | 40.2632 | 60 | 2 | 115 | NONE |  |  | TIME | 0.438 |  | 1.1168 | 23.2874 | [16 empty] | 1 | 18 |  |  | 2.3 | 114.5 | 2 | 90.5
2015-09-15 | wl | 8:00 | 7 | 7.3 | 0.31 | 40.7895 | 60 | 1.4 | 142 | none |  |  | time | 0.461 |  | 0.95912 | 21.05 | [8 empty] | 0.2 | 43 | 0.1 | 45 |  |  | 0 | 16
2015-09-15 | wl | 10:00 | 4 | 7.3 | 0.31 | 40.7895 | 60 | 0 | 121.5 | none |  |  | time | 0.422 |  | 0.95912 | 19.2692 | 0 | 70.5 | 0 | 90 | 0 | 66.5
2015-09-15 | DH | 13:00 | 12 | 7.8 | 0.312 | 41.0526 | 60 | 2.4 | 122.5 | NONE |  |  | TIME | 0.426 |  | 1.0248 | 20.7841 | [16 empty] | 1.4 | 46 | 2.5 | 28 | 1.2 | 26.5
2015-09-18 | CBW | 22:00 | 9 | 7.9 | 0.283 | 37.2368 | 45 | 4.58 | 127 | NONE |  |  | TIME | 0.423 |  | 1.038 | 20.9023 | [18 empty] | 1.71 | 109 | 3.78 | 107.5 | 3.01 | 81

## FILTER STUDY
Hour
| DATE | 2018-11-01 | 2018-11-02 | 2018-11-03 | 2018-11-04 | 2018-11-05 | 2018-11-06 | 2018-11-07 | 2018-11-08 | 2018-11-09 | 2018-11-10 | 2018-11-11 | 2018-11-12 | 2018-11-13 | 2018-11-14 | 2018-11-15 | 2018-11-16 | 2018-11-17 | 2018-11-18 | 2018-11-19 | 2018-11-20 | 2018-11-21 | 2018-11-22 | 2018-11-23 | 2018-11-24 | 2018-11-25 | 2018-11-26 | 2018-11-27 | 2018-11-28 | 2018-11-29 | 2018-11-30 | 2018-12-01
| DOSE | 13433.3333 | 11922.5 | 10726 | 10965 | 12180 | 11103.3333 | 10595 | 9805 | 10400 | 10744.8 | 10316.6667 | 10400 | 9517.75 | 9406.6667 | 9506.6667 | 9722.5 | 10123.3333 | 9763.3333 | 10155 | 10240 | 11638 | 13055 | 13120 | 13766.6667 | 12467.5 | 13749.8 | 17217.7143 | 15308 | 14035 | 15585 |  |  | NUMBER OF WASHS
| Alum Dose:TOC Ratio | 941.5309 | 865.7102 | 811.1204 | 870.7837 | 942.0081 | 852.0902 | 763.9658 | 722.5404 | 805.7085 | 819.8843 | 775.2802 | 804.6149 | 772.5336 | 763.5173 | 804.5731 | 818.2835 | 824.3286 | 778.3357 | 798.3931 | 763.7291 | 799.477 | 909.7005 | 926.4045 | 990.1577 | 884.44 | 937.4864 | 1176.0452 | 1053.8116 | 948.4232 | 1054.7284 | #VALUE!
| UV 254 | 0.54217 | 0.52333 | 0.5025 | 0.4785 | 0.49133 | 0.49517 | 0.527 | 0.51567 | 0.4905 | 0.498 | 0.50567 | 0.49117 | 0.46817 | 0.46817 | 0.449 | 0.4515 | 0.46667 | 0.47667 | 0.48333 | 0.5095 | 0.55317 | 0.54533 | 0.53817 | 0.52833 | 0.53567 | 0.55733 | 0.55633 | 0.552 | 0.56233 | 0.5615
RAW | FLOWS | 32.598 | 31.179 | 30.054 | 31.693 | 34.632 | 31.46 | 27.548 | 27.924 | 33.593 | 31.877 | 33.059 | 31.922 | 31.256 | 30.76 | 29.199 | 31.386 | 31.096 | 29.153 | 31.493 | 30.66 | 34.381 | 31.693 | 30.618 | 32.732 | 32.289 | 31.833 | 35.89 | 29.571 | 33.423 | 33.203 | 0
FILTERS | [34 empty] | Days | GAL USED
| FILT 1 |  | 27 |  |  | 85 |  |  |  | 92.5 |  |  | 76 |  |  |  | 103 |  |  |  |  | 101 |  | 59 |  |  | 59.5 |  | 46 |  | 51 |  |  | 10 | 1 |  |  | 172929.1667 |  |  |  | 172929.1667 |  | 185937.5 | 185937.5 | 185937.5 | 185937.5 | 1089608.3333
| FILT 2 |  | 56 |  |  |  | 96 |  |  |  | 96 |  |  | 76.5 |  |  |  | 96.5 |  |  |  | 95.5 |  | 58.5 |  |  | 57.5 |  | 48 |  | 48 |  |  | 10 | 2 | 172929.1667 | 172929.1667 |  | 172929.1667 | 222281.25 | 172929.1667 | [6 empty] | 913997.9167
| FILT 3 | 15 |  |  | 72 |  |  |  | 91 |  |  | 63 |  |  |  | 104 |  |  | 84 |  |  | 71.5 |  | 36.5 |  | 48 |  | 49.5 |  | 46 |  |  |  | 11 | 3 | [12 empty] | 0
| FILT 4 |  | 54 |  |  | 72.5 |  |  |  | 90.5 |  |  | 71.5 |  |  |  | 107 |  |  |  | 98.5 |  |  | 62 |  | 50.5 |  | 54 |  | 48 |  |  |  | 10 | 4 |  |  | 172929.1667 |  |  |  |  | 167720.8333 |  |  |  |  | 340650
| FILT 5 |  | 63 |  |  |  |  | 114 |  |  |  | 95 |  |  |  | 100.5 |  |  |  | 92 |  |  | 76 |  | 51 |  | 56 |  | 40 |  | 50 |  |  | 10 | 5 | 174491.6667 |  |  | 179700 |  |  |  |  | 192708.3333 | 182291.6667 | 192708.3333 | 192708.3333 | 1114608.3333
| FILT 6 |  | 34.5 |  |  |  | 97 |  |  |  | 96 |  |  |  |  | 114.5 |  |  |  | 91 |  |  | 82.5 |  | 55.5 |  |  | 56.5 |  | 43 |  |  |  | 9 | 6 |  | 170845.8333 |  |  |  | 170845.8333 | 170845.8333 | [5 empty] | 512537.5
| FILT 7 | 18 |  |  |  |  | 105 |  |  |  | 97 |  |  |  | 97 |  |  |  | 100.5 |  |  | 81.5 |  | 46 |  | 43 |  | 44.5 | 18.5 |  | 66 |  |  | 11 | 7 |  |  |  |  | 169283.3333 | [7 empty] | 169283.3333
| FILT 8 |  |  |  | 76 |  |  |  | 105 |  |  | 72.5 |  |  |  |  | 107.5 |  |  | 76 |  |  | 75 |  | 49 |  | 58 |  | 39 |  | 52 |  |  | 10 | 8 |  |  | 167720.8333 |  |  |  |  | 167720.8333 |  |  |  |  | 335441.6667
| FILT 9 | 11 |  |  |  | 96 |  |  |  |  | 111 |  |  |  | 106.5 |  |  |  | 94 |  |  |  | 96 |  | 53 |  |  | 57.5 |  | 55 |  |  |  | 9 | 9 | 174491.6667 |  |  | 169283.3333 | [5 empty] | 187500 | 187500 | 187500 | 906275
| FILT 10 | 13 |  |  |  | 98 |  |  |  | 104 |  |  |  | 83 |  |  |  | 93 |  |  |  | 99.5 |  | 59 |  | 46.5 |  | 49 |  | 55.5 |  |  |  | 10 | 10 |  | 174491.6667 |  |  |  | 174491.6667 | 174491.6667 |  | 187500 |  |  |  | 710975
| FILT 11 | 9 |  |  |  | 96 |  |  |  | 96.5 |  |  | 78 |  |  |  | 93 |  |  |  | 94 |  |  | 64 |  | 50 |  | 45 | 31 |  | 44 |  |  | 11 | 11 |  |  | 170845.8333 |  | 169283.3333 |  |  | 168762.5 |  |  |  |  | 508891.6667
| FILT 12 | 7 |  |  |  | 96 |  |  |  | 92.5 |  |  | 77 |  |  |  | 105 |  |  |  | 97 |  |  | 64.5 |  | 47 |  | 48 | 36 |  | 40 |  |  | 11 | 12 | 170845.8333 |  |  | 169283.3333 | [6 empty] | 246354.1667 | 183854.1667 | 770337.5
NUMBER WASHED |  | 6 | 5 | 0 | 2 | 6 | 3 | 1 | 2 | 5 | 4 | 3 | 4 | 2 | 2 | 3 | 5 | 2 | 3 | 3 | 3 | 5 | 4 | 8 | 4 | 6 | 4 | 8 | 7 | 5 | 7 | 0 | 0 |  | 13 |  | 165637.5 | [7 empty] | 241145.8333 |  |  | 406783.3333
GAL USED |  | 1089608.3333 | 913997.9167 | 0 | 340650 | 1114608.3333 | 512537.5 | 169283.3333 | 335441.6667 | 906275 | 710975 | 508891.6667 | 770337.5 | 406783.3333 | 341158.3333 | 496912.5 | 861495.8333 | 355220.8333 | 515129.1667 | 512537.5 | 532304.1667 | 873487.5 | 702641.6667 | 1397979.1667 | 704725 | 1065662.5 | 806312.5 | 1456820.8333 | 1221937.5 | 885975 | 1247979.1667 | 0 | 21757668.75 |  | 14 | [6 empty] | 162512.5 |  | 178645.8333 |  |  |  | 341158.3333
| UV TIMES 100 | 54.2167 | 52.3333 | 50.25 | 47.85 | 49.1333 | 49.5167 | 52.7 | 51.5667 | 49.05 | 49.8 | 50.5667 | 49.1167 | 46.8167 | 46.8167 | 44.9 | 45.15 | 46.6667 | 47.6667 | 48.3333 | 50.95 | 55.3167 | 54.5333 | 53.8167 | 52.8333 | 53.5667 | 55.7333 | 55.6333 | 55.2 | 56.2333 | 56.15 |  |  |  | 15 |  |  | 165637.5 |  | 165637.5 | 165637.5 | [6 empty] | 496912.5
[35 empty] | 16 | 170845.8333 |  |  | 166679.1667 |  |  |  | 165637.5 |  |  | 179687.5 | 178645.8333 | 861495.8333
[35 empty] | 17 |  | 171366.6667 | [7 empty] | 183854.1667 |  |  | 355220.8333
[35 empty] | 18 |  |  | 170845.8333 |  |  |  | 165637.5 |  | 178645.8333 |  |  |  | 515129.1667
[35 empty] | 19 |  |  |  |  | 170845.8333 | 170845.8333 |  | 170845.8333 |  |  |  |  | 512537.5
[35 empty] | 20 |  |  |  | 167720.8333 | [6 empty] | 180729.1667 | 183854.1667 | 532304.1667
[35 empty] | 21 | 170845.8333 | 172408.3333 | 172408.3333 |  |  |  | 172408.3333 |  |  | 185416.6667 |  |  | 873487.5
[35 empty] | 22 |  |  |  |  | 172408.3333 | 172408.3333 |  | 172408.3333 | 185416.6667 |  |  |  | 702641.6667
[35 empty] | 23 | 169283.3333 | 172929.1667 | 169283.3333 | 169283.3333 |  |  | 169283.3333 |  |  | 185937.5 | 179687.5 | 182291.6667 | 1397979.1667
[35 empty] | 24 |  |  |  |  | 172929.1667 | 172929.1667 |  | 172929.1667 | 185937.5 |  |  |  | 704725
[35 empty] | 25 |  |  | 172929.1667 | 172929.1667 |  |  | 172929.1667 |  |  | 175000 | 185937.5 | 185937.5 | 1065662.5
[35 empty] | 26 | 167200 | 175533.3333 |  |  | 231008.3333 |  |  | 232570.8333 |  |  |  |  | 806312.5
[35 empty] | 27 |  |  | 203791.6667 | 203791.6667 |  | 0 | 233091.6667 |  | 191145.8333 | 187500 | 250000 | 187500 | 1456820.8333
[35 empty] | 28 | 172929.1667 | 172929.1667 |  |  | 170325 |  | 170845.8333 | 170325 |  |  | 183854.1667 | 180729.1667 | 1221937.5
[35 empty] | 29 |  |  | 170845.8333 | 172929.1667 |  | 170845.8333 |  |  | 183854.1667 | 187500 |  |  | 885975
[35 empty] | 30 | 174491.6667 | 174491.6667 |  |  | 174491.6667 |  | 175012.5 | 174491.6667 |  |  | 187500 | 187500 | 1247979.1667
[35 empty] | 31 | [12 empty] | 0

## Total Flows
Water Production and Waste (MGD) | [7 empty] | 2018-11-01
Day | Raw Flow | Finished 1 Flow | Finished 2 Flow | Combined Finished | Finished South Meter 1 | Finished South Meter 2 | Finished Conway #66 | Finished Perry #67 | Blowdown | Backwash | Decant Flow | Decant Actual Flow | Plant 1 Raw Flow, MGD | Plant 2 Raw Flow, MGD | Plant 3 Raw Flow, MGD | Plant 1 Polymer Dose, mg/L | Plant 2 Polymer Dose, mg/L | Plant 3 Polymer Dose, mg/L | Plant 1 Settled Turb. | Plant 2 Settled Turb. | Plant 3 Settled Turb.
1 | 32.598 | 13.822 | 14.938 | 28.76 |  | 13.815 | 4.532 | 10.406 | 1.3311 | 1.0896 | 2.103 | 1.5278 | 10.7 | 10.7 | 11.7 | 975 | 950 | 908.3333 | 0.37375 | 0.35175 | 0.4035
2 | 31.179 | 14.026 | 14.108 | 28.134 |  | 14.024 | 4.549 | 9.559 | 1.2551 | 0.914 | 2.182 | 1.6258 | 10.2 | 10.2 | 11.2 | 910 | 870 | 751.875 | 0.3815 | 0.372 | 0.337
3 | 30.054 | 13.805 | 13.676 | 27.481 |  | 13.796 | 4.592 | 9.084 | 1.4551 |  | 1.574 | 1.6258 | 9.7 | 9.7 | 10.7 | 836 | 792 | 696 | 0.361 | 0.366 | 0.336
4 | 31.693 | 14.083 | 14.519 | 28.602 |  | 14.068 | 4.53 | 9.989 | 1.6121 | 0.34065 | 1.712 | 1.6646 | 10.275 | 10.275 | 11.275 | 786.25 | 765 | 620 | 0.32975 | 0.27625 | 0.314
5 | 34.632 | 14.727 | 15.766 | 30.493 |  | 14.727 | 4.843 | 10.923 | 1.3607 | 1.1146 | 1.63 | 1.7597 | 11.34 | 11.34 | 12.34 | 851 | 858 | 713.5 | 0.33125 | 0.33175 | 0.32075
6 | 31.46 | 13.19 | 14.847 | 28.037 |  | 13.188 | 4.606 | 10.241 | 1.1607 | 0.51254 | 1.262 | 0.0013968 | 10.3 | 10.3 | 11.3 | 753.3333 | 735 | 568.3333 | 0.3435 | 0.363 | 0.289
7 | 27.548 | 10.764 | 13.162 | 23.926 |  | 10.763 | 4.369 | 8.793 | 1.1807 | 0.16928 | 0.678 | 0.00098496 | 10.075 | 10.075 | 11.075 | 732.5 | 710 | 587.5 | 0.36825 | 0.35325 | 0.331
8 | 27.924 | 13.266 | 14.026 | 27.292 |  | 13.26 | 4.03 | 9.996 | 1.5252 | 0.33544 | 0.766 | 1.9181 | 9.85 | 9.85 | 10.85 | 712.5 | 630 | 722.5 | 0.4295 | 0.384 | 0.32825
9 | 33.593 | 14.245 | 15.444 | 29.689 |  | 14.236 | 4.582 | 10.862 | 0.96539 | 0.90628 | 0.813 | 1.5134 | 10.75 | 10.75 | 11.75 | 765 | 662.5 | 724 | 0.47325 | 0.466 | 0.36475
10 | 31.877 | 13.589 | 15.219 | 28.808 |  | 13.58 | 4.653 | 10.566 | 1.4405 | 0.71098 | 1.162 | 2.0203 | 10.58 | 10.58 | 11.58 | 729 | 683 | 709 | 0.6565 | 0.58825 | 0.47875
11 | 33.059 | 13.748 | 14.35 | 28.098 |  | 13.734 | 4.308 | 10.042 | 1.1999 | 0.50889 | 0.919 | 2.1197 | 10.1 | 10.1 | 11.1 | 650 | 676.6667 | 724.3333 | 0.52325 | 0.3715 | 0.32525
12 | 31.922 | 13.501 | 15.104 | 28.605 |  | 13.487 | 4.571 | 10.533 | 1.2507 | 0.77034 | 0.719 | 2.1182 | 10.2 | 10.2 | 11.2 | 646.6667 | 706.6667 | 714.3333 | 0.482 | 0.368 | 0.2825
13 | 31.256 | 11.452 | 16.554 | 28.006 |  | 11.44 | 4.953 | 11.601 | 1.3717 | 0.40678 | 0.861 | 1.993 | 9.25 | 9.25 | 10.25 | 571.25 | 600 | 635 | 0.357 | 0.31975 | 0.236
14 | 30.76 | 13.703 | 16.057 | 29.76 |  | 13.688 | 5.509 | 10.548 | 1.5145 | 0.34116 | 0.952 | 1.9685 | 9.1667 | 9.1667 | 10.1667 | 518.3333 | 547.5 | 610 | 0.38225 | 0.31625 | 0.25275
15 | 29.199 | 11.901 | 14.059 | 25.96 |  | 11.886 | 4.353 | 9.706 | 1.2308 | 0.49691 | 0.881 | 1.8547 | 9.3 | 9.3 | 10.3 | 490 | 491.6667 | 606.6667 | 0.3655 | 0.2955 | 0.26075
16 | 31.386 | 11.472 | 16.005 | 27.477 |  | 11.459 | 4.854 | 11.151 | 1.0589 | 0.8615 | 1.19 | 1.8547 | 9.55 | 9.55 | 10.55 | 462.5 | 470 | 575 | 0.33725 | 0.2445 | 0.3335
17 | 31.096 | 12.463 | 15.525 | 27.988 |  | 12.455 | 4.442 | 11.083 | 1.3481 | 0.35522 | 0.526 | 1.6243 | 9.9667 | 9.9667 | 10.9667 | 450 | 460 | 556.6667 | 0.4225 | 0.329 | 0.396
18 | 29.153 | 11.216 | 15.169 | 26.385 |  | 11.211 | 4.468 | 10.701 | 1.1262 | 0.51513 | 0.854 | 1.7294 | 9.6333 | 9.6333 | 10.6333 | 470 | 453.3333 | 546.6667 | 0.3745 | 0.311 | 0.395
19 | 31.493 | 12.123 | 16.543 | 28.666 | 2.294 | 9.829 | 4.787 | 11.756 | 1.3773 | 0.51254 | 0.846 | 1.8792 | 10 | 10 | 11 | 490 | 491.25 | 525 | 0.4165 | 0.376 | 0.34925
20 | 30.66 | 11.57 | 15.918 | 27.488 | 5.803 | 5.767 | 5.505 | 10.413 | 1.232 | 0.5323 | 0.83 | 1.8648 | 10 | 10 | 11 | 563.75 | 590 | 525 | 0.40325 | 0.33775 | 0.36875
21 | 34.381 | 14.144 | 16.71 | 30.854 | 7.034 | 7.11 | 5.178 | 11.532 | 1.2657 | 0.87349 | 0.953 | 1.9512 | 10.52 | 10.52 | 11.52 | 599.5 | 637 | 553.9 | 0.54475 | 0.393 | 0.5515
22 | 31.693 | 12.822 | 14.839 | 27.661 | 6.498 | 6.324 | 4.049 | 10.79 | 1.4644 | 0.70264 | 1.102 | 2.3315 | 10.3 | 10.3 | 11.3 | 722.5 | 668.75 | 697.5 | 0.62975 | 0.407 | 0.63025
23 | 30.618 | 12.027 | 14.577 | 26.604 | 6.161 | 5.866 | 4.307 | 10.27 | 1.4217 | 1.398 | 1.061 | 2.3109 | 10.175 | 10.175 | 11.175 | 876.25 | 763.75 | 795 | 0.61975 | 0.5425 | 0.5695
24 | 32.732 | 12.845 | 16.057 | 28.902 | 6.46 | 6.385 | 4.644 | 11.413 | 1.0234 | 0.70473 | 1.088 | 2.8414 | 10.7 | 10.7 | 11.7 | 946.6667 | 840 | 916.6667 | 0.5235 | 0.5055 | 0.6635
25 | 32.289 | 12.866 | 15.75 | 28.616 | 6.539 | 6.327 | 4.605 | 11.145 | 1.887 | 1.0657 | 1.182 | 2.4725 | 10.075 | 10.1 | 11.175 | 911.25 | 842.5 | 1003.875 | 0.50225 | 0.5145 | 0.541
26 | 31.833 | 12.29 | 16.02 | 28.31 | 5.974 | 6.316 | 5.009 | 11.011 | 1.4541 | 0.80631 | 1.005 | 2.4903 | 10.26 | 7.6 | 13.6 | 999.6 | 930.2 | 1120.7 | 0.48825 | 0.49875 | 0.6015
27 | 35.89 | 12.999 | 17.383 | 30.382 | 6.279 | 6.72 | 5.423 | 11.96 | 1.553 | 1.4568 | 1.514 | 2.4925 | 11.7571 | 11.7571 | 12.7857 | 1250.8571 | 1218.5 | 1498.1429 | 0.537 | 0.5115 | 0.6
28 | 29.571 | 11.536 | 15.24 | 26.776 | 3.527 | 8.009 | 4.191 | 11.049 | 1.2869 | 1.2219 | 1.083 | 3.0201 | 10.36 | 10.36 | 11.36 | 1317 | 1351 | 1372.4 | 0.27525 | 0.22025 | 0.36175
29 | 33.423 | 12.551 | 16.71 | 29.261 |  | 12.541 | 4.333 | 12.377 | 1.1798 | 0.88597 | 1.128 | 2.2604 | 10.325 | 10.325 | 11.325 | 1302.5 | 1363.75 | 1236.25 | 0.28075 | 0.28975 | 0.34875
30 | 33.203 | 11.408 | 17.734 | 29.142 |  | 11.403 | 4.072 | 13.662 | 1.3379 | 1.248 | 1.058 | 2.4651 | 11 | 11 | 12 | 1295 | 1345 | 1162.5 | 0.37125 | 0.34275 | 0.35075
31 | [11 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Total | 948.175 | 384.154 | 462.009 | 846.163 | 56.569 | 327.414 | 138.847 | 323.162 | 39.8707 | 21.7577 | 33.634 |  | 306.4088 | 303.7738 | 338.8774 | #DIV/0! | #DIV/0! | #DIV/0! | 12.8848 | 11.347 | 11.9213
Average | 31.6058 | 12.8051 | 15.4003 | 28.2054 | 5.6569 | 10.9138 | 4.6282 | 10.7721 | 1.329 | 0.75026 | 1.1211 |  | 10.2136 | 10.1258 | 11.2959 | #DIV/0! | #DIV/0! | #DIV/0! | 0.42949 | 0.37823 | 0.39738
Maximum | 35.89 | 14.727 | 17.734 | 30.854 | 7.034 | 14.727 | 5.509 | 13.662 | 1.887 | 1.4568 | 2.182 |  | 11.7571 | 11.7571 | 13.6 | #DIV/0! | #DIV/0! | #DIV/0! | 0.6565 | 0.58825 | 0.6635
Minimum | 27.548 | 10.764 | 13.162 | 23.926 | 2.294 | 5.767 | 4.03 | 8.793 | 0.96539 | 0.16928 | 0.526 |  | 9.1667 | 7.6 | 10.1667 | #DIV/0! | #DIV/0! | #DIV/0! | 0.27525 | 0.22025 | 0.236
Finished Water Pumped (from South + Conway+ Perry Meters) | [7 empty] | 845.992
Finished Water Pumped (Raw Flow - Blowdown + Backwash) | [7 empty] | 886.5467
Finished Water Pumped (Raw Flow -Decant + Sludge) | [7 empty] | 910.541
Total Decant Flow |  |  | 33.634 |  |  | MG
Total Sudge Pumped (est) |  |  | 4
Total Blowdown Flow |  |  | 39.8707
Total Backwash Flow |  |  | 21.7577
Total Waste Flow from Decant and Sludge | [7 empty] | 37.634
Total Waste Flow from Blowdown and Backwash | [7 empty] | 61.6283

## Flows
Surface Water System Monthly Operation Report
Water Production Log
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  | 2018-11-01
Plant Name: Bull Creek SWTP |  |  | Plant Id #: | A26001 |  | Capacity (MGD): 45
| Number and Grade of Operator in Charge |  | Hours in Operation | Water Pumped (MG) |  |  |  | Peak Hourly Flow Rate (MGD)
Day | 1st Shift | 2nd Shift |  | Raw | Finished1 | Finished2 | Combined
1 | 4 | 20 | 24 | 32.598 | 13.822 | 14.938 | 28.76 | 33.1
2 | 4 | 20 | 24 | 31.179 | 14.026 | 14.108 | 28.134 | 33.1
3 | 4 | 20 | 24 | 30.054 | 13.805 | 13.676 | 27.481 | 30.1
4 | 4 | 20 | 24 | 31.693 | 14.083 | 14.519 | 28.602 | 35.2
5 | 4 | 20 | 24 | 34.632 | 14.727 | 15.766 | 30.493 | 37
6 | 4 | 20 | 24 | 31.46 | 13.19 | 14.847 | 28.037 | 31.9
7 | 17 | 18 | 24 | 27.548 | 10.764 | 13.162 | 23.926 | 31.9
8 | 17 | 18 | 24 | 27.924 | 13.266 | 14.026 | 27.292 | 31
9 | 17 | 18 | 24 | 33.593 | 14.245 | 15.444 | 29.689 | 34
10 | 17 | 18 | 24 | 31.877 | 13.589 | 15.219 | 28.808 | 34
11 | 17 | 18 | 24 | 33.059 | 13.748 | 14.35 | 28.098 | 32.5
12 | 17 | 18 | 24 | 31.922 | 13.501 | 15.104 | 28.605 | 32
13 | 17 | 18 | 24 | 31.256 | 11.452 | 16.554 | 28.006 | 31.9
14 | 20 | 4 | 24 | 30.76 | 13.703 | 16.057 | 29.76 | 31
15 | 20 | 4 | 24 | 29.199 | 11.901 | 14.059 | 25.96 | 29.4
16 | 16 | 4 | 24 | 31.386 | 11.472 | 16.005 | 27.477 | 31.9
17 | 20 | 4 | 24 | 31.096 | 12.463 | 15.525 | 27.988 | 31.9
18 | 20 | 4 | 24 | 29.153 | 11.216 | 15.169 | 26.385 | 31.9
19 | 20 | 4 | 24 | 31.493 | 12.123 | 16.543 | 28.666 | 31.9
20 | 20 | 4 | 24 | 30.66 | 11.57 | 15.918 | 27.488 | 31.9
21 | 18 | 17 | 24 | 34.381 | 14.144 | 16.71 | 30.854 | 34.6
22 | 18 | 17 | 24 | 31.693 | 12.822 | 14.839 | 27.661 | 32.8
23 | 18 | 17 | 24 | 30.618 | 12.027 | 14.577 | 26.604 | 33.1
24 | 18 | 17 | 24 | 32.732 | 12.845 | 16.057 | 28.902 | 33.1
25 | 18 | 17 | 24 | 32.289 | 12.866 | 15.75 | 28.616 | 33.1
26 | 18 | 17 | 24 | 31.833 | 12.29 | 16.02 | 28.31 | 33.7
27 | 18 | 17 | 24 | 35.89 | 12.999 | 17.383 | 30.382 | 37
28 | 4 | 20 | 24 | 29.571 | 11.536 | 15.24 | 26.776 | 34
29 | 4 | 20 | 24 | 33.423 | 12.551 | 16.71 | 29.261 | 34
30 | 4 | 20 | 24 | 33.203 | 11.408 | 17.734 | 29.142 | 34
31
Total |  |  | 720 | 948.175 | 384.154 | 462.009 | 846.163 | 987
Average |  |  | 24 | 31.6058 | 12.8051 | 15.4003 | 28.2054 | 32.9
Maximum |  |  | 24 | 35.89 | 14.727 | 17.734 | 30.854 | 37
Minimum |  |  | 24 | 27.548 | 10.764 | 13.162 | 23.926 | 29.4
| #3-Lederman A #21-Nobles D | #4-Hughes B #5-Nicolosi B | #12-Eaddy A #20 Brookover A | #14-Wall A #16-Eaton A | #17-Holden B #18-Mercer A
Prepared by: ___________________________________________ |  |  |  |  | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## Raw & Coagulated
Surface Water System Monthly Operation Report
Chemical & Physical Analyses of
Raw, Coagulated, & Settled Water
Bureau of Water
System Name: Grand Strand Regional | [6 empty] | System Number: 2620004
Certified Lab ID#: 26102 | [6 empty] | 2018-11-01
| Raw Water | [6 empty] | Coagulated Water |  | Settled Water
Day | pH | Alkalinity (mg/L) | Temp (oC) | Hardness (mg/L) | Turbidity (NTU) | True Color (CU) | Apparent Color (CU) | pH | Alkalinity (mg/L) | Turbidity (NTU) | Disinfectant Residual (mg/L)
1 | 6.4967 | 18.3333 | 18.7833 | 17.3333 | 14.9 | 125.6667 | 209.5 | 6.0511 | 12.5556 | 0.44 | 0.47
2 | 6.4667 | 20.5 | 19.2 | 18.5 | 14.6 | 121.5 | 200.1667 | 6.0428 | 11.1667 | 0.396 | 0.6
3 | 6.43 | 20.6667 | 19.1333 | 18.3333 | 14.1 | 112.8333 | 192.6667 | 6.0272 | 11 | 0.405 | 0.53
4 | 6.4667 | 18.8683 | 18.6333 | 18.8333 | 13.8 | 104.8333 | 186.6667 | 6.0056 | 10.7222 | 0.393 | 0.53
5 | 6.435 | 20.1667 | 18.9333 | 18 | 13.7 | 113.8333 | 181 | 5.9706 | 10.7778 | 0.373 | 0.47
6 | 6.4333 | 20 | 19.65 | 16.8333 | 12.8 | 117.5 | 171.5 | 5.9628 | 11.1667 | 0.385 | 0.46
7 | 6.405 | 17.6667 | 19.75 | 16 | 11.1 | 121.5 | 171.8333 | 5.8911 | 9.3889 | 0.433 | 0.52
8 | 6.4333 | 16.1667 | 19.7 | 15.8333 | 10.4 | 119.1667 | 169.8333 | 6.03 | 9.4444 | 0.531 | 0.53
9 | 6.44 | 16.3333 | 19.6333 | 15.8333 | 11.7 | 111 | 174.1667 | 6.0361 | 9.7778 | 0.567 | 0.53
10 | 6.425 | 16.8333 | 19.6667 | 16.1667 | 11.7 | 113.3333 | 173.5 | 6.0683 | 10.7222 | 0.804 | 0.45
11 | 6.4217 | 17.5 | 18.6167 | 16.3333 | 10.8 | 118 | 173.6667 | 6.0506 | 10.3889 | 0.636 | 0.51
12 | 6.4167 | 17.8333 | 17.8167 | 16.8333 | 10.6 | 114 | 171.8333 | 6.0758 | 10.5556 | 0.587 | 0.45
13 | 6.4533 | 17.5 | 17.7167 | 17.3333 | 10.5 | 107.8333 | 160 | 6.0406 | 11 | 0.427 | 0.46
14 | 6.3783 | 16.3333 | 17.3333 | 16.1667 | 18 | 110.1667 | 162.3333 | 6.0539 | 9.6667 | 0.43 | 0.48
15 | 6.5333 | 18.8333 | 16.65 | 17.1667 | 9.85 | 105.8333 | 157.6667 | 6.0856 | 10.0556 | 0.395 | 0.45
16 | 6.5433 | 18.5 | 16.3833 | 19 | 14.2 | 108.5 | 174.6667 | 6.0106 | 10.0556 | 0.364 | 0.49
17 | 6.5333 | 20 | 15.9 | 18.6667 | 16.1 | 111.5 | 202 | 6.03 | 10.8333 | 0.468 | 0.47
18 | 6.4833 | 18.5 | 15.6333 | 18.5 | 16.1 | 115.6667 | 201.3333 | 6.02 | 9.2778 | 0.47 | 0.55
19 | 6.4567 | 17.8333 | 15.6667 | 18.5 | 15.6 | 116.3333 | 198.8333 | 6.0122 | 9.6111 | 0.491 | 0.55
20 | 6.425 | 17.6667 | 15.6667 | 17 | 15.5 | 121.1667 | 200.5 | 5.955 | 9.3333 | 0.499 | 0.46
21 | 6.4 | 15.6667 | 15.0833 | 15.3333 | 14 | 131.3333 | 205.5 | 6.0239 | 9.2778 | 0.721 | 0.55
22 | 6.43 | 13.3333 | 14.8 | 13.5 | 12.9 | 126.6667 | 196.6667 | 6.075 | 9.2778 | 0.782 | 0.57
23 | 6.32 | 12.5 | 14.3 | 12.3333 | 13.1 | 125.8333 | 195 | 5.9694 | 7.9444 | 0.741 | 0.61
24 | 6.3517 | 11.5 | 14.45 | 12.8333 | 12.7 | 120 | 182.8333 | 5.9889 | 8.2778 | 0.748 | 0.71
25 | 6.2983 | 11.6667 | 14.4833 | 13.5 | 10.8 | 125.1667 | 179.6667 | 5.9861 | 7.8889 | 0.608 | 0.5
26 | 6.2 | 10.8333 | 14.5833 | 12.3333 | 9.98 | 126 | 179.3333 | 6.0028 | 7.6111 | 0.636 | 0.59
27 | 6.2683 | 10.3333 | 14.1667 | 13.1667 | 9.97 | 126.5 | 177 | 6.1011 | 8.3889 | 0.694 | 0.68
28 | 6.255 | 12 | 14.1167 | 15.8333 | 9.32 | 127.6667 | 173 | 6.1733 | 9.3333 | 0.616 | 0.68
29 | 6.29 | 12.6667 | 13.5 | 16.8333 | 8.45 | 131.1667 | 173.6667 | 6.1494 | 9 | 0.462 | 0.62
30 | 6.3067 | 12 | 13.35 | 18.5 | 9.05 | 131.8333 | 176.5 | 6.1406 | 9.3333 | 0.435 | 0.68
31
Avg. | 6.4066 | 16.2845 | 16.7767 | 16.3778 | 12.544 | 118.7444 | 182.4278 | 6.0343 | 9.7944 | 0.53123 | 0.53833
Max. | 6.5433 | 20.6667 | 19.75 | 19 | 18 | 131.8333 | 209.5 | 6.1733 | 12.5556 | 0.804 | 0.71
Min. | 6.2 | 10.3333 | 13.35 | 12.3333 | 8.45 | 104.8333 | 157.6667 | 5.8911 | 7.6111 | 0.364 | 0.45
Prepared by: ____________________________________________ | [7 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## Finished
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2018-11-01
Finished Water 1
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.14 | 22.5 | 17.9 | 4 |  |  | 29 | 0.064 | 1 | 0.4766
2 | 7.175 | 24 | 18.2333 | 4.2 |  |  | 33.5 | 0.058 | 1.1667 | 0.5051
3 | 7.2083 | 20.5 | 18.3 | 4.1 |  |  | 34.5 | 0.057 | 1 | 0.483
4 | 7.2267 | 21.5 | 18.0667 | 4 |  |  | 35 | 0.068 | 1 | 0.482
5 | 7.1283 | 23 | 18.2167 | 4.1 |  |  | 43.5 | 0.058 | 1.6667 | 0.5375
6 | 7.295 | 25 | 18.8 | 3.9 |  |  | 41 | 0.055 | 1.1667 | 0.5392
7 | 7.185 | 20 | 18.8833 | 3.7 |  |  | 36 | 0.069 | 1 | 0.5272
8 | 7.3417 | 21 | 18.7667 | 3.9 |  |  | 39.5 | 0.073 | 1 | 0.4964
9 | 7.435 | 21 | 18.7833 | 4.1 |  |  | 35 | 0.073 | 1.3333 | 0.5031
10 | 7.9467 | 23 | 18.8833 | 4.1 |  |  | 33.5 | 0.083 | 1 | 0.5187
11 | 7.3233 | 21 | 17.75 | 4.3 |  |  | 36 | 0.08 | 1.1667 | 0.498
12 | 7.2717 | 28.5 | 17.2 | 4.4 | 0.31 | 0.01 | 29.5 | 0.073 | 1 | 0.502
13 | 7.3533 | 21 | 16.8 | 4.3 |  |  | 38 | 0.072 | 1.3333 | 0.4879
14 | 7.1983 | 20 | 16.55 | 4.2 |  |  | 40.5 | 0.073 | 1.6667 | 0.4626
15 | 7.3917 | 20.5 | 15.9333 | 4.2 |  |  | 40 | 0.07 | 2 | 0.498
16 | 7.32 | 20.5 | 15.5167 | 4.1 |  |  | 37 | 0.065 | 1.1667 | 0.4432
17 | 7.1933 | 21 | 14.7833 | 4.3 |  |  | 39 | 0.06 | 1.3333 | 0.4042
18 | 7.265 | 20 | 14.5167 | 3.9 |  |  | 38.5 | 0.06 | 1.5 | 0.5316
19 | 7.275 | 21 | 14.3333 | 4 |  |  | 40 | 0.071 | 2 | 0.498
20 | 7.4217 | 20.5 | 14.4333 | 4.1 |  |  | 41 | 0.082 | 1.3333 | 0.523
21 | 7.6567 | 22.5 | 14.1333 | 4 |  |  | 51 | 0.076 | 1.8333 | 0.5102
22 | 7.4917 | 21 | 13.7 | 4 |  |  | 43 | 0.069 | 1.6667 | 0.5455
23 | 7.415 | 21 | 13.3667 | 4.2 |  |  | 38.5 | 0.063 | 1.6667 | 0.4899
24 | 7.55 | 20.5 | 13.2833 | 3.9 |  |  | 34 | 0.066 | 1.3333 | 0.4919
25 | 7.6983 | 20 | 13.3167 | 3.8 |  |  | 35 | 0.069 | 1 | 0.4683
26 | 7.68 | 20.5 | 13.6333 | 4 | 0.35 | 0.01 | 39.5 | 0.072 | 1 | 0.5274
27 | 7.985 | 20.5 | 13.5667 | 3.9 |  |  | 35 | 0.07 | 1.5 | 0.5496
28 | 7.3933 | 20 | 12.7333 | 4.2 |  |  | 54 | 0.055 | 1 | 0.5324
29 | 7.315 | 21 | 12.1167 | 3.8 |  |  | 56.5 | 0.054 | 1.1667 | 0.5207
30 | 7.395 | 18.5 | 12.05 | 3.7 |  |  | 56.5 | 0.06 | 1 | 0.5229
31
Avg. | 7.3892 | 21.3667 | 15.8183 | 4.0467 | 0.33 | 0.01 | 39.4333 | 0.067267 | 1.3 | 0.50254
Max. | 7.985 | 28.5 | 18.8833 | 4.4 | 0.35 | 0.01 | 56.5 | 0.083 | 2 | 0.5496
Min. | 7.1283 | 18.5 | 12.05 | 3.7 | 0.31 | 0.01 | 29 | 0.054 | 1 | 0.4042
Notes: | Phosphate reported as P
Prepared by: ____________________________________________ | [6 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## Finished2
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2018-11-01
Finished Water 2
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.225 | 22 | 20.9 | 3.7 |  |  | 36.5 | 0.07 | 1.3333 | 0.4864
2 | 7.2217 | 24.5 | 20.8833 | 3.6 |  |  | 34 | 0.057 | 1.3333 | 0.4694
3 | 7.2533 | 22.5 | 20.3333 | 3.5 |  |  | 35.5 | 0.06 | 1 | 0.4771
4 | 7.2417 | 21.5 | 20.3667 | 3.6 |  |  | 31.5 | 0.066 | 1 | 0.4761
5 | 7.4167 | 27.5 | 20.4 | 3.6 |  |  | 39.5 | 0.067 | 1.6667 | 0.666
6 | 7.3683 | 25.5 | 20.9667 | 3.4 |  |  | 47.5 | 0.06 | 1.1667 | 0.4924
7 | 7.225 | 21 | 20.1667 | 3.7 |  |  | 37.5 | 0.07 | 1 | 0.5082
8 | 7.385 | 21 | 20.15 | 3.8 |  |  | 40 | 0.076 | 1 | 0.4601
9 | 7.405 | 21.5 | 19.8167 | 3.7 |  |  | 36 | 0.072 | 1.3333 | 0.4362
10 | 7.915 | 23 | 19.9 | 3.7 |  |  | 34 | 0.09 | 1 | 0.4514
11 | 7.2883 | 21 | 18.9833 | 4 |  |  | 36 | 0.083 | 1 | 0.4126
12 | 7.3333 | 20.5 | 18.4833 | 4.2 | 0.35 | 0.01 | 38 | 0.09 | 1 | 0.4683
13 | 7.3517 | 21.5 | 18.6667 | 4.1 |  |  | 39 | 0.081 | 1.3333 | 0.4459
14 | 7.29 | 21.5 | 18.1833 | 3.5 |  |  | 40.5 | 0.076 | 1.6667 | 0.4607
15 | 7.5383 | 20 | 17.8833 | 4 |  |  | 39 | 0.064 | 1.8333 | 0.4839
16 | 7.35 | 21 | 17.95 | 3.9 |  |  | 36.5 | 0.058 | 1 | 0.478
17 | 7.2133 | 21 | 17.5333 | 4 |  |  | 40 | 0.063 | 1.3333 | 0.4245
18 | 7.2517 | 20.5 | 17.1667 | 3.5 |  |  | 35 | 0.057 | 1.5 | 0.5166
19 | 7.2983 | 21 | 17.1333 | 3.8 |  |  | 41 | 0.064 | 2 | 0.502
20 | 7.4367 | 21 | 17.4167 | 4 |  |  | 43.5 | 0.071 | 1.3333 | 0.5365
21 | 7.5917 | 23 | 16.8167 | 4 |  |  | 51.5 | 0.083 | 1.6667 | 0.5082
22 | 7.4967 | 21.5 | 16.1833 | 3.9 |  |  | 43.5 | 0.069 | 1.5 | 0.501
23 | 7.4967 | 22 | 15.65 | 3.9 |  |  | 39.5 | 0.069 | 1.5 | 0.4899
24 | 7.6467 | 21 | 15.95 | 4 |  |  | 37 | 0.063 | 1.3333 | 0.1886
25 | 7.9567 | 20 | 16.0833 | 3.6 |  |  | 36 | 0.069 | 1.1667 | 0.1568
26 | 7.5317 | 21 | 15.7833 | 3.9 | 0.35 | 0.009 | 36 | 0.074 | 1 | 0.2249
27 | 7.7867 | 20.5 | 15.2 | 4.1 |  |  | 35.5 | 0.07 | 1.8333 | 0.4544
28 | 7.295 | 20.5 | 15.1833 | 4.2 |  |  | 56.5 | 0.059 | 1.1667 | 0.5062
29 | 7.2717 | 20.5 | 15.0167 | 4.1 |  |  | 52.5 | 0.054 | 1.1667 | 0.502
30 | 7.35 | 18.5 | 14.45 | 4.2 |  |  | 58.5 | 0.06 | 1.3333 | 0.1556
31
Avg. | 7.4144 | 21.5833 | 17.9867 | 3.84 | 0.35 | 0.0095 | 40.2333 | 0.068833 | 1.3167 | 0.44466
Max. | 7.9567 | 27.5 | 20.9667 | 4.2 | 0.35 | 0.01 | 58.5 | 0.09 | 2 | 0.666
Min. | 7.2133 | 18.5 | 14.45 | 3.4 | 0.35 | 0.009 | 31.5 | 0.054 | 1 | 0.1556
Notes: | Phosphate reported as P
Prepared by: ____________________________________________ | [6 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## Chems lbs
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2018-11-01
Pounds or Gallons of Chemicals Used
Day | Pre Disinf (gal) | Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | Post Disenfectant (gal) (gal) |  | Post-pH (gal) | Fluoride (gal) | Phosphate (gal) | Zinc (gal) | Filter Aid (gal) | Polymer (gal) | Pre-pH (gal) | PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 446.7274 | 5030.2666 |  | 2502.783 | 789.0296 | 120.0979 | 224.6442 | 63.9874 | 54.0264 | 7.7338 | 2.8613 | 13.8033 | 531.84 | 888.1057
2 | 442.8104 | 4467.4026 |  | 2526.3941 | 771.1845 | 113.5711 | 230.3035 | 62.7441 | 53.0882 | 7.6035 | 2.5907 | 12.6679 | 388.6307 | 864.3172
3 | 442.4904 | 4072.0943 |  | 2502.783 | 751.8288 | 109.3179 | 238.8807 | 63.5029 | 51.8571 | 7.4411 | 2.4038 | 11.9266 | 251.52 | 840.5286
4 | 450.1492 | 4149.5529 |  | 2372.9716 | 783.8841 | 115.1736 | 255.8043 | 63.5232 | 53.7571 | 7.6224 | 2.5316 | 10.9721 | 210.1383 | 840.5286
5 | 487.8691 | 4579.2014 |  | 2833.3805 | 831.2929 | 122.5405 | 303.3022 | 67.3241 | 57.3831 | 8.0971 | 2.8278 | 11.8759 | 209.9362 | 840.5286
6 | 457.1712 | 4156.0727 |  | 2896.2399 | 752.8934 | 112.046 | 310.2171 | 61.3423 | 53.4711 | 7.249 | 2.5521 | 10.1423 | 193.4576 | 840.6858
7 | 394.954 | 3553.4208 |  | 3211.1178 | 652.2547 | 89.8756 | 256.6994 | 52.0057 | 45.3502 | 6.083 | 2.6144 | 8.7494 | 186.2686 | 840.5286
8 | 412.5964 | 3406.0855 |  | 3553.4797 | 756.5905 | 101.3038 | 288.1272 | 59.7443 | 51.8976 | 6.9785 | 2.7197 | 10.3156 | 226.0859 | 896.0352
9 | 483.1279 | 3994.2904 |  | 3765.9801 | 848.7617 | 104.8306 | 313.7135 | 65.0152 | 55.432 | 7.7493 | 2.8605 | 10.7556 | 300.3819 | 964.2291
10 | 467.6846 | 3977.9152 |  | 3097.7842 | 742.8332 | 101.2844 | 255.8349 | 57.2912 | 48.7221 | 6.8438 | 2.8089 | 10.4484 | 321.0356 | 880.4934
11 | 485.7828 | 4142.9988 |  | 2707.413 | 768.3217 | 110.4218 | 243.2139 | 62.236 | 52.6783 | 7.3085 | 2.6846 | 10.2992 | 146.3739 | 888.1057
12 | 441.3294 | 3994.6579 |  | 2880.5616 | 795.7429 | 108.949 | 254.4212 | 81.7722 | 53.4503 | 5.1325 | 2.6878 | 10.4752 | 136.4717 | 866.9604
13 | 427.7847 | 3935.6077 |  | 2986.8118 | 791.6458 | 102.2305 | 273.7407 | 80.257 | 52.4417 | 5.1177 | 2.4145 | 9.8291 | 106.4774 | 729.5154
14 | 403.9961 | 3888.4112 |  | 2801.7264 | 840.6305 | 119.5769 | 297.737 | 86.9506 | 56.4896 | 5.595 | 2.366 | 9.8511 |  | 772.2026
15 | 368.2396 | 3652.0999 |  | 2746.765 | 727.5732 | 108.0126 | 274.7949 | 76.1935 | 48.3897 | 5.0834 | 2.4795 | 7.9561 |  | 808.8106
16 | 378.4828 | 3913.4099 |  | 2750.7002 | 760.8296 | 111.5908 | 278.5431 | 78.3207 | 50.5768 | 5.0145 | 2.4523 | 7.8121 |  | 808.8106
17 | 363.3926 | 3873.3595 |  | 3163.8955 | 754.0112 | 110.1206 | 258.9305 | 80.1567 | 51.5222 | 4.9108 | 2.5489 | 7.4197 |  | 808.8106
18 | 360.4763 | 3619.265 |  | 2927.7839 | 711.6228 | 102.5248 | 251.9987 | 76.8739 | 50.1962 | 4.9959 | 2.5521 | 7.2456 |  | 808.8106
19 | 372.7707 | 3922.6205 |  | 3063.5182 | 775.4583 | 114.2848 | 281.3408 | 83.0608 | 54.633 | 5.4122 | 2.6523 | 7.8013 |  | 808.8106
20 | 360.4217 | 3851.8959 |  | 3258.3199 | 743.5758 | 110.6614 | 271.0863 | 79.0296 | 52.3745 | 5.1898 | 2.6582 | 8.3568 |  | 808.8106
21 | 400.3321 | 4671.6306 |  | 3579.4519 | 805.3315 | 114.0952 | 287.7803 | 87.8524 | 57.908 | 5.9265 | 2.7843 | 9.5209 | 91.4844 | 808.8106
22 | 375.8967 | 4933.303 |  | 3128.4788 | 724.8316 | 96.7255 | 252.3156 | 79.3098 | 51.9658 | 5.0681 | 2.7717 | 10.1635 | 436.5153 | 808.8106
23 | 368.4919 | 4845.5169 |  | 2939.5895 | 696.6249 | 92.8338 | 223.7325 | 76.38 | 50.1928 | 4.8507 | 2.696 | 11.5174 | 594.7837 | 808.8106
24 | 391.1261 | 5176.2781 |  | 2864.8208 | 757.3083 | 101.0044 | 231.5978 | 83.2049 | 55.3567 | 5.4138 | 2.8045 | 13.2135 | 777.856 | 808.8106
25 | 380.4541 | 4863.2939 |  | 2609.0332 | 757.0739 | 101.0677 | 218.2232 | 90.125 | 53.641 | 5.3732 | 2.6807 | 14.0267 | 744.5446 | 808.8106
26 | 550.6109 | 5226.3661 |  | 2890.3113 | 737.5202 | 93.5513 | 190.7024 | 73.53 | 52.931 | 5.3137 | 2.7171 | 13.5897 | 865.1256 | 805.0044
27 | 404.3043 | 6473.3691 |  | 3440.4834 | 799.4391 | 110.7247 | 187.9202 | 94.8546 | 57.1779 | 5.6628 | 3.0839 | 18.546 | 988.0196 | 808.8106
28 | 347.7151 | 5353.2563 |  | 3494.4518 | 710.9705 | 96.9799 | 108.6273 | 77.7897 | 50.7588 | 5.1487 | 2.7635 | 18.875 | 661.412 | 818.326
29 | 395.633 | 5582.7165 |  | 3394.0841 | 777.4136 | 111.3325 | 128.0272 | 83.7422 | 55.3783 | 5.452 | 2.7434 | 20.0678 | 437.6484 | 816.7401
30 | 390.3769 | 5786.9465 |  | 3523.9657 | 763.6151 | 109.655 | 138.1556 | 84.7243 | 55.1365 | 5.3097 | 2.9433 | 18.2951 | 520.32 | 834.185
31
Tot | 12453.1983 | 133093.3056 |  | 90415.0799 | 22880.0937 | 3216.3847 | 7330.4161 | 2232.8445 | 1588.184 | 180.6808 | 80.2553 | 346.5188 | 9326.3273 | 24932.7474
Avg | 415.1066 | 4436.4435 |  | 3013.836 | 762.6698 | 107.2128 | 244.3472 | 74.4282 | 52.9395 | 6.0227 | 2.6752 | 11.5506 | 405.4925 | 831.0916
Max | 550.6109 | 6473.3691 |  | 3765.9801 | 848.7617 | 122.5405 | 313.7135 | 94.8546 | 57.908 | 8.0971 | 3.0839 | 20.0678 | 988.0196 | 964.2291
Min | 347.7151 | 3406.0855 |  | 2372.9716 | 652.2547 | 89.8756 | 108.6273 | 52.0057 | 45.3502 | 4.8507 | 2.366 | 7.2456 | 91.4844 | 729.5154
* Please specify the chemical compound(s) and units used. Include product name if applicable
Pre-ph=Liquid Lime |  |  |  | Pre & Post Disinfectant= Sodium Hypochlorite | [5 empty] | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC | [5 empty] | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Polytec 1114 PWG | [5 empty] | Coagulant= Aluminum Sulfate
PAC= WaterCarb CW |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## Chem Dose
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2018-11-01
Chemical dosage mg/l
Day | Pre Disinf (gal) | * Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | * Post Disenfectant (gal) (gal) |  | * Post-pH (gal) | * Fluoride (gal) | * Phosphate (gal) | * Zinc (gal) | Filter Aid | * Polymer (gal) | Pre-pH | * PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 1.8075 | 99.2276 |  | 23.0147 | 4.0133 | 0.75571 | 5.8996 | 0.50189 | 1.0992 | 0.10118 | 0.050191 | 0.48973 | 12.2203 | 3.2667
2 | 1.8732 | 92.1351 |  | 24.2892 | 4.0098 | 0.73054 | 6.2173 | 0.50309 | 1.1041 | 0.10169 | 0.050861 | 0.45945 | 9.3501 | 3.3239
3 | 1.9419 | 87.126 |  | 24.9629 | 4.002 | 0.71989 | 6.6099 | 0.52127 | 1.1042 | 0.10188 | 0.1 | 0.44284 | 6.3493 | 3.3534
4 | 1.8734 | 84.1919 |  | 22.4441 | 4.0091 | 0.72873 | 6.7791 | 0.501 | 1.0997 | 0.10027 | 0.1 | 0.39143 | 5.0157 | 3.18
5 | 1.858 | 85.0246 |  | 24.5246 | 3.9879 | 0.72726 | 7.5141 | 0.49805 | 1.1011 | 0.099914 | 0.1 | 0.3974 | 4.5531 | 2.9101
6 | 1.9167 | 84.9487 |  | 27.5962 | 3.9282 | 0.72323 | 8.3245 | 0.49355 | 1.1159 | 0.097285 | 0.1 | 0.36912 | 4.6056 | 3.2041
7 | 1.891 | 82.9448 |  | 34.9414 | 3.9879 | 0.6798 | 7.9996 | 0.49032 | 1.1091 | 0.095662 | 0.050786 | 0.37314 | 4.5302 | 3.6584
8 | 1.9488 | 78.4351 |  | 38.1461 | 4.0553 | 0.67174 | 7.9808 | 0.49381 | 1.1127 | 0.096211 | 0.051648 | 0.38568 | 5.6245 | 3.8475
9 | 1.8969 | 76.4581 |  | 33.6049 | 4.182 | 0.639 | 7.9766 | 0.49399 | 1.0925 | 0.098212 | 0.050318 | 0.36966 | 6.8741 | 3.4416
10 | 1.9351 | 80.2436 |  | 29.1305 | 3.772 | 0.63627 | 6.7343 | 0.44862 | 0.98962 | 0.089388 | 0.050916 | 0.37008 | 7.4722 | 3.3119
11 | 1.9381 | 80.5856 |  | 24.5493 | 4 | 0.7112 | 6.5566 | 0.49965 | 1.097 | 0.09787 | 0.050844 | 0.37402 | 3.558 | 3.2211
12 | 1.8235 | 80.4678 |  | 27.0496 | 4.0693 | 0.68927 | 6.6976 | 0.49701 | 1.0934 | 0.09692 | 0.050844 | 0.37367 | 3.2866 | 3.2564
13 | 1.8052 | 80.9675 |  | 28.645 | 4.135 | 0.6606 | 7.1789 | 0.49823 | 1.0957 | 0.098708 | 0.050821 | 0.35812 | 2.8189 | 2.7986
14 | 1.7323 | 81.2865 |  | 27.3032 | 4.1321 | 0.72715 | 7.494 | 0.50797 | 1.1107 | 0.10155 | 0.1 | 0.33777 |  | 3.0101
15 | 1.6634 | 80.428 |  | 28.1986 | 4.0998 | 0.75297 | 7.9222 | 0.51029 | 1.0907 | 0.10577 | 0.0508 | 0.31272 |  | 3.3213
16 | 1.5905 | 80.1774 |  | 26.2713 | 4.0505 | 0.73497 | 7.4788 | 0.49557 | 1.077 | 0.098579 | 0.050641 | 0.29011 |  | 3.0899
17 | 1.5413 | 80.0969 |  | 30.4994 | 3.9409 | 0.71204 | 6.8942 | 0.49793 | 1.0772 | 0.094778 | 0.050523 | 0.27051 |  | 3.1187
18 | 1.6309 | 79.8306 |  | 30.1044 | 3.9454 | 0.7032 | 7.0742 | 0.50655 | 1.1132 | 0.10228 | 0.050523 | 0.28021 |  | 3.3266
19 | 1.5612 | 80.093 |  | 29.1595 | 3.9572 | 0.72149 | 7.2721 | 0.50377 | 1.1152 | 0.10198 | 0.050461 | 0.27769 |  | 3.0794
20 | 1.5505 | 80.7858 |  | 31.8563 | 3.9571 | 0.72856 | 7.3093 | 0.49986 | 1.1149 | 0.10198 | 0.05072 | 0.31021 |  | 3.1631
21 | 1.5358 | 87.374 |  | 31.2084 | 3.8182 | 0.66921 | 7.0021 | 0.49504 | 1.0982 | 0.10376 | 0.05074 | 0.31487 | 2.1388 | 2.8207
22 | 1.5643 | 100.0937 |  | 29.5899 | 3.8332 | 0.63282 | 6.8504 | 0.49849 | 1.0993 | 0.09897 | 0.052758 | 0.37492 | 10.4015 | 3.06
23 | 1.5874 | 101.7644 |  | 28.7795 | 3.8304 | 0.63149 | 6.3025 | 0.49915 | 1.1039 | 0.098489 | 0.050439 | 0.44175 | 14.3397 | 3.1674
24 | 1.5761 | 101.6898 |  | 26.2361 | 3.833 | 0.63244 | 6.0401 | 0.50052 | 1.1207 | 0.10118 | 0.1 | 0.4665 | 17.8827 | 2.9628
25 | 1.5541 | 96.8519 |  | 24.2214 | 3.8701 | 0.63917 | 5.7755 | 0.54757 | 1.0968 | 0.10143 | 0.051424 | 0.50016 | 18.0818 | 3.0035
26 | 2.2814 | 105.5734 |  | 27.217 | 3.8109 | 0.59803 | 5.1188 | 0.45157 | 1.094 | 0.10139 | 0.051076 | 0.48982 | 19.3517 | 3.0322
27 | 1.4858 | 115.9817 |  | 28.7356 | 3.8491 | 0.65954 | 4.6966 | 0.5428 | 1.1012 | 0.10068 | 0.050238 | 0.62287 | 20.7149 | 2.7021
28 | 1.5509 | 116.4084 |  | 35.4231 | 3.8842 | 0.65546 | 3.0868 | 0.5051 | 1.1092 | 0.10387 | 0.051522 | 0.71929 | 15.6942 | 3.3181
29 | 1.5613 | 107.407 |  | 30.4405 | 3.8865 | 0.68856 | 3.3168 | 0.49757 | 1.1074 | 0.10065 | 0.051073 | 0.6998 | 10.4145 | 2.93
30 | 1.5507 | 112.0739 |  | 31.8147 | 3.8331 | 0.68096 | 3.5669 | 0.50546 | 1.1071 | 0.098418 | 0.05093 | 0.64059 | 11.6436 | 3.0124
31
Tot | 52.0269 | 2700.673 |  | 859.9576 | 118.6835 | 20.6413 | 195.6703 | 15.0057 | 32.9509 | 2.991 | 1.8211 | 12.5041 | 216.9221 | 94.8923
Avg | 1.7342 | 90.0224 |  | 28.6653 | 3.9561 | 0.68804 | 6.5223 | 0.50019 | 1.0984 | 0.099698 | 0.060703 | 0.4168 | 9.4314 | 3.1631
Max | 2.2814 | 116.4084 |  | 38.1461 | 4.182 | 0.75571 | 8.3245 | 0.54757 | 1.1207 | 0.10577 | 0.1 | 0.71929 | 20.7149 | 3.8475
Min | 1.4858 | 76.4581 |  | 22.4441 | 3.772 | 0.59803 | 3.0868 | 0.44862 | 0.98962 | 0.089388 | 0.050191 | 0.27051 | 2.1388 | 2.7021
* Please specify the chemical compound(s) and units used. Include product name if applicable | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 23 | 30
Pre-ph = Liquid Lime |  |  |  | Pre and Post Disinfectant= Sodium Hypochlorite |  |  |  |  | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC |  |  |  |  | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Polytec 1114 PWG |  |  |  |  | Coagulant= Aluminum Sulfate
PAC= WaterCarb CW |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Supervisor

## Turbidity
Surface Water System Monthly Operation Report
Compliance with Turbidity Requirements for Filtered Systems &
Bacteriological Analysis for Raw and Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  | 2018-11-01
Lab Cert ID #: 26102 |  |  |  | Total Population: | >10,000
| Combined Filtered Water Turbidity Compliance |  |  |  | Bacteriological Analysis
Day | Maximum Filtered Water Turbidity | (A) Number of Turbidity Measurements | (B) Number of Turbidity Measurements <= 95% Limit | Number of Turbidity Measurements > Max Allowed | Raw Water |  | Finished1 Finished2
[5 empty] | Total Coliform per 100 mls | E.coli per 100 mls | Total Coliform P/A | Total Coliform P/A
1 | 0.06 | 18 | 18 | 0 | 657 | 10 | A | A
2 | 0.087 | 18 | 18 | 0 | 594 | 20 | A | A
3 | 0.043 | 18 | 18 | 0 | 586 | <10 | A | A
4 | 0.038 | 18 | 18 | 0 | 546 | 63 | A | A
5 | 0.061 | 18 | 18 | 0 | 749 | 52 | A | A
6 | 0.045 | 18 | 18 | 0 | 323 | 10 | A | A
7 | 0.047 | 18 | 18 | 0 | 309 | 20 | A | A
8 | 0.044 | 18 | 18 | 0 | 529 | 31 | A | A
9 | 0.092 | 18 | 18 | 0 | 471 | 20 | A | A
10 | 0.056 | 18 | 18 | 0 | 554 | 41 | A | A
11 | 0.045 | 18 | 18 | 0 | 364 | 10 | A | A
12 | 0.076 | 18 | 18 | 0 | 404 | 10 | A | A
13 | 0.059 | 18 | 18 | 0 | 331 | 10 | A | A
14 | 0.066 | 18 | 18 | 0 | 359 | 63 | A | A
15 | 0.05 | 18 | 18 | 0 | 504 | 10 | A | A
16 | 0.061 | 18 | 18 | 0 | 857 | 52 | A | A
17 | 0.058 | 18 | 18 | 0 | 1616 | 85 | A | A
18 | 0.052 | 18 | 18 | 0 | 1112 | 63 | A | A
19 | 0.048 | 18 | 18 | 0 | 727 | 41 | A | A
20 | 0.052 | 18 | 18 | 0 | 359 | 10 | A | A
21 | 0.083 | 18 | 18 | 0 | 253 | 10 | A | A
22 | 0.039 | 18 | 18 | 0 | 383 | 41 | A | A
23 | 0.042 | 18 | 18 | 0 | 355 | 31 | A | A
24 | 0.023 | 18 | 18 | 0 | 272 | 30 | A | A
25 | 0.041 | 18 | 18 | 0 | 318 | 10 | A | A
26 | 0.037 | 18 | 18 | 0 | 305 | 10 | A | A
27 | 0.042 | 18 | 18 | 0 | 288 | 20 | A | A
28 | 0.036 | 18 | 18 | 0 | 121 | <10 | A | A
29 | 0.051 | 18 | 18 | 0 | 97 | 10 | A | A
30 | 0.044 | 18 | 18 | 0 | 279 | <10 | A | A
31
| Total | 540 | 540 | 0
Max. Allow. Turbidity: |  | 1 NTU |  | Type of Plant: |  | Super Pulsator/Greenleaf Filters
95% Turbidity Limit: |  | 0.3 NTU |  | Max. Approved Filtration Rate: |  | 6 |  | (gpm/ft2)
The percentage of turbidity measurements |  |  |  | 100
meeting the specific limit is equal to: B/A x 100
Prepared by: ____________________________________________ |  |  |  |  | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## Indiv Filter
Surface Water System Monthly Operation Report
Turbidity Requirements for Individual Filters For Complaince With
Long Term 2 Enhanced Surface Water Treatment Rule
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  |  |  | 2018-11-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lab Cert ID #: 26102 |  |  | Population: >10,000
Turbidity Requirements |  |  |  | Individual Filters
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Was the turbidity recorded every 15 minutes for each
individual filter (while in operation) for the entire
month? | bar: Individual Filters 1 to Individual Filters 12
2 | Were 95% of the Turbidity Measurements less than
the 0.15 NTU Limit (excluding the 15 minute period
after a backwash cycle)? | bar: Individual Filters 1 to Individual Filters 12
3 | Were there any consecutive measurements greater
than 0.30 NTU? | bar: Individual Filters 1 to Individual Filters 12
Prepared by: |  |  |  | Individual Filters 5: Date:; Individual Filters 7: 2018-12-06
(signature) William Lederman Plant Superintendent

## Individual Filters
0 | Surface Water System Monthly Operation Report
Individual Filter Performance Worksheet
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  | 2018-11-01
Lab Cert ID #: 26102 |  | Total Population Served: >10,000
1. Was the turbidity recorded every 15 minutes for each individual filter |  |  |  |  | yes
(while in operation) for the entire month?
2a. Was there a failure of any of the continuous turbidity monitoring equipment during the month? |  |  |  |  | no
2b. If there was a failure, were grab samples taken from the filter effluent every 4 hours? |  |  |  |  | N.A.
2c. If there was failure of any continuous monitoring equipment, was it repaired within
5 working days? |  |  |  |  | N.A.
3a. Did any individual filter(s) have a measured effluent turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart? |  |  |  |  | no
3b. If the answer to 3a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
3c. If the answer to 3a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | N.A.
4a. Did any individual filter(s) have a measured effluent turbidity level of > 0.5 NTU in two consecutive
measurements taken 15 minutes apart, excluding the first four hours of operation after the filter
has been backwashed or otherwise taken out of service? |  |  |  |  | no
4b. If the answer to 4a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
4c. If the answer to 4a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | N.A.
5a. Did any individual filter(s) have a measured turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 3 months? |  |  |  |  | no
5b. If the answer to 5a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
5c. If the answer to 5a was "yes", have arrangements been made for a filter self-assessment to be
conducted within 14 days of the exceedance? |  |  |  |  | N.A.
6a. Did any individual filter(s) have a measured turbidity level of > 2.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 2 months? |  |  |  |  | no
6b. If the answer to 6a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
6c. If the answer to 6a was "yes", have arrangements been made to have a CPE conducted by the
Department or by a third party approved by the Department within 30 days of the exceedance? |  |  |  |  | N.A.
Prepared by: ___________________________________________ |  |  | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## MOR CT
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-11-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.47 | 11.8 | 22.8814 | 10.7542 | 6.15 | 18.5 | 10 | 1.0754
2 | 0.62 | 11.8 | 22.8814 | 14.1864 | 6.12 | 19.6 | 10 | 1.4186
3 | 0.53 | 10.7 | 25.2336 | 13.3738 | 6.15 | 19.9 | 10 | 1.3374
4 | 0.53 | 12.7 | 21.2598 | 11.2677 | 6.14 | 19.1 | 10 | 1.1268
5 | 0.48 | 11 | 23.1273 | 11.1011 | 6.02 | 18.5 | 10 | 1.1101
6 | 0.59 | 11.3 | 23.8938 | 14.0973 | 6.08 | 19.7 | 10 | 1.4097
7 | 0.56 | 10 | 25.44 | 14.2464 | 6.13 | 18.7 | 10 | 1.4246
8 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.11 | 18.8 | 10 | 1.3758
9 | 0.58 | 12 | 22.5 | 13.05 | 6.19 | 19.9 | 10 | 1.305
10 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.41 | 18.7 | 10 | 1.1115
11 | 0.51 | 9.8 | 25.9592 | 13.2392 | 6.05 | 17.3 | 10 | 1.3239
12 | 0.45 | 10.4 | 24.4615 | 11.0077 | 6.02 | 16.6 | 10 | 1.1008
13 | 0.46 | 9.3 | 27.3548 | 12.5832 | 6.11 | 16.5 | 10 | 1.2583
14 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.2 | 10 | 1.313
15 | 0.45 | 9.3 | 27.3548 | 12.3097 | 6.06 | 18.5 | 10 | 1.231
16 | 0.49 | 9.5 | 26.7789 | 13.1217 | 6.06 | 15.7 | 10 | 1.3122
17 | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.06 | 14.9 | 15 | 1.0395
18 | 0.78 | 10.3 | 24.699 | 19.2652 | 6.18 | 14.9 | 15 | 1.2843
19 | 0.56 | 10.7 | 25.2336 | 14.1308 | 6.12 | 15.4 | 10 | 1.4131
20 | 0.59 | 9.7 | 26.2268 | 15.4738 | 5.99 | 14.6 | 13 | 1.1903
21 | 0.69 | 10.5 | 24.2286 | 16.7177 | 6.14 | 13.8 | 15 | 1.1145
22 | 0.64 | 10 | 25.44 | 16.2816 | 6.16 | 14.5 | 15 | 1.0854
23 | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 13.1 | 15 | 1.0346
24 | 0.78 | 11 | 23.1273 | 18.0393 | 6.03 | 14 | 15 | 1.2026
25 | 0.5 | 11.7 | 23.0769 | 11.5385 | 6.08 | 15 | 10 | 1.1538
26 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.01 | 12.9 | 15 | 1.0533
27 | 0.72 | 12.5 | 21.6 | 15.552 | 6.02 | 14.4 | 15 | 1.0368
28 | 0.68 | 10.7 | 23.7757 | 16.1675 | 6.01 | 12.1 | 15 | 1.0778
29 | 0.62 | 10.7 | 25.2336 | 15.6449 | 6.22 | 13.5 | 15 | 1.043
30 | 0.69 | 12 | 22.5 | 15.525 | 6.2 | 13 | 15 | 1.035
31
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## CT AVG (hidden)
|  |  |  | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT
1 | #DIV/0! | 17.55 | 15 | 6.095 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 17.55 | 15 | 6.105 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 18.875 | 15 | 6.1475 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0!
2 | #DIV/0! | 18.25 | 15 | 6.0925 | 6.5 | 10 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 18.3 | 15 | 6.115 | 6.5 | 10 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 19.825 | 15 | 6.155 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
3 | #DIV/0! | 18 | 15 | 6.0575 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 18.025 | 15 | 6.0925 | 6.5 | 10 | 0 | #DIV/0! | 0.58 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 19.425 | 15 | 6.1375 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
4 | #DIV/0! | 17.4 | 15 | 6.035 | 6.5 | 10 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 17.6 | 15 | 6.075 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 19.025 | 15 | 6.125 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
5 | #DIV/0! | 18.075 | 15 | 6.005 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 18.1 | 15 | 6.03 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 19.625 | 15 | 6.0675 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
6 | #DIV/0! | 18.625 | 15 | 5.9725 | 6 | 8 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 18.675 | 15 | 5.9925 | 6 | 8 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 20.125 | 20 | 6.045 | 6.5 | 7 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0!
7 | #DIV/0! | 18.675 | 15 | 6.0125 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 18.75 | 15 | 6.0325 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 20.4 | 20 | 6.0625 | 6.5 | 7 | 0 | #DIV/0! | 0.52 | #DIV/0! | #DIV/0!
8 | #DIV/0! | 18.575 | 15 | 6.03 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 18.775 | 15 | 6.0675 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 20.275 | 20 | 6.13 | 6.5 | 7 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
9 | #DIV/0! | 18.61 | 15 | 6.075 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 18.725 | 15 | 6.1025 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 19.975 | 20 | 6.13 | 6.5 | 7 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
10 | #DIV/0! | 18.65 | 15 | 6.115 | 6.5 | 10 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 18.8 | 15 | 6.2125 | 6.5 | 10 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 19.975 | 20 | 6.2325 | 6.5 | 7 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
11 | #DIV/0! | 17.325 | 15 | 6.1 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 17.3 | 15 | 6.11 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 18.7 | 15 | 6.16 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0!
12 | #DIV/0! | 16.475 | 15 | 6.11 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 16.575 | 15 | 6.1075 | 6.5 | 10 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 18.15 | 15 | 6.175 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
13 | #DIV/0! | 16.475 | 15 | 6.1375 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 16.6 | 15 | 6.16 | 6.5 | 10 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 18.25 | 15 | 6.1975 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
14 | #DIV/0! | 16.125 | 15 | 6.1025 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 16.25 | 15 | 6.1475 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 18.125 | 15 | 6.1775 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0!
15 | #DIV/0! | 16.1 | 15 | 6.08 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 16.25 | 15 | 6.1275 | 6.5 | 10 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 18 | 15 | 6.175 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0!
16 | #DIV/0! | 15.7 | 15 | 6.0475 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 15.6 | 15 | 6.0775 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 17.05 | 15 | 6.1325 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
17 | #DIV/0! | 15.25 | 15 | 6.04 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 15.225 | 15 | 6.0775 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 15.5 | 15 | 6.0775 | 6.5 | 10 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0!
18 | #DIV/0! | 14.95 | 15 | 6.05 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 15.125 | 15 | 6.045 | 6.5 | 10 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 15.725 | 15 | 6.04 | 6.5 | 10 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0!
19 | #DIV/0! | 15.15 | 15 | 6.07 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 15.15 | 15 | 6.0675 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 15.725 | 15 | 6.0725 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0!
20 | #DIV/0! | 14.625 | 10 | 6.0125 | 6.5 | 15 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 15.1 | 15 | 6.01 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 16.225 | 15 | 6.0225 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0!
21 | #DIV/0! | 14.5 | 10 | 6.08 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 15.375 | 15 | 6.08 | 6.5 | 10 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 15.35 | 15 | 6.11 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
22 | #DIV/0! | 13.675 | 10 | 6.07 | 6.5 | 15 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 15.025 | 15 | 6.045 | 6.5 | 10 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 15.55 | 15 | 6.07 | 6.5 | 10 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0!
23 | #DIV/0! | 13.3 | 10 | 6.05 | 6.5 | 15 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 14.675 | 10 | 6.0525 | 6.5 | 15 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 15.525 | 15 | 6.12 | 6.5 | 10 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0!
24 | #DIV/0! | 13.825 | 10 | 6.055 | 6.5 | 15 | 0 | #DIV/0! | 0.79 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 14.3 | 10 | 6.06 | 6.5 | 15 | 0 | #DIV/0! | 0.74 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 14.975 | 15 | 6.0525 | 6.5 | 10 | 0 | #DIV/0! | 0.71 | #DIV/0! | #DIV/0!
25 | #DIV/0! | 13.25 | 10 | 6.0825 | 6.5 | 15 | 0 | #DIV/0! | 0.73 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 14.825 | 10 | 6.095 | 6.5 | 15 | 0 | #DIV/0! | 0.7 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 15.025 | 15 | 6.0675 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0!
26 | #DIV/0! | 13.375 | 10 | 6.0275 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 14.75 | 10 | 6.07 | 6.5 | 15 | 0 | #DIV/0! | 0.66 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 14.85 | 10 | 6.05 | 6.5 | 15 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
27 | #DIV/0! | 12.925 | 10 | 6.1575 | 6.5 | 15 | 0 | #DIV/0! | 0.78 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 13.95 | 10 | 6.1875 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 14.3 | 10 | 6.135 | 6.5 | 15 | 0 | #DIV/0! | 0.72 | #DIV/0! | #DIV/0!
28 | #DIV/0! | 12.525 | 10 | 6.165 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 13.275 | 10 | 6.205 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 13.825 | 10 | 6.1925 | 6.5 | 15 | 0 | #DIV/0! | 0.72 | #DIV/0! | #DIV/0!
29 | #DIV/0! | 12.05 | 10 | 6.1475 | 6.5 | 15 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0! | 29 | #DIV/0! | 12.55 | 10 | 6.21 | 6.5 | 15 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0! | 29 | #DIV/0! | 13.375 | 10 | 6.23 | 6.5 | 15 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0!
30 | #DIV/0! | 12.075 | 10 | 6.15 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 30 | #DIV/0! | 12.65 | 10 | 6.255 | 6.5 | 15 | 0 | #DIV/0! | 0.8 | #DIV/0! | #DIV/0! | 30 | #DIV/0! | 13.35 | 10 | 6.2175 | 6.5 | 15 | 0 | #DIV/0! | 0.69 | #DIV/0! | #DIV/0!
31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE!
ONLY FILL GREEN
|  |  |  | TEST | [8 empty] | DALY CAL SHEET FLOW, DALY AVG TEMP & PH Min CT Calculater
| Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# |  |  |  | Settle temp |  | use temp | Settle PH |  | use ph |  | FLOW CAL SHEET | t10#
| Plt 1 | 18.8 | 15 | Plt 1 PH | 6.09 | 6.5 | plt 1 flow | 12 | 21.2 |  |  |  | Plt 1 | 16.475 | 15 | Plt 1 PH | 6.11 | 6.5 | plt 1 flow | 11 | 23.1273
| Plt 2 | 18.9 | 15 | Plt 2 PH | 6.13 | 6.5 | plt 2 flow | 12 | 21.2 |  |  |  | Plt 2 | 16.575 | 15 | Plt 2 PH | 6.1075 | 6.5 | plt 2 flow | 11 | 23.1273
| Plt 3 | 19.5 | 15 | Plt 3 PH | 6.24 | 6.5 | plt 3 flow | 12 | 22.5 |  |  |  | Plt 3 | 18.15 | 15 | Plt 3 PH | 6.175 | 6.5 | plt 3 flow | 12 | 22.5
2019-08-12 09:20
|  | min CT | TARGET CT |  | temp | ph | min ct table | [7 empty] | min CT | TARGET CT |  | temp | ph | min ct table
| ct plt 1 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 1 | 0.43239 | 0.53239 |  | 15 | 6.5 | 10
| ct plt 2 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 2 | 0.43239 | 0.53239 |  | 15 | 6.5 | 10
| ct plt 3 | 0.44444 | 0.54444 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 3 | 0.44444 | 0.54444 |  | 15 | 6.5 | 10
Bill's Cal | flow | temp | ph | t10# | cal ct table | MIN CT | target ct
plt1 | 12 | 18.8 | 6.09 | 21.2 | 7.1064 | 0.33521 | 0.43521
plt2 | 12 | 18.9 | 6.13 | 21.2 | 7.1599 | 0.33773 | 0.43773
plt3 | 12 | 19.5 | 6.24 | 22.5 | 7.1424 | 0.31744 | 0.41744

## CT Calc
Surface Water System Monthly Operation Report
Disinfection Information
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | 2018-11-01
| Min. Disinfect. Resid. | Sample Type for | CT calc/CT table Disinfectant Sequence | [5 empty] | SUM (CT calc/CT table)
Day | at Point-of-Entry to Distribution System (mg/L) | Point-of-Entry (POE) | 1st | 2nd | 3rd | 4th | 5th | 6th
1 | 2.9 | A | 1.0754 | 0 | 0 | 0 | 0 | 0 | 1.0754
2 | 3.2 | A | 1.4186 | 0 | 0 | 0 | 0 | 0 | 1.4186
3 | 3.1 | A | 1.3374 | 0 | 0 | 0 | 0 | 0 | 1.3374
4 | 3 | A | 1.1268 | 0 | 0 | 0 | 0 | 0 | 1.1268
5 | 2.9 | A | 1.1101 | 0 | 0 | 0 | 0 | 0 | 1.1101
6 | 3.2 | A | 1.4097 | 0 | 0 | 0 | 0 | 0 | 1.4097
7 | 3.2 | A | 1.4246 | 0 | 0 | 0 | 0 | 0 | 1.4246
8 | 2.8 | A | 1.3758 | 0 | 0 | 0 | 0 | 0 | 1.3758
9 | 2.8 | A | 1.305 | 0 | 0 | 0 | 0 | 0 | 1.305
10 | 2.5 | A | 1.1115 | 0 | 0 | 0 | 0 | 0 | 1.1115
11 | 2.9 | A | 1.3239 | 0 | 0 | 0 | 0 | 0 | 1.3239
12 | 2.8 | A | 1.1008 | 0 | 0 | 0 | 0 | 0 | 1.1008
13 | 2.9 | A | 1.2583 | 0 | 0 | 0 | 0 | 0 | 1.2583
14 | 2.8 | A | 1.313 | 0 | 0 | 0 | 0 | 0 | 1.313
15 | 2.9 | A | 1.231 | 0 | 0 | 0 | 0 | 0 | 1.231
16 | 3.1 | A | 1.3122 | 0 | 0 | 0 | 0 | 0 | 1.3122
17 | 3.2 | A | 1.0395 | 0 | 0 | 0 | 0 | 0 | 1.0395
18 | 3.2 | A | 1.2843 | 0 | 0 | 0 | 0 | 0 | 1.2843
19 | 3 | A | 1.4131 | 0 | 0 | 0 | 0 | 0 | 1.4131
20 | 3.1 | A | 1.1903 | 0 | 0 | 0 | 0 | 0 | 1.1903
21 | 3.5 | A | 1.1145 | 0 | 0 | 0 | 0 | 0 | 1.1145
22 | 3.3 | A | 1.0854 | 0 | 0 | 0 | 0 | 0 | 1.0854
23 | 3.4 | A | 1.0346 | 0 | 0 | 0 | 0 | 0 | 1.0346
24 | 3.2 | A | 1.2026 | 0 | 0 | 0 | 0 | 0 | 1.2026
25 | 3.5 | A | 1.1538 | 0 | 0 | 0 | 0 | 0 | 1.1538
26 | 3.3 | A | 1.0533 | 0 | 0 | 0 | 0 | 0 | 1.0533
27 | 3.6 | A | 1.0368 | 0 | 0 | 0 | 0 | 0 | 1.0368
28 | 3.6 | A | 1.0778 | 0 | 0 | 0 | 0 | 0 | 1.0778
29 | 3.6 | A | 1.043 | 0 | 0 | 0 | 0 | 0 | 1.043
30 | 3.4 | A | 1.035 | 0 | 0 | 0 | 0 | 0 | 1.035
31
A. Number of days SUM (CT calc/CT table) <1: |  |  | 0 |  | Days the Distribution Residual was <0.2 mg/L
[5 empty] | Day | Duration (hrs) |  | Date Reported
B. Compliance with disinfection residual criteria |  |  |  |  | None | None |  | None
at Point-of-Entry to distribution system: |  |  | Yes |  | None | None |  | None
Prepared by: _________________________________________________ | [6 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Superintendent

## CT (1)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-11-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.49 | 10.6 | 24 | 11.76 | 6.1 | 17.3 | 10 | 1.176
2 | 0.65 | 10.7 | 23.7757 | 15.4542 | 6.1 | 17.8 | 10 | 1.5454
3 | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.03 | 18 | 10 | 1.4425
4 | 0.65 | 9.7 | 26.2268 | 17.0474 | 6.03 | 16.8 | 10 | 1.7047
5 | 0.47 | 12 | 21.2 | 9.964 | 5.98 | 17.6 | 8 | 1.2455
6 | 0.46 | 10 | 25.44 | 11.7024 | 5.97 | 19.1 | 8 | 1.4628
7 | 0.63 | 10 | 25.44 | 16.0272 | 6.05 | 18.4 | 10 | 1.6027
8 | 0.53 | 9.6 | 26.5 | 14.045 | 6.14 | 18.7 | 10 | 1.4045
9 | 0.6 | 11 | 23.1273 | 13.8764 | 6.08 | 18.5 | 10 | 1.3876
10 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.41 | 18.7 | 10 | 1.1115
11 | 0.51 | 9.8 | 25.9592 | 13.2392 | 6.05 | 17.3 | 10 | 1.3239
12 | 0.52 | 10.1 | 25.1881 | 13.0978 | 6.19 | 16.4 | 10 | 1.3098
13 | 0.54 | 10.3 | 24.699 | 13.3375 | 6.1 | 16.5 | 10 | 1.3337
14 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.2 | 10 | 1.313
15 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.22 | 15.7 | 10 | 1.313
16 | 0.49 | 9.5 | 26.7789 | 13.1217 | 6.06 | 15.7 | 10 | 1.3122
17 | 0.57 | 9.3 | 27.3548 | 15.5923 | 6.06 | 14.9 | 15 | 1.0395
18 | 0.57 | 10.3 | 24.699 | 14.0784 | 6.15 | 15 | 10 | 1.4078
19 | 0.58 | 10.3 | 24.699 | 14.3254 | 6.01 | 15 | 10 | 1.4325
20 | 0.59 | 9.7 | 26.2268 | 15.4738 | 5.99 | 14.6 | 13 | 1.1903
21 | 0.69 | 10.5 | 24.2286 | 16.7177 | 6.14 | 13.8 | 15 | 1.1145
22 | 0.6 | 10.5 | 24.2286 | 14.5371 | 5.95 | 13.4 | 13 | 1.1182
23 | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 13.1 | 15 | 1.0346
24 | 0.79 | 11 | 23.1273 | 18.2705 | 6.03 | 12.9 | 15 | 1.218
25 | 0.73 | 10.7 | 23.7757 | 17.3563 | 6.08 | 13.6 | 15 | 1.1571
26 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.01 | 12.9 | 15 | 1.0533
27 | 0.78 | 12 | 21.2 | 16.536 | 6.27 | 12.9 | 15 | 1.1024
28 | 0.68 | 10.7 | 23.7757 | 16.1675 | 6.01 | 12.1 | 15 | 1.0778
29 | 0.69 | 10.8 | 23.5556 | 16.2533 | 6.11 | 12.2 | 15 | 1.0836
30 | 0.68 | 11 | 23.1273 | 15.7265 | 6.12 | 12.4 | 15 | 1.0484
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) Randall Johnson Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (2)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-11-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.51 | 10.6 | 24 | 12.24 | 6.11 | 17.3 | 10 | 1.224
2 | 0.61 | 10.7 | 23.7757 | 14.5032 | 6.1 | 17.8 | 10 | 1.4503
3 | 0.58 | 9.7 | 26.2268 | 15.2115 | 6.09 | 18 | 10 | 1.5212
4 | 0.56 | 11.3 | 22.5133 | 12.6074 | 6.06 | 17.9 | 10 | 1.2607
5 | 0.48 | 11 | 23.1273 | 11.1011 | 6.02 | 18.5 | 10 | 1.1101
6 | 0.64 | 10.3 | 24.699 | 15.8074 | 6.02 | 18 | 10 | 1.5807
7 | 0.56 | 10 | 25.44 | 14.2464 | 6.13 | 18.7 | 10 | 1.4246
8 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.11 | 18.8 | 10 | 1.3758
9 | 0.53 | 10 | 25.44 | 13.4832 | 6.11 | 18.7 | 10 | 1.3483
10 | 0.46 | 10.3 | 24.699 | 11.3616 | 6.39 | 18.9 | 10 | 1.1362
11 | 0.6 | 9.8 | 25.9592 | 15.5755 | 6.08 | 17.2 | 10 | 1.5576
12 | 0.45 | 10.4 | 24.4615 | 11.0077 | 6.02 | 16.6 | 10 | 1.1008
13 | 0.46 | 9.3 | 27.3548 | 12.5832 | 6.11 | 16.5 | 10 | 1.2583
14 | 0.48 | 9.3 | 27.3548 | 13.1303 | 6.12 | 16.4 | 10 | 1.313
15 | 0.45 | 9.3 | 27.3548 | 12.3097 | 6.06 | 18.5 | 10 | 1.231
16 | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.14 | 16 | 10 | 1.5045
17 | 0.48 | 10.3 | 24.699 | 11.8555 | 6.14 | 15.6 | 10 | 1.1856
18 | 0.78 | 10.3 | 24.699 | 19.2652 | 6.18 | 14.9 | 15 | 1.2843
19 | 0.55 | 9.7 | 26.2268 | 14.4247 | 6.03 | 15.3 | 10 | 1.4425
20 | 0.51 | 9.7 | 26.2268 | 13.3757 | 5.98 | 15 | 8 | 1.672
21 | 0.61 | 10.3 | 24.699 | 15.0664 | 6.08 | 16 | 10 | 1.5066
22 | 0.64 | 10 | 25.44 | 16.2816 | 6.16 | 14.5 | 15 | 1.0854
23 | 0.61 | 10 | 25.44 | 15.5184 | 6.06 | 14.4 | 15 | 1.0346
24 | 0.78 | 11 | 23.1273 | 18.0393 | 6.03 | 14 | 15 | 1.2026
25 | 0.75 | 9.6 | 26.5 | 19.875 | 6.12 | 14.4 | 15 | 1.325
26 | 0.7 | 10.9 | 23.3394 | 16.3376 | 6.06 | 14.5 | 15 | 1.0892
27 | 0.68 | 10.9 | 23.3394 | 15.8708 | 6.13 | 14.3 | 15 | 1.0581
28 | 0.7 | 11 | 23.1273 | 16.1891 | 6.3 | 13 | 15 | 1.0793
29 | 0.65 | 9.6 | 26.5 | 17.225 | 6.21 | 12.5 | 15 | 1.1483
30 | 0.8 | 11.1 | 22.9189 | 18.3351 | 6.27 | 12.6 | 15 | 1.2223
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (3)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2018-11-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.47 | 11.8 | 22.8814 | 10.7542 | 6.15 | 18.5 | 10 | 1.0754
2 | 0.62 | 11.8 | 22.8814 | 14.1864 | 6.12 | 19.6 | 10 | 1.4186
3 | 0.53 | 10.7 | 25.2336 | 13.3738 | 6.15 | 19.9 | 10 | 1.3374
4 | 0.53 | 12.7 | 21.2598 | 11.2677 | 6.14 | 19.1 | 10 | 1.1268
5 | 0.67 | 12.6 | 21.4286 | 14.3571 | 6.05 | 19.3 | 10 | 1.4357
6 | 0.59 | 11.3 | 23.8938 | 14.0973 | 6.08 | 19.7 | 10 | 1.4097
7 | 0.52 | 11.1 | 24.3243 | 12.6486 | 6.08 | 20.4 | 7 | 1.8069
8 | 0.53 | 11 | 24.5455 | 13.0091 | 6.1 | 20.3 | 7 | 1.8584
9 | 0.58 | 12 | 22.5 | 13.05 | 6.19 | 19.9 | 10 | 1.305
10 | 0.6 | 11.3 | 23.8938 | 14.3363 | 6.3 | 19.9 | 10 | 1.4336
11 | 0.56 | 11 | 24.5455 | 13.7455 | 6.16 | 18.4 | 10 | 1.3745
12 | 0.53 | 11 | 24.5455 | 13.0091 | 6.2 | 18.3 | 10 | 1.3009
13 | 0.54 | 11.3 | 23.8938 | 12.9027 | 6.16 | 18.2 | 10 | 1.2903
14 | 0.55 | 10.3 | 26.2136 | 14.4175 | 6.2 | 17.8 | 10 | 1.4417
15 | 0.55 | 10.3 | 26.2136 | 14.4175 | 6.12 | 18.5 | 10 | 1.4417
16 | 0.6 | 10.3 | 26.2136 | 15.7282 | 6.19 | 18 | 10 | 1.5728
17 | 0.7 | 11.3 | 23.8938 | 16.7257 | 6.04 | 13.3 | 15 | 1.115
18 | 0.75 | 10.3 | 26.2136 | 19.6602 | 6.13 | 15.5 | 10 | 1.966
19 | 0.56 | 10.7 | 25.2336 | 14.1308 | 6.12 | 15.4 | 10 | 1.4131
20 | 0.48 | 10.7 | 25.2336 | 12.1121 | 6.01 | 17.9 | 10 | 1.2112
21 | 0.6 | 11.8 | 22.8814 | 13.7288 | 6.09 | 15.5 | 10 | 1.3729
22 | 0.57 | 11 | 24.5455 | 13.9909 | 6.18 | 15.7 | 10 | 1.3991
23 | 0.75 | 11.7 | 23.0769 | 17.3077 | 6.18 | 14.8 | 15 | 1.1538
24 | 0.73 | 12 | 22.5 | 16.425 | 6 | 14.6 | 13 | 1.2635
25 | 0.5 | 11.7 | 23.0769 | 11.5385 | 6.08 | 15 | 10 | 1.1538
26 | 0.68 | 11.6 | 23.2759 | 15.8276 | 6.14 | 14.4 | 15 | 1.0552
27 | 0.72 | 12.5 | 21.6 | 15.552 | 6.02 | 14.4 | 15 | 1.0368
28 | 0.72 | 11.7 | 23.0769 | 16.6154 | 6.19 | 14 | 15 | 1.1077
29 | 0.62 | 10.7 | 25.2336 | 15.6449 | 6.22 | 13.5 | 15 | 1.043
30 | 0.69 | 12 | 22.5 | 15.525 | 6.2 | 13 | 15 | 1.035
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2018-12-06
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## ct CAL
ONLY FILL GREEN
TEST
Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# | Flows from Plant Check Sheet
Plt 1 | 12.4 | 10 | Plt 1 PH | 6.12 | 6.5 | plt 1 flow | 11 | 23.1273 | Raw PLT 1 | 11
Plt 2 | 12.7 | 10 | Plt 2 PH | 6.25 | 6.5 | plt 2 flow | 11 | 23.1273 | Raw PLT 2 | 11
Plt 3 | 13.3 | 10 | Plt 3 PH | 6.21 | 6.5 | plt 3 flow | 12 | 22.5 | Raw PLT 3 | 12
| min CT | TARGET CT |  | temp | ph | min ct table
ct plt 1 | 0.64858 | 0.74858 |  | 10 | 6.5 | 15
ct plt 2 | 0.64858 | 0.74858 |  | 10 | 6.5 | 15
ct plt 3 | 0.66667 | 0.76667 |  | 10 | 6.5 | 15

## Turbidity Analysis
South Carolina Department of Health and Environmental Control
Bureau of Drinking Water Protection
Turbidity Analysis Input Form
System Number .............................................................…………… |  |  | 2620004
Name of Water System ................................................……………. |  |  | GSWSA
Analytical Method ..........................................................…………… |  |  | 001
Contaminant ID ..............................................................…………… |  |  | 0100
Compliance Period Begin (mo/day/yr) ........................………………. |  |  | 2018-11-01
Compliance Period End (mo/day/yr) ..........................……………….. |  |  | 2018-11-30
Number of Samples Required ....................................……………….. |  |  | 180
Number of Samples Taken .........................................………………. |  |  | 540
Highest Turbidity for Compliance Period ..................………………… |  |  | 0.092
Lowest Turbidity for Compliance Period ...................………………… |  |  | 0.023
Average Turbidity for Compliance Period ..................………………… |  |  | 0.0526
Laboratory ID ..................................................................…………… |  |  | 26102
Laboratory Name ...........................................................……………. |  |  | GSWSA /BCSWTP
Comments:
Signature ________________________________ Date |  | 2018-12-06
William Lederman Plant Supervisor
This signature certifies that all samples were collected, analyzed and reported according to the State Primary Drinking
Water Regulations.
DHEC 1975 (Rev. 5/00)

## Distribution
Surface Water System Monthly Operation Report
Distribution System Disinfectant Residual Data
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: |  | 2016-08-01
Lab Cert ID #: 26102 |  |  | Lab # for lab conducting HPC analyses: 26102
Day | No. of Sites Disinfect. Residual was Measured | No. of Sites Disinfect. Residual NOT Measured, but HPC Measured | No. of Sites where Disinfect. Residual NOT Detected & HPC NOT Measured | No. of Sites where Disinfectant Residual was NOT Detected and HPC > 500/ml | No. of Sites Disinfect. Residual NOT Measured and HPC > 500/ml | Average Disinfectant Residual (mg/L)
1 |  | 0 | 0 | 0 | 0
2 |  | 0 | 0 | 0 | 0
3 |  | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 0 | 0
5 |  | 0 | 0 | 0 | 0
6 |  | 0 | 0 | 0 | 0
7 |  | 0 | 0 | 0 | 0
8 |  | 0 | 0 | 0 | 0
9 |  | 0 | 0 | 0 | 0
10 |  | 0 | 0 | 0 | 0
11 |  | 0 | 0 | 0 | 0
12 |  | 0 | 0 | 0 | 0
13 |  | 0 | 0 | 0 | 0
14 |  | 0 | 0 | 0 | 0
15 |  | 0 | 0 | 0 | 0
16 |  | 0 | 0 | 0 | 0
17 |  | 0 | 0 | 0 | 0
18 |  | 0 | 0 | 0 | 0
19 |  | 0 | 0 | 0 | 0
20 |  | 0 | 0 | 0 | 0
21 |  | 0 | 0 | 0 | 0
22 |  | 0 | 0 | 0 | 0
23 |  | 0 | 0 | 0 | 0
24 |  | 0 | 0 | 0 | 0
25 |  | 0 | 0 | 0 | 0
26 |  | 0 | 0 | 0 | 0
27 |  | 0 | 0 | 0 | 0
28 |  | 0 | 0 | 0 | 0
29 |  | 0 | 0 | 0 | 0
30 |  | 0 | 0 | 0 | 0
31 |  | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | Avg. Resid.
| a | b | c | d | e | #DIV/0!
Compliance with Distribution System Disinfectant Residual Criteria |  |  |  |  | #DIV/0!
V = ( c + d + e ) / ( a + b ) x 100 = ( + + ) / ( + ) x 100 =
For Previous Month: V =
Prepared by: __________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## Chloramine
Surface Water System Monthly Operation Report
For Systems Using Chlorine and/or Chloramines
To Maintain A Residual In The Distribution System
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | For (Month/yr): | 2016-08-01
Month/Year | *Average Residual |  | Quarterly Average (mg/L)
| Chlorine (mg/L) | Chloramines (mg/L)
2016-01-02 |  | 3.42 | 3.17
2016-02-03 |  | 2.79 |  | *Average residual values may be obtained from page 10 of 15 of this form
2016-03-03 |  | 3.3
2016-04-02 |  | 3.42 | 3.14
2016-05-03 |  | 3.46
2016-06-02 |  | 2.75
2016-07-02 |  | 3.42
2016-08-02 |  | 2.86
2016-09-02
2015-10-02 |  | 3.11 | 2.99
2015-11-02 |  | 2.78
2015-12-02 |  | 3.08
RAA at the end of the most recent quarter: |  |  | 3.1
Prepared by: _________________________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## TOC
Surface Water System Monthly Operation Report
Compliance With DBP Precursor Removal Requirements
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  |  | For (Month/yr): |  | 2016-08-01
Lab Cert ID #: 26102
Month | Source Water |  | Treated Water TOC (mg/L) | (A) Actual % TOC Removal | (B) Required % TOC Removal | Basis for Required % Removal | Removal Ratio (A) / (B) | Quarterly Average Ratio | RAA1 Ratio (Last 4 Quarters)
| Alkalinity (mg/L) | TOC (mg/L)
2016-01-01 | 14 | 21.88 | 4.05 | 81.4899 | 50 | Step 1 | 1.6298 | 1.51
2016-02-01 | 20 | 9.738 | 2.72 | 72.0682 | 50 | Step 1 | 1.4414
2016-03-01 | 14 | 10.23 | 2.81 | 72.5318 | 50 | Step 1 | 1.4506
2016-04-01 | 21 | 9.776 | 2.82 | 71.1538 | 50 | Step 1 | 1.4231 | 1.3387 | 1.37
2016-05-01 | 23 | 10.09 | 2.97 | 70.5649 | 50 | Step 1 | 1.4113
2016-06-01 | 23 | 8.579 | 3.51 | 59.0861 | 50 | Step 1 | 1.1817
2016-07-01 | 24 | 8.27 | 3.538 | 57.2189 | 50 | Step 1 | 1.1444
2016-08-01 | 22 | 11.4 | 3.69 | 67.6316 | 50 | Step 1 | 1.3526
2016-09-01
2015-10-01 | 21 | 12.04 | 3.49 | 71.0133 | 50 | Step 1 | 1.4203 | 1.5
2015-11-01 | 28 | 17.264 | 4.18 | 75.7878 | 50 | Step 1 | 1.5158
2015-12-01 | 18 | 18.612 | 4.11 | 77.9175 | 50 | Step 1 | 1.5583
1 RAA = Running Annual Average, Computed Quarterly
Alternate Criteria
**Should only be filled out if Alternate Criteria 3 or 4 are being used
Month | Source water |  |  |  | Finished water
| DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m) |  | DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m)
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
Alternate Criteria
Alt. 1 | Source Water TOC < 2.0 mg/L
Alt. 2 | Treated Water TOC < 2.0 mg/L
Alt. 3 | Source Water SUVA < 2.0 L/mg-m
Alt. 4 | Treated Water SUVA < 2.0 L/mg-m
Prepared by: ____________________________________________ | [5 empty] | Date:
(signature) Clint Elliott Lab Supervisor

## Bacteria(new)
Bacteriological Analysis Sample Summary
1. Please fill out page 2 of this form if you have a total coliform posative sample and repeat samples.
2. Submit this form to SCDHEC along with a copy of your labrotories chain of custody no later than ten (10) days after the end of the compliance period.
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
COMPLIANCE PERIOD |  |  | 2016-09-01
CYCLE |  |  | M
(Q)-QUARTERLY (M)-MONTHLY
CHLORINE RESIDUAL |  |  | #DIV/0!
Lab ID measuring chlorine residual |  |  | 26102
# OF INITIAL SAMPLES |  |  | 0
# OF INITIAL TC POSITIVE SAMPLES |  |  | 0
# OF E. COLI POSITIVE SAMPLES |  |  | 0
TOTAL COLIFORM ANALYSIS METHOD CODE |  |  | SM9223B-2004
E. COLI ANALYSIS METHOD |  |  | SM9223B-2004
Lab ID |  |  | 26102
SIGNATURE
Date
Bacteriological Analysis Individual Samples (Part 2)
PART 2 CAN BE USED FOR ALL TOTAL COLIFORM SAMPLES AND ASSOCIATED
REPEATS AND SOURCE WATER SAMPLES
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
LAB ID |  |  | #VALUE!
TYPE | REPEAT | LAB SAMPLE NUMBER | COLLECTION DATE (MM/DD/YYYY) | [7 empty] | SAMPLING LOCATION |  | SOURCE ID | TOTAL A/P | E.COLI A/P | TOTAL/FREE CHLORINE RESIDUAL
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
Explanation: | [11 empty] | Comments
Type (RT, RP or GW ) |  |  |  | RT = Routine; RP=Repeat; GW=Groundwater
Repeat (only if sample type =RP) |  |  |  | DN = Downstream; UP=Upstream;
Lab Sample # |  |  |  | # assigned by lab for that particular sample
Collection Date (mmddyyyy) |  |  |  | Date sample was collected
Sampling Location |  |  |  | Physical address where sample was collected
Source ID(only used for source samples) |  |  |  | 5 digit DHEC Source ID (ie. G_ _ _ _ _)
Total Coliform (A or P) |  |  |  | Indicate with an "A" if absent or a "P" if present
E. Coli = (A or P) |  |  |  | E = Ecoli Positive
Total/Free Chlorine Residual |  |  |  | Chlorine Residual Reading
Within 24 hours of learning of a total coliform-positive (TC+) sample result, REPEAT samples must be collected and analyzed for total coliforms:
One REPEAT sample must be collected from the same tap as the TC+ sample.
One REPEAT sample must be collected within five service connections upstream of the TC+ sample.
One REPEAT sample must be collected within five service connections downstream of the TC+ sample.
If the system is served by Ground water then a Triggered Source sample must be collected prior to treatment from each source in use at the time the total coliform-positive sample was collected. The number of samples taken PER WELL must equal the number of positive TCR samples. If you collected three TC+ samples, then three well samples must be taken at EACH WELL that was in service at the time.
The triggered source water sample must be analyzed for the presence of E.coli.
If any triggered source water sample is E.coli-positive, the Ground Water system (GWS) must either take corrective action, as directed by the state, or the GWS must take 5 additional source water sampleswithin 24 hours.
If the GW system Purchases some or all af there water they must notify the wholesale system (s) within 24 hours.
If any REPEAT sample is TC+:
The system must analyze that total coliform-positive culture for E.coli.
The system must collect another set of REPEAT samples, as before, unless the E.coli MCL has been violated or an assessment has been triggered.
For a system on quarterly monitoring, a TC+ result requires a minimum of three ROUTINE samples be collected the following month.
CALL SCDHEC on the same day you learned of the E. coli-positive (EC+) result, or by the end of the next business day if the result came in after business hours
Please submit a copy of your labrotories chain of custody along with this form.

## Bacteria
Bacteriological Analysis Sample Summary (Part 1)
PART 1 CAN BE USED IN ONE (1) OF TWO (2) WAYS
1. If the system has had no Total Coliform (TC) Positives samples for a compliance cycle or,
2. If the system wants to report those samples that were initial TC Absent and use Part 2 for
the TC Present and all repeats.
DESCRIPTION
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
0 | 4 | 0 | 1 | 2 | 0 | 1 | 6 | 2 |  |  |  |  | First day of month / quarter
1 | 2 | 0 | [10 empty] | # of Initial Total Coliform Negative
0 | 4 | 0 | 2 | 2 | 0 | 1 | 6 | [5 empty] | M=Month; Q=Quarter; Y=Year
| 2 | 6 | 1 | 0 | 2 |  |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
Note: This can be used for any system that does
not have a total coliform positive
DOES SYSTEM ADD DISINFECTION | [8 empty] | YES
AVERAGE DISINFECTION RESIDUAL | [8 empty] | 3 | . | 4 | 2
AND/OR
Bacteriological Analysis Individual Samples (Part 2)
NOTE: This form would only be used for the initial routine (RT) TC or TC/FC Positive and
and the Repeats that are required by regulation.
PART 2 CAN MUST BE USED FOR ALL TOTAL COLIFORM POSITIVES AND ALL ASSOCIATED
REPEATS
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
|  | 2 | 6 | 1 | 0 | 2 |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
[15 empty] | Total | Fecal (F) or | Free/Total
[13 empty] | TYPE | Lab Sample ID | Coliform | E Coli (E) + | Chlorine
SAMPLE ID # AND LOCATION | [8 empty] | COLLECTION DATE (MMDDYYYY) |  |  |  | (RT or RP) | Number | A/P | If Present | Residual*
.
.
.
.
.
.
Explanation:
Collection Date (mmddyyyy)………………..Date sample was collected
Lab Sample #…………………………………# assigned by lab for that particular sample
Type (RT or RP)………………………………RT = Routine; RP=Repeat
Sampling Point ID……………………………..If lab has something that identifies site other than physical location
Sampling Location……………………………Physical address where sample was collected from
Total Coliform (A or P)…………………….Indicate with an "A" if absent or a "P" if present
FC (F = FC+ or E = Ecoli+)…………………..F= Fecal Coliform Positive; E = Ecoli Positive
Total/Free Chlorine Residual…………………………Chlorine Residiual Reading

## TOC Sample ID
TOC SAMPLE ID LOG
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  | 2018-11-01
Lab Cert ID #: 26102
Treated | TOC | Raw | TOC | Alkalinity
D-02011608 |  | D-02011611 |  | 20
D-02011609
D-02011610

## Calculation for TOC
| TOC | [6 empty] | Sample Number | [5 empty] | Raw
| Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled |  | Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled | Alkalinity
Week 1
| 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 |  | D-07061506 | D-07061507 | D-07061511 | D-07061508 | D-07061509 | D-07061510 | 36
2.47
5.88
Week 2
#DIV/0!
#DIV/0!
Week 3
#DIV/0!
#DIV/0!
Week 4 | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786
2.931
7.579
Average | 2.7005 | 2.555 | 6.7295 | 4.2765 | 2.8045 | 2.619 | [5 empty] | Average Alkalinity Raw |  | 36
Max | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786 | 3.726
Min | 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 | 2.7407
Average Treated TOC |  |  | 3.2333
Average % TOC Removal |  |  | 51.9528
Max % TOC Removal |  |  | 59.2738
Min % TOC Removal |  |  | 44.6318
TOC Sample ID Number Submittal
Treated | TOC |  |  | Raw | TOC | Alkalinity

## Chem Cost
2018-11-01
Chemical Usage / Dosage / Cost
Chemical | Usage |  | Dosage (mg/l) |  |  | Cost ($) |  |  | Alternate Units |  |  | density as is |  | Purity
| Unit | Total | Average | Maximum | Minimum | $/Unit | Total $ | $/1000 gal water | Unit | Total | $/unit | g/ml | lb/gal | wt. % | lb/gal
Pre Chlorine | gals | 12453.1983 | 1.7342 | 2.2814 | 1.4858 | 0.81 | 10087.0906 | 0.011921 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Aluminum Sulfate | gals | 133093.3056 | 90.0224 | 116.4084 | 76.4581 | 1.69 | 224927.6864 | 0.26582 | lbs | 1473875.2657 | 0.15225 | 1.325 | 11.05 | 48.5 | 5.36
Pre Caustic | gals | 0 | 0 | 0 | 0 | 1.86 | 0 | 0 | lbs | 0 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Post Chlorine | gals | 22880.0937 | 3.9561 | 4.182 | 3.772 | 0.81 | 18532.8759 | 0.021902 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Ammonia | gals | 3216.3847 | 0.68804 | 0.75571 | 0.59803 | 0.68 | 2187.1416 | 0.0025848 |  |  |  | 0.928 | 7.74 | 19.5 | 1.51
Post Caustic | gals | 7330.4161 | 6.5223 | 8.3245 | 3.0868 | 1.86 | 13634.574 | 0.016113 | lbs | 93536.1098 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Lime | gals | 90415.0799 | 28.6653 | 38.1461 | 22.4441 | 0.055 | 4972.8294 | 0.0058769
Fluoride | gals | 2232.8445 | 0.50019 | 0.54757 | 0.44862 | 3.2 | 7145.1024 | 0.0084441 | lbs | 22551.7296
Activated Carbon | lbs | 24932.7474 | 3.1631 | 3.8475 | 2.7021 | 0.89 | 22190.1452 | 0.026224
Polymer | gals | 346.5188 | 0.4168 | 0.71929 | 0.27051 | 11.95 | 4140.8994 | 0.0048937 | lbs | 2980.0615 | 1.39
Filter Aid | gals | 9326.3273 | 9.4314 | 20.7149 | 2.1388 | 5.59 | 52134.1694 | 0.061612 | lbs | 80206.4144 | 0.65
Zinc Chloride Dosed as Zinc | gals | 180.6808 | 0.099698 | 0.10577 | 0.089388 | 6.89 | 1244.8908 | 0.0014712 | lbs | 2366.9187 | 0.526
Corrosion Inhibitor Dosed as Phosphorus | gals | 1588.184 | 1.0984 | 1.1207 | 0.98962 | 11.72 | 18613.5165 | 0.021998 | lbs | 23028.668 | 0.808
|  |  | Total Chemical Cost |  |  |  | 379810.9216
|  |  | Cost per 1000 gallons |  |  |  | 0.44886

## Extras
| TOC | [25 empty] | pH |  |  |  | Alkalinity |  |  |  | Hardness |  |  |  | Turbidity |  |  |  | Color |  |  |  | Temp |  |  |  | TRC |  |  | Fluoride |  |  | Flow (MG) |  |  |  | COLIFORM
| Finish1 | Finish2 | Raw |  | Conductivity |  |  | TDS |  |  | Chloride |  |  |  | Sodium |  |  | Sulfate |  |  | Iron |  |  | Manganese |  |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 |  | Finish1 | Finish2 |  | Raw | Finish1 | Finish2 |  | Raw | Finish1 | Finish2
Week 1 |  |  |  |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | 7.14 | 7.225 | 6.4967 |  | 22.5 | 22 | 18.3333 |  | 29 | 36.5 | 17.3333 |  | 0.064 | 0.07 | 14.9 |  | 1 | 1.3333 | 125.6667 |  | 17.9 | 20.9 | 18.7833 |  | 4 | 3.7 |  | 0.4766 | 0.4864 |  | 32.598 | 13.822 | 14.938 |  | 657 | A | A
|  |  |  | Week 1 | [6 empty] | 11.1 | 11.3 | 7.27 |  |  |  |  | 21.8 | 21.9 | 7.46 | [6 empty] | 7.175 | 7.2217 | 6.4667 |  | 24 | 24.5 | 20.5 |  | 33.5 | 34 | 18.5 |  | 0.058 | 0.057 | 14.6 |  | 1.1667 | 1.3333 | 121.5 |  | 18.2333 | 20.8833 | 19.2 |  | 4.2 | 3.6 |  | 0.5051 | 0.4694 |  | 14.026 | 14.026 | 14.108 |  | 594 | A | A
|  |  |  | Week 2 | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  |  |  |  | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.2083 | 7.2533 | 6.43 |  | 20.5 | 22.5 | 20.6667 |  | 34.5 | 35.5 | 18.3333 |  | 0.057 | 0.06 | 14.1 |  | 1 | 1 | 112.8333 |  | 18.3 | 20.3333 | 19.1333 |  | 4.1 | 3.5 |  | 0.483 | 0.4771 |  | 13.805 | 13.805 | 13.676 |  | 586 | A | A
|  |  |  | Week 3 | [22 empty] | 7.2267 | 7.2417 | 6.4667 |  | 21.5 | 21.5 | 18.8683 |  | 35 | 31.5 | 18.8333 |  | 0.068 | 0.066 | 13.8 |  | 1 | 1 | 104.8333 |  | 18.0667 | 20.3667 | 18.6333 |  | 4 | 3.6 |  | 0.482 | 0.4761 |  | 14.083 | 14.083 | 14.519 |  | 546 | A | A
|  |  |  | Week 4 | [10 empty] | 13.3 | 13.5 | 9.1 | [9 empty] | 7.1283 | 7.4167 | 6.435 |  | 23 | 27.5 | 20.1667 |  | 43.5 | 39.5 | 18 |  | 0.058 | 0.067 | 13.7 |  | 1.6667 | 1.6667 | 113.8333 |  | 18.2167 | 20.4 | 18.9333 |  | 4.1 | 3.6 |  | 0.5375 | 0.666 |  | 14.727 | 14.727 | 15.766 |  | 749 | A | A
[27 empty] | 7.295 | 7.3683 | 6.4333 |  | 25 | 25.5 | 20 |  | 41 | 47.5 | 16.8333 |  | 0.055 | 0.06 | 12.8 |  | 1.1667 | 1.1667 | 117.5 |  | 18.8 | 20.9667 | 19.65 |  | 3.9 | 3.4 |  | 0.5392 | 0.4924 |  | 13.19 | 13.19 | 14.847 |  | 323 | A | A
#DIV/0! | [26 empty] | 7.185 | 7.225 | 6.405 |  | 20 | 21 | 17.6667 |  | 36 | 37.5 | 16 |  | 0.069 | 0.07 | 11.1 |  | 1 | 1 | 121.5 |  | 18.8833 | 20.1667 | 19.75 |  | 3.7 | 3.7 |  | 0.5272 | 0.5082 |  | 10.764 | 10.764 | 13.162 |  | 309 | A | A
#DIV/0! |  |  |  | Average | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.8 | 11.95 | 8.535 |  | 13.3 | 13.5 | 9.1 | 23.65 | 23.8 | 8.705 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.3417 | 7.385 | 6.4333 |  | 21 | 21 | 16.1667 |  | 39.5 | 40 | 15.8333 |  | 0.073 | 0.076 | 10.4 |  | 1 | 1 | 119.1667 |  | 18.7667 | 20.15 | 19.7 |  | 3.9 | 3.8 |  | 0.4964 | 0.4601 |  | 13.266 | 13.266 | 14.026 |  | 529 | A | A
Week 2 | 2.74 | 2.51 | 7.02 | Max | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  | 13.3 | 13.5 | 9.1 | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.435 | 7.405 | 6.44 |  | 21 | 21.5 | 16.3333 |  | 35 | 36 | 15.8333 |  | 0.073 | 0.072 | 11.7 |  | 1.3333 | 1.3333 | 111 |  | 18.7833 | 19.8167 | 19.6333 |  | 4.1 | 3.7 |  | 0.5031 | 0.4362 |  | 14.245 | 14.245 | 15.444 |  | 471 | A | A
|  |  |  | Min | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.1 | 11.3 | 7.27 |  | 13.3 | 13.5 | 9.1 | 21.8 | 21.9 | 7.46 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.9467 | 7.915 | 6.425 |  | 23 | 23 | 16.8333 |  | 33.5 | 34 | 16.1667 |  | 0.083 | 0.09 | 11.7 |  | 1 | 1 | 113.3333 |  | 18.8833 | 19.9 | 19.6667 |  | 4.1 | 3.7 |  | 0.5187 | 0.4514 |  | 13.589 | 13.589 | 15.219 |  | 554 | A | A
[27 empty] | 7.3233 | 7.2883 | 6.4217 |  | 21 | 21 | 17.5 |  | 36 | 36 | 16.3333 |  | 0.08 | 0.083 | 10.8 |  | 1.1667 | 1 | 118 |  | 17.75 | 18.9833 | 18.6167 |  | 4.3 | 4 |  | 0.498 | 0.4126 |  | 13.748 | 13.748 | 14.35 |  | 364 | A | A
[15 empty] | Flow (MG) | [11 empty] | 7.2717 | 7.3333 | 6.4167 |  | 28.5 | 20.5 | 17.8333 |  | 29.5 | 38 | 16.8333 |  | 0.073 | 0.09 | 10.6 |  | 1 | 1 | 114 |  | 17.2 | 18.4833 | 17.8167 |  | 4.4 | 4.2 |  | 0.502 | 0.4683 |  | 13.501 | 13.501 | 15.104 |  | 404 | A | A
[15 empty] | Raw | Comb Fin |  |  | Aluminum |  |  | Phosph Fin1 |  | Phosph Fin2 |  |  | 7.3533 | 7.3517 | 6.4533 |  | 21 | 21.5 | 17.5 |  | 38 | 39 | 17.3333 |  | 0.072 | 0.081 | 10.5 |  | 1.3333 | 1.3333 | 107.8333 |  | 16.8 | 18.6667 | 17.7167 |  | 4.3 | 4.1 |  | 0.4879 | 0.4459 |  | 11.452 | 11.452 | 16.554 |  | 331 | A | A
[14 empty] | 1 | 32.598 | 28.76 |  |  | 1 Filter | 2 Filter | 3 Filter | Total | Ortho | Total | Ortho |  | 7.1983 | 7.29 | 6.3783 |  | 20 | 21.5 | 16.3333 |  | 40.5 | 40.5 | 16.1667 |  | 0.073 | 0.076 | 18 |  | 1.6667 | 1.6667 | 110.1667 |  | 16.55 | 18.1833 | 17.3333 |  | 4.2 | 3.5 |  | 0.4626 | 0.4607 |  | 13.703 | 13.703 | 16.057 |  | 359 | A | A
2.74 | [13 empty] | 2 | 31.179 | 28.134 |  | Week 1 |  |  |  | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.3917 | 7.5383 | 6.5333 |  | 20.5 | 20 | 18.8333 |  | 40 | 39 | 17.1667 |  | 0.07 | 0.064 | 9.85 |  | 2 | 1.8333 | 105.8333 |  | 15.9333 | 17.8833 | 16.65 |  | 4.2 | 4 |  | 0.498 | 0.4839 |  | 11.901 | 11.901 | 14.059 |  | 504 | A | A
7.02 | [13 empty] | 3 | 30.054 | 27.481 |  | Week 2 | 0.036 | 0.036 | 0.029 | [5 empty] | 7.32 | 7.35 | 6.5433 |  | 20.5 | 21 | 18.5 |  | 37 | 36.5 | 19 |  | 0.065 | 0.058 | 14.2 |  | 1.1667 | 1 | 108.5 |  | 15.5167 | 17.95 | 16.3833 |  | 4.1 | 3.9 |  | 0.4432 | 0.478 |  | 11.472 | 11.472 | 16.005 |  | 857 | A | A
Week 3 | [13 empty] | 4 | 31.693 | 28.602 |  | Week 3 |  |  |  | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.1933 | 7.2133 | 6.5333 |  | 21 | 21 | 20 |  | 39 | 40 | 18.6667 |  | 0.06 | 0.063 | 16.1 |  | 1.3333 | 1.3333 | 111.5 |  | 14.7833 | 17.5333 | 15.9 |  | 4.3 | 4 |  | 0.4042 | 0.4245 |  | 12.463 | 12.463 | 15.525 |  | 1616 | A | A
[14 empty] | 5 | 34.632 | 30.493 |  | Week 4 | [8 empty] | 7.265 | 7.2517 | 6.4833 |  | 20 | 20.5 | 18.5 |  | 38.5 | 35 | 18.5 |  | 0.06 | 0.057 | 16.1 |  | 1.5 | 1.5 | 115.6667 |  | 14.5167 | 17.1667 | 15.6333 |  | 3.9 | 3.5 |  | 0.5316 | 0.5166 |  | 11.216 | 11.216 | 15.169 |  | 1112 | A | A
[14 empty] | 6 | 31.46 | 28.037 | [10 empty] | 7.275 | 7.2983 | 6.4567 |  | 21 | 21 | 17.8333 |  | 40 | 41 | 18.5 |  | 0.071 | 0.064 | 15.6 |  | 2 | 2 | 116.3333 |  | 14.3333 | 17.1333 | 15.6667 |  | 4 | 3.8 |  | 0.498 | 0.502 |  | 12.123 | 12.123 | 16.543 |  | 727 | A | A
[14 empty] | 7 | 27.548 | 23.926 | [10 empty] | 7.4217 | 7.4367 | 6.425 |  | 20.5 | 21 | 17.6667 |  | 41 | 43.5 | 17 |  | 0.082 | 0.071 | 15.5 |  | 1.3333 | 1.3333 | 121.1667 |  | 14.4333 | 17.4167 | 15.6667 |  | 4.1 | 4 |  | 0.523 | 0.5365 |  | 11.57 | 11.57 | 15.918 |  | 359 | A | A
[14 empty] | 8 | 27.924 | 27.292 |  | Average | 0.036 | 0.036 | 0.029 | 0.681 | 0.048 | 0.6905 | 0.0445 |  | 7.6567 | 7.5917 | 6.4 |  | 22.5 | 23 | 15.6667 |  | 51 | 51.5 | 15.3333 |  | 0.076 | 0.083 | 14 |  | 1.8333 | 1.6667 | 131.3333 |  | 14.1333 | 16.8167 | 15.0833 |  | 4 | 4 |  | 0.5102 | 0.5082 |  | 14.144 | 14.144 | 16.71 |  | 253 | A | A
[14 empty] | 9 | 33.593 | 29.689 |  | Max | 0.036 | 0.036 | 0.029 | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.4917 | 7.4967 | 6.43 |  | 21 | 21.5 | 13.3333 |  | 43 | 43.5 | 13.5 |  | 0.069 | 0.069 | 12.9 |  | 1.6667 | 1.5 | 126.6667 |  | 13.7 | 16.1833 | 14.8 |  | 4 | 3.9 |  | 0.5455 | 0.501 |  | 12.822 | 12.822 | 14.839 |  | 383 | A | A
#DIV/0! | [13 empty] | 10 | 31.877 | 28.808 |  | Min | 0.036 | 0.036 | 0.029 | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.415 | 7.4967 | 6.32 |  | 21 | 22 | 12.5 |  | 38.5 | 39.5 | 12.3333 |  | 0.063 | 0.069 | 13.1 |  | 1.6667 | 1.5 | 125.8333 |  | 13.3667 | 15.65 | 14.3 |  | 4.2 | 3.9 |  | 0.4899 | 0.4899 |  | 12.027 | 12.027 | 14.577 |  | 355 | A | A
#DIV/0! | [13 empty] | 11 | 33.059 | 28.098 | [10 empty] | 7.55 | 7.6467 | 6.3517 |  | 20.5 | 21 | 11.5 |  | 34 | 37 | 12.8333 |  | 0.066 | 0.063 | 12.7 |  | 1.3333 | 1.3333 | 120 |  | 13.2833 | 15.95 | 14.45 |  | 3.9 | 4 |  | 0.4919 | 0.1886 |  | 12.845 | 12.845 | 16.057 |  | 272 | A | A
Week 4 | [13 empty] | 12 | 31.922 | 28.605 |  | Average 1,2,3 |  | 0.033667 | [6 empty] | 7.6983 | 7.9567 | 6.2983 |  | 20 | 20 | 11.6667 |  | 35 | 36 | 13.5 |  | 0.069 | 0.069 | 10.8 |  | 1 | 1.1667 | 125.1667 |  | 13.3167 | 16.0833 | 14.4833 |  | 3.8 | 3.6 |  | 0.4683 | 0.1568 |  | 12.866 | 12.866 | 15.75 |  | 318 | A | A
[14 empty] | 13 | 31.256 | 28.006 | [10 empty] | 7.68 | 7.5317 | 6.2 |  | 20.5 | 21 | 10.8333 |  | 39.5 | 36 | 12.3333 |  | 0.072 | 0.074 | 9.98 |  | 1 | 1 | 126 |  | 13.6333 | 15.7833 | 14.5833 |  | 4 | 3.9 |  | 0.5274 | 0.2249 |  | 12.29 | 12.29 | 16.02 |  | 305 | A | A
[14 empty] | 14 | 30.76 | 29.76 | [8 empty] | Day |  | 7.985 | 7.7867 | 6.2683 |  | 20.5 | 20.5 | 10.3333 |  | 35 | 35.5 | 13.1667 |  | 0.07 | 0.07 | 9.97 |  | 1.5 | 1.8333 | 126.5 |  | 13.5667 | 15.2 | 14.1667 |  | 3.9 | 4.1 |  | 0.5496 | 0.4544 |  | 12.999 | 12.999 | 17.383 |  | 288 | A | A
[14 empty] | 15 | 29.199 | 25.96 | [8 empty] | 28 |  | 7.3933 | 7.295 | 6.255 |  | 20 | 20.5 | 12 |  | 54 | 56.5 | 15.8333 |  | 0.055 | 0.059 | 9.32 |  | 1 | 1.1667 | 127.6667 |  | 12.7333 | 15.1833 | 14.1167 |  | 4.2 | 4.2 |  | 0.5324 | 0.5062 |  | 11.536 | 11.536 | 15.24 |  | 121 | A | A
[14 empty] | 16 | 31.386 | 27.477 | [8 empty] | 29 |  | 7.315 | 7.2717 | 6.29 |  | 21 | 20.5 | 12.6667 |  | 56.5 | 52.5 | 16.8333 |  | 0.054 | 0.054 | 8.45 |  | 1.1667 | 1.1667 | 131.1667 |  | 12.1167 | 15.0167 | 13.5 |  | 3.8 | 4.1 |  | 0.5207 | 0.502 |  | 12.551 | 12.551 | 16.71 |  | 97 | A | A
#DIV/0! | [13 empty] | 17 | 31.096 | 27.988 | [8 empty] | 30 |  | 7.395 | 7.35 | 6.3067 |  | 18.5 | 18.5 | 12 |  | 56.5 | 58.5 | 18.5 |  | 0.06 | 0.06 | 9.05 |  | 1 | 1.3333 | 131.8333 |  | 12.05 | 14.45 | 13.35 |  | 3.7 | 4.2 |  | 0.5229 | 0.1556 |  | 11.408 | 11.408 | 17.734 |  | 279 | A | A
#DIV/0! | [13 empty] | 18 | 29.153 | 26.385 | [8 empty] | 31 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Average | 2.74 | 2.51 | 7.02 | [10 empty] | 19 | 31.493 | 28.666 | [8 empty] | Avg 1 |  | 7.2125 | 7.2921 | 6.4458 | Avg 1 | 22.1875 | 23.1875 | 19.046 | Avg 1 | 36.5 | 37.75 | 17.4583 | Avg 1 | 0.06275 | 0.06575 | 13.175 | Avg 1 | 1.125 | 1.1875 | 117.1042 | Avg 1 | 18.3958 | 20.5208 | 19.2229 | Avg 1 | 3.9875 | 3.6125 | Avg 1 | 0.50588 | 0.50446 | Avg 1 | 15.8074 | 13.4604 | 14.3802 | Avg 1 | 536.625
Max | 2.74 | 2.51 | 7.02 | [10 empty] | 20 | 30.66 | 27.488 | [8 empty] | Avg 2 |  | 7.4171 | 7.446 | 6.4383 | Avg 2 | 22.1429 | 21.2857 | 17.3095 | Avg 2 | 36.0714 | 37.5 | 16.5476 | Avg 2 | 0.074857 | 0.079429 | 11.8786 | Avg 2 | 1.3571 | 1.3095 | 111.4524 | Avg 2 | 17.4143 | 18.8452 | 18.2048 | Avg 2 | 4.2286 | 3.8857 | Avg 2 | 0.49576 | 0.45129 | Avg 2 | 13.1627 | 13.1627 | 15.2553 | Avg 2 | 426.7143
Min | 2.74 | 2.51 | 7.02 | [10 empty] | 21 | 34.381 | 30.854 | [8 empty] | Avg 3 |  | 7.3798 | 7.3919 | 6.449 | Avg 3 | 20.9375 | 21.375 | 16.75 | Avg 3 | 41 | 41.3125 | 16.6042 | Avg 3 | 0.06825 | 0.06675 | 14.6875 | Avg 3 | 1.5625 | 1.4792 | 119.625 | Avg 3 | 14.3479 | 16.9812 | 15.4292 | Avg 3 | 4.075 | 3.875 | Avg 3 | 0.4932 | 0.49459 | Avg 3 | 12.2296 | 12.2296 | 15.6608 | Avg 3 | 707.75
[14 empty] | 22 | 31.693 | 27.661 | [8 empty] | Avg 4 |  | 6.6271 | 6.6048 | 5.4962 | Avg 4 | 17.625 | 17.75 | 10.125 | Avg 4 | 38.8125 | 39 | 12.875 | Avg 4 | 0.05575 | 0.056125 | 8.7837 | Avg 4 | 1 | 1.125 | 111.0417 | Avg 4 | 11.3375 | 13.4583 | 12.3312 | Avg 4 | 3.4125 | 3.5125 | Avg 4 | 0.45165 | 0.27356 | Avg 4 | 10.8119 | 10.8119 | 14.3618 | Avg 4 | 210
Fin1 | [13 empty] | 23 | 30.618 | 26.604 | [12 empty] | pH | Alk | Hard |  | Turb | Color | Temp |  | Coliform | TRC | Fluoride
CCR Data | High |  | Low | Avg | [9 empty] | 24 | 32.732 | 28.902 | [8 empty] | Avg 1 |  | Raw |  | 6.4458 | 19.046 | 17.4583 |  | 13.175 | 117.1042 | 19.2229 |  | 536.625
Turbidity | 0.092 |  | 0.023 | 0.0526 | [9 empty] | 25 | 32.289 | 28.616 | [8 empty] | Avg 2 |  |  |  | 6.4383 | 17.3095 | 16.5476 |  | 11.8786 | 111.4524 | 18.2048 |  | 426.7143
Fluoride | 0.5496 |  | 0.4042 | 0.50254 | [9 empty] | 26 | 31.833 | 28.31 | [8 empty] | Avg 3 |  |  |  | 6.449 | 16.75 | 16.6042 |  | 14.6875 | 119.625 | 15.4292 |  | 707.75
Sulfate | 25.5 |  | 21.8 | 23.65 | [9 empty] | 27 | 35.89 | 30.382 | [8 empty] | Avg 4 |  |  |  | 5.4962 | 10.125 | 12.875 |  | 8.7837 | 111.0417 | 12.3312 |  | 210
Iron | 0.003 |  | 0.003 | 0.003 | [9 empty] | 28 | 29.571 | 26.776 | [8 empty] | Avg 1 |  | Finished |  | 7.2125 | 22.1875 | 36.5 |  | 0.06275 | 1.125 | 18.3958 |  |  | 3.9875 | 0.50588
Manganes | 0.029 |  | 0.029 | 0.029 | [9 empty] | 29 | 33.423 | 29.261 | [8 empty] | Avg 2 |  |  |  | 7.4171 | 22.1429 | 36.0714 |  | 0.074857 | 1.3571 | 17.4143 |  |  | 4.2286 | 0.49576
pH | 7.985 |  | 7.1283 | 7.3892 | [9 empty] | 30 | 33.203 | 29.142 | [8 empty] | Avg 3 |  |  |  | 7.3798 | 20.9375 | 41 |  | 0.06825 | 1.5625 | 14.3479 |  |  | 4.075 | 0.4932
Color | 2 |  | 1 | 1.3 | [9 empty] | 31 | [10 empty] | Avg 4 |  |  |  | 6.6271 | 17.625 | 38.8125 |  | 0.05575 | 1 | 11.3375 |  |  | 3.4125 | 0.45165
Chloride | 12.5 |  | 11.1 | 11.8
TOC | 2.74 |  | 2.74 | 2.74
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.681
o-phosph |  |  |  | 0.048
Aluminum |  |  |  | 0.033667
Fin2
CCR Data | High |  | Low | Avg
Turbidity | 0.092 |  | 0.023 | 0.047438
Fluoride | 0.666 |  | 0 | 0.43032
Sulfate | 25.7 |  | 21.9 | 23.8
Iron | 0.006 |  | 0.006 | 0.006
Manganes | 0.033 |  | 0.033 | 0.033
pH | 7.9567 |  | 7.2133 | 7.4144
Color | 2 |  | 1 | 1.3167
Chloride | 12.6 |  | 11.3 | 11.95
TOC | 2.51 |  | 2.51 | 2.51
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.6905
o-phosph |  |  |  | 0.0445
Aluminum |  |  |  | 0.033667
TOC Ratio |  |  |  | #REF!
TOC % Removal |  |  |  | #REF!

## LAB
DAILY LAB SHEET
2018-11-01
|  | RAW | [13 empty] | Filtered #1 |  |  |  | Filtered #2 |  |  |  | Filtered #3 |  |  |  | Treated #1 | Treated #2 | Treated #3 | Settled #1 | [11 empty] | Settled #2 | [11 empty] | Settled #3 | [12 empty] | Finished Plant #1 | [16 empty] | Finished Plant #2
|  | pH | Temp | Alk | DO | TOC | DOC | UV-254 | SUVA | Factor | Low | High | Total Coliform | E. coli | Temp. °C | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | pH | pH | pH | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Settled Water Average TOC | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T |  | Decant Flow | Back Wash Water | Backwash Waste Sludge flow | Alum sludge | Raw
1 | [12 empty] | 657 | 10 | [62 empty] | 0.4766 | [6 empty] | A | [9 empty] | 0.4864 | [6 empty] | A |  | 2.103 | 0 | 0 | 0
2 | [12 empty] | 594 | 20 | [62 empty] | 0.5051 | [6 empty] | A | [9 empty] | 0.4694 | [6 empty] | A |  | 2.182 | 0 | 0 | 0
3 | [12 empty] | 586 | <10 | [62 empty] | 0.483 | [6 empty] | A | [9 empty] | 0.4771 | [6 empty] | A |  | 1.574 | 0 | 0 | 0
4 | [12 empty] | 546 | 63 | [62 empty] | 0.482 | [6 empty] | A | [9 empty] | 0.4761 | [6 empty] | A |  | 1.712 | 0 | 0 | 0
5 |  | 6.69 | 18.6 | 25 |  | 12.02 | 11.76 | 0.501 | 4.26 | 23.4731 | 117.3653 | 234.7305 | 749 | 52 |  |  | 3 | 0.09 | 0.42 |  | 2 | 0.054 | 0.44 |  | 2 | 0.053 | 0.26 | 5.9 | 5.94 | 5.94 |  |  |  | 5.98 | 17.6 | 6 | 0.424 | 3.71 | 3.617 | 0.056 | 69.1348 | 1.5482 |  |  |  | 6 | 17.6 | 6 | 0.435 | 3.699 | 3.649 | 0.057 | 69.2263 | 1.5621 |  |  |  | 6.06 | 19.3 | 5 | 0.287 | 3.671 | 3.649 | 0.055 | 69.4592 | 1.5073 | 3.6933 | 7.23 | 18.1 | 3 | 0.055 | 26 | 50 | 4.8 |  |  | 0.5375 |  |  | 3.546 | 3.583 | 0.081 | 2.2607 | A | 7.91 | 19.6 | 4 | 0.067 | 29 | 44 | 7.3 |  |  | 0.666 |  |  | 3.576 | 3.603 | 0.085 | 2.3591 | A |  | 1.63 | 0 | 0 | 0
6 |  | 6.61 | 19.1 | [9 empty] | 323 | 10 |  |  | 2 | 0.058 | 0.4 |  | 2 | 0.067 | 0.35 |  | 2 | 0.066 | 0.65 | 5.87 | 5.87 | 5.87 |  |  |  | 6.95 | 18.4 | 6 | 0.431 | [8 empty] | 5.99 | 18.5 | 6 | 0.415 | [8 empty] | 6.05 | 19.9 | 4 | 0.253 | [6 empty] | 7.42 | 18.6 | 2 | 0.055 | 27 | 47 | 4.5 |  |  | 0.5392 | [6 empty] | A | 7.48 | 21 | 2 | 0.06 | 29 | 52 | 4.2 |  |  | 0.4924 | [6 empty] | A |  | 1.262 | 0 | 0 | 0
7 |  | 6.55 | 19.7 | [9 empty] | 309 | 20 |  |  | 3 | 0.059 | 0.34 |  | 3 | 0.053 | 0.38 |  | 2 | 0.054 | 0.57 | 5.79 | 5.89 | 5.91 |  |  |  | 5.98 | 18.6 | 6 | 0.362 | [8 empty] | 6.01 | 18.6 | 6 | 0.37 | [8 empty] | 6.06 | 20.3 | 6 | 0.291 | [6 empty] | 7.13 | 18.6 | 3 | 0.054 | 29 | 55 | 4.4 |  |  | 0.5272 | [6 empty] | A | 7.2 | 20.3 | 4 | 0.063 | 28 | 52 | 4 |  |  | 0.5082 | [6 empty] | A |  | 0.678 | 0 | 0 | 0
8 | [12 empty] | 529 | 31 | [62 empty] | 0.4964 | [6 empty] | A | [9 empty] | 0.4601 | [6 empty] | A |  | 0.766 | 0 | 0 | 0
9 |  | 6.56 | 19.5 | [9 empty] | 471 | 20 |  |  | 3 | 0.065 | 0.34 |  | 2 | 0.06 | 0.48 |  | 3 | 0.084 | 0.84 | 5.77 | 5.95 | 5.99 |  |  |  | 6.08 | 18.6 | 9 | 0.608 | [8 empty] | 6.08 | 18.5 | 10 | 0.62 | [8 empty] | 6.11 | 20 | 5 | 0.286 | [6 empty] | 7.47 | 18.5 | 3 | 0.06 | 23 | 44 | 4.5 |  |  | 0.5031 | [6 empty] | A | 7.43 | 19.9 | 3 | 0.066 | 31 | 46 | 3.8 |  |  | 0.4362 | [6 empty] | A |  | 0.813 | 0 | 0 | 0
10 | 6.22 | 11 | 12 | 9.84 | 128 | 17.9 | 14.6 | 0.555 | 3.8 | 26.3063 | 131.5315 | 263.0631 | 554 | 41 | [62 empty] | 0.5187 | [6 empty] | A | [9 empty] | 0.4514 | [6 empty] | A |  | 1.162 | 0 | 0 | 0
11 | [12 empty] | 364 | 10 | [62 empty] | 0.498 | [6 empty] | A | [9 empty] | 0.4126 | [6 empty] | A |  | 0.919 | 0 | 0 | 0
12 | [12 empty] | 404 | 10 | [62 empty] | 0.502 | [6 empty] | A | [9 empty] | 0.4683 | [6 empty] | A |  | 0.719 | 0 | 0 | 0
13 | [12 empty] | 331 | 10 | [62 empty] | 0.4879 | [6 empty] | A | [9 empty] | 0.4459 | [6 empty] | A |  | 0.861 | 0 | 0 | 0
14 | [12 empty] | 359 | 63 | [62 empty] | 0.4626 | [6 empty] | A | [9 empty] | 0.4607 | [6 empty] | A |  | 0.952 | 0 | 0 | 0
15 | [12 empty] | 504 | 10 | [62 empty] | 0.498 | [6 empty] | A | [9 empty] | 0.4839 | [6 empty] | A |  | 0.881 | 0 | 0 | 0
16 | [12 empty] | 857 | 52 | [62 empty] | 0.4432 | [6 empty] | A | [9 empty] | 0.478 | [6 empty] | A |  | 1.19 | 0 | 0 | 0
17 | [12 empty] | 1616 | 85 | [62 empty] | 0.4042 | [6 empty] | A | [9 empty] | 0.4245 | [6 empty] | A |  | 0.526 | 0 | 0 | 0
18 | [12 empty] | 1112 | 63 | [62 empty] | 0.5316 | [6 empty] | A | [9 empty] | 0.5166 | [6 empty] | A |  | 0.854 | 0 | 0 | 0
19 | [12 empty] | 727 | 41 | [62 empty] | 0.498 | [6 empty] | A | [9 empty] | 0.502 | [6 empty] | A |  | 0.846 | 0 | 0 | 0
20 |  | 6.71 | 15.3 | [9 empty] | 359 | 10 |  |  | 2 | 0.061 | 0.45 |  | 3 | 0.07 | 0.52 |  | 3 | 0.057 | 0.57 | 5.93 | 5.95 | 5.9 |  |  |  | 6.01 | 14.6 | 9 | 0.585 | [8 empty] | 6.04 | 14.8 | 8 | 0.499 | [8 empty] | 6.03 | 15.3 | 7 | 0.407 | [6 empty] | 7.51 | 14.4 | 3 | 0.06 | 21 | 52 | 4.9 |  |  | 0.523 | [6 empty] | A | 7.48 | 16.9 | 3 | 0.062 | 24 | 55 | 4.5 |  |  | 0.5365 | [6 empty] | A |  | 0.83 | 0 | 0 | 0
21 |  | 6.59 | 14.9 | [9 empty] | 253 | 10 |  |  | 3 | 0.11 | 0.39 |  | 3 | 0.121 | 0.35 |  | 3 | 0.106 | 0.43 | 6 | 5.96 | 5.96 |  |  |  | 6.06 | 13.2 | 11 | 0.639 | [8 empty] | 6.06 | 14.5 | 10 | 0.435 | [8 empty] | 6.11 | 15 | 11 | 0.534 | [6 empty] | 7.69 | 14 | 3 | 0.067 | 25 | 58 | 4.5 |  |  | 0.5102 | [6 empty] | A | 7.66 | 16.3 | 3 | 0.081 | 25 | 59 | 4.3 |  |  | 0.5082 | [6 empty] | A |  | 0.953 | 0 | 0 | 0
22 | [12 empty] | 383 | 41 | [62 empty] | 0.5455 | [6 empty] | A | [9 empty] | 0.501 | [6 empty] | A |  | 1.102 | 0 | 0 | 0
23 | [12 empty] | 355 | 31 | [62 empty] | 0.4899 | [6 empty] | A | [9 empty] | 0.4899 | [6 empty] | A |  | 1.061 | 0 | 0 | 0
24 | [12 empty] | 272 | 30 | [62 empty] | 0.4919 | [6 empty] | A | [9 empty] | 0.1886 | [6 empty] | A |  | 1.088 | 0 | 0 | 0
25 | [12 empty] | 318 | 10 | [62 empty] | 0.4683 | [6 empty] | A | [9 empty] | 0.1568 | [6 empty] | A |  | 1.182 | 0 | 0 | 0
26 |  | 6.43 | 14.6 | [9 empty] | 305 | 10 |  |  | 2 | 0.063 | 0.62 |  | 3 | 0.089 |  |  | 3 | 0.08 | 0.51 | 5.79 |  | 5.83 |  |  |  | 5.95 |  | 8 | 0.54 | [8 empty] | 6.03 | 14.2 | 9 | 0.557 | [8 empty] | 6 | 15 | 10 | 0.697 | [6 empty] | 7.6 | 13.6 | 2 | 0.064 | 21 | 41 | 3.9 |  |  | 0.5274 | [6 empty] | A | 7.49 | 15.9 | 2 | 0.055 | 22 | 36 | 4 |  |  | 0.2249 | [6 empty] | A |  | 1.005 | 0 | 0 | 0
27 | [12 empty] | 288 | 20 | [62 empty] | 0.5496 | [6 empty] | A | [9 empty] | 0.4544 | [6 empty] | A |  | 1.514 | 0 | 0 | 0
28 |  | 6.44 | 13.8 | [9 empty] | 121 | <10 |  |  | 4 | 0.074 | 0.45 |  | 3 | 0.064 | 0.35 |  | 4 | 0.07 | 0.43 | 6.18 | 6.18 | 6.17 |  |  |  | 6.01 | 12.1 | 8 | 0.525 | [8 empty] | 5.98 | 13.7 | 8 | 0.522 | [8 empty] | 5.99 | 13.7 | 12 | 0.7189 | [6 empty] | 7.09 | 12.5 | 4 | 0.051 | 20 | 50 | 4.3 |  |  | 0.5324 | [6 empty] | A | 7.02 | 14.5 | 3 | 0.035 | 20 | 50 | 4.2 |  |  | 0.5062 | [6 empty] | A |  | 1.083 | 0 | 0 | 0
29 |  | 6.54 | 13.2 | 12 |  | 14 | 13.98 | 0.594 | 4.249 | 23.5354 | 117.6768 | 235.3535 | 97 | 10 |  |  | 3 | 0.059 | 0.44 |  | 3 | 0.059 | 0.61 |  | 2 | 0.055 | 0.62 | 6.15 | 6.17 | 6.16 |  |  |  | 6.22 | 11.5 | 6 | 0.385 | 3.878 | 3.783 | 0.06 | 72.3 | 1.586 |  |  |  | 6.28 | 11.9 | 6 | 0.376 | 3.875 | 3.742 | 0.06 | 72.3214 | 1.6034 |  |  |  | 6.27 | 12.9 | 9 | 0.559 | 3.917 | 3.735 | 0.059 | 72.0214 | 1.5797 | 3.89 | 7.35 | 11.9 | 3 | 0.054 | 22 | 55 | 3.8 |  |  | 0.5207 |  |  | 3.668 | 3.724 | 0.077 | 2.0677 | A | 7.27 | 14.8 | 3 | 0.056 | 20 | 50 | 4.1 |  |  | 0.502 |  |  | 3.691 | 3.712 | 0.08 | 2.1552 | A |  | 1.128 | 0 | 0 | 0
30 |  | 6.6 | 12.8 | [9 empty] | 279 | <10 |  |  | 2 | 0.058 | 0.48 |  | 3 | 0.144 | 0.56 |  | 2 | 0.057 | 0.45 | 5.98 | 6.12 | 6.1 |  |  |  | 6.22 | 11.5 | 7 | 0.455 | [8 empty] | 6.28 | 11.8 | 6 | 0.42 | [8 empty] | 6.25 | 12.8 | 7 | 0.443 | [6 empty] | 7.43 | 11.8 | 2 | 0.065 | 22 | 57 | 3.5 |  |  | 0.5229 | [6 empty] | A | 7.4 | 14.3 | 2 | 0.057 | 26 | 48 | 4 |  |  | 0.1556 | [6 empty] | A |  | 1.058 | 0 | 0 | 0
[104 empty] | 0 | 0 | 0
[6 empty] | 14.64 |  |  | 4.103 | 24.4382 | 122.1912 | 244.3824 |  |  |  | #DIV/0! | 2.7 |  |  | #DIV/0! | 2.7 |  |  | #DIV/0! | 2.6 | [5 empty] | #DIV/0! | #DIV/0! | [5 empty] | 3.794 |  |  | 70.7174 |  | #DIV/0! | #DIV/0! | [5 empty] | 3.787 |  |  | 70.7739 |  | #DIV/0! | #DIV/0! | [5 empty] | 3.794 |  |  | 70.7403 |  | 3.7917 | [12 empty] | 3.607 | [16 empty] | 3.6335 |  |  |  |  | Sum | 33.634 | 0 | 0 | 0
[102 empty] | Max | 2.182 | 0 | 0 | 0
[102 empty] | Avg. | 1.1211 | 0 | 0 | 0
Note on DK37: Sum
Note on DK38: Max
Note on DK39: Avg.

## LAB pH
[5 empty] | pH |  |  |  | Meter: | VSTAS40B2
[9 empty] | Probe: | 8102BNUWP
Date | Time | Analyst | Slope | Std. | Lot Number | Sample ID | QC | Temp | PH | Comments
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
SETTLED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | Dup.
# 2
|  |  |  | 10 | 156700
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | D
# 2
SETTLED # 1
# 2
# 3
|  |  |  | 10 | 156700