## NEW (hidden)
THIS PAGE IS FOR SETTING UP A NEW MONTH FROM THE TEMPLET
Change monthly date
to first day of month here : | 2019-04-01
Example 2/1/19
Change file name at : | FILE - Same As - Computer - (F) -
User - BC_LAB - 2019 DATA FILE -
GSWSA BC current MONTH and YEAR
Example GSWSA BC JANUARY 2019
Unprotect the new workbook at : | FILE - PROTECT WORKBOOK -
ENCRYPT WITH PASSWORD :
REMOVE PASSWORD *******
Share the new workbook at : | REVIEW - SHARE WORKBOOK :
ADD A CHECK MARK TO
ALLOW CHANGES

## PLANT CHECK
BULL CREEK PLANT CHECK
SHEET KEY
DATE/TIME |  | 2019-08-12 08:48 |  |  |  |  | OPERATOR |  | JMM/CBW |  |  | FILL IN BEFORE GOING ON PLANT CK.
FILL IN AFTER GOING ON PLANT CK.
Raw Water Pumps |  |  | 2,3,4,6 |  |  | Raw UV | 0.471 | mg/l |  |  |  | FOR MIDNIGHT PLANT OK
Caison Level |  | 12.2 | SCADA Raw flow |  | 41.1 | Raw TOC | 12.3947 | mg/l |  |  |  | THIS IS WHAT YOU TRANSFER TO DAILY
Control Valve% Open Raw |  |  | 62 | Plant 1 | 68 | Plant 2 | 76 | Plant 3 | 50 |  |  | NO NEED TO TYPE IN THESE BLANKS FOR ROUNDS ONLY
MGD
Total Raw Flow |  |  | 41.1 |  | MGD | Fin North1 Flow |  |  | 0 | Master Meter Readings
Plant 1 Raw Flow |  |  | 13.7 |  | MGD | Fin 1 Pumps |  |  |  | South 1 |  | 0
Plant 2 Raw Flow |  |  | 13.7 |  | MGD | Fin Coastal1 Flow |  | 12192 | 17.5565 | South 2 |  | 0
Plant 3 Raw Flow |  |  | 13.7 |  | MGD | Fin 1 Pumps |  | 1,2,3 |  | Conway |  | 0
Total Filter Flow |  |  | 40.5 |  | MGD | Fin Perry 2 Flow |  | 10066 | 14.495 | Perry |  | 0
Plant 1 Filter Flow |  |  | 13 |  | MGD | Fin 2 Pumps |  | 1,2 |  | Raw PLT 1 |  | 0
Plant 2 Filter Flow |  |  | 13 |  | MGD | Fin Conway 2 Flow |  | 4290 | 6.1776 | Raw PLT 2 |  | 0
Plant 3 Filter Flow |  |  | 14.5 |  | MGD | Fin 2 Pumps |  | 1,2 |  | Raw PLT 3 |  | 0
[12 empty] | Flow | Totalizer
Chemical |  |  | DOSE |  | Calculated |  | Measured |  |  | Decant Weir flow |  | 1797 | 0
|  |  | ppm |  | Feed ml/min |  | Feed ml/min |  |  | Sludge Bl.Dwn meter |  | 2.296 | 0
Alum | DESIRED DOSE |  | 80 |  | 4482.64 |  | 6800 |  |  | Thickener Torque 1 |  | 40 | Sludge Judge | 2 | feet
[5 empty] | 4482.64 |  | 6800 |  |  | Thickener Torque 2 |  |  | Sludge Judge
[5 empty] | 4581.28 |  |  |  |  | BACKWASH WATER USED
Tank Levels
[5 empty] | 13447.92 |  | 13600 |  | 80.9047 |  | BULK
[11 empty] | ALUM 1 | ALUM 2 | ALUM 3 | ALUM 4 | ALUM 5
Polymer | Plant 1 | basin 1 | 0.22 |  | 786.7531 |  | 800 |  | 0.22208 | Alum | 4825 | 5131 | 5131 | 2830 | 2830
NUMBER OF BASIN | 2 | basin 2 | 0.25 |  | 894.0376 |  | 910 |  | 0.25262 | Caustic 1 |  | 3106 |  | 8914 | 8914
Polymer | Plant 2 | basin 3 | 0.21 |  | 750.9915 |  | 750 |  | 0.2082 |  |  | CL2 Pre/Post |  | CL2 Post
NUMBER OF BASIN | 2 | basin 4 | 0.22 |  | 786.7531 |  | 800 |  | 0.22208 |  | CL2 | 14 |  | 15
Polymer | Plant 3 | basin 5 | 0.19 |  | 679.4685 |  | 700 |  | 0.19432 | Phosphate |  | 2132
NUMBER OF BASIN | 2 | basin 6 | 0.19 |  | 679.4685 |  | 650 |  | 0.18044 | Fluoride |  | 750
Polymer |  | Thickener | 1400 |  |  |  | 1400 |  | 2.6631 | CAL~FLO |  | 5.58
Fliter Aid |  | plt1 | 0.07 |  | 1724.8636 |  | 1700 |  | 0.068991 | Zinc |  | 2494
Fliter Aid |  | plt2 | 0.07 |  | 1724.8636 |  | 1700 |  | 0.068991 | Polymer |  | 20
Fliter Aid |  | plt3 | 0.06 |  | 1649.0455 |  | 1650 |  | 0.060035 | Ammonia |  | 11.41
Chlorine |  | Pre 1 | 1.9 |  | 554.8997 |  | 560 |  | 1.9175 | Hylime LBS/Day |  | 0
Chlorine |  | Pre 2 | 1.9 |  | 554.8997 |  | 560 |  | 1.9175 | PAC LBS/Day |  | 650
Chlorine |  | Pre 3 | 1.5 |  | 488.6262 |  | 530 |  | 1.627 | BI-SULFITE |  | 990
[10 empty] | FILTER AIDE |  | 0
Caustic |  | Post 1 | 6.3 |  | 561.3784 |  | 570 |  | 6.3968 | ALUM TOWER |  |  | 0
Caustic |  | Post 2 | 10.1 |  | 501.9162 |  | 500 |  | 10.0614
Caustic |  | Pre 1 | 0 |  | 0 |  |  |  | 0
Caustic |  | Pre 2 | 0 |  | 0 |  |  |  | 0
Caustic |  | Pre 3 | 0 |  | 0 |  |  |  | 0
Chemical |  |  |  |  | Calculated |  |  |  | Calculated
|  |  | Plant 1&2 | Plt 3 | Fin 1 ml/min |  |  |  | Fin 2 ml/min
Chlorine |  | Post | 3.9 | 4 | 1997.7025 | 3.8689 | 1980 |  | 1182.4435 | 3.9923 | 1180 |  |  | FOR FREE NH2
Phosphate |  |  | 1.1 |  | 124.41 | 1.1052 | 125 |  | 69.3825 | 1.1098 | 70 |  |  | NH3 FIN 1
Zinc |  |  | 0.1 |  | 17.9947 | 0.10003 | 18 |  | 10.0355 | 0.099646 | 10 |  |  | 275.2953
Ammonia | All Cl2 / | 5.295 | 0.71531 |  | 407.6944 | 0.48249 | 275 |  | 241.315 | 0.75819 | 241 |  |  | NH3 FIN 2
Fluoride |  |  | 0.5 |  | 150.0761 | 0.49975 | 150 |  | 83.6963 | 0.48987 | 82 |  |  | 241.2324
grams/min
| Hylime Pounds per Day |  | 0 | Pump Speed |  |  | PPM | 0 |  |  | PLT 1 | PLT 2 | PLT 3 | RAW |  |  | FIN 1 NH3 | [6 empty] | FIN 2 NH3
220 | PAC Pounds per Day |  | 697.7974 | Pump Speed |  | 690 | PPM | 2.0357 | Cal~flow Pump % |  |  |  |  | 156 |  |  | (((((D14+D15)*8.34*((D46)/E57)/(E58/100)))/7.74)*3785/1440) | [6 empty] | ((((D16*8.34*(E46/E57)/(E58/100)))/7.74)*3785/1440)
[10 empty] | PPM | 0 | 0 | 0 | 9592.034
Free Chlorine on Filters |  |  | PLT 1 | 0.37 |  | 0.42 | PLT 3 | 0.28
Chlorine Strenght % weight/volume |  |  |  |  | Post | 2 | Pre | 0.1 |  | min CT | TARGET CT |  | Stream Current
Post Chlorine Dose / Ammonia Dose |  |  |  | 4.9 |  | Decant Ph |  |  | CT PLT 1 | 0.38 | 0.48 | PLT 1 | -2.06
Aquos Ammonia %Strength |  |  |  | 19.5 |  | Decant cl2 | 0.01 |  | CT PLT 2 | 0.38 | 0.48 | PLT 2 | -0.92
CL2 SPG | 1.17 |  | NH3 SPG | 0.928 |  | Decant pump | 17 |  | CT PLT 3 | 0.36 | 0.46 | PLT 3 | -10
| RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [8 empty] | SETTLED | [8 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
|  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW |  |  | DOSE |  |  |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  |  |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST
TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL |  | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLY THICKENER | DECANT | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC
0:00
43689.3666 | 2,3,4,6 | 62 | 13.7 | 13.7 | 13.7 | 41.1 | 13 | 13 | 14.5 | 40.5 | ,1,2,3 | 17.5565 | 1,2 | 20.6726 | 38.2291 | 2.5877 | 43689.3666 | 80.9047 | 9592.034 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9175 | 1.9175 | 1.627 | 0.22208 | 0.25262 | 0.2082 | 0.22208 | 0.19432 | 0.18044 | 2.6631 | 2 | 0.068991 | 0.068991 | 0.060035 | 1.1052 | 0.49975 | 0.10003 | 3.8689 | 0.48249 | 6.3968 | 1.1098 | 0.48987 | 0.099646 | 3.9923 | 0.75819 | 10.0614
[18 empty] | 13600 | [6 empty] | 0 | 0 | 0 | 560 | 560 | 530 | 800 | 910 | 750 | 800 | 700 | 650 | 1400 |  | 1700 | 1700 | 1650 | 125 | 150 | 18 | 1980 | 275 | 570 | 70 | 82 | 10 | 1180 | 241 | 500
[34 empty] | FINISHED SOUTH 1 |  | END: | 0
[34 empty] | FINISHED SOUTH 2 |  | END: | 0
[34 empty] | FINISHED CONWAY |  | END: | 0
[34 empty] | FINISHED PERRY |  | END: | 0
[34 empty] | RAW PLANT 1 |  | END: | 0
[34 empty] | RAW PLANT 2 |  | END: | 0
[34 empty] | RAW PLANT 3 |  | END: | 0
[34 empty] | DECANT |  | END: | 0
[34 empty] | BLOW DOWN |  | END: | 0
Note on M3: Ctrl+s Will save the sheet
Note on M4: Ctrl+m Will remove all ml/min
Note on M5: Ctrl+o Will remove all Master Meter
Note on D12: PLANT 3 FLOW IS MAX FOR CT CAL. IN LESS BASIN IS DOWN
Note on D20: RAW FLOW X mg/Lx4.18=ml/min Ex. 29.9x61.6x4.18=Total PPM
Note on D26: ((5000*PPM*1440)/(1000*1000*454))/(FLOW*8.34)*#OF BASIN
Note on D30: BASIN 5-6 IS NOT TO BE LOWER THAN 1-4
Note on M39: FROM SCADA TOTAL LBS YESTERDAY
Note on D50: DOSE - AVG FILTER RES PLT 1 & PLT 2 X 8.34 X FIN FLOW PLT 1 PLT 2 /%SOL/(8.34 X SPF) X 3785 / 1440 = ML/MIN
Note on D51: Fin Flow X PPM X 4.35= ML/MIN
Note on D52: PPM X 2.63 / .38 X FLOW= ML/MIM
Note on D53: ML/MIN X 1440 / 3785 / FLOW / 8.34 = PPM
Note on F53: FOLW X 8.34 X ((CL2 mg/l / CL2/NH3) / (NH3% / 100) / 7.74) X 3785 / 1440 = ML/MIN
Note on D54: ML/MIN/2.63*1.9/8.34/FLOW=PPM

## LIME CAL (hidden)
PUMP % | MIL/MIN | FOR CALCULATION FACTOR
5 | 307.4366 | #N/A | #N/A | #N/A | 152
6 | 368.924
7 | 430.4114
8 | 491.8988
9 | 553.3862
10 | 614.8736
11 | 676.361
12 | 737.8484
13 | 799.3358
14 | 860.8232
15 | 922.3106
16 | 983.798
17 | 1045.2854
18 | 1106.7728
19 | 1168.2602
20 | 1229.7476
21 | 1291.235
22 | 1352.7224
23 | 1414.2098
24 | 1475.6972
25 | 1537.1846
26 | 1598.672
27 | 1660.1594
28 | 1721.6468
29 | 1783.1342
30 | 1844.6216
31 | 1906.109
32 | 1967.5964
33 | 2029.0838
34 | 2090.5712
35 | 2152.0586
36 | 2213.546
37 | 2275.0334
38 | 2336.5208
39 | 2398.0082
40 | 2459.4956
41 | 2520.983
42 | 2582.4704
43 | 2643.9578
44 | 2705.4452
45 | 2766.9326
46 | 2828.42
47 | 2889.9074
48 | 2951.3948
49 | 3012.8822
50 | 3074.3696
51 | 3135.857
52 | 3197.3444
53 | 3258.8318
54 | 3320.3192
55 | 3381.8066
56 | 3443.294
57 | 3504.7814
58 | 3566.2688
59 | 3627.7562
60 | 3689.2436
61 | 3750.731
62 | 3812.2184
63 | 3873.7058
64 | 3935.1932
65 | 3996.6806
66 | 4058.168
67 | 4119.6554
68 | 4181.1428
69 | 4242.6302
70 | 4304.1176
71 | 4365.605
72 | 4427.0924
73 | 4488.5798
74 | 4550.0672
75 | 4611.5546
76 | 4673.042
77 | 4734.5294
78 | 4796.0168
79 | 4857.5042
80 | 4918.9916
81 | 4980.479
82 | 5041.9664
83 | 5103.4538
84 | 5164.9412
85 | 5226.4286
86 | 5287.916
87 | 5349.4034
88 | 5410.8908
89 | 5472.3782
90 | 5533.8656
91 | 5595.353
92 | 5656.8404
93 | 5718.3278
94 | 5779.8152
95 | 5841.3026
96 | 5902.79
97 | 5964.2774
98 | 6025.7648
99 | 6087.2522
100 | 6148.7396
101 | 6210.227
102 | 6271.7144
103 | 6333.2018
104 | 6394.6892
105 | 6456.1766
106 | 6517.664
107 | 6579.1514
108 | 6640.6388
109 | 6702.1262
110 | 6763.6136
111 | 6825.101
112 | 6886.5884
113 | 6948.0758
114 | 7009.5632
115 | 7071.0506
116 | 7132.538
117 | 7194.0254
118 | 7255.5128
119 | 7317.0002
120 | 7378.4876
121 | 7439.975
122 | 7501.4624
123 | 7562.9498
124 | 7624.4372
125 | 7685.9246
126 | 7747.412
127 | 7808.8994
128 | 7870.3868
129 | 7931.8742
130 | 7993.3616
131 | 8054.849
132 | 8116.3364
133 | 8177.8238
134 | 8239.3112
135 | 8300.7986
136 | 8362.286
137 | 8423.7734
138 | 8485.2608
139 | 8546.7482
140 | 8608.2356
141 | 8669.723
142 | 8731.2104
143 | 8792.6978
144 | 8854.1852
145 | 8915.6726
146 | 8977.16
147 | 9038.6474
148 | 9100.1348
149 | 9161.6222
150 | 9223.1096
151 | 9284.597
152 | 9346.0844
153 | 9407.5718
154 | 9469.0592
155 | 9530.5466
156 | 9592.034
157 | 9653.5214
158 | 9715.0088
159 | 9776.4962
160 | 9837.9836
161 | 9899.471
162 | 9960.9584
163 | 10022.4458
164 | 10083.9332
165 | 10145.4206
166 | 10206.908
167 | 10268.3954
168 | 10329.8828
169 | 10391.3702
170 | 10452.8576
171 | 10514.345
172 | 10575.8324
173 | 10637.3198
174 | 10698.8072
175 | 10760.2946
176 | 10821.782
177 | 10883.2694
178 | 10944.7568
179 | 11006.2442
180 | 11067.7316
181 | 11129.219
182 | 11190.7064
183 | 11252.1938
184 | 11313.6812
185 | 11375.1686
186 | 11436.656
187 | 11498.1434
188 | 11559.6308
189 | 11621.1182
190 | 11682.6056
191 | 11744.093
192 | 11805.5804
193 | 11867.0678
194 | 11928.5552
195 | 11990.0426
196 | 12051.53
197 | 12113.0174
198 | 12174.5048
199 | 12235.9922
200 | 12297.4796
201 | 12358.967
202 | 12420.4544
203 | 12481.9418
204 | 12543.4292
205 | 12604.9166
206 | 12666.404
207 | 12727.8914
208 | 12789.3788

## CHEM 1 (hidden)
CHEMICAL TRANSFER SHEET PLANT 3 | [7 empty] | CHEMICAL TRANSFER SHEET PLANT 1 and 2
DATE | 2019-08-12 08:48 | TIME | 43689.3666 | OPERATORS |  | JMM/CBW |  | DATE | 2019-08-12 08:48 | TIME | 43689.3666 |  | OPERATORS |  | JMM/CBW
ALUM START 24HR. LEVEL |  |  |  | GAL. |  |  |  |  | PAC TOTAL |  | LB/DAY |  | LIME TOTAL |  |  | GAL/DAY
START |  | GAL. FINISH |  | GAL. |  |  |  |  | AMMONIA |  | GAL/DAY |  | CHLORINE |  |  | GAUDAY
START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER START 24HR. LEVEL |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | TOTAL GAL. POLYMER USED 24HR.
START |  | GAL. FINISH |  | GAL.
| FINISH 24HR. LEVEL |  |  | GAL.
|  |  |  | TOTAL GAL. ALUM USED 24HR. |  |  | GAL. | CAUSTIC START 24HR. LEVEL |  |  |  | GAL.
[8 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
POLYMER START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL.
POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | [8 empty] | TOTAL GAL. CAUSTIC USED 24HR.
TOTAL GAL. POLYMER USED 24HR.
[8 empty] | PHOSPHATE START 24HR. LEVEL |  |  |  | GAL.
CAUSTIC START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. |  | START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | PHOSPHATE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. PHOSPHATE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | ZINC CHLORIDE START 24HR. LEVEL |  |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL. |  |  |  | ZINC CHLORIDE FINISH 24HR. LEVEL |  |  |  |  | GAL. | TOTAL GAL. ZINC USED 24HR.
|  |  |  | TOTAL GAL. CAUSTIC USED 24HR. |  |  | GAL.
[8 empty] | FILTER AIDE START 24HR. LEVEL |  |  |  | GAL.
PRE HYPOCHLORITE START 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER AIDE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. FILTER AIDE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
PRE HYPOCHLORITE FINISH 24HR. LEVEL |  |  |  |  | GAL. | FINISH
|  |  | TOTAL GAL. HYPOCHLORITE USED 24HR. |  |  |  | GAL
FILTER AIDE START 24HR. LEVEL
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER CAUSTIC START 24HR. LEVEL | [5 empty] | GAL.
FILTER AIDE FINISH 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH
[8 empty] | FILTER CAUSTIC FINISH 24HR. LEVEL | [6 empty] | GAL.
LIME START |  |  | FT FINISH |  | FT TOTAL | [6 empty] | TOTAL FILT. CAUSTIC USED 24HR. |  |  |  |  | GAL.

## RUN TIME
WEEKLY DATE | 2019-08-12 08:48 | TIME | 43689.3666 | OPERATOR | JMM/CBW
PUMP AND MOTOR RUN TIME LOG
LOCATION | RUN TIMES |  | LOCATION | RUN TIMES
South Pump #1 |  | Hr | Sludge Bl. Dwn Pump #1 |  | Hr
South Pump #2 |  | Hr | Sludge Bl. Dwn Pump #2 |  | Hr
South Pump #3 |  | Hr | Spill Lagoon Pump #1 |  | Hr
South Pump #4 |  | Hr | Spill Lagoon Pump #2 |  | Hr
North Pump #5 |  | Hr | Sludge Spray Pump #1 |  | Hr
North Pump #6 |  | Hr | Sludge Spray Pump #2 |  | Hr
North Pump #7 |  | Hr | Sludge Spray Pump #3 |  | Hr
North Pump #8 |  | Hr
|  | Boge Compressor Lime Pack |  |  | Hr
Finish Vac Pump #1 |  | Hr | Lime Pack Compressor #1 |  | Hr
Finish Vac Pump #2 |  | Hr
|  |  | Plant #3 Compressor #1 |  | Hr
Service Water Pump #1 |  | Hr | Plant #3 Compressor #2 |  | Hr
Service Water Pump #2 |  | Hr | Boge Compressor Plant #3 |  | Hr
Service Water Pump #3 |  | Hr
|  |  | Finished #2 Pump #1 |  | Hr
Hydro Tank Compressor |  | Hr | Finished #2 Pump #2 |  | Hr
|  |  | Finished #2 Pump #3 |  | Hr
Plant #3 Filter Blower #1 |  | Hr
Plant #3 Filter Blower #2 |  | Hr | Raw Header |  | Psi
Plant #3 Backwash pump #1 |  | Hr | Raw Pump #1 |  | Hr
Plant #3 Backwash pump #2 |  | Hr | Raw Pump #2 |  | Hr
Plant #3 Backwash VFD #1 |  | Hr | Raw Pump #3 |  | Hr
Plant #3 Backwash VFD #2 |  | Hr | Raw Pump #4 |  | Hr
Plant #3 Chemical spill #1 |  | Hr | Raw Pump #5 |  | Hr
Plant #3 Chemical spill #2 |  | Hr | Raw Pump #6 |  | Hr
Plant #3 Biulding spill #1 |  | Hr | COMMENTS
Plant #3 Biulding spill #2 |  | Hr
Plant #1/2 Filter Blower #1 |  | Hr
Plant #1/2 Filter Blower #2 |  | Hr
Plant #1/2 backwash pump #1 |  | Hr
Plant #1/2 backwash pump #2 |  | Hr
Plant #1/2 backwash VFD #1 |  | Hr
Plant #1/2 backwash VFD #2 |  | Hr

## 1
DATE: | 2019-04-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-01 | [23 empty] | DATE: | 2019-04-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43556.0047 | 1,2,3 | 58 | 10.5 | 10.5 | 10.5 | 31.5 | 10 | 10 | 10 | 30 | ,1,3 | 11.3904 | 1,2 | 16.5816 | 27.972 | 11.0146 | 43556.0047 | 55.1092 | 5287.916 | 0 | 723.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4021 | 1.4021 | 1.5134 | 0.19197 | 0.1811 | 0.18835 | 0.12894 | 0.13764 | 0.13764 | 1.4742 | 3 | 0.070168 | 0.070168 | 0.070168 | 1.1034 | 0.49808 | 0.10114 | 3.8011 | 0.71391 | 4.6685 | 1.1034 | 0.50241 | 0.10114 | 4.0038 | 0.73444 | 8.4617 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.413 | 6 | 0.63 | 17 | 10.5 | 0.53274 |  | 6.21 | 0.523 | 7 | 0.58 | 17.8 | 10.5 | 0.53274 | 6.21 | 0.236 | 5 | 0.63 | 17.5 | 10.5 | 0.50889 | [13 empty] | 7.57 | 0.062 | 1 | 4.2 | 16.1 |  |  |  | 7.25 | 0.064 | 1 | 4.1 | 16.1 |  |  |  | 3.7 | 3.5 | 3.9 | [18 empty] | 7100 | [6 empty] | 0 | 0 | 0 | 315 | 315 | 340 | 530 | 500 | 520 | 356 | 380 | 380 | 775 |  | 1330 | 1330 | 1330 | 96 | 115 | 14 | 1535 | 313 | 320 | 48 | 58 | 7 | 790 | 161 | 290 |  | 1:00 | 0.63 | 10.5 | 24.2286 | 15.264 | 6.19 | 17 | 10 | 1.5264 | 15 | 6.5 | 0.41274 | 1:00 | 0.58 | 10.5 | 24.2286 | 14.0526 | 6.21 | 17.8 | 10 | 1.4053 | 15 | 6.5 | 0.41274 | 1:00 | 0.63 | 10.5 | 25.7143 | 16.2 | 6.21 | 17.5 | 10 | 1.62 | 15 | 6.5 | 0.38889
2:00 | [72 empty] | 43556.4654 | 1,2,3,5 | 41 | 10.8 | 10.8 | 10.8 | 32.4 | 10.3 | 10.3 | 10.3 | 30.9 | ,1,3 | 11.988 | 1,3 | 16.6176 | 28.6056 | 11 | 43556.4654 | 55.0877 | 5287.916 | 0 | 792.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4045 | 1.4045 | 1.5126 | 0.19368 | 0.19368 | 0.19544 | 0.13205 | 0.14086 | 0.14086 | 1.4742 | 3 | 0.07171 | 0.07171 | 0.070429 | 1.1159 | 0.5046 | 0.098195 | 3.7659 | 0.68648 | 4.3201 | 1.1159 | 0.5046 | 0.098195 | 4.0031 | 0.70862 | 8.2152 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.67 | 19 | 20 | 9.91 | 90 | 138 | 16.9 | 0.351 |  | 6.22 | 10 | 0.048 | 6.17 | 11 |  | 6.1 | 10 | [8 empty] | 0.04 | [14 empty] | 0.022 | 1 | 0.36 |  | 0.039 | 0.031 | 1 | 0.44 |  | 0.028 | 1 | 0.46 | [38 empty] | 7300 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 350 | 550 | 550 | 555 | 375 | 400 | 400 | 775 |  | 1400 | 1400 | 1375 | 100 | 120 | 14 | 1520 | 310 | 305 | 50 | 60 | 7 | 800 | 160 | 290 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43556.8619 | 2,3,5 | 85 | 10.4 | 10.4 | 10.4 | 31.2 | 9.9 | 9.9 | 9.9 | 29.7 | ,1,3 | 11.988 | 1,3 | 16.4261 | 28.4141 | 0.96192 | 43556.8619 | 54.8555 | 5164.9412 | 0 | 792.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5062 | 1.5062 | 1.5287 | 0.19747 | 0.19747 | 0.19747 | 0.14042 | 0.14957 | 0.14993 | 1.4742 | 1 | 0.070344 | 0.070344 | 0.070077 | 1.103 | 0.49874 | 0.10216 | 3.8089 | 0.705 | 4.5978 | 1.0914 | 0.49874 | 0.10216 | 4.0219 | 0.7096 | 8.724 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.46 | 0.06 | 1 | 4.1 | 16.1 |  |  |  | 7.36 | 0.062 | 1 | 4.2 | 15.9 |  |  |  | 3.9 | 3.5 | 3.7 | [18 empty] | 7000 | [6 empty] | 0 | 0 | 0 | 335 | 335 | 340 | 540 | 540 | 540 | 384 | 409 | 410 | 775 |  | 1320 | 1320 | 1315 | 95 | 114 | 14 | 1510 | 306 | 312 | 47 | 57 | 7 | 760 | 154 | 296 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43556.9716 | 2,3,5 | 85 | 10.1 | 10.1 | 10.1 | 30.3 | 9.6 | 9.6 | 9.6 | 28.8 | ,1,3 | 11.988 | 1,3 | 16.4261 | 28.4141 | 0.96192 | 43556.9716 | 55.2745 | 5164.9412 | 0 | 792.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5069 | 1.5069 | 1.5997 | 0.19957 | 0.19957 | 0.19957 | 0.13932 | 0.15062 | 0.14874 | 1.4742 | 1 | 0.070069 | 0.070069 | 0.070069 | 1.1375 | 0.51432 | 0.10535 | 3.8226 | 0.71277 | 4.7415 | 1.1255 | 0.51432 | 0.10535 | 4.0078 | 0.71277 | 8.9966 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.63 | 19 | 18 | 10.1 | 85 | 141 | 16.8 | 0.338 |  | 6.13 | 10 | 0.048 | 6.14 | 10 |  | 6.11 | 11 | [8 empty] | 0.046 | [14 empty] | 0.018 | 1 | 0.34 |  | 0.04 | 0.044 | 1 | 0.38 |  | 0.028 | 1 | 0.49 | [38 empty] | 6850 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 345 | 530 | 530 | 530 | 370 | 400 | 395 | 775 |  | 1275 | 1275 | 1275 | 95 | 114 | 14 | 1470 | 300 | 312 | 47 | 57 | 7 | 734 | 150 | 296 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.039 | [9 empty] | 6.21 | 0.577 | 6 | 0.73 | 16.2 | 10.8 | 0.54453 |  | 6.19 | 0.612 | 7 | 0.63 | 16.7 | 10.8 | 0.54453 | 6.21 | 0.546 | 6 | 0.78 | 16.8 | 10.8 | 0.52 |  |  |  | 0.006 |  |  |  |  | 0.018 |  |  |  | 0.009 | 7.2 | 0.049 | 1 | 3.9 | 15.9 | 20 | 31 | 0.015 | 7.24 | 0.054 | 1 | 3.9 | 15.7 | 20 | 30 | 0.012 | 3.9 | 3.5 | 3.4 | [55 empty] | 9:00 | 0.73 | 10.8 | 23.5556 | 17.1956 | 6.21 | 16.2 | 10 | 1.7196 | 15 | 6.5 | 0.42453 | 9:00 | 0.63 | 10.8 | 23.5556 | 14.84 | 6.19 | 16.7 | 10 | 1.484 | 15 | 6.5 | 0.42453 | 9:00 | 0.78 | 10.8 | 25 | 19.5 | 6.21 | 16.8 | 10 | 1.95 | 15 | 6.5 | 0.4
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.61 | 20 | 18 | 10 | 86 | 140 | 16.4 | 0.334 |  | 6.15 | 12 | 0.045 | 6.2 | 12 |  | 6.12 | 12 | [8 empty] | 0.042 | [14 empty] | 0.018 | 1 | 0.32 |  | 0.042 | 0.02 | 1 | 0.34 |  | 0.062 | 1 | 0.52 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.18 | 0.399 | 5 | 0.69 | 15.9 | 10.8 | 0.54453 |  | 6.21 | 0.4 | 5 | 0.59 | 16.7 | 10.8 | 0.54453 | 6.21 | 0.289 | 4 | 0.67 | 16.5 | 10.8 | 0.52 | [13 empty] | 7.12 | 0.05 | 1 | 4.2 | 15.8 |  |  |  | 7.16 | 0.056 | 1 | 3.8 | 16.3 |  |  |  | 3.9 | 3.5 | 3.6 | [55 empty] | 13:00 | 0.69 | 10.8 | 23.5556 | 16.2533 | 6.18 | 15.9 | 10 | 1.6253 | 15 | 6.5 | 0.42453 | 13:00 | 0.59 | 10.8 | 23.5556 | 13.8978 | 6.21 | 16.7 | 10 | 1.3898 | 15 | 6.5 | 0.42453 | 13:00 | 0.67 | 10.8 | 25 | 16.75 | 6.21 | 16.5 | 10 | 1.675 | 15 | 6.5 | 0.4
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.6 | 20 | 18 | 10.1 | 80 | 139 | 16.5 | 0.326 |  | 6.14 | 11 | 0.044 | 6.16 | 12 |  | 6.12 | 11 | [8 empty] | 0.041 | [14 empty] | 0.018 | 1 | 0.33 |  | 0.041 | 0.032 | 1 | 0.34 |  | 0.051 | 1 | 0.49 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.16 | 0.055 | 1 | 4.2 | 15.7 |  |  |  | 7.24 | 0.054 | 1 | 3.8 | 16.2 |  |  |  | 4 | 3.6 | 3.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.52 | 19 | 19 | 10.1 | 87 | 139 | 16.5 | 0.346 |  | 6.1 | 10 | 0.046 | 6.15 | 10 |  | 6.15 | 10 | [8 empty] | 0.038 | [14 empty] | 0.018 | 1 | 0.32 |  | 0.036 | 0.031 | 1 | 0.34 |  | 0.045 | 1 | 0.51 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.037 | [9 empty] | 6.19 | 0.357 | 5 | 0.66 | 16.5 | 10.4 | 0.52881 |  | 6.2 | 0.459 | 6 | 0.49 | 17 | 10.5 | 0.53274 | 6.2 | 0.225 | 5 | 0.68 | 17 | 10.4 | 0.50519 |  |  |  | 0.012 | [9 empty] | 7.52 | 0.064 | 1 | 4.5 | 15.5 | 20 | 32 | 0.015 | 7.41 | 0.062 | 1 | 4.3 | 15.8 | 20 | 31 | 0.012 | 4.1 | 3.5 | 4 | [55 empty] | 21:00 | 0.66 | 10.4 | 24.4615 | 16.1446 | 6.19 | 16.5 | 10 | 1.6145 | 15 | 6.5 | 0.40881 | 21:00 | 0.49 | 10.5 | 24.2286 | 11.872 | 6.2 | 17 | 10 | 1.1872 | 15 | 6.5 | 0.41274 | 21:00 | 0.68 | 10.4 | 25.9615 | 17.6538 | 6.2 | 17 | 10 | 1.7654 | 15 | 6.5 | 0.38519
22:00 | [72 empty] | DOSE |  | TOTAL | 41.8 | 41.8 | 41.8 | 125.4 | 39.8 | 39.8 | 39.8 | 119.4 | 0 | 47.3544 | 0 | 66.0514 | 113.4058 | 23.9384 | TOTAL | 220.3269 | 20905.7144 | 0 | 3102.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8198 | 5.8198 | 6.1544 | 0.78268 | 0.77182 | 0.78082 | 0.54074 | 0.57868 | 0.57716 | 5.897 | 8 | 0.28229 | 0.28229 | 0.28074 | 4.4598 | 2.0157 | 0.40685 | 15.1986 | 2.8182 | 18.3278 | 4.4362 | 2.0201 | 0.40685 | 16.0366 | 2.8654 | 34.3975 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.79 | 19 | 19 | 10.1 | 84 | 139 | 16.4 | 0.33 |  | 6.18 | 10 | 0.051 | 6.15 | 10 |  | 6.08 | 10 | [8 empty] | 0.037 | [14 empty] | 0.02 | 1 | 0.3 |  | 0.038 | 0.021 | 1 | 0.32 |  | 0.042 | 1 | 0.48 | [22 empty] | AVERAGE | 10.45 | 10.45 | 10.45 | 31.35 | 9.95 | 9.95 | 9.95 | 29.85 |  | 11.8386 |  | 16.5128 | 28.3514 | 5.9846 | AVERAGE | 55.0817 | 5226.4286 |  | 775.5066 | 0 | 0 | 0 | 0 | 0 | 0 | 1.455 | 1.455 | 1.5386 | 0.19567 | 0.19295 | 0.19521 | 0.13519 | 0.14467 | 0.14429 | 1.4742 | 2 | 0.070573 | 0.070573 | 0.070186 | 1.115 | 0.50393 | 0.10171 | 3.7996 | 0.70454 | 4.582 | 1.1091 | 0.50502 | 0.10171 | 4.0092 | 0.71636 | 8.5994 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.82 | 116 | 112 | 60.31 | 512 | 836 | 99.5 | 2.025 | 0.076 | 36.92 | 63 | 0.282 | 36.97 | 65 | 0 | 36.68 | 64 | 0 | 24.77 | 1.746 | 22 | 2.71 | 65.6 | 42.5 | 2.1506 | 0.244 | 24.81 | 1.994 | 25 | 2.29 | 68.2 | 42.6 | 2.1545 | 24.83 | 1.296 | 20 | 2.76 | 67.8 | 42.5 | 2.0541 | 0.114 | 6 | 1.97 | 0.018 | 0.236 | 0.179 | 6 | 2.16 | 0.018 | 0.256 | 6 | 2.95 | 0.009 | 44.03 | 0.34 | 6 | 25.1 | 95.1 | 40 | 63 | 0.03 | 43.66 | 0.352 | 6 | 24.1 | 96 | 40 | 61 | 0.024 | 23.5 | 21.1 | 22.2 |  |  | MINIMUM | 10.1 | 10.1 | 10.1 | 30.3 | 9.6 | 9.6 | 9.6 | 28.8 |  | 11.3904 |  | 16.4261 | 27.972 | 0.96192 | MINIMUM | 54.8555 | 5164.9412 |  | 723.1718 | [6 empty] | 1.4021 | 1.4021 | 1.5126 | 0.19197 | 0.1811 | 0.18835 | 0.12894 | 0.13764 | 0.13764 | 1.4742 | 1 | 0.070069 | 0.070069 | 0.070069 | 1.103 | 0.49808 | 0.098195 | 3.7659 | 0.68648 | 4.3201 | 1.0914 | 0.49874 | 0.098195 | 4.0031 | 0.70862 | 8.2152 |  | MIN | 0.63 | 10.5 | 24.2286 | 15.264 | 6.19 | 17 | 10 | 1.5264 |  |  |  | MIN | 0.49 | 10.5 | 24.2286 | 11.872 | 6.2 | 17 | 10 | 1.1872 |  |  |  | MIN | 0.63 | 10.5 | 25.7143 | 16.2 | 6.21 | 17.5 | 10 | 1.62 |  |  |  | 1.1872
AVERAGE | 6.6367 | 19.3333 | 18.6667 | 10.0517 | 85.3333 | 139.3333 | 16.5833 | 0.3375 | 0.038 | 6.1533 | 10.5 | 0.047 | 6.1617 | 10.8333 |  | 6.1133 | 10.6667 |  | 6.1925 | 0.4365 | 5.5 | 0.6775 | 16.4 | 10.625 | 0.53765 | 0.040667 | 6.2025 | 0.4985 | 6.25 | 0.5725 | 17.05 | 10.65 | 0.53863 | 6.2075 | 0.324 | 5 | 0.69 | 16.95 | 10.625 | 0.51352 | 0.019 | 1 | 0.32833 | 0.009 | 0.039333 | 0.029833 | 1 | 0.36 | 0.018 | 0.042667 | 1 | 0.49167 |  | 7.3383 | 0.056667 | 1 | 4.1833 | 15.85 | 20 | 31.5 | 0.015 | 7.2767 | 0.058667 | 1 | 4.0167 | 16 | 20 | 30.5 | 0.012 | 3.9167 | 3.5167 | 3.7 |  |  | MAXIMUM | 10.8 | 10.8 | 10.8 | 32.4 | 10.3 | 10.3 | 10.3 | 30.9 |  | 11.988 |  | 16.6176 | 28.6056 | 11.0146 | MAXIMUM | 55.2745 | 5287.916 |  | 792.9515 | [6 empty] | 1.5069 | 1.5069 | 1.5997 | 0.19957 | 0.19957 | 0.19957 | 0.14042 | 0.15062 | 0.14993 | 1.4742 | 3 | 0.070573 | 0.070573 | 0.070186 | 1.1375 | 0.51432 | 0.10535 | 3.8226 | 0.71391 | 4.7415 | 1.1255 | 0.51432 | 0.10535 | 4.0219 | 0.73444 | 8.9966
MINIMUM | 6.52 | 19 | 18 | 9.91 | 80 | 138 | 16.4 | 0.326 | 0.037 | 6.1 | 10 | 0.044 | 6.14 | 10 |  | 6.08 | 10 |  | 6.18 | 0.357 | 5 | 0.63 | 15.9 | 10.4 | 0.52881 | 0.037 | 6.19 | 0.4 | 5 | 0.49 | 16.7 | 10.5 | 0.53274 | 6.2 | 0.225 | 4 | 0.63 | 16.5 | 10.4 | 0.50519 | 0.018 | 1 | 0.3 | 0.006 | 0.036 | 0.02 | 1 | 0.32 | 0.018 | 0.028 | 1 | 0.46 |  | 7.12 | 0.049 | 1 | 3.9 | 15.5 | 20 | 31 | 0.015 | 7.16 | 0.054 | 1 | 3.8 | 15.7 | 20 | 30 | 0.012 | 3.7 | 3.5 | 3.4 | [15 empty] | Ml/Min |  | TOTAL | 28250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 1300 | 1375 | 2150 | 2120 | 2145 | 1485 | 1589 | 1585 | 3100 | 0 | 5325 | 5325 | 5295 | 386 | 463 | 56 | 6035 | 1229 | 1249 | 192 | 232 | 28 | 3084 | 625 | 1172
MAXIMUM | 6.79 | 20 | 20 | 10.1 | 90 | 141 | 16.9 | 0.351 | 0.039 | 6.22 | 12 | 0.051 | 6.2 | 12 |  | 6.15 | 12 |  | 6.21 | 0.577 | 6 | 0.73 | 17 | 10.8 | 0.54453 | 0.046 | 6.21 | 0.612 | 7 | 0.63 | 17.8 | 10.8 | 0.54453 | 6.21 | 0.546 | 6 | 0.78 | 17.5 | 10.8 | 0.52 | 0.022 | 1 | 0.36 | 0.012 | 0.042 | 0.044 | 1 | 0.44 | 0.018 | 0.062 | 1 | 0.52 |  | 7.57 | 0.064 | 1 | 4.5 | 16.1 | 20 | 32 | 0.015 | 7.41 | 0.064 | 1 | 4.3 | 16.3 | 20 | 31 | 0.012 | 4.1 | 3.6 | 4 | [17 empty] | AVERAGE | 7062.5 | [9 empty] | 325 | 325 | 343.75 | 537.5 | 530 | 536.25 | 371.25 | 397.25 | 396.25 | 775 |  | 1331.25 | 1331.25 | 1323.75 | 96.5 | 115.75 | 14 | 1508.75 | 307.25 | 312.25 | 48 | 58 | 7 | 771 | 156.25 | 293
# 0F DAYS IN THE MONTH |  | 30 |  | TOTAL AVG COAG PH: |  |  |  | 6.1428 |  | TOTAL AVG COAG ALK: |  |  |  | 10.6667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.612 |  |  |  |  | TOTAL AVG SETTLED PH: | [6 empty] | 6.2008 | TOTAL MIN SETTLED DISEN.: | [7 empty] | 0.49 | TOTAL FILTER MAX NTU | [6 empty] | 0.062 | [20 empty] | Pump Station MIN |  | 3.4 | [17 empty] | MINIMUM | 6850 | [9 empty] | 315 | 315 | 340 | 530 | 500 | 520 | 356 | 380 | 380 | 775 |  | 1275 | 1275 | 1275 | 95 | 114 | 14 | 1470 | 300 | 305 | 47 | 57 | 7 | 734 | 150 | 290
[90 empty] | MAXIMUM | 7300 | [9 empty] | 335 | 335 | 350 | 550 | 550 | 555 | 384 | 409 | 410 | 775 |  | 1400 | 1400 | 1375 | 100 | 120 | 14 | 1535 | 313 | 320 | 50 | 60 | 7 | 800 | 161 | 296
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.178 |  | TOTAL MGD: |  | 0.011 |  |  | FINISHED SOUTH 1 |  | START: | 23827590 |  | END: | 23827601 |  |  | Alum | 4858 | 6194 | 6194 | 8745 | 8745 | 0 | [44 empty] | 0.49 | 10.5 | 24.2286 | 11.872 | 6.2 | 17 | 10 | 1.1872
[73 empty] | FINISHED 2 | 13.66 |  | TOTAL MGD: |  | 13.167 |  |  | FINISHED SOUTH 2 |  | START: | 44833633 |  | END: | 44846800 |  |  | Caustic | 7062 | 6140 | 6140
[73 empty] | TOTAL RAW | 31.023 |  | TOTAL MGD: |  | 3.825 |  |  | FINISHED CONWAY |  | START: | 10638214 |  | END: | 10642039 |  |  | Hypochlorite | 14 |  | 33
[76 empty] | TOTAL MGD: |  | 9.835 |  |  | FINISHED PERRY |  | START: | 34678498 |  | END: | 34688333 |  |  | Phosphate | 1550
[76 empty] | TOTAL MGD: |  | 10.227 |  |  | RAW PLANT 1 |  | START: | 31780516 |  | END: | 31790743 |  |  | Fluoride | 2900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.351 |  |  | RAW PLANT 2 |  | START: | 31742266 |  | END: | 31752617 |  |  | Cal~Flo | 12.77 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.445 |  |  | RAW PLANT 3 |  | START: | 8375461 |  | END: | 8385906 |  |  | Zinc | 2683
[76 empty] | TOTAL MGD: |  | 0.555 |  |  | DECANT |  | START: | 1938000 |  | END: | 1938555 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 0.83503 |  |  | BLOW DOWN |  | START: | 9240.034 |  | END: | 9240.869 |  |  | NH3 | 11.08 |  | BI-SUL | 1100
[90 empty] | Lime | 0 |  | FILTER AIDE | 1 | [25 empty] | 1.0202
[82 empty] | BACKWASH WATER USED : |  |  |  |  | 0 |  |  | Cabon | 500
[91 empty] | FINISHED SOUTH 1 |  | END: | 23827601
[91 empty] | FINISHED SOUTH 2 |  | END: | 44846800
[91 empty] | FINISHED CONWAY |  | END: | 10642039
[91 empty] | FINISHED PERRY |  | END: | 34688333
[91 empty] | RAW PLANT 1 |  | END: | 31790743
[91 empty] | RAW PLANT 2 |  | END: | 31752617
[91 empty] | RAW PLANT 3 |  | END: | 8385906
[91 empty] | DECANT |  | END: | 1938555
[91 empty] | BLOW DOWN |  | END: | 9240.869
Note on AX36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 2
DATE: | 2019-04-02 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 3 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 3 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 3 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CBW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-02 | [23 empty] | DATE: | 2019-04-02
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-02 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43557.0088 | 2,3,5 | 85 | 10.1 | 10.1 | 10.1 | 30.3 | 9.6 | 9.6 | 9.6 | 28.8 | 1,3,1,3 | 10.345 | 1,3 | 17.3851 | 27.7301 | 0.96192 | 43557.0088 | 56.0814 | 5164.9412 | 0 | 792.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5069 | 1.5069 | 1.5997 | 0.19957 | 0.19957 | 0.19957 | 0.13932 | 0.15062 | 0.14874 | 1.4742 | 1 | 0.070069 | 0.070069 | 0.070069 | 1.1375 | 0.51432 | 0.10535 | 3.8226 | 0.71277 | 4.7415 | 1.1255 | 0.51432 | 0.10535 | 4.0078 | 0.71277 | 8.9966 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.22 | 0.418 | 6 | 0.74 | 16.2 | 10.1 | 0.51701 |  | 6.17 | 0.625 | 6 | 0.62 | 17 | 10.1 | 0.51701 | 6.18 | 0.221 | 5 | 0.68 | 16.8 | 10.1 | 0.49407 | [13 empty] | 7.56 | 0.061 | 1 | 4.3 | 15.7 |  |  |  | 7.44 | 0.059 | 1 | 4 | 15.6 |  |  |  | 4 | 3.4 | 4 | [18 empty] | 6950 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 345 | 530 | 530 | 530 | 370 | 400 | 395 | 775 |  | 1275 | 1275 | 1275 | 95 | 114 | 14 | 1470 | 300 | 312 | 47 | 57 | 7 | 734 | 150 | 296 |  | 1:00 | 0.74 | 10.1 | 25.1881 | 18.6392 | 6.22 | 16.2 | 10 | 1.8639 | 15 | 6.5 | 0.39701 | 1:00 | 0.62 | 10.1 | 25.1881 | 15.6166 | 6.17 | 17 | 10 | 1.5617 | 15 | 6.5 | 0.39701 | 1:00 | 0.68 | 10.1 | 26.7327 | 18.1782 | 6.18 | 16.8 | 10 | 1.8178 | 15 | 6.5 | 0.37407
2:00 | [72 empty] | 43557.1233 | 2,3,5 | 85 | 9.5 | 9.5 | 9.5 | 28.5 | 9 | 9 | 9 | 27 | 1,3,1,3 | 10.345 | 1,3 | 17.3851 | 27.7301 | 0.96192 | 43557.1233 | 54.905 | 4673.042 | 0 | 792.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.4838 | 1.4838 | 0.20016 | 0.20016 | 0.20016 | 0.099282 | 0.15212 | 0.15212 | 1.4742 | 1 | 0.070344 | 0.070344 | 0.070344 | 1.0983 | 0.51011 | 0.096324 | 3.802 | 0.7096 | 4.6361 | 1.0728 | 0.50049 | 0.096324 | 4.0173 | 0.7096 | 8.7859 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.68 | 19 | 19 | 10.3 | 78 | 138 | 16.5 | 0.338 |  | 6.14 | 10 | 0.05 | 6.13 | 11 |  | 6.07 | 11 | [8 empty] | 0.041 | [14 empty] | 0.023 | 1 | 0.39 |  | 0.039 | 0.029 | 1 | 0.31 |  | 0.038 | 1 | 0.56 | [38 empty] | 6400 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 500 | 500 | 500 | 248 | 380 | 380 | 775 |  | 1200 | 1200 | 1200 | 86 | 106 | 12 | 1370 | 280 | 286 | 42 | 52 | 6 | 690 | 140 | 271 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43557.353 | 2,3,5 | 85 | 9.5 | 9.5 | 9.5 | 28.5 | 9 | 9 | 9 | 27 | 1,3,1,3 | 11.016 | 1,3 | 15.1992 | 26.2152 | 0.96192 | 43557.353 | 54.2187 | 4796.0168 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4096 | 1.4838 | 1.4838 | 0.20016 | 0.20016 | 0.17614 | 0.14412 | 0.13611 | 0.15212 | 1.4742 | 2.5 | 0.067999 | 0.067413 | 0.067413 | 1.0728 | 0.50049 | 0.096324 | 3.7066 | 0.60823 | 4.6361 | 1.0728 | 0.50049 | 0.096324 | 3.7939 | 0.65892 | 8.7859 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.42 | 0.058 | 1 | 4.5 | 15.6 |  |  |  | 7.36 | 0.06 | 1 | 4.1 | 15.4 |  |  |  | 3.8 | 3.4 | 3.4 | [18 empty] | 6320 | [6 empty] | 0 | 0 | 0 | 285 | 300 | 300 | 500 | 500 | 440 | 360 | 340 | 380 | 775 |  | 1160 | 1150 | 1150 | 84 | 104 | 12 | 1360 | 240 | 286 | 42 | 52 | 6 | 640 | 130 | 271 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43557.6115 | 2,3,5 | 85 | 8.7 | 8.7 | 8.7 | 26.1 | 8.2 | 8.2 | 8.2 | 24.6 | 1,3,1,3 | 9.7128 | 1,3 | 13.8139 | 23.5267 | 0.96192 | 43557.6115 | 55.8319 | 4488.5798 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5199 | 1.5199 | 1.5199 | 0.19234 | 0.19671 | 0.19234 | 0.14863 | 0.153 | 0.14426 | 1.4077 | 2.5 | 0.070129 | 0.069486 | 0.070773 | 1.1214 | 0.50178 | 0.10572 | 3.7369 | 0.63976 | 4.8927 | 1.1214 | 0.50706 | 0.12334 | 3.8879 | 0.63976 | 9.4295 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.49 | 19 | 17 | 10.1 | 81 | 140 | 16.2 | 0.331 |  | 6.08 | 10 | 0.047 | 6.11 | 9 |  | 6.03 | 10 | [8 empty] | 0.042 | [14 empty] | 0.045 | 1 | 0.28 |  | 0.044 | 0.02 | 1 | 0.24 |  | 0.037 | 1 | 0.55 | [38 empty] | 5960 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 280 | 440 | 450 | 440 | 340 | 350 | 330 | 740 |  | 1090 | 1080 | 1100 | 80 | 95 | 12 | 1250 | 230 | 275 | 40 | 48 | 7 | 600 | 115 | 265 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43557.8474 | 2,3,5 | 33 | 8.2 | 8.3 | 8.3 | 24.8 | 7.7 | 7.8 | 7.8 | 23.3 | 1,3,1,3 | 8.172 | 1,3 | 14.724 | 22.896 | 2.3112 | 43557.8474 | 55.2094 | 4304.1176 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.503 | 1.4838 | 1.4838 | 0.19943 | 0.19943 | 0.19703 | 0.14892 | 0.14892 | 0.14892 | 1.4077 | 1 | 0.070572 | 0.069667 | 0.069667 | 1.0975 | 0.50297 | 0.10254 | 3.8055 | 0.72105 | 4.9509 | 1.12 | 0.49975 | 0.09262 | 3.9992 | 0.73105 | 9.4268 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.16 | 0.627 | 6 | 0.61 | 15.5 | 9.3 | 0.48557 |  | 6.13 | 0.633 | 6 | 0.6 | 16 | 9.3 | 0.48557 | 6.16 | 0.527 | 6 | 0.65 | 16.6 | 9.4 | 0.46815 |  |  |  | 0.01 |  |  |  |  | 0.015 |  |  |  | 0.009 | 7.12 | 0.05 | 1 | 4.3 | 15.3 | 20 | 38 | 0.018 | 7.14 | 0.059 | 1 | 3.8 | 15.1 | 20 | 35 | 0.018 | 4 | 3.4 | 4.1 | [18 empty] | 5600 | [6 empty] | 0 | 0 | 0 | 260 | 260 | 260 | 430 | 430 | 430 | 325 | 325 | 325 | 740 |  | 1030 | 1030 | 1030 | 74 | 90 | 11 | 1203 | 245 | 263 | 38 | 45 | 5 | 612 | 125 | 252 |  | 9:00 | 0.61 | 9.3 | 27.3548 | 16.6865 | 6.16 | 15.5 | 10 | 1.6686 | 15 | 6.5 | 0.36557 | 9:00 | 0.6 | 9.3 | 27.3548 | 16.4129 | 6.13 | 16 | 10 | 1.6413 | 15 | 6.5 | 0.36557 | 9:00 | 0.65 | 9.4 | 28.7234 | 18.6702 | 6.16 | 16.6 | 10 | 1.867 | 15 | 6.5 | 0.34815
10:00 | [72 empty] | 43557.9794 | 2,3,5 | 33 | 8.7 | 8.7 | 8.7 | 26.1 | 8.2 | 8.2 | 8.2 | 24.6 | 1,3,1,3 | 8.172 | 1,3 | 14.724 | 22.896 | 2.3112 | 43557.9794 | 55.2698 | 4427.0924 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5199 | 1.5199 | 1.5199 | 0.19234 | 0.19671 | 0.19234 | 0.14863 | 0.153 | 0.14426 | 1.4077 | 1 | 0.070129 | 0.069486 | 0.070773 | 1.0934 | 0.50178 | 0.096912 | 3.7976 | 0.72042 | 4.8927 | 1.0934 | 0.4965 | 0.10572 | 4.0026 | 0.72877 | 9.4295 |  | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.6 | 18 | 18 | 9.86 | 78 | 137 | 16 | 0.323 |  | 6.08 | 10 | 0.047 | 6.06 | 11 |  | 6 | 10 | [8 empty] | 0.038 | [14 empty] | 0.034 | 1 | 0.34 |  | 0.038 | 0.017 | 1 | 0.33 |  | 0.031 | 1 | 0.44 | [38 empty] | 5900 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 280 | 440 | 450 | 440 | 340 | 350 | 330 | 740 |  | 1090 | 1080 | 1100 | 78 | 95 | 11 | 1270 | 259 | 275 | 39 | 47 | 6 | 644 | 131 | 265 |  | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.13 | 0.776 | 6 | 0.59 | 15 | 9.3 | 0.48557 |  | 6.15 | 0.647 | 7 | 0.63 | 15.5 | 9.3 | 0.48557 | 6.11 | 0.628 | 6 | 0.63 | 15.7 | 9.3 | 0.46444 | [13 empty] | 7.2 | 0.05 | 1 | 4.6 | 15.1 |  |  |  | 7.44 | 0.063 | 1 | 3.8 | 14.9 |  |  |  | 4 | 3.5 | 3.5 | [55 empty] | 13:00 | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.13 | 15 | 10 | 1.6139 | 15 | 6.5 | 0.36557 | 13:00 | 0.63 | 9.3 | 27.3548 | 17.2335 | 6.15 | 15.5 | 10 | 1.7234 | 15 | 6.5 | 0.36557 | 13:00 | 0.63 | 9.3 | 29.0323 | 18.2903 | 6.11 | 15.7 | 10 | 1.829 | 15 | 6.5 | 0.34444
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.64 | 20 | 19 | 9.34 | 82 | 134 | 15.5 | 0.337 |  | 6.14 | 10 | 0.05 | 6.12 | 9 |  | 6 | 9 | [8 empty] | 0.046 | [14 empty] | 0.037 | 1 | 0.27 |  | 0.04 | 0.031 | 1 | 0.26 |  | 0.034 | 1 | 0.42 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.68 | 0.051 | 1 | 4.6 | 15.1 |  |  |  | 7.55 | 0.06 | 1 | 4.3 | 15.1 |  |  |  | 4 | 3.5 | 1.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.69 | 20 | 20 | 9.25 | 83 | 134 | 15.7 | 0.332 |  | 6.17 | 10 | 0.048 | 6.13 | 10 |  | 6.07 | 10 | [8 empty] | 0.039 | [14 empty] | 0.033 | 1 | 0.3 |  | 0.039 | 0.033 | 1 | 0.28 |  | 0.04 | 1 | 0.45 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.04 | [9 empty] | 6.16 | 0.344 | 4 | 0.54 | 14.9 | 8.2 | 0.60349 |  | 6.18 | 0.313 | 4 | 0.59 | 15.7 | 8.2 | 0.44233 | 6.17 | 0.197 | 4 | 0.61 | 15.6 | 8.2 | 0.4237 |  |  |  | 0.013 | [9 empty] | 7.47 | 0.063 | 1 | 4.2 | 15.1 | 20 | 32 | 0.013 | 7.51 | 0.068 | 1 | 3.8 | 15.1 | 20 | 31 | 0.008 | 4 | 3.5 | 3.7 | [55 empty] | 21:00 | 0.54 | 8.2 | 31.0244 | 16.7532 | 6.16 | 14.9 | 15 | 1.1169 | 10 | 6.5 | 0.48349 | 21:00 | 0.59 | 8.2 | 31.0244 | 18.3044 | 6.18 | 15.7 | 10 | 1.8304 | 15 | 6.5 | 0.32233 | 21:00 | 0.61 | 8.2 | 32.9268 | 20.0854 | 6.17 | 15.6 | 10 | 2.0085 | 15 | 6.5 | 0.3037
22:00 | [72 empty] | DOSE |  | TOTAL | 54.7 | 54.8 | 54.8 | 164.3 | 51.7 | 51.8 | 51.8 | 155.3 | 0 | 57.7627 | 0 | 93.2314 | 150.9941 | 8.4701 | TOTAL | 331.5162 | 27853.7898 | 0 | 3488.9868 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9432 | 8.9981 | 9.0908 | 1.184 | 1.1928 | 1.1576 | 0.8289 | 0.89377 | 0.89042 | 8.6457 | 9 | 0.41924 | 0.41646 | 0.41904 | 6.6209 | 3.0314 | 0.60318 | 22.6712 | 4.1118 | 28.7499 | 6.6058 | 3.0186 | 0.61969 | 23.7088 | 4.1809 | 54.8542 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.72 | 20 | 20 | 9.24 | 84 | 135 | 15.2 | 0.348 |  | 6.08 | 10 | 0.049 | 6.15 | 10 |  | 6.04 | 10 | [8 empty] | 0.04 | [14 empty] | 0.031 | 1 | 0.36 |  | 0.04 | 0.038 | 1 | 0.47 |  | 0.033 | 1 | 0.34 | [22 empty] | AVERAGE | 9.1167 | 9.1333 | 9.1333 | 27.3833 | 8.6167 | 8.6333 | 8.6333 | 25.8833 |  | 9.6271 |  | 15.5386 | 25.1657 | 1.4117 | AVERAGE | 55.2527 | 4642.2983 |  | 581.4978 | 0 | 0 | 0 |  |  |  | 1.4905 | 1.4997 | 1.5151 | 0.19734 | 0.19879 | 0.19293 | 0.13815 | 0.14896 | 0.1484 | 1.441 | 1.5 | 0.069874 | 0.069411 | 0.06984 | 1.1035 | 0.50524 | 0.10053 | 3.7785 | 0.68531 | 4.7916 | 1.101 | 0.5031 | 0.10328 | 3.9515 | 0.69681 | 9.1424 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.82 | 116 | 113 | 58.09 | 486 | 818 | 95.1 | 2.009 | 0.081 | 36.69 | 60 | 0.291 | 36.7 | 60 | 0 | 36.21 | 60 | 0 | 24.67 | 2.165 | 22 | 2.48 | 61.6 | 36.9 | 2.0916 | 0.246 | 24.63 | 2.218 | 23 | 2.44 | 64.2 | 36.9 | 1.9305 | 24.62 | 1.573 | 21 | 2.57 | 64.7 | 37 | 1.8504 | 0.203 | 6 | 1.94 | 0.023 | 0.24 | 0.168 | 6 | 1.89 | 0.015 | 0.213 | 6 | 2.76 | 0.009 | 44.45 | 0.333 | 6 | 26.5 | 91.9 | 40 | 70 | 0.031 | 44.44 | 0.369 | 6 | 23.8 | 91.2 | 40 | 66 | 0.026 | 23.8 | 20.7 | 20.4 |  |  | MINIMUM | 8.2 | 8.3 | 8.3 | 24.8 | 7.7 | 7.8 | 7.8 | 23.3 |  | 8.172 |  | 13.8139 | 22.896 | 0.96192 | MINIMUM | 54.2187 | 4304.1176 |  | 475.7709 | [6 empty] | 1.4096 | 1.4838 | 1.4838 | 0.19234 | 0.19671 | 0.17614 | 0.099282 | 0.13611 | 0.14426 | 1.4077 | 1 | 0.067999 | 0.067413 | 0.067413 | 1.0728 | 0.50049 | 0.096324 | 3.7066 | 0.60823 | 4.6361 | 1.0728 | 0.4965 | 0.09262 | 3.7939 | 0.63976 | 8.7859 |  | MIN | 0.54 | 8.2 | 31.0244 | 16.7532 | 6.16 | 14.9 | 15 | 1.1169 |  |  |  | MIN | 0.62 | 10.1 | 25.1881 | 15.6166 | 6.17 | 17 | 10 | 1.5617 |  |  |  | MIN | 0.68 | 10.1 | 26.7327 | 18.1782 | 6.18 | 16.8 | 10 | 1.8178 |  |  |  | 1.1169
AVERAGE | 6.6367 | 19.3333 | 18.8333 | 9.6817 | 81 | 136.3333 | 15.85 | 0.33483 | 0.0405 | 6.115 | 10 | 0.0485 | 6.1167 | 10 |  | 6.035 | 10 |  | 6.1675 | 0.54125 | 5.5 | 0.62 | 15.4 | 9.225 | 0.52291 | 0.041 | 6.1575 | 0.5545 | 5.75 | 0.61 | 16.05 | 9.225 | 0.48262 | 6.155 | 0.39325 | 5.25 | 0.6425 | 16.175 | 9.25 | 0.46259 | 0.033833 | 1 | 0.32333 | 0.0115 | 0.04 | 0.028 | 1 | 0.315 | 0.015 | 0.0355 | 1 | 0.46 |  | 7.4083 | 0.0555 | 1 | 4.4167 | 15.3167 | 20 | 35 | 0.0155 | 7.4067 | 0.0615 | 1 | 3.9667 | 15.2 | 20 | 33 | 0.013 | 3.9667 | 3.45 | 3.4 |  |  | MAXIMUM | 10.1 | 10.1 | 10.1 | 30.3 | 9.6 | 9.6 | 9.6 | 28.8 |  | 11.016 |  | 17.3851 | 27.7301 | 2.3112 | MAXIMUM | 56.0814 | 5164.9412 |  | 792.9515 | [6 empty] | 1.5199 | 1.5199 | 1.5997 | 0.20016 | 0.20016 | 0.20016 | 0.14892 | 0.153 | 0.15212 | 1.4742 | 2.5 | 0.070572 | 0.070344 | 0.070773 | 1.1375 | 0.51432 | 0.10572 | 3.8226 | 0.72105 | 4.9509 | 1.1255 | 0.51432 | 0.12334 | 4.0173 | 0.73105 | 9.4295
MINIMUM | 6.49 | 18 | 17 | 9.24 | 78 | 134 | 15.2 | 0.323 | 0.04 | 6.08 | 10 | 0.047 | 6.06 | 9 |  | 6 | 9 |  | 6.13 | 0.344 | 4 | 0.54 | 14.9 | 8.2 | 0.48557 | 0.038 | 6.13 | 0.313 | 4 | 0.59 | 15.5 | 8.2 | 0.44233 | 6.11 | 0.197 | 4 | 0.61 | 15.6 | 8.2 | 0.4237 | 0.023 | 1 | 0.27 | 0.01 | 0.038 | 0.017 | 1 | 0.24 | 0.015 | 0.031 | 1 | 0.34 |  | 7.12 | 0.05 | 1 | 4.2 | 15.1 | 20 | 32 | 0.013 | 7.14 | 0.059 | 1 | 3.8 | 14.9 | 20 | 31 | 0.008 | 3.8 | 3.4 | 1.7 | [15 empty] | MIL/MIN |  | TOTAL | 37130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1730 | 1745 | 1765 | 2840 | 2860 | 2780 | 1983 | 2145 | 2140 | 4545 | 0 | 6845 | 6815 | 6855 | 497 | 604 | 72 | 7923 | 1554 | 1697 | 248 | 301 | 37 | 3920 | 791 | 1620
MAXIMUM | 6.72 | 20 | 20 | 10.3 | 84 | 140 | 16.5 | 0.348 | 0.041 | 6.17 | 10 | 0.05 | 6.15 | 11 |  | 6.07 | 11 |  | 6.22 | 0.776 | 6 | 0.74 | 16.2 | 10.1 | 0.60349 | 0.046 | 6.18 | 0.647 | 7 | 0.63 | 17 | 10.1 | 0.51701 | 6.18 | 0.628 | 6 | 0.68 | 16.8 | 10.1 | 0.49407 | 0.045 | 1 | 0.39 | 0.013 | 0.044 | 0.038 | 1 | 0.47 | 0.015 | 0.04 | 1 | 0.56 |  | 7.68 | 0.063 | 1 | 4.6 | 15.7 | 20 | 38 | 0.018 | 7.55 | 0.068 | 1 | 4.3 | 15.6 | 20 | 35 | 0.018 | 4 | 3.5 | 4.1 | [17 empty] | AVERAGE | 6188.3333 | [9 empty] | 288.3333 | 290.8333 | 294.1667 | 473.3333 | 476.6667 | 463.3333 | 330.5 | 357.5 | 356.6667 | 757.5 |  | 1140.8333 | 1135.8333 | 1142.5 | 82.8333 | 100.6667 | 12 | 1320.5 | 259 | 282.8333 | 41.3333 | 50.1667 | 6.1667 | 653.3333 | 131.8333 | 270
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0889 |  | TOTAL AVG COAG ALK: |  |  |  | 10 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.776 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.16 |  |  |  |  | 0.045 |  |  |  |  | 0.54 | [6 empty] | 0.045 | [16 empty] | Pump Station MIN |  | 1.7 | [17 empty] | MINIMUM | 5600 | [9 empty] | 260 | 260 | 260 | 430 | 430 | 430 | 248 | 325 | 325 | 740 |  | 1030 | 1030 | 1030 | 74 | 90 | 11 | 1203 | 230 | 263 | 38 | 45 | 5 | 600 | 115 | 252
[90 empty] | MAXIMUM | 6950 | [9 empty] | 325 | 325 | 345 | 530 | 530 | 530 | 370 | 400 | 395 | 775 |  | 1275 | 1275 | 1275 | 95 | 114 | 14 | 1470 | 300 | 312 | 47 | 57 | 7 | 734 | 150 | 296
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.163 |  | TOTAL MGD: |  | 0.015 |  |  | FINISHED SOUTH 1 |  | START: | 23827601 |  | END: | 23827616 |  |  | Alum | 4876 | 5774 | 5774 | 7938 | 7938 | 0 | [44 empty] | 0.54 | 8.2 | 31.0244 | 16.7532 | 6.16 | 14.9 | 15 | 1.1169
[73 empty] | FINISHED 2 | 17.165 |  | TOTAL MGD: |  | 11.148 |  |  | FINISHED SOUTH 2 |  | START: | 44846800 |  | END: | 44857948 |  |  | Caustic | 6932 | 8063 | 8063
[73 empty] | TOTAL RAW | 26.83 |  | TOTAL MGD: |  | 4.982 |  |  | FINISHED CONWAY |  | START: | 10642039 |  | END: | 10647021 |  |  | Hypochlorite | 17 |  | 28
[76 empty] | TOTAL MGD: |  | 12.183 |  |  | FINISHED PERRY |  | START: | 34688333 |  | END: | 34700516 |  |  | Phosphate | 1502
[76 empty] | TOTAL MGD: |  | 8.897 |  |  | RAW PLANT 1 |  | START: | 31790743 |  | END: | 31799640 |  |  | Fluoride | 2900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.001 |  |  | RAW PLANT 2 |  | START: | 31752617 |  | END: | 31761618 |  |  | Cal~Flo | 11.15 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 8.932 |  |  | RAW PLANT 3 |  | START: | 8385906 |  | END: | 8394838 |  |  | Zinc | 2679
[76 empty] | TOTAL MGD: |  | 0.745 |  |  | DECANT |  | START: | 1938555 |  | END: | 1939300 |  |  | Polymer | 26
[76 empty] | TOTAL MGD: |  | 0.7343 |  |  | BLOW DOWN |  | START: | 9240.869 |  | END: | 9241.6033 |  |  | NH3 | 10.9 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 480
23827616
44857948
10647021
34700516
31799640
31761618
8394838
1939300
9241.6033
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 3
DATE: | 2019-04-03 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-03 | [23 empty] | DATE: | 2019-04-03
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-03 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43558.0029 | 2,3,5 | 33 | 8.7 | 8.7 | 8.7 | 26.1 | 8.2 | 8.2 | 8.2 | 24.6 | 1,3,1,3 | 8.172 | 1,3 | 14.724 | 22.896 | 2.3112 | 43558.0029 | 55.2698 | 4427.0924 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5199 | 1.5199 | 1.5199 | 0.19234 | 0.19671 | 0.19234 | 0.14863 | 0.153 | 0.14426 | 1.4077 | 1 | 0.070129 | 0.069486 | 0.070773 | 1.0934 | 0.50178 | 0.096912 | 3.7976 | 0.72042 | 4.8927 | 1.0934 | 0.4965 | 0.10572 | 4.0026 | 0.72877 | 9.4295 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.466 | 5 | 0.72 | 15 | 9.3 | 0.48557 |  | 6.14 | 0.371 | 5 | 0.61 | 16 | 9.3 | 0.48557 | 6.14 | 0.2 | 4 | 0.57 | 15.5 | 9.4 | 0.46815 | [13 empty] | 7.53 | 0.061 | 1 | 4.2 | 14.7 |  |  |  | 7.28 | 0.07 | 1 | 4.1 | 14.9 |  |  |  | 3.9 | 3.5 | 3.7 | [18 empty] | 5900 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 280 | 440 | 450 | 440 | 340 | 350 | 330 | 740 |  | 1090 | 1080 | 1100 | 78 | 95 | 11 | 1270 | 259 | 275 | 39 | 47 | 6 | 644 | 131 | 265 |  | 1:00 | 0.72 | 9.3 | 27.3548 | 19.6955 | 6.19 | 15 | 10 | 1.9695 | 15 | 6.5 | 0.36557 | 1:00 | 0.61 | 9.3 | 27.3548 | 16.6865 | 6.14 | 16 | 10 | 1.6686 | 15 | 6.5 | 0.36557 | 1:00 | 0.57 | 9.4 | 28.7234 | 16.3723 | 6.14 | 15.5 | 10 | 1.6372 | 15 | 6.5 | 0.34815
2:00 | [72 empty] | 43558.1223 | 2,3,5 | 33 | 9.3 | 9.3 | 9.4 | 28 | 8.8 | 8.8 | 8.9 | 26.5 | 1,3,1,3 | 8.172 | 1,3 | 14.724 | 22.896 | 2.3112 | 43558.1223 | 55.4488 | 4734.5294 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 1.5175 | 1.5004 | 0.20038 | 0.20038 | 0.20038 | 0.15131 | 0.1497 | 0.1497 | 1.4077 | 1 | 0.070144 | 0.070144 | 0.069949 | 1.0972 | 0.50202 | 0.098514 | 3.79 | 0.72055 | 4.7415 | 1.1107 | 0.48664 | 0.097407 | 4.0079 | 0.73295 | 9.737 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.62 | 19 | 20 | 9.59 | 88 | 137 | 15.4 | 0.35 |  | 6.12 | 10 | 0.047 | 6.09 | 10 |  | 6.04 | 10 | [8 empty] | 0.039 | [14 empty] | 0.029 | 1 | 0.36 |  | 0.038 | 0.038 | 1 | 0.43 |  | 0.035 | 1 | 0.41 | [38 empty] | 6350 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 490 | 490 | 490 | 370 | 370 | 370 | 740 |  | 1170 | 1170 | 1180 | 84 | 102 | 12 | 1360 | 278 | 286 | 43 | 50 | 6 | 700 | 143 | 297 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43558.3583 | 2,3,5 | 55 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3 | 9 | 1,3 | 15.8 | 24.8 | 2.3 | 8:36 | 55 | 4796 | 0 | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.5 | 1.4 | 0.2 | 0.19 | 0.19 | 0.16 | 0.14 | 0.06 | 1.41 | 1 | 0.07 | 0.07 | 0.07 | 1.1 | 0.5 | 0.1 | 3.8 | 0.7 | 4.8 | 1.1 | 0.51 | 0.1 | 4 | 0.7 | 9.3 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.42 | 0.064 | 1 | 4 | 14.6 |  |  |  | 7.27 | 0.062 | 1 | 3.8 | 14.6 |  |  |  | 4 | 3.5 | 1.8 | [18 empty] | 6680 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 300 | 520 | 480 | 480 | 400 | 360 | 400 | 740 |  | 1240 | 1240 | 1240 | 88 | 107 | 13 | 1350 | 275 | 309 | 44 | 55 | 6 | 730 | 150 | 295 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.61 | 17 | 24 | 9.26 | 89 | 143 | 15.9 | 0.329 |  | 6.15 | 9 | 0.048 | 6.12 | 8 |  | 6.06 | 8 | [8 empty] | 0.04 | [14 empty] | 0.027 | 1 | 0.45 |  | 0.038 | 0.042 | 1 | 0.52 |  | 0.035 | 1 | 0.41 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43558.8327 | 2,3,5 | 55 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 8.9914 | 1,3 | 15.8026 | 24.7939 | 1.0354 | 43558.8327 | 55.137 | 3504.7814 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5316 | 1.5316 | 1.4359 | 0.18628 | 0.17463 | 0.17463 | 0.15523 | 0.14747 | 0.14747 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8021 | 0.71614 | 4.8473 | 1.1371 | 0.5216 | 0.093217 | 3.9969 | 0.7701 | 9.2554 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.047 | [9 empty] | 6.13 | 0.464 | 6 | 0.66 | 15.1 | 9.9 | 0.50915 |  | 6.14 | 0.361 | 5 | 0.56 | 15.7 | 10 | 0.51308 | 6.12 | 0.459 | 4 | 0.5 | 15.2 | 10 | 0.49037 |  |  |  | 0.01 | [9 empty] | 7.13 | 0.06 | 1 | 3.4 | 15.1 | 21 | 32 | 0.013 | 7.18 | 0.058 | 1 | 3.6 | 15.5 | 23 | 34 | 0.011 | 3.9 | 3.6 | 3.8 | [18 empty] | 6630 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 300 | 480 | 450 | 450 | 400 | 380 | 380 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1430 | 292 | 309 | 46 | 56 | 6 | 770 | 157 | 295 |  | 9:00 | 0.66 | 9.9 | 25.697 | 16.96 | 6.13 | 15.1 | 10 | 1.696 | 15 | 6.5 | 0.38915 | 9:00 | 0.56 | 10 | 25.44 | 14.2464 | 6.14 | 15.7 | 10 | 1.4246 | 15 | 6.5 | 0.39308 | 9:00 | 0.5 | 10 | 27 | 13.5 | 6.12 | 15.2 | 10 | 1.35 | 15 | 6.5 | 0.37037
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.6 | 20 | 15 | 10.1 | 83 | 146 | 15.5 | 0.333 |  | 6.32 | 11 | 0.069 | 6.33 | 10 |  | 6.25 | 11 | [8 empty] | 0.044 | [14 empty] | 0.033 | 1 | 0.36 |  | 0.04 | 0.039 | 1 | 0.41 |  | 0.034 | 1 | 0.42 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.27 | 0.493 | 5 | 0.51 | 15.3 | 10.1 | 0.51701 |  | 6.24 | 0.41 | 5 | 0.48 | 16.1 | 10.2 | 0.52094 | 6.26 | 0.425 | 4 | 0.41 | 15.4 | 10.2 | 0.49778 | [13 empty] | 7.24 | 0.058 | 1 | 3.5 | 14.9 |  |  |  | 7.19 | 0.057 | 1 | 3.4 | 16.7 |  |  |  | 3.9 | 3.5 | 3.8 | [55 empty] | 13:00 | 0.51 | 10.1 | 25.1881 | 12.8459 | 6.27 | 15.3 | 10 | 1.2846 | 15 | 6.5 | 0.39701 | 13:00 | 0.48 | 10.2 | 24.9412 | 11.9718 | 6.24 | 16.1 | 10 | 1.1972 | 15 | 6.5 | 0.40094 | 13:00 | 0.41 | 10.2 | 26.4706 | 10.8529 | 6.26 | 15.4 | 10 | 1.0853 | 15 | 6.5 | 0.37778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.6 | 21 | 18 | 8.71 | 80 | 133 | 15.8 | 0.333 |  | 6.21 | 10 | 0.069 | 6.13 | 11 |  | 6.1 | 11 | [8 empty] | 0.039 | [14 empty] | 0.042 | 1 | 0.29 |  | 0.039 | 0.043 | 1 | 0.3 |  | 0.043 | 1 | 0.22 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.1 | 0.052 | 1 | 3.6 | 15.1 |  |  |  | 7.13 | 0.054 | 1 | 3.3 | 16.3 |  |  |  | 3.8 | 3.5 | 3.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.55 | 20 | 18 | 8.05 | 81 | 129 | 15.9 | 0.333 |  | 6.09 | 12 | 0.049 | 6.12 | 12 |  | 6.04 | 12 | [8 empty] | 0.037 | [14 empty] | 0.031 | 1 | 0.32 |  | 0.037 | 0.032 | 1 | 0.44 |  | 0.033 | 1 | 0.48 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.044 | [9 empty] | 6.12 | 0.487 | 4 | 0.69 | 14.7 | 9.8 | 0.69783 |  | 6.13 | 0.352 | 4 | 0.58 | 15.5 | 9.8 | 0.50522 | 6.15 | 0.481 | 3 | 0.53 | 15.4 | 9.8 | 0.48296 |  |  |  | 0.009 | [9 empty] | 7.19 | 0.062 | 1 | 3.7 | 15 | 20 | 32 | 0.011 | 7.21 | 0.063 | 1 | 3.7 | 15.3 | 21 | 32 | 0.012 | 3.7 | 3.5 | 3.6 | [55 empty] | 21:00 | 0.69 | 9.8 | 25.9592 | 17.9118 | 6.12 | 14.7 | 15 | 1.1941 | 10 | 6.5 | 0.57783 | 21:00 | 0.58 | 9.8 | 25.9592 | 15.0563 | 6.13 | 15.5 | 10 | 1.5056 | 15 | 6.5 | 0.38522 | 21:00 | 0.53 | 9.8 | 27.551 | 14.602 | 6.15 | 15.4 | 10 | 1.4602 | 15 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 37.6 | 37.6 | 37.7 | 112.9 | 35.6 | 35.6 | 35.7 | 106.9 | 0 | 34.3354 | 0 | 61.0506 | 95.3859 | 7.9578 | TOTAL | 220.8556 | 17462.4032 | 0 | 1935.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 6.069 | 6.069 | 5.8563 | 0.779 | 0.76173 | 0.75735 | 0.61516 | 0.59016 | 0.50142 | 5.633 | 5 | 0.28062 | 0.27997 | 0.28106 | 4.4029 | 2.0068 | 0.39641 | 15.1897 | 2.8571 | 19.2815 | 4.4411 | 2.0147 | 0.39635 | 16.0074 | 2.9318 | 37.722 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.51 | 19 | 18 | 7.52 | 83 | 125 | 15.6 | 0.34 |  | 6.01 | 10 | 0.052 | 6.02 | 10 |  | 6 | 10 | [8 empty] | 0.037 | [14 empty] | 0.028 | 1 | 0.36 |  | 0.038 | 0.028 | 1 | 0.39 |  | 0.031 | 1 | 0.47 | [22 empty] | AVERAGE | 9.4 | 9.4 | 9.425 | 28.225 | 8.9 | 8.9 | 8.925 | 26.725 |  | 8.5838 |  | 15.2626 | 23.8465 | 1.9894 | AVERAGE | 55.2139 | 4365.6008 |  | 483.7577 | 0 | 0 | 0 |  |  |  | 1.5173 | 1.5173 | 1.4641 | 0.19475 | 0.19043 | 0.18934 | 0.15379 | 0.14754 | 0.12536 | 1.4082 | 1.25 | 0.070154 | 0.069993 | 0.070266 | 1.1007 | 0.50169 | 0.099103 | 3.7974 | 0.71428 | 4.8204 | 1.1103 | 0.50368 | 0.099086 | 4.0019 | 0.73295 | 9.4305 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.49 | 116 | 113 | 53.23 | 504 | 813 | 94.1 | 2.018 | 0.091 | 36.9 | 62 | 0.334 | 36.81 | 61 | 0 | 36.49 | 62 | 0 | 24.71 | 1.91 | 20 | 2.58 | 60.1 | 39.1 | 2.2096 | 0.236 | 24.65 | 1.494 | 19 | 2.23 | 63.3 | 39.3 | 2.0248 | 24.67 | 1.565 | 15 | 2.01 | 61.5 | 39.4 | 1.9393 | 0.19 | 6 | 2.14 | 0.019 | 0.23 | 0.222 | 6 | 2.49 | 0 | 0.211 | 6 | 2.41 | 0 | 43.61 | 0.357 | 6 | 22.4 | 89.4 | 41 | 64 | 0.024 | 43.26 | 0.364 | 6 | 21.9 | 93.3 | 44 | 66 | 0.023 | 23.2 | 21.1 | 20.6 |  |  | MINIMUM | 8.7 | 8.7 | 8.7 | 26.1 | 8.2 | 8.2 | 8.2 | 24.6 |  | 8.172 |  | 14.724 | 22.896 | 1.0354 | MINIMUM | 55 | 3504.7814 |  | 475.7709 | [6 empty] | 1.5 | 1.5 | 1.4 | 0.18628 | 0.17463 | 0.17463 | 0.14863 | 0.14 | 0.06 | 1.4077 | 1 | 0.07 | 0.069486 | 0.069949 | 1.0934 | 0.5 | 0.096912 | 3.79 | 0.7 | 4.7415 | 1.0934 | 0.48664 | 0.093217 | 3.9969 | 0.7 | 9.2554 |  | MIN | 0.69 | 9.8 | 25.9592 | 17.9118 | 6.12 | 14.7 | 15 | 1.1941 |  |  |  | MIN | 0.48 | 10.2 | 24.9412 | 11.9718 | 6.24 | 16.1 | 10 | 1.1972 |  |  |  | MIN | 0.41 | 10.2 | 26.4706 | 10.8529 | 6.26 | 15.4 | 10 | 1.0853 |  |  |  | 1.0853
AVERAGE | 6.5817 | 19.3333 | 18.8333 | 8.8717 | 84 | 135.5 | 15.6833 | 0.33633 | 0.0455 | 6.15 | 10.3333 | 0.055667 | 6.135 | 10.1667 |  | 6.0817 | 10.3333 |  | 6.1775 | 0.4775 | 5 | 0.645 | 15.025 | 9.775 | 0.55239 | 0.039333 | 6.1625 | 0.3735 | 4.75 | 0.5575 | 15.825 | 9.825 | 0.5062 | 6.1675 | 0.39125 | 3.75 | 0.5025 | 15.375 | 9.85 | 0.48481 | 0.031667 | 1 | 0.35667 | 0.0095 | 0.038333 | 0.037 | 1 | 0.415 |  | 0.035167 | 1 | 0.40167 |  | 7.2683 | 0.0595 | 1 | 3.7333 | 14.9 | 20.5 | 32 | 0.012 | 7.21 | 0.060667 | 1 | 3.65 | 15.55 | 22 | 33 | 0.0115 | 3.8667 | 3.5167 | 3.4333 |  |  | MAXIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9 |  | 15.8026 | 24.8 | 2.3112 | MAXIMUM | 55.4488 | 4796 |  | 507.489 | [6 empty] | 1.5316 | 1.5316 | 1.5199 | 0.20038 | 0.20038 | 0.20038 | 0.16 | 0.153 | 0.1497 | 1.41 | 2 | 0.070344 | 0.070344 | 0.070773 | 1.1123 | 0.50297 | 0.10099 | 3.8021 | 0.72055 | 4.8927 | 1.1371 | 0.5216 | 0.10572 | 4.0079 | 0.7701 | 9.737
MINIMUM | 6.51 | 17 | 15 | 7.52 | 80 | 125 | 15.4 | 0.329 | 0.044 | 6.01 | 9 | 0.047 | 6.02 | 8 |  | 6 | 8 |  | 6.12 | 0.464 | 4 | 0.51 | 14.7 | 9.3 | 0.48557 | 0.037 | 6.13 | 0.352 | 4 | 0.48 | 15.5 | 9.3 | 0.48557 | 6.12 | 0.2 | 3 | 0.41 | 15.2 | 9.4 | 0.46815 | 0.027 | 1 | 0.29 | 0.009 | 0.037 | 0.028 | 1 | 0.3 |  | 0.031 | 1 | 0.22 |  | 7.1 | 0.052 | 1 | 3.4 | 14.6 | 20 | 32 | 0.011 | 7.13 | 0.054 | 1 | 3.3 | 14.6 | 21 | 32 | 0.011 | 3.7 | 3.5 | 1.8 | [15 empty] | MIL/MIN |  | TOTAL | 25560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 1220 | 1180 | 1930 | 1870 | 1860 | 1510 | 1460 | 1480 | 2960 | 0 | 4740 | 4730 | 4760 | 340 | 412 | 49 | 5410 | 1104 | 1179 | 172 | 208 | 24 | 2844 | 581 | 1152
MAXIMUM | 6.62 | 21 | 24 | 10.1 | 89 | 146 | 15.9 | 0.35 | 0.047 | 6.32 | 12 | 0.069 | 6.33 | 12 |  | 6.25 | 12 |  | 6.27 | 0.493 | 6 | 0.72 | 15.3 | 10.1 | 0.69783 | 0.044 | 6.24 | 0.41 | 5 | 0.61 | 16.1 | 10.2 | 0.52094 | 6.26 | 0.481 | 4 | 0.57 | 15.5 | 10.2 | 0.49778 | 0.042 | 1 | 0.45 | 0.01 | 0.04 | 0.043 | 1 | 0.52 |  | 0.043 | 1 | 0.48 |  | 7.53 | 0.064 | 1 | 4.2 | 15.1 | 21 | 32 | 0.013 | 7.28 | 0.07 | 1 | 4.1 | 16.7 | 23 | 34 | 0.012 | 4 | 3.6 | 3.9 | [17 empty] | AVERAGE | 6390 | [9 empty] | 305 | 305 | 295 | 482.5 | 467.5 | 465 | 377.5 | 365 | 370 | 740 |  | 1185 | 1182.5 | 1190 | 85 | 103 | 12.25 | 1352.5 | 276 | 294.75 | 43 | 52 | 6 | 711 | 145.25 | 288
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1222 |  | TOTAL AVG COAG ALK: |  |  |  | 10.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.493 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.41 | [5 empty] | 6.1692 |  |  |  |  | 0.043 |  |  |  |  | 0.41 | [6 empty] | 0.043 | [16 empty] | Pump Station MIN |  | 1.8 | [17 empty] | MINIMUM | 5900 | [9 empty] | 280 | 280 | 280 | 440 | 450 | 440 | 340 | 350 | 330 | 740 |  | 1090 | 1080 | 1100 | 78 | 95 | 11 | 1270 | 259 | 275 | 39 | 47 | 6 | 644 | 131 | 265
[90 empty] | MAXIMUM | 6680 | [9 empty] | 320 | 320 | 300 | 520 | 490 | 490 | 400 | 380 | 400 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1430 | 292 | 309 | 46 | 56 | 6 | 770 | 157 | 297
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.341 |  | TOTAL MGD: |  | 0.019 |  |  | FINISHED SOUTH 1 |  | START: | 23827616 |  | END: | 23827635 |  |  | Alum | 4907 | 10200 | 10200 | 7525 | 7525 | 0 | [44 empty] | 0.41 | 10.2 | 26.4706 | 10.8529 | 6.26 | 15.4 | 10 | 1.0853
[73 empty] | FINISHED 2 | 15.857 |  | TOTAL MGD: |  | 11.322 |  |  | FINISHED SOUTH 2 |  | START: | 44857948 |  | END: | 44869270 |  |  | Caustic | 6835 | 8040 | 8040
[73 empty] | TOTAL RAW | 29.927 |  | TOTAL MGD: |  | 4.822 |  |  | FINISHED CONWAY |  | START: | 10647021 |  | END: | 10651843 |  |  | Hypochlorite | 16 |  | 27
[76 empty] | TOTAL MGD: |  | 11.035 |  |  | FINISHED PERRY |  | START: | 34700516 |  | END: | 34711551 |  |  | Phosphate | 1443
[76 empty] | TOTAL MGD: |  | 9.847 |  |  | RAW PLANT 1 |  | START: | 31799640 |  | END: | 31809487 |  |  | Fluoride | 2650 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.969 |  |  | RAW PLANT 2 |  | START: | 31761618 |  | END: | 31771587 |  |  | Cal~Flo | 9.33 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.111 |  |  | RAW PLANT 3 |  | START: | 8394838 |  | END: | 8404949 |  |  | Zinc | 2485
[76 empty] | TOTAL MGD: |  | 0.75 |  |  | DECANT |  | START: | 1939300 |  | END: | 1940050 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.87993 |  |  | BLOW DOWN |  | START: | 9241.6033 |  | END: | 9242.4833 |  |  | NH3 | 11 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 507
23827635
44869270
10651843
34711551
31809487
31771587
8404949
1940050
9242.4833
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.comBCOperator:
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 4
DATE: | 2019-04-04 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-04 | [23 empty] | DATE: | 2019-04-04
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-04 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43559.0024 | 2,3,5 | 55 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 8.9914 | 1,3 | 15.8026 | 24.7939 | 1.0354 | 43559.0024 | 55.137 | 3504.7814 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5316 | 1.5316 | 1.4359 | 0.18628 | 0.17463 | 0.17463 | 0.15523 | 0.14747 | 0.14747 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8021 | 0.71614 | 4.8473 | 1.1371 | 0.5216 | 0.093217 | 3.9969 | 0.7701 | 9.2554 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.09 | 0.476 | 4 | 0.65 | 15.5 | 9.8 | 0.50522 |  | 6.11 | 0.325 | 4 | 0.6 | 15.5 | 9.8 | 0.50522 | 6.07 | 0.455 | 3 | 0.55 | 16 | 9.8 | 0.48296 | [13 empty] | 7.15 | 0.06 | 1 | 3.8 | 15 |  |  |  | 7.12 | 0.059 | 1 | 3.8 | 16 |  |  |  | 3.7 | 3.5 | 3.8 | [18 empty] | 6630 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 300 | 480 | 450 | 450 | 400 | 380 | 380 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1430 | 292 | 309 | 46 | 56 | 6 | 770 | 157 | 295 |  | 1:00 | 0.65 | 9.8 | 25.9592 | 16.8735 | 6.09 | 15.5 | 10 | 1.6873 | 15 | 6.5 | 0.38522 | 1:00 | 0.6 | 9.8 | 25.9592 | 15.5755 | 6.11 | 15.5 | 10 | 1.5576 | 15 | 6.5 | 0.38522 | 1:00 | 0.55 | 9.8 | 27.551 | 15.1531 | 6.07 | 16 | 10 | 1.5153 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43559.3833 | 2,3,5 | 60 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 10.6646 | 1,3 | 16.7846 | 27.4493 | 1.0354 | 43559.4625 | 50.064 | 3504.7814 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7231 | 1.5316 | 1.4359 | 0.18628 | 0.17075 | 0.17075 | 0.13971 | 0.12418 | 0.13971 | 1.4077 | 0 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49831 | 0.10099 | 3.794 | 0.69898 | 4.8473 | 1.0876 | 0.51228 | 0.093217 | 3.9798 | 0.73576 | 9.2554 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.58 | 20 | 18 | 7.7 | 80 | 126 | 16.6 | 0.303 |  | 6.06 | 11 | 0.043 | 6.04 | 11 |  | 6 | 11 | [8 empty] | 0.029 | [14 empty] | 0.026 | 1 | 0.34 |  | 0.032 | 0.033 | 1 | 0.36 |  | 0.031 | 1 | 0.45 | [38 empty] | 6020 | [6 empty] | 0 | 0 | 0 | 360 | 320 | 300 | 480 | 440 | 440 | 360 | 320 | 360 | 740 |  | 1240 | 1240 | 1240 | 88 | 107 | 13 | 1390 | 285 | 309 | 44 | 55 | 6 | 740 | 150 | 295 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43559.8011 | 2,3,5 | 60 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 10.6646 | 1,3 | 16.7846 | 27.4493 | 1.1578 | 43559.8011 | 50.064 | 3135.857 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6273 | 1.5316 | 1.4359 | 0.18628 | 0.17851 | 0.17075 | 0.13971 | 0.13195 | 0.13195 | 1.4077 | 1 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49366 | 0.10099 | 3.8086 | 0.69898 | 4.8473 | 1.0876 | 0.50297 | 0.093217 | 3.9588 | 0.76029 | 9.2554 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.18 | 0.058 | 1 | 3.8 | 15 |  |  |  | 7.2 | 0.057 | 1 | 3.8 | 16 |  |  |  | 3.3 | 3.6 | 4.1 | [18 empty] | 6020 | [6 empty] | 0 | 0 | 0 | 340 | 320 | 300 | 480 | 460 | 440 | 360 | 340 | 340 | 740 |  | 1240 | 1240 | 1240 | 88 | 106 | 13 | 1400 | 285 | 309 | 44 | 54 | 6 | 750 | 155 | 295 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.59 | 15 | 16 | 7.49 | 81 | 124 | 15.9 | 0.318 |  | 6.04 | 11 | 0.059 | 6.07 | 10 |  | 5.97 | 10 | [8 empty] | 0.036 | [14 empty] | 0.024 | 1 | 0.4 |  | 0.033 | 0.045 | 1 | 0.37 |  | 0.03 | 1 | 0.35 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.032 | [9 empty] | 6.07 | 0.383 | 5 | 0.68 | 15.2 | 9.9 | 0.50915 |  | 6.04 | 0.308 | 4 | 0.66 | 15.9 | 10.1 | 0.51701 | 6.08 | 0.305 | 4 | 0.65 | 15.7 | 10.1 | 0.49407 |  |  |  | 0.011 | [9 empty] | 7.08 | 0.054 | 1 | 3.9 | 15.1 | 21 | 37 | 0.014 | 7.11 | 0.059 | 1 | 3.6 | 16.2 | 21 | 32 | 0.013 | 3.7 | 3.6 | 3.9 | [55 empty] | 9:00 | 0.68 | 9.9 | 25.697 | 17.4739 | 6.07 | 15.2 | 10 | 1.7474 | 15 | 6.5 | 0.38915 | 9:00 | 0.66 | 10.1 | 25.1881 | 16.6242 | 6.04 | 15.9 | 10 | 1.6624 | 15 | 6.5 | 0.39701 | 9:00 | 0.65 | 10.1 | 26.7327 | 17.3762 | 6.08 | 15.7 | 10 | 1.7376 | 15 | 6.5 | 0.37407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.6 | 17 | 16 | 7.12 | 77 | 117 | 16.4 | 0.333 |  | 6.04 | 10 | 0.057 | 6 | 11 |  | 5.98 | 10 | [8 empty] | 0.042 | [14 empty] | 0.023 | 1 | 0.42 |  | 0.037 | 0.026 | 1 | 0.42 |  | 0.03 | 1 | 0.26 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.04 | 0.363 | 4 | 0.75 | 15.4 | 9.8 | 0.50522 |  | 6.01 | 0.248 | 3 | 0.55 | 16.6 | 9.9 | 0.50915 | 6.04 | 0.307 | 4 | 0.65 | 16.1 | 9.9 | 0.48667 | [13 empty] | 7.41 | 0.052 | 1 | 4.6 | 15.1 |  |  |  | 7.26 | 0.056 | 1 | 3.8 | 16.9 |  |  |  | 3.5 | 3.7 | 2.3 | [55 empty] | 13:00 | 0.75 | 9.8 | 25.9592 | 19.4694 | 6.04 | 15.4 | 10 | 1.9469 | 15 | 6.5 | 0.38522 | 13:00 | 0.55 | 9.9 | 25.697 | 14.1333 | 6.01 | 16.6 | 10 | 1.4133 | 15 | 6.5 | 0.38915 | 13:00 | 0.65 | 9.9 | 27.2727 | 17.7273 | 6.04 | 16.1 | 10 | 1.7727 | 15 | 6.5 | 0.36667
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.58 | 20 | 17 | 7.18 | 81 | 113 | 16.3 | 0.325 |  | 6.07 | 11 | 0.058 | 6.04 | 11 |  | 5.99 | 10 | [8 empty] | 0.041 | [14 empty] | 0.024 | 1 | 0.38 |  | 0.038 | 0.046 | 1 | 0.37 |  | 0.029 | 1 | 0.28 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.05 | 0.051 | 1 | 4 | 15.6 |  |  |  | 7.04 | 0.05 | 1 | 3.7 | 16.9 |  |  |  | 3.9 | 3.6 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.58 | 20 | 17 | 6.87 | 78 | 115 | 16.2 | 0.331 |  | 6.1 | 10 | 0.058 | 6.11 | 10 |  | 5.99 | 10 | [8 empty] | 0.038 | [14 empty] | 0.022 | 1 | 0.37 |  | 0.039 | 0.017 | 1 | 0.37 |  | 0.03 | 1 | 0.29 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.04 | [9 empty] | 6.13 | 0.481 | 4 | 0.76 | 15.3 | 9.8 | 0.50522 |  | 6.07 | 0.303 | 4 | 0.6 | 15.9 | 9.8 | 0.50522 | 6.05 | 0.462 | 3 | 0.68 | 16.1 | 9.8 | 0.48296 |  |  |  | 0.011 | [9 empty] | 7.15 | 0.058 | 1 | 4.4 | 15 | 21 | 36 | 0.02 | 7.16 | 0.054 | 1 | 4 | 15.6 | 21 | 31 | 0.015 | 3.6 | 3.6 | 3.6 | [55 empty] | 21:00 | 0.76 | 9.8 | 25.9592 | 19.729 | 6.13 | 15.3 | 10 | 1.9729 | 15 | 6.5 | 0.38522 | 21:00 | 0.6 | 9.8 | 25.9592 | 15.5755 | 6.07 | 15.9 | 10 | 1.5576 | 15 | 6.5 | 0.38522 | 21:00 | 0.68 | 9.8 | 27.551 | 18.7347 | 6.05 | 16.1 | 10 | 1.8735 | 15 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 29.4 | 29.4 | 29.4 | 88.2 | 27.9 | 27.9 | 27.9 | 83.7 | 0 | 30.3206 | 0 | 49.3718 | 79.6925 | 3.2285 | TOTAL | 155.265 | 10145.4198 | 0 | 1506.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 4.882 | 4.5948 | 4.3077 | 0.55883 | 0.5239 | 0.51614 | 0.43464 | 0.4036 | 0.41912 | 4.223 | 3 | 0.21103 | 0.21103 | 0.21103 | 3.2876 | 1.4949 | 0.30296 | 11.4048 | 2.1141 | 14.542 | 3.3123 | 1.5369 | 0.27965 | 11.9355 | 2.2662 | 27.7663 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 20 | 18 | 7.23 | 80 | 118 | 16.2 | 0.334 |  | 6.01 | 10 | 0.06 | 6.06 | 10 |  | 5.99 | 10 | [8 empty] | 0.039 | [14 empty] | 0.026 | 1 | 0.44 |  | 0.039 | 0.026 | 1 | 0.41 |  | 0.03 | 1 | 0.33 | [22 empty] | AVERAGE | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 10.1069 |  | 16.4573 | 26.5642 | 1.0762 | AVERAGE | 51.755 | 3381.8066 |  | 502.2026 | 0 | 0 | 0 |  |  |  | 1.6273 | 1.5316 | 1.4359 | 0.18628 | 0.17463 | 0.17205 | 0.14488 | 0.13453 | 0.13971 | 1.4077 | 1 | 0.070344 | 0.070344 | 0.070344 | 1.0959 | 0.49831 | 0.10099 | 3.8016 | 0.7047 | 4.8473 | 1.1041 | 0.51228 | 0.093217 | 3.9785 | 0.75538 | 9.2554 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.46 | 112 | 102 | 43.59 | 477 | 713 | 97.6 | 1.944 | 0.072 | 36.32 | 63 | 0.335 | 36.32 | 63 | 0 | 35.92 | 61 | 0 | 24.33 | 1.703 | 17 | 2.84 | 61.4 | 39.3 | 2.0248 | 0.225 | 24.23 | 1.184 | 15 | 2.41 | 63.9 | 39.6 | 2.0366 | 24.24 | 1.529 | 14 | 2.53 | 63.9 | 39.6 | 1.9467 | 0.145 | 6 | 2.35 | 0.022 | 0.218 | 0.193 | 6 | 2.3 | 0 | 0.18 | 6 | 1.96 | 0 | 43.02 | 0.333 | 6 | 24.5 | 90.8 | 42 | 73 | 0.034 | 42.89 | 0.335 | 6 | 22.7 | 97.6 | 42 | 63 | 0.028 | 21.7 | 21.6 | 21.1 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 8.9914 |  | 15.8026 | 24.7939 | 1.0354 | MINIMUM | 50.064 | 3135.857 |  | 491.63 | [6 empty] | 1.5316 | 1.5316 | 1.4359 | 0.18628 | 0.17075 | 0.17075 | 0.13971 | 0.12418 | 0.13195 | 1.4077 | 0 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49366 | 0.10099 | 3.794 | 0.69898 | 4.8473 | 1.0876 | 0.50297 | 0.093217 | 3.9588 | 0.73576 | 9.2554 |  | MIN | 0.65 | 9.8 | 25.9592 | 16.8735 | 6.09 | 15.5 | 10 | 1.6873 |  |  |  | MIN | 0.55 | 9.9 | 25.697 | 14.1333 | 6.01 | 16.6 | 10 | 1.4133 |  |  |  | MIN | 0.55 | 9.8 | 27.551 | 15.1531 | 6.07 | 16 | 10 | 1.5153 |  |  |  | 1.4133
AVERAGE | 6.5767 | 18.6667 | 17 | 7.265 | 79.5 | 118.8333 | 16.2667 | 0.324 | 0.036 | 6.0533 | 10.5 | 0.055833 | 6.0533 | 10.5 |  | 5.9867 | 10.1667 |  | 6.0825 | 0.42575 | 4.25 | 0.71 | 15.35 | 9.825 | 0.5062 | 0.0375 | 6.0575 | 0.296 | 3.75 | 0.6025 | 15.975 | 9.9 | 0.50915 | 6.06 | 0.38225 | 3.5 | 0.6325 | 15.975 | 9.9 | 0.48667 | 0.024167 | 1 | 0.39167 | 0.011 | 0.036333 | 0.032167 | 1 | 0.38333 |  | 0.03 | 1 | 0.32667 |  | 7.17 | 0.0555 | 1 | 4.0833 | 15.1333 | 21 | 36.5 | 0.017 | 7.1483 | 0.055833 | 1 | 3.7833 | 16.2667 | 21 | 31.5 | 0.014 | 3.6167 | 3.6 | 3.5167 |  |  | MAXIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 10.6646 |  | 16.7846 | 27.4493 | 1.1578 | MAXIMUM | 55.137 | 3504.7814 |  | 507.489 | [6 empty] | 1.7231 | 1.5316 | 1.4359 | 0.18628 | 0.17851 | 0.17463 | 0.15523 | 0.14747 | 0.14747 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8086 | 0.71614 | 4.8473 | 1.1371 | 0.5216 | 0.093217 | 3.9969 | 0.7701 | 9.2554
MINIMUM | 6.53 | 15 | 16 | 6.87 | 77 | 113 | 15.9 | 0.303 | 0.032 | 6.01 | 10 | 0.043 | 6 | 10 |  | 5.97 | 10 |  | 6.04 | 0.363 | 4 | 0.65 | 15.2 | 9.8 | 0.50522 | 0.029 | 6.01 | 0.248 | 3 | 0.55 | 15.5 | 9.8 | 0.50522 | 6.04 | 0.305 | 3 | 0.55 | 15.7 | 9.8 | 0.48296 | 0.022 | 1 | 0.34 | 0.011 | 0.032 | 0.017 | 1 | 0.36 |  | 0.029 | 1 | 0.26 |  | 7.05 | 0.051 | 1 | 3.8 | 15 | 21 | 36 | 0.014 | 7.04 | 0.05 | 1 | 3.6 | 15.6 | 21 | 31 | 0.013 | 3.3 | 3.5 | 2.3 | [15 empty] | MIL/MIN |  | TOTAL | 18670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 960 | 900 | 1440 | 1350 | 1330 | 1120 | 1040 | 1080 | 2220 | 0 | 3720 | 3720 | 3720 | 266 | 321 | 39 | 4220 | 862 | 927 | 134 | 165 | 18 | 2260 | 462 | 885
MAXIMUM | 6.6 | 20 | 18 | 7.7 | 81 | 126 | 16.6 | 0.334 | 0.04 | 6.1 | 11 | 0.06 | 6.11 | 11 |  | 6 | 11 |  | 6.13 | 0.481 | 5 | 0.76 | 15.5 | 9.9 | 0.50915 | 0.042 | 6.11 | 0.325 | 4 | 0.66 | 16.6 | 10.1 | 0.51701 | 6.08 | 0.462 | 4 | 0.68 | 16.1 | 10.1 | 0.49407 | 0.026 | 1 | 0.44 | 0.011 | 0.039 | 0.046 | 1 | 0.42 |  | 0.031 | 1 | 0.45 |  | 7.41 | 0.06 | 1 | 4.6 | 15.6 | 21 | 37 | 0.02 | 7.26 | 0.059 | 1 | 4 | 16.9 | 21 | 32 | 0.015 | 3.9 | 3.7 | 4.1 | [17 empty] | AVERAGE | 6223.3333 | [9 empty] | 340 | 320 | 300 | 480 | 450 | 443.3333 | 373.3333 | 346.6667 | 360 | 740 |  | 1240 | 1240 | 1240 | 88.6667 | 107 | 13 | 1406.6667 | 287.3333 | 309 | 44.6667 | 55 | 6 | 753.3333 | 154 | 295
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0311 |  | TOTAL AVG COAG ALK: |  |  |  | 10.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.481 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.55 | [5 empty] | 6.0667 |  |  |  |  | 0.046 |  |  |  |  | 0.55 | [6 empty] | 0.046 | [16 empty] | Pump Station MIN |  | 2.3 | [17 empty] | MINIMUM | 6020 | [9 empty] | 320 | 320 | 300 | 480 | 440 | 440 | 360 | 320 | 340 | 740 |  | 1240 | 1240 | 1240 | 88 | 106 | 13 | 1390 | 285 | 309 | 44 | 54 | 6 | 740 | 150 | 295
[90 empty] | MAXIMUM | 6630 | [9 empty] | 360 | 320 | 300 | 480 | 460 | 450 | 400 | 380 | 380 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1430 | 292 | 309 | 46 | 56 | 6 | 770 | 157 | 295
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.582 |  | TOTAL MGD: |  | 0.012 |  |  | FINISHED SOUTH 1 |  | START: | 23827635 |  | END: | 23827647 |  |  | Alum | 4984 | 9238 | 9238 | 9220 | 9220 | 0 | [44 empty] | 0.55 | 9.9 | 25.697 | 14.1333 | 6.01 | 16.6 | 10 | 1.4133
[73 empty] | FINISHED 2 | 15.629 |  | TOTAL MGD: |  | 11.57 |  |  | FINISHED SOUTH 2 |  | START: | 44869270 |  | END: | 44880840 |  |  | Caustic | 6705 | 8030 | 8030
[73 empty] | TOTAL RAW | 29.878 |  | TOTAL MGD: |  | 4.581 |  |  | FINISHED CONWAY |  | START: | 10651843 |  | END: | 10656424 |  |  | Hypochlorite | 21 |  | 31
[76 empty] | TOTAL MGD: |  | 11.048 |  |  | FINISHED PERRY |  | START: | 34711551 |  | END: | 34722599 |  |  | Phosphate | 1360
[76 empty] | TOTAL MGD: |  | 9.954 |  |  | RAW PLANT 1 |  | START: | 31809487 |  | END: | 31819441 |  |  | Fluoride | 2650 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.073 |  |  | RAW PLANT 2 |  | START: | 31771587 |  | END: | 31781660 |  |  | Cal~Flo | 16.5 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.851 |  |  | RAW PLANT 3 |  | START: | 8404949 |  | END: | 8414800 |  |  | Zinc | 2471
[76 empty] | TOTAL MGD: |  | 0.617 |  |  | DECANT |  | START: | 1940050 |  | END: | 1940667 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.79311 |  |  | BLOW DOWN |  | START: | 9242.4833 |  | END: | 9243.2764 |  |  | NH3 | 10 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 492
23827647
44880840
10656424
34722599
31819441
31781660
8414800
1940667
9243.2764
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 5
DATE: | 2019-04-05 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-05 | [23 empty] | DATE: | 2019-04-05
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-05 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43560.0038 | 2,3,5 | 60 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 10.6646 | 1,3 | 16.7846 | 27.4493 | 1.1578 | 43560.0038 | 50.064 | 3135.857 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6273 | 1.5316 | 1.4359 | 0.18628 | 0.17851 | 0.17075 | 0.13971 | 0.13195 | 0.13195 | 1.4077 | 1 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49366 | 0.10099 | 3.8086 | 0.69898 | 4.8473 | 1.0876 | 0.50297 | 0.093217 | 3.9588 | 0.76029 | 9.2554 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.464 | 4 | 0.68 | 15.5 | 9.8 | 0.50522 |  | 6.12 | 0.332 | 4 | 0.6 | 15.5 | 9.8 | 0.50522 | 6.1 | 0.315 | 3 | 0.65 | 16.5 | 9.8 | 0.48296 | [13 empty] | 7.18 | 0.054 | 1 | 4.1 | 15.5 |  |  |  | 7.15 | 0.052 | 1 | 4.2 | 16.5 |  |  |  | 4 | 3.7 | 1.6 | [18 empty] | 6020 | [6 empty] | 0 | 0 | 0 | 340 | 320 | 300 | 480 | 460 | 440 | 360 | 340 | 340 | 740 |  | 1240 | 1240 | 1240 | 88 | 106 | 13 | 1400 | 285 | 309 | 44 | 54 | 6 | 750 | 155 | 295 |  | 1:00 | 0.68 | 9.8 | 25.9592 | 17.6522 | 6.1 | 15.5 | 10 | 1.7652 | 15 | 6.5 | 0.38522 | 1:00 | 0.6 | 9.8 | 25.9592 | 15.5755 | 6.12 | 15.5 | 10 | 1.5576 | 15 | 6.5 | 0.38522 | 1:00 | 0.65 | 9.8 | 27.551 | 17.9082 | 6.1 | 16.5 | 10 | 1.7908 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43560.34 | 2,3,5 | 56 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 9.347 | 1,3 | 17.6126 | 26.9597 | 1.1578 | 43560.34 | 49.8977 | 3074.3696 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6273 | 1.6273 | 1.5316 | 0.2018 | 0.2018 | 0.15523 | 0.13971 | 0.13971 | 0.13971 | 1.4077 | 1 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49831 | 0.10099 | 3.8026 | 0.71124 | 4.8473 | 1.0876 | 0.51228 | 0.093217 | 4.0069 | 0.78482 | 9.2554 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.58 | 22 | 18 | 7.18 | 78 | 116 | 17 | 0.312 |  | 6.06 | 11 | 0.049 | 6.08 | 11 |  | 6.03 | 11 | [8 empty] | 0.035 | [14 empty] | 0.024 | 1 | 0.4 |  | 0.035 | 0.035 | 1 | 0.36 |  | 0.03 | 1 | 0.3 | [38 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 320 | 520 | 520 | 400 | 360 | 360 | 360 | 740 |  | 1240 | 1240 | 1240 | 88 | 107 | 13 | 1420 | 290 | 309 | 44 | 55 | 6 | 770 | 160 | 295 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43560.8109 | 2,3,5 | 56 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 9.347 | 1,3 | 17.6126 | 26.9597 | 1.3104 | 43560.8109 | 49.8977 | 3258.8318 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6273 | 1.6273 | 1.6273 | 0.19404 | 0.2018 | 0.14747 | 0.14747 | 0.13971 | 0.13971 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8076 | 0.71124 | 5.0983 | 1.1371 | 0.54023 | 0.093217 | 4.0279 | 0.75538 | 9.7261 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.15 | 0.052 | 1 | 4 | 15.5 |  |  |  | 7.1 | 0.05 | 1 | 4 | 16.5 |  |  |  | 3.7 | 3.7 | 1.9 | [18 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 340 | 500 | 520 | 380 | 380 | 360 | 360 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1420 | 290 | 325 | 46 | 58 | 6 | 760 | 154 | 310 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.61 | 20 | 19 | 7.05 | 78 | 115 | 17.1 | 0.318 |  | 6.05 | 10 | 0.061 | 6.06 | 11 |  | 6.01 | 10 | [8 empty] | 0.041 | [14 empty] | 0.023 | 1 | 0.34 |  | 0.04 | 0.042 | 1 | 0.3 |  | 0.024 | 1 | 0.23 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.032 | [9 empty] | 6.07 | 0.363 | 5 | 0.78 | 15.7 | 9.7 | 0.50129 |  | 6.06 | 0.252 | 4 | 0.54 | 16.5 | 9.9 | 0.50915 | 6.12 | 0.228 | 4 | 0.61 | 16.6 | 10 | 0.49037 |  |  |  | 0.011 | [9 empty] | 7.04 | 0.055 | 1 | 4.1 | 15.6 | 22 | 30 | 0.013 | 7.4 | 0.058 | 1 | 4.2 | 16.5 | 21 | 33 | 0.011 | 4.1 | 3.7 | 3.8 | [55 empty] | 9:00 | 0.78 | 9.7 | 26.2268 | 20.4569 | 6.07 | 15.7 | 10 | 2.0457 | 15 | 6.5 | 0.38129 | 9:00 | 0.54 | 9.9 | 25.697 | 13.8764 | 6.06 | 16.5 | 10 | 1.3876 | 15 | 6.5 | 0.38915 | 9:00 | 0.61 | 10 | 27 | 16.47 | 6.12 | 16.6 | 10 | 1.647 | 15 | 6.5 | 0.37037
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.6 | 21 | 20 | 7.09 | 76 | 114 | 16.9 | 0.31 |  | 5.98 | 11 | 0.055 | 5.99 | 10 |  | 6 | 11 | [8 empty] | 0.038 | [14 empty] | 0.023 | 1 | 0.38 |  | 0.037 | 0.068 | 1 | 0.42 |  | 0.066 | 1 | 0.44 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.03 | 0.384 | 4 | 0.67 | 15.8 | 9.9 | 0.50915 |  | 6.11 | 0.25 | 4 | 0.73 | 16.7 | 10 | 0.51308 | 6.05 | 0.255 | 4 | 0.59 | 16.7 | 10 | 0.49037 | [13 empty] | 7.08 | 0.053 | 1 | 3.8 | 15.6 |  |  |  | 7.14 | 0.055 | 1 | 4 | 16.6 |  |  |  | 4 | 3.6 | 3.6 | [55 empty] | 13:00 | 0.67 | 9.9 | 25.697 | 17.217 | 6.03 | 15.8 | 10 | 1.7217 | 15 | 6.5 | 0.38915 | 13:00 | 0.73 | 10 | 25.44 | 18.5712 | 6.11 | 16.7 | 10 | 1.8571 | 15 | 6.5 | 0.39308 | 13:00 | 0.59 | 10 | 27 | 15.93 | 6.05 | 16.7 | 10 | 1.593 | 15 | 6.5 | 0.37037
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.62 | 18 | 16 | 6.82 | 77 | 115 | 16.6 | 0.312 |  | 6.14 | 11 | 0.061 | 6.11 | 12 |  | 6.02 | 12 | [8 empty] | 0.041 | [14 empty] | 0.02 | 1 | 0.31 |  | 0.038 | 0.044 | 1 | 0.34 |  | 0.051 | 1 | 0.3 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.09 | 0.056 | 1 | 3.9 | 15.8 |  |  |  | 7.15 | 0.057 | 1 | 3.5 | 16.7 |  |  |  | 3.9 | 3.6 | 4.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.67 | 21 | 19 | 6.81 | 75 | 109 | 16.7 | 0.304 |  | 6.08 | 12 | 0.053 | 6.12 | 12 |  | 6.06 | 12 | [8 empty] | 0.038 | [14 empty] | 0.022 | 1 | 0.36 |  | 0.038 | 0.024 | 1 | 0.34 |  | 0.047 | 1 | 0.39 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.037 | [9 empty] | 6.19 | 0.43 | 5 | 0.66 | 15.8 | 9.8 | 0.50522 |  | 6.18 | 0.264 | 4 | 0.67 | 16.5 | 9.8 | 0.50522 | 6.12 | 0.441 | 4 | 0.59 | 16.6 | 9.8 | 0.48296 |  |  |  | 0.012 | [9 empty] | 7.3 | 0.06 | 1 | 3.8 | 15.6 | 22 | 36 | 0.019 | 7.4 | 0.062 | 2 | 4 | 16.1 | 22 | 32 | 0.015 | 4 | 3.7 | 4.2 | [55 empty] | 21:00 | 0.66 | 9.8 | 25.9592 | 17.1331 | 6.19 | 15.8 | 10 | 1.7133 | 15 | 6.5 | 0.38522 | 21:00 | 0.67 | 9.8 | 25.9592 | 17.3927 | 6.18 | 16.5 | 10 | 1.7393 | 15 | 6.5 | 0.38522 | 21:00 | 0.59 | 9.8 | 27.551 | 16.2551 | 6.12 | 16.6 | 10 | 1.6255 | 15 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 29.4 | 29.4 | 29.4 | 88.2 | 27.9 | 27.9 | 27.9 | 83.7 | 0 | 29.3587 | 0 | 52.0099 | 81.3686 | 3.6259 | TOTAL | 149.8595 | 9469.0584 | 0 | 1474.8899 | 0 | 0 | 0 | 0 | 0 | 0 | 4.882 | 4.7863 | 4.5948 | 0.58211 | 0.58211 | 0.47345 | 0.42688 | 0.41136 | 0.41136 | 4.223 | 4 | 0.21103 | 0.21103 | 0.21103 | 3.2876 | 1.4949 | 0.30296 | 11.4188 | 2.1215 | 14.793 | 3.3123 | 1.5555 | 0.27965 | 11.9936 | 2.3005 | 28.2369 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.62 | 20 | 19 | 6.94 | 77 | 115 | 16.7 | 0.309 |  | 6.1 | 11 | 0.06 | 6.1 | 12 |  | 6.03 | 11 | [8 empty] | 0.038 | [14 empty] | 0.022 | 1 | 0.4 |  | 0.04 | 0.042 | 1 | 0.41 |  | 0.045 | 1 | 0.39 | [22 empty] | AVERAGE | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.7862 |  | 17.3366 | 27.1229 | 1.2086 | AVERAGE | 49.9532 | 3156.3528 |  | 491.63 | 0 | 0 | 0 |  |  |  | 1.6273 | 1.5954 | 1.5316 | 0.19404 | 0.19404 | 0.15782 | 0.14229 | 0.13712 | 0.13712 | 1.4077 | 1.3333 | 0.070344 | 0.070344 | 0.070344 | 1.0959 | 0.49831 | 0.10099 | 3.8063 | 0.70715 | 4.931 | 1.1041 | 0.51849 | 0.093217 | 3.9979 | 0.76683 | 9.4123 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.7 | 122 | 111 | 41.89 | 461 | 684 | 101 | 1.865 | 0.069 | 36.41 | 66 | 0.339 | 36.46 | 68 | 0 | 36.15 | 67 | 0 | 24.39 | 1.641 | 18 | 2.79 | 62.8 | 39.2 | 2.0209 | 0.231 | 24.47 | 1.098 | 16 | 2.54 | 65.2 | 39.5 | 2.0327 | 24.39 | 1.239 | 15 | 2.44 | 66.4 | 39.6 | 1.9467 | 0.134 | 6 | 2.19 | 0.023 | 0.228 | 0.255 | 6 | 2.17 | 0 | 0.263 | 6 | 2.05 | 0 | 42.84 | 0.33 | 6 | 23.7 | 93.6 | 44 | 66 | 0.032 | 43.34 | 0.334 | 7 | 23.9 | 98.9 | 43 | 65 | 0.026 | 23.7 | 22 | 19.6 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.347 |  | 16.7846 | 26.9597 | 1.1578 | MINIMUM | 49.8977 | 3074.3696 |  | 491.63 | [6 empty] | 1.6273 | 1.5316 | 1.4359 | 0.18628 | 0.17851 | 0.14747 | 0.13971 | 0.13195 | 0.13195 | 1.4077 | 1 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49366 | 0.10099 | 3.8026 | 0.69898 | 4.8473 | 1.0876 | 0.50297 | 0.093217 | 3.9588 | 0.75538 | 9.2554 |  | MIN | 0.66 | 9.8 | 25.9592 | 17.1331 | 6.19 | 15.8 | 10 | 1.7133 |  |  |  | MIN | 0.54 | 9.9 | 25.697 | 13.8764 | 6.06 | 16.5 | 10 | 1.3876 |  |  |  | MIN | 0.59 | 10 | 27 | 15.93 | 6.05 | 16.7 | 10 | 1.593 |  |  |  | 1.3876
AVERAGE | 6.6167 | 20.3333 | 18.5 | 6.9817 | 76.8333 | 114 | 16.8333 | 0.31083 | 0.0345 | 6.0683 | 11 | 0.0565 | 6.0767 | 11.3333 |  | 6.025 | 11.1667 |  | 6.0975 | 0.41025 | 4.5 | 0.6975 | 15.7 | 9.8 | 0.50522 | 0.0385 | 6.1175 | 0.2745 | 4 | 0.635 | 16.3 | 9.875 | 0.50817 | 6.0975 | 0.30975 | 3.75 | 0.61 | 16.6 | 9.9 | 0.48667 | 0.022333 | 1 | 0.365 | 0.0115 | 0.038 | 0.0425 | 1 | 0.36167 |  | 0.043833 | 1 | 0.34167 |  | 7.14 | 0.055 | 1 | 3.95 | 15.6 | 22 | 33 | 0.016 | 7.2233 | 0.055667 | 1.1667 | 3.9833 | 16.4833 | 21.5 | 32.5 | 0.013 | 3.95 | 3.6667 | 3.2667 |  |  | MAXIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 10.6646 |  | 17.6126 | 27.4493 | 1.3104 | MAXIMUM | 50.064 | 3258.8318 |  | 491.63 | [6 empty] | 1.6273 | 1.6273 | 1.6273 | 0.2018 | 0.2018 | 0.17075 | 0.14747 | 0.13971 | 0.13971 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8086 | 0.71124 | 5.0983 | 1.1371 | 0.54023 | 0.093217 | 4.0279 | 0.78482 | 9.7261
MINIMUM | 6.58 | 18 | 16 | 6.81 | 75 | 109 | 16.6 | 0.304 | 0.032 | 5.98 | 10 | 0.049 | 5.99 | 10 |  | 6 | 10 |  | 6.03 | 0.363 | 4 | 0.66 | 15.5 | 9.7 | 0.50129 | 0.035 | 6.06 | 0.25 | 4 | 0.54 | 15.5 | 9.8 | 0.50522 | 6.05 | 0.228 | 3 | 0.59 | 16.5 | 9.8 | 0.48296 | 0.02 | 1 | 0.31 | 0.011 | 0.035 | 0.024 | 1 | 0.3 |  | 0.024 | 1 | 0.23 |  | 7.04 | 0.052 | 1 | 3.8 | 15.5 | 22 | 30 | 0.013 | 7.1 | 0.05 | 1 | 3.5 | 16.1 | 21 | 32 | 0.011 | 3.7 | 3.6 | 1.6 | [15 empty] | MIL/MIN |  | TOTAL | 18020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 1000 | 960 | 1500 | 1500 | 1220 | 1100 | 1060 | 1060 | 2220 | 0 | 3720 | 3720 | 3720 | 266 | 321 | 39 | 4240 | 865 | 943 | 134 | 167 | 18 | 2280 | 469 | 900
MAXIMUM | 6.67 | 22 | 20 | 7.18 | 78 | 116 | 17.1 | 0.318 | 0.037 | 6.14 | 12 | 0.061 | 6.12 | 12 |  | 6.06 | 12 |  | 6.19 | 0.464 | 5 | 0.78 | 15.8 | 9.9 | 0.50915 | 0.041 | 6.18 | 0.332 | 4 | 0.73 | 16.7 | 10 | 0.51308 | 6.12 | 0.441 | 4 | 0.65 | 16.7 | 10 | 0.49037 | 0.024 | 1 | 0.4 | 0.012 | 0.04 | 0.068 | 1 | 0.42 |  | 0.066 | 1 | 0.44 |  | 7.3 | 0.06 | 1 | 4.1 | 15.8 | 22 | 36 | 0.019 | 7.4 | 0.062 | 2 | 4.2 | 16.7 | 22 | 33 | 0.015 | 4.1 | 3.7 | 4.5 | [17 empty] | AVERAGE | 6006.6667 | [9 empty] | 340 | 333.3333 | 320 | 500 | 500 | 406.6667 | 366.6667 | 353.3333 | 353.3333 | 740 |  | 1240 | 1240 | 1240 | 88.6667 | 107 | 13 | 1413.3333 | 288.3333 | 314.3333 | 44.6667 | 55.6667 | 6 | 760 | 156.3333 | 300
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0567 |  | TOTAL AVG COAG ALK: |  |  |  | 11.1667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.464 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.1042 |  |  |  |  | 0.068 |  |  |  |  | 0.54 | [6 empty] | 0.068 | [16 empty] | Pump Station MIN |  | 1.6 | [17 empty] | MINIMUM | 6000 | [9 empty] | 340 | 320 | 300 | 480 | 460 | 380 | 360 | 340 | 340 | 740 |  | 1240 | 1240 | 1240 | 88 | 106 | 13 | 1400 | 285 | 309 | 44 | 54 | 6 | 750 | 154 | 295
[90 empty] | MAXIMUM | 6020 | [9 empty] | 340 | 340 | 340 | 520 | 520 | 440 | 380 | 360 | 360 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1420 | 290 | 325 | 46 | 58 | 6 | 770 | 160 | 310
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.575 |  | TOTAL MGD: |  | 0.011 |  |  | FINISHED SOUTH 1 |  | START: | 23827647 |  | END: | 23827658 |  |  | Alum | 4864 | 11000 | 11000 | 8700 | 8700 | 0 | [44 empty] | 0.54 | 9.9 | 25.697 | 13.8764 | 6.06 | 16.5 | 10 | 1.3876
[73 empty] | FINISHED 2 | 15.323 |  | TOTAL MGD: |  | 11.564 |  |  | FINISHED SOUTH 2 |  | START: | 44880840 |  | END: | 44892404 |  |  | Caustic | 6585 | 7960 | 7960
[73 empty] | TOTAL RAW | 29.629 |  | TOTAL MGD: |  | 4.236 |  |  | FINISHED CONWAY |  | START: | 10656424 |  | END: | 10660660 |  |  | Hypochlorite | 19 |  | 41
[76 empty] | TOTAL MGD: |  | 11.087 |  |  | FINISHED PERRY |  | START: | 34722599 |  | END: | 34733686 |  |  | Phosphate | 1358
[76 empty] | TOTAL MGD: |  | 9.721 |  |  | RAW PLANT 1 |  | START: | 31819441 |  | END: | 31829162 |  |  | Fluoride | 2700 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.834 |  |  | RAW PLANT 2 |  | START: | 31781660 |  | END: | 31791494 |  |  | Cal~Flo | 15 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.074 |  |  | RAW PLANT 3 |  | START: | 8414800 |  | END: | 8424874 |  |  | Zinc | 2478
[76 empty] | TOTAL MGD: |  | 0.645 |  |  | DECANT |  | START: | 1940667 |  | END: | 1941312 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.7395 |  |  | BLOW DOWN |  | START: | 9243.2764 |  | END: | 9244.0159 |  |  | NH3 | 10 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 492
23827658
44892404
10660660
34733686
31829162
31791494
8424874
1941312
9244.0159
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 6
DATE: | 2019-04-06 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-06 | [23 empty] | DATE: | 2019-04-06
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-06 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43561.0087 | 2,3,5 | 56 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 9.347 | 1,3 | 17.6126 | 26.9597 | 1.3104 | 43561.0087 | 49.8977 | 3258.8318 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6273 | 1.6273 | 1.6273 | 0.19404 | 0.2018 | 0.14747 | 0.14747 | 0.13971 | 0.13971 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8076 | 0.71124 | 5.0983 | 1.1371 | 0.54023 | 0.093217 | 4.0279 | 0.75538 | 9.7261 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.427 | 4 | 0.65 | 16 | 9.8 | 0.50522 |  | 6.15 | 0.278 | 4 | 0.68 | 17 | 9.8 | 0.50522 | 6.12 | 0.338 | 4 | 0.6 | 17 | 9.8 | 0.48296 | [13 empty] | 7.3 | 0.058 | 1 | 3.8 | 15.5 |  |  |  | 7.32 | 0.055 | 1 | 3.8 | 16.5 |  |  |  | 3.6 | 3.7 | 1.7 | [18 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 340 | 500 | 520 | 380 | 380 | 360 | 360 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1420 | 290 | 325 | 46 | 58 | 6 | 760 | 154 | 310 |  | 1:00 | 0.65 | 9.8 | 25.9592 | 16.8735 | 6.14 | 16 | 10 | 1.6873 | 15 | 6.5 | 0.38522 | 1:00 | 0.68 | 9.8 | 25.9592 | 17.6522 | 6.15 | 17 | 10 | 1.7652 | 15 | 6.5 | 0.38522 | 1:00 | 0.6 | 9.8 | 27.551 | 16.5306 | 6.12 | 17 | 10 | 1.6531 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43561.3225 | 2,3,5 | 56 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 9.3787 | 1,3 | 13.9925 | 23.3712 | 1.3104 | 43561.3225 | 50.2304 | 3258.8318 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2444 | 1.5316 | 1.5316 | 0.18628 | 0.18628 | 0.18628 | 0.13971 | 0.12418 | 0.15523 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49831 | 0.10099 | 3.7981 | 0.71124 | 5.0983 | 1.0876 | 0.51228 | 0.093217 | 4.0107 | 0.73576 | 9.7261 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.68 | 22 | 20 | 7.35 | 75 | 116 | 17.4 | 0.294 |  | 6.06 | 12 | 0.05 | 6.12 | 12 |  | 6.05 | 12 | [8 empty] | 0.038 | [14 empty] | 0.02 | 1 | 0.38 |  | 0.039 | 0.03 | 1 | 0.35 |  | 0.044 | 1 | 0.36 | [38 empty] | 6040 | [6 empty] | 0 | 0 | 0 | 260 | 320 | 320 | 480 | 480 | 480 | 360 | 320 | 400 | 740 |  | 1240 | 1240 | 1240 | 88 | 107 | 13 | 1410 | 290 | 325 | 44 | 55 | 6 | 730 | 150 | 310 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43561.7829 | 2,3,5 | 56 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 9.3787 | 1,3 | 13.9925 | 23.3712 | 1.3104 | 43561.7829 | 49.8977 | 3381.8066 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4359 | 1.4359 | 1.4359 | 0.18628 | 0.18628 | 0.18628 | 0.14747 | 0.13583 | 0.13583 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.7917 | 0.72595 | 5.0983 | 1.1371 | 0.5216 | 0.093217 | 3.9998 | 0.73576 | 9.7261 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.28 | 0.052 | 1 | 3.9 | 15.5 |  |  |  | 7.3 | 0.058 | 1 | 3.8 | 16.5 |  |  |  | 3.5 | 3.7 | 2.4 | [18 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 480 | 480 | 480 | 380 | 350 | 350 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1440 | 296 | 325 | 46 | 56 | 6 | 740 | 150 | 310 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.65 | 23 | 18 | 7.75 | 73 | 112 | 17.4 | 0.296 |  | 6.04 | 11 | 0.054 | 6.1 | 12 |  | 6.05 | 11 | [8 empty] | 0.041 | [14 empty] | 0.021 | 1 | 0.33 |  | 0.04 | 0.044 | 1 | 0.35 |  | 0.039 | 1 | 0.43 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.029 | [9 empty] | 6.12 | 0.369 | 4 | 0.58 | 16.1 | 9.5 | 0.49343 |  | 6.13 | 0.298 | 4 | 0.56 | 17.1 | 9.5 | 0.49343 | 6.15 | 0.256 | 3 | 0.56 | 17.1 | 9.6 | 0.47556 |  |  |  | 0.015 | [9 empty] | 7.44 | 0.054 | 1 | 3.7 | 16.1 | 22 | 32 | 0.011 | 7.29 | 0.052 | 1 | 3.5 | 16.7 | 23 | 31 | 0.011 | 3.5 | 3.7 | 4.3 | [55 empty] | 9:00 | 0.58 | 9.5 | 26.7789 | 15.5318 | 6.12 | 16.1 | 10 | 1.5532 | 15 | 6.5 | 0.37343 | 9:00 | 0.56 | 9.5 | 26.7789 | 14.9962 | 6.13 | 17.1 | 10 | 1.4996 | 15 | 6.5 | 0.37343 | 9:00 | 0.56 | 9.6 | 28.125 | 15.75 | 6.15 | 17.1 | 10 | 1.575 | 15 | 6.5 | 0.35556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.76 | 20 | 18 | 7.24 | 74 | 109 | 17.4 | 0.298 |  | 6.14 | 10 | 0.075 | 6.17 | 12 |  | 6.12 | 12 | [8 empty] | 0.041 | [14 empty] | 0.022 | 1 | 0.2 |  | 0.037 | 0.037 | 1 | 0.32 |  | 0.037 | 1 | 0.37 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.13 | 0.309 | 4 | 0.48 | 16.2 | 9.5 | 0.49343 |  | 6.2 | 0.278 | 3 | 0.57 | 17.2 | 9.5 | 0.49343 | 6.21 | 0.25 | 3 | 0.49 | 17.2 | 9.6 | 0.47556 | [13 empty] | 7.37 | 0.053 | 1 | 4.1 | 16.2 |  |  |  | 7.39 | 0.05 | 1 | 3.7 | 17 |  |  |  | 3.6 | 3.8 | 4.1 | [55 empty] | 13:00 | 0.48 | 9.5 | 26.7789 | 12.8539 | 6.13 | 16.2 | 10 | 1.2854 | 15 | 6.5 | 0.37343 | 13:00 | 0.57 | 9.5 | 26.7789 | 15.264 | 6.2 | 17.2 | 10 | 1.5264 | 15 | 6.5 | 0.37343 | 13:00 | 0.49 | 9.6 | 28.125 | 13.7812 | 6.21 | 17.2 | 10 | 1.3781 | 15 | 6.5 | 0.35556
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.7 | 21 | 19 | 7.02 | 73 | 112 | 17.5 | 0.303 |  | 6.12 | 11 | 0.045 | 6.15 | 11 |  | 6.09 | 12 | [8 empty] | 0.037 | [14 empty] | 0.023 | 1 | 0.18 |  | 0.033 | 0.034 | 1 | 0.29 |  | 0.036 | 1 | 0.34 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.38 | 0.049 | 1 | 3.6 | 16.4 |  |  |  | 7.36 | 0.052 | 1 | 3.4 | 17.6 |  |  |  | 3.7 | 3.8 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.7 | 20 | 19 | 6.7 | 73 | 111 | 17.1 | 0.302 |  | 6.14 | 11 | 0.059 | 6.16 | 11 |  | 6.11 | 11 | [8 empty] | 0.038 | [14 empty] | 0.022 | 1 | 0.24 |  | 0.041 | 0.044 | 1 | 0.3 |  | 0.034 | 1 | 0.36 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.036 | [9 empty] | 6.18 | 0.371 | 4 | 0.52 | 16 | 9.8 | 0.50522 |  | 6.2 | 0.293 | 4 | 0.63 | 16.6 | 9.8 | 0.50522 | 6.18 | 0.319 | 4 | 0.54 | 17.1 | 9.8 | 0.48296 |  |  |  | 0.011 | [9 empty] | 7.45 | 0.051 | 1 | 3.7 | 15.9 | 22 | 30 | 0.012 | 7.46 | 0.055 | 1 | 3.7 | 16.3 | 22 | 33 | 0.015 | 3.7 | 3.7 | 4 | [55 empty] | 21:00 | 0.52 | 9.8 | 25.9592 | 13.4988 | 6.18 | 16 | 10 | 1.3499 | 15 | 6.5 | 0.38522 | 21:00 | 0.63 | 9.8 | 25.9592 | 16.3543 | 6.2 | 16.6 | 10 | 1.6354 | 15 | 6.5 | 0.38522 | 21:00 | 0.54 | 9.8 | 27.551 | 14.8776 | 6.18 | 17.1 | 10 | 1.4878 | 15 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 29.4 | 29.4 | 29.4 | 88.2 | 27.9 | 27.9 | 27.9 | 83.7 | 0 | 28.1045 | 0 | 45.5976 | 73.7021 | 3.9312 | TOTAL | 150.0258 | 9899.4702 | 0 | 1474.8899 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3077 | 4.5948 | 4.5948 | 0.56659 | 0.57435 | 0.52002 | 0.43464 | 0.39972 | 0.43076 | 4.223 | 6 | 0.21103 | 0.21103 | 0.21103 | 3.3123 | 1.5043 | 0.30296 | 11.3974 | 2.1484 | 15.295 | 3.3618 | 1.5741 | 0.27965 | 12.0384 | 2.2269 | 29.1782 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.7 | 20 | 18 | 6.94 | 78 | 112 | 17 | 0.317 |  | 6.14 | 11 | 0.051 | 6.19 | 12 |  | 6.1 | 11 | [8 empty] | 0.04 | [14 empty] | 0.018 | 1 | 0.29 |  | 0.04 | 0.044 | 1 | 0.34 |  | 0.037 | 1 | 0.34 | [22 empty] | AVERAGE | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.3682 |  | 15.1992 | 24.5674 | 1.3104 | AVERAGE | 50.0086 | 3299.8234 |  | 491.63 | 0 | 0 | 0 |  |  |  | 1.4359 | 1.5316 | 1.5316 | 0.18886 | 0.19145 | 0.17334 | 0.14488 | 0.13324 | 0.14359 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1041 | 0.50142 | 0.10099 | 3.7991 | 0.71614 | 5.0983 | 1.1206 | 0.5247 | 0.093217 | 4.0128 | 0.7423 | 9.7261 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 40.19 | 126 | 112 | 43 | 446 | 672 | 103.8 | 1.81 | 0.065 | 36.64 | 66 | 0.334 | 36.89 | 70 | 0 | 36.52 | 69 | 0 | 24.57 | 1.476 | 16 | 2.23 | 64.3 | 38.6 | 1.9973 | 0.235 | 24.68 | 1.147 | 15 | 2.44 | 67.9 | 38.6 | 1.9973 | 24.66 | 1.163 | 14 | 2.19 | 68.4 | 38.8 | 1.917 | 0.126 | 6 | 1.62 | 0.026 | 0.23 | 0.233 | 6 | 1.95 | 0 | 0.227 | 6 | 2.2 | 0 | 44.22 | 0.317 | 6 | 22.8 | 95.6 | 44 | 62 | 0.023 | 44.12 | 0.322 | 6 | 21.9 | 100.6 | 45 | 64 | 0.026 | 21.6 | 22.4 | 19.8 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.347 |  | 13.9925 | 23.3712 | 1.3104 | MINIMUM | 49.8977 | 3258.8318 |  | 491.63 | [6 empty] | 1.2444 | 1.4359 | 1.4359 | 0.18628 | 0.18628 | 0.14747 | 0.13971 | 0.12418 | 0.13583 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.0876 | 0.49831 | 0.10099 | 3.7917 | 0.71124 | 5.0983 | 1.0876 | 0.51228 | 0.093217 | 3.9998 | 0.73576 | 9.7261 |  | MIN | 0.48 | 9.5 | 26.7789 | 12.8539 | 6.13 | 16.2 | 10 | 1.2854 |  |  |  | MIN | 0.56 | 9.5 | 26.7789 | 14.9962 | 6.13 | 17.1 | 10 | 1.4996 |  |  |  | MIN | 0.49 | 9.6 | 28.125 | 13.7812 | 6.21 | 17.2 | 10 | 1.3781 |  |  |  | 1.2854
AVERAGE | 6.6983 | 21 | 18.6667 | 7.1667 | 74.3333 | 112 | 17.3 | 0.30167 | 0.0325 | 6.1067 | 11 | 0.055667 | 6.1483 | 11.6667 |  | 6.0867 | 11.5 |  | 6.1425 | 0.369 | 4 | 0.5575 | 16.075 | 9.65 | 0.49932 | 0.039167 | 6.17 | 0.28675 | 3.75 | 0.61 | 16.975 | 9.65 | 0.49932 | 6.165 | 0.29075 | 3.5 | 0.5475 | 17.1 | 9.7 | 0.47926 | 0.021 | 1 | 0.27 | 0.013 | 0.038333 | 0.038833 | 1 | 0.325 |  | 0.037833 | 1 | 0.36667 |  | 7.37 | 0.052833 | 1 | 3.8 | 15.9333 | 22 | 31 | 0.0115 | 7.3533 | 0.053667 | 1 | 3.65 | 16.7667 | 22.5 | 32 | 0.013 | 3.6 | 3.7333 | 3.3 |  |  | MAXIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.3787 |  | 17.6126 | 26.9597 | 1.3104 | MAXIMUM | 50.2304 | 3381.8066 |  | 491.63 | [6 empty] | 1.6273 | 1.6273 | 1.6273 | 0.19404 | 0.2018 | 0.18628 | 0.14747 | 0.13971 | 0.15523 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8076 | 0.72595 | 5.0983 | 1.1371 | 0.54023 | 0.093217 | 4.0279 | 0.75538 | 9.7261
MINIMUM | 6.65 | 20 | 18 | 6.7 | 73 | 109 | 17 | 0.294 | 0.029 | 6.04 | 10 | 0.045 | 6.1 | 11 |  | 6.05 | 11 |  | 6.12 | 0.309 | 4 | 0.48 | 16 | 9.5 | 0.49343 | 0.037 | 6.13 | 0.278 | 3 | 0.56 | 16.6 | 9.5 | 0.49343 | 6.12 | 0.25 | 3 | 0.49 | 17 | 9.6 | 0.47556 | 0.018 | 1 | 0.18 | 0.011 | 0.033 | 0.03 | 1 | 0.29 |  | 0.034 | 1 | 0.34 |  | 7.28 | 0.049 | 1 | 3.6 | 15.5 | 22 | 30 | 0.011 | 7.29 | 0.05 | 1 | 3.4 | 16.3 | 22 | 31 | 0.011 | 3.5 | 3.7 | 1.7 | [15 empty] | MIL/MIN |  | TOTAL | 18040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 960 | 960 | 1460 | 1480 | 1340 | 1120 | 1030 | 1110 | 2220 | 0 | 3720 | 3720 | 3720 | 268 | 323 | 39 | 4270 | 876 | 975 | 136 | 169 | 18 | 2230 | 454 | 930
MAXIMUM | 6.76 | 23 | 20 | 7.75 | 78 | 116 | 17.5 | 0.317 | 0.036 | 6.14 | 12 | 0.075 | 6.19 | 12 |  | 6.12 | 12 |  | 6.18 | 0.427 | 4 | 0.65 | 16.2 | 9.8 | 0.50522 | 0.041 | 6.2 | 0.298 | 4 | 0.68 | 17.2 | 9.8 | 0.50522 | 6.21 | 0.338 | 4 | 0.6 | 17.2 | 9.8 | 0.48296 | 0.023 | 1 | 0.38 | 0.015 | 0.041 | 0.044 | 1 | 0.35 |  | 0.044 | 1 | 0.43 |  | 7.45 | 0.058 | 1 | 4.1 | 16.4 | 22 | 32 | 0.012 | 7.46 | 0.058 | 1 | 3.8 | 17.6 | 23 | 33 | 0.015 | 3.7 | 3.8 | 4.3 | [17 empty] | AVERAGE | 6013.3333 | [9 empty] | 300 | 320 | 320 | 486.6667 | 493.3333 | 446.6667 | 373.3333 | 343.3333 | 370 | 740 |  | 1240 | 1240 | 1240 | 89.3333 | 107.6667 | 13 | 1423.3333 | 292 | 325 | 45.3333 | 56.3333 | 6 | 743.3333 | 151.3333 | 310
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1139 |  | TOTAL AVG COAG ALK: |  |  |  | 11.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.427 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.48 | [5 empty] | 6.1592 |  |  |  |  | 0.044 |  |  |  |  | 0.48 | [6 empty] | 0.044 | [16 empty] | Pump Station MIN |  | 1.7 | [17 empty] | MINIMUM | 6000 | [9 empty] | 260 | 300 | 300 | 480 | 480 | 380 | 360 | 320 | 350 | 740 |  | 1240 | 1240 | 1240 | 88 | 107 | 13 | 1410 | 290 | 325 | 44 | 55 | 6 | 730 | 150 | 310
[90 empty] | MAXIMUM | 6040 | [9 empty] | 340 | 340 | 340 | 500 | 520 | 480 | 380 | 360 | 400 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1440 | 296 | 325 | 46 | 58 | 6 | 760 | 154 | 310
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.017 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23827658 |  | END: | 23827667 |  |  | Alum | 4852 | 10383 | 10383 | 8211 | 8211 | 0 | [44 empty] | 0.48 | 9.5 | 26.7789 | 12.8539 | 6.13 | 16.2 | 10 | 1.2854
[73 empty] | FINISHED 2 | 15.764 |  | TOTAL MGD: |  | 11.008 |  |  | FINISHED SOUTH 2 |  | START: | 44892404 |  | END: | 44903412 |  |  | Caustic | 6468 | 7963 | 7963
[73 empty] | TOTAL RAW | 29.173 |  | TOTAL MGD: |  | 4.794 |  |  | FINISHED CONWAY |  | START: | 10660660 |  | END: | 10665454 |  |  | Hypochlorite | 17 |  | 40
[76 empty] | TOTAL MGD: |  | 10.97 |  |  | FINISHED PERRY |  | START: | 34733686 |  | END: | 34744656 |  |  | Phosphate | 1346
[76 empty] | TOTAL MGD: |  | 9.628 |  |  | RAW PLANT 1 |  | START: | 31829162 |  | END: | 31838790 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.733 |  |  | RAW PLANT 2 |  | START: | 31791494 |  | END: | 31801227 |  |  | Cal~Flo | 13.5 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.812 |  |  | RAW PLANT 3 |  | START: | 8424874 |  | END: | 8434686 |  |  | Zinc | 2450
[76 empty] | TOTAL MGD: |  | 0.474 |  |  | DECANT |  | START: | 1941312 |  | END: | 1941786 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.98629 |  |  | BLOW DOWN |  | START: | 9244.0159 |  | END: | 9245.0022 |  |  | NH3 | 10 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 492
23827667
44903412
10665454
34744656
31838790
31801227
8434686
1941786
9245.0022
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 7
DATE: | 2019-04-07 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-07 | [23 empty] | DATE: | 2019-04-07
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-07 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43562.0004 | 2,3,5 | 56 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 9.3787 | 1,3 | 13.9925 | 23.3712 | 1.3104 | 43562.0004 | 49.8977 | 3381.8066 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4359 | 1.4359 | 1.4359 | 0.18628 | 0.18628 | 0.18628 | 0.14747 | 0.13583 | 0.13583 | 1.4077 | 2 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.7917 | 0.72595 | 5.0983 | 1.1371 | 0.5216 | 0.093217 | 3.9998 | 0.73576 | 9.7261 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.393 | 4 | 0.54 | 16.5 | 9.8 | 0.50522 |  | 6.21 | 0.322 | 4 | 0.62 | 17 | 9.8 | 0.50522 | 6.18 | 0.333 | 3 | 0.55 | 17.5 | 9.8 | 0.48296 | [13 empty] | 7.42 | 0.048 | 1 | 4.6 | 16 |  |  |  | 7.32 | 0.052 | 1 | 4.4 | 17 |  |  |  | 3.6 | 3.6 | 1.9 | [18 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 480 | 480 | 480 | 380 | 350 | 350 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1440 | 296 | 325 | 46 | 56 | 6 | 740 | 150 | 310 |  | 1:00 | 0.54 | 9.8 | 25.9592 | 14.018 | 6.19 | 16.5 | 10 | 1.4018 | 15 | 6.5 | 0.38522 | 1:00 | 0.62 | 9.8 | 25.9592 | 16.0947 | 6.21 | 17 | 10 | 1.6095 | 15 | 6.5 | 0.38522 | 1:00 | 0.55 | 9.8 | 27.551 | 15.1531 | 6.18 | 17.5 | 10 | 1.5153 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43562.3432 | 2,3,5 | 48 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 10.9656 | 1,3 | 12.5654 | 23.531 | 1.3104 | 43562.3432 | 49.8977 | 3258.8318 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4359 | 1.6273 | 1.5316 | 0.18628 | 0.2018 | 0.17075 | 0.15523 | 0.12418 | 0.13971 | 1.4077 | 4 | 0.069776 | 0.070344 | 0.070344 | 1.0876 | 0.49831 | 0.10099 | 3.8107 | 0.73576 | 5.0983 | 1.0876 | 0.51228 | 0.093217 | 3.9598 | 0.73576 | 9.7261 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.68 | 22 | 20 | 7 | 76 | 112 | 18 | 0.29 |  | 6.14 | 12 | 0.048 | 6.16 | 12 |  | 6.1 | 12 | [8 empty] | 0.034 | [14 empty] | 0.02 | 1 | 0.36 |  | 0.035 | 0.032 | 1 | 0.36 |  | 0.033 | 1 | 0.32 | [38 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 300 | 340 | 320 | 480 | 520 | 440 | 400 | 320 | 360 | 740 |  | 1230 | 1240 | 1240 | 88 | 107 | 13 | 1460 | 300 | 325 | 44 | 55 | 6 | 740 | 150 | 310 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43562.8866 | 2,3,5 | 48 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 10.9656 | 1,3 | 12.5654 | 23.531 | 1.525 | 43562.8866 | 49.8977 | 3135.857 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4359 | 1.5316 | 1.5316 | 0.18628 | 0.18628 | 0.15523 | 0.15523 | 0.13195 | 0.13195 | 1.4077 | 5 | 0.070344 | 0.070344 | 0.070344 | 1.0505 | 0.50297 | 0.10099 | 3.8162 | 0.7235 | 5.0983 | 1.1371 | 0.50297 | 0.093217 | 3.9788 | 0.75538 | 9.7261 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.37 | 0.048 | 1 | 4.2 | 16 |  |  |  | 7.28 | 0.05 | 1 | 4 | 17 |  |  |  | 4.1 | 3.6 | 2.1 | [18 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 300 | 320 | 320 | 480 | 480 | 400 | 400 | 340 | 340 | 740 |  | 1240 | 1240 | 1240 | 85 | 108 | 13 | 1450 | 295 | 325 | 46 | 54 | 6 | 750 | 154 | 310 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.67 | 18 | 18 | 6.96 | 78 | 111 | 17.9 | 0.312 |  | 6.07 | 12 | 0.055 | 6.09 | 11 |  | 6.05 | 12 | [8 empty] | 0.038 | [14 empty] | 0.018 | 1 | 0.21 |  | 0.048 | 0.031 | 1 | 0.25 |  | 0.034 | 1 | 0.33 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.032 | [9 empty] | 6.15 | 0.379 | 4 | 0.58 | 16.1 | 9.5 | 0.49343 |  | 6.18 | 0.274 | 4 | 0.61 | 16.3 | 9.5 | 0.49343 | 6.17 | 0.255 | 4 | 0.49 | 17 | 9.6 | 0.47556 |  |  |  | 0.013 | [9 empty] | 7.52 | 0.051 | 1 | 3.9 | 16.1 | 21 | 35 | 0.011 | 7.61 | 0.049 | 1 | 4 | 17.9 | 20 | 24 | 0.011 | 4.2 | 3.7 | 3.5 | [55 empty] | 9:00 | 0.58 | 9.5 | 26.7789 | 15.5318 | 6.15 | 16.1 | 10 | 1.5532 | 15 | 6.5 | 0.37343 | 9:00 | 0.61 | 9.5 | 26.7789 | 16.3352 | 6.18 | 16.3 | 10 | 1.6335 | 15 | 6.5 | 0.37343 | 9:00 | 0.49 | 9.6 | 28.125 | 13.7812 | 6.17 | 17 | 10 | 1.3781 | 15 | 6.5 | 0.35556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.64 | 19 | 18 | 6.63 | 79 | 110 | 18.1 | 0.311 |  | 6.08 | 11 | 0.054 | 6.1 | 12 |  | 6.06 | 12 | [8 empty] | 0.036 | [14 empty] | 0.051 | 1 | 0.4 |  | 0.035 | 0.057 | 1 | 0.42 |  | 0.037 | 1 | 0.34 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.388 | 4 | 0.56 | 16.7 | 9.5 | 0.49343 |  | 6.14 | 0.283 | 3 | 0.57 | 17.2 | 9.5 | 0.49343 | 6.16 | 0.258 | 4 | 0.67 | 17.4 | 9.6 | 0.47556 | [13 empty] | 7.71 | 0.05 | 1 | 4.6 | 16.6 |  |  |  | 7.67 | 0.048 | 1 | 4.5 | 17.9 |  |  |  | 4.3 | 3.6 | 3.6 | [55 empty] | 13:00 | 0.56 | 9.5 | 26.7789 | 14.9962 | 6.1 | 16.7 | 10 | 1.4996 | 15 | 6.5 | 0.37343 | 13:00 | 0.57 | 9.5 | 26.7789 | 15.264 | 6.14 | 17.2 | 10 | 1.5264 | 15 | 6.5 | 0.37343 | 13:00 | 0.67 | 9.6 | 28.125 | 18.8438 | 6.16 | 17.4 | 10 | 1.8844 | 15 | 6.5 | 0.35556
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.64 | 18 | 17 | 6.28 | 76 | 109 | 17.7 | 0.304 |  | 6.06 | 10 | 0.051 | 6.08 | 11 |  | 6.05 | 12 | [8 empty] | 0.038 | [14 empty] | 0.04 | 1 | 0.27 |  | 0.033 | 0.02 | 1 | 0.25 |  | 0.033 | 1 | 0.3 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.47 | 0.051 | 1 | 3.6 | 16.6 |  |  |  | 7.56 | 0.05 | 1 | 3.7 | 17.8 |  |  |  | 4.4 | 3.6 | 4.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.63 | 20 | 18 | 6.06 | 76 | 107 | 17.6 | 0.308 |  | 6.14 | 12 | 0.053 | 6.16 | 12 |  | 6.09 | 12 | [8 empty] | 0.033 | [14 empty] | 0.034 | 2 | 0.11 |  | 0.036 | 0.055 | 2 | 0.17 |  | 0.034 | 2 | 0.19 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.039 | [9 empty] | 6.15 | 0.496 | 6 | 0.57 | 16.7 | 9.8 | 0.50522 |  | 6.19 | 0.371 | 4 | 0.52 | 17.1 | 9.8 | 0.50522 | 6.19 | 0.312 | 4 | 0.6 | 17.1 | 9.8 | 0.48296 |  |  |  | 0.01 | [9 empty] | 7.42 | 0.055 | 1 | 3.9 | 16.6 | 22 | 40 | 0.013 | 7.42 | 0.052 | 1 | 4 | 16.6 | 23 | 37 | 0.014 | 4.2 | 3.9 | 4.4 | [55 empty] | 21:00 | 0.57 | 9.8 | 25.9592 | 14.7967 | 6.15 | 16.7 | 10 | 1.4797 | 15 | 6.5 | 0.38522 | 21:00 | 0.52 | 9.8 | 25.9592 | 13.4988 | 6.19 | 17.1 | 10 | 1.3499 | 15 | 6.5 | 0.38522 | 21:00 | 0.6 | 9.8 | 27.551 | 16.5306 | 6.19 | 17.1 | 10 | 1.6531 | 15 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 29.4 | 29.4 | 29.4 | 88.2 | 27.9 | 27.9 | 27.9 | 83.7 | 0 | 31.3099 | 0 | 39.1234 | 70.4333 | 4.1458 | TOTAL | 149.6931 | 9776.4954 | 0 | 1474.8899 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3077 | 4.5948 | 4.4991 | 0.55883 | 0.57435 | 0.51226 | 0.45793 | 0.39195 | 0.40748 | 4.223 | 11 | 0.21046 | 0.21103 | 0.21103 | 3.2505 | 1.5043 | 0.30296 | 11.4186 | 2.1852 | 15.295 | 3.3618 | 1.5369 | 0.27965 | 11.9384 | 2.2269 | 29.1782 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.6 | 19 | 18 | 6.09 | 77 | 106 | 17.8 | 0.327 |  | 6.03 | 11 | 0.05 | 6.05 | 11 |  | 6 | 11 | [8 empty] | 0.039 | [14 empty] | 0.035 | 1 | 0.21 |  | 0.037 | 0.045 | 1 | 0.29 |  | 0.033 | 1 | 0.26 | [22 empty] | AVERAGE | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 10.4366 |  | 13.0411 | 23.4778 | 1.3819 | AVERAGE | 49.8977 | 3258.8318 |  | 491.63 | 0 | 0 | 0 |  |  |  | 1.4359 | 1.5316 | 1.4997 | 0.18628 | 0.19145 | 0.17075 | 0.15264 | 0.13065 | 0.13583 | 1.4077 | 3.6667 | 0.070155 | 0.070344 | 0.070344 | 1.0835 | 0.50142 | 0.10099 | 3.8062 | 0.72841 | 5.0983 | 1.1206 | 0.51228 | 0.093217 | 3.9795 | 0.7423 | 9.7261 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.86 | 116 | 109 | 39.02 | 462 | 655 | 107.1 | 1.852 | 0.071 | 36.52 | 68 | 0.311 | 36.64 | 69 | 0 | 36.35 | 71 | 0 | 24.59 | 1.656 | 18 | 2.25 | 66 | 38.6 | 1.9973 | 0.218 | 24.72 | 1.25 | 15 | 2.32 | 67.6 | 38.6 | 1.9973 | 24.7 | 1.158 | 15 | 2.31 | 69 | 38.8 | 1.917 | 0.198 | 7 | 1.56 | 0.023 | 0.224 | 0.24 | 7 | 1.74 | 0 | 0.204 | 7 | 1.74 | 0 | 44.91 | 0.303 | 6 | 24.8 | 97.9 | 43 | 75 | 0.024 | 44.86 | 0.301 | 6 | 24.6 | 104.2 | 43 | 61 | 0.025 | 24.8 | 22 | 19.8 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.3787 |  | 12.5654 | 23.3712 | 1.3104 | MINIMUM | 49.8977 | 3135.857 |  | 491.63 | [6 empty] | 1.4359 | 1.4359 | 1.4359 | 0.18628 | 0.18628 | 0.15523 | 0.14747 | 0.12418 | 0.13195 | 1.4077 | 2 | 0.069776 | 0.070344 | 0.070344 | 1.0505 | 0.49831 | 0.10099 | 3.7917 | 0.7235 | 5.0983 | 1.0876 | 0.50297 | 0.093217 | 3.9598 | 0.73576 | 9.7261 |  | MIN | 0.54 | 9.8 | 25.9592 | 14.018 | 6.19 | 16.5 | 10 | 1.4018 |  |  |  | MIN | 0.52 | 9.8 | 25.9592 | 13.4988 | 6.19 | 17.1 | 10 | 1.3499 |  |  |  | MIN | 0.49 | 9.6 | 28.125 | 13.7812 | 6.17 | 17 | 10 | 1.3781 |  |  |  | 1.3499
AVERAGE | 6.6433 | 19.3333 | 18.1667 | 6.5033 | 77 | 109.1667 | 17.85 | 0.30867 | 0.0355 | 6.0867 | 11.3333 | 0.051833 | 6.1067 | 11.5 |  | 6.0583 | 11.8333 |  | 6.1475 | 0.414 | 4.5 | 0.5625 | 16.5 | 9.65 | 0.49932 | 0.036333 | 6.18 | 0.3125 | 3.75 | 0.58 | 16.9 | 9.65 | 0.49932 | 6.175 | 0.2895 | 3.75 | 0.5775 | 17.25 | 9.7 | 0.47926 | 0.033 | 1.1667 | 0.26 | 0.0115 | 0.037333 | 0.04 | 1.1667 | 0.29 |  | 0.034 | 1.1667 | 0.29 |  | 7.485 | 0.0505 | 1 | 4.1333 | 16.3167 | 21.5 | 37.5 | 0.012 | 7.4767 | 0.050167 | 1 | 4.1 | 17.3667 | 21.5 | 30.5 | 0.0125 | 4.1333 | 3.6667 | 3.3 |  |  | MAXIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 10.9656 |  | 13.9925 | 23.531 | 1.525 | MAXIMUM | 49.8977 | 3381.8066 |  | 491.63 | [6 empty] | 1.4359 | 1.6273 | 1.5316 | 0.18628 | 0.2018 | 0.18628 | 0.15523 | 0.13583 | 0.13971 | 1.4077 | 5 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8162 | 0.73576 | 5.0983 | 1.1371 | 0.5216 | 0.093217 | 3.9998 | 0.75538 | 9.7261
MINIMUM | 6.6 | 18 | 17 | 6.06 | 76 | 106 | 17.6 | 0.29 | 0.032 | 6.03 | 10 | 0.048 | 6.05 | 11 |  | 6 | 11 |  | 6.1 | 0.379 | 4 | 0.54 | 16.1 | 9.5 | 0.49343 | 0.033 | 6.14 | 0.274 | 3 | 0.52 | 16.3 | 9.5 | 0.49343 | 6.16 | 0.255 | 3 | 0.49 | 17 | 9.6 | 0.47556 | 0.018 | 1 | 0.11 | 0.01 | 0.033 | 0.02 | 1 | 0.17 |  | 0.033 | 1 | 0.19 |  | 7.37 | 0.048 | 1 | 3.6 | 16 | 21 | 35 | 0.011 | 7.28 | 0.048 | 1 | 3.7 | 16.6 | 20 | 24 | 0.011 | 3.6 | 3.6 | 1.9 | [15 empty] | MIL/MIN |  | TOTAL | 18000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 960 | 940 | 1440 | 1480 | 1320 | 1180 | 1010 | 1050 | 2220 | 0 | 3710 | 3720 | 3720 | 263 | 323 | 39 | 4350 | 891 | 975 | 136 | 165 | 18 | 2230 | 454 | 930
MAXIMUM | 6.68 | 22 | 20 | 7 | 79 | 112 | 18.1 | 0.327 | 0.039 | 6.14 | 12 | 0.055 | 6.16 | 12 |  | 6.1 | 12 |  | 6.19 | 0.496 | 6 | 0.58 | 16.7 | 9.8 | 0.50522 | 0.039 | 6.21 | 0.371 | 4 | 0.62 | 17.2 | 9.8 | 0.50522 | 6.19 | 0.333 | 4 | 0.67 | 17.5 | 9.8 | 0.48296 | 0.051 | 2 | 0.4 | 0.013 | 0.048 | 0.057 | 2 | 0.42 |  | 0.037 | 2 | 0.34 |  | 7.71 | 0.055 | 1 | 4.6 | 16.6 | 22 | 40 | 0.013 | 7.67 | 0.052 | 1 | 4.5 | 17.9 | 23 | 37 | 0.014 | 4.4 | 3.9 | 4.4 | [17 empty] | AVERAGE | 6000 | [9 empty] | 300 | 320 | 313.3333 | 480 | 493.3333 | 440 | 393.3333 | 336.6667 | 350 | 740 |  | 1236.6667 | 1240 | 1240 | 87.6667 | 107.6667 | 13 | 1450 | 297 | 325 | 45.3333 | 55 | 6 | 743.3333 | 151.3333 | 310
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0839 |  | TOTAL AVG COAG ALK: |  |  |  | 11.5556 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.496 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.49 | [5 empty] | 6.1675 |  |  |  |  | 0.057 |  |  |  |  | 0.49 | [6 empty] | 0.057 | [16 empty] | Pump Station MIN |  | 1.9 | [17 empty] | MINIMUM | 6000 | [9 empty] | 300 | 300 | 300 | 480 | 480 | 400 | 380 | 320 | 340 | 740 |  | 1230 | 1240 | 1240 | 85 | 107 | 13 | 1440 | 295 | 325 | 44 | 54 | 6 | 740 | 150 | 310
[90 empty] | MAXIMUM | 6000 | [9 empty] | 300 | 340 | 320 | 480 | 520 | 480 | 400 | 350 | 360 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1460 | 300 | 325 | 46 | 56 | 6 | 750 | 154 | 310
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.901 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23827667 |  | END: | 23827676 |  |  | Alum | 4847 | 9482 | 9482 | 7874 | 7874 | 0 | [44 empty] | 0.52 | 9.8 | 25.9592 | 13.4988 | 6.19 | 17.1 | 10 | 1.3499
[73 empty] | FINISHED 2 | 15.339 |  | TOTAL MGD: |  | 11.892 |  |  | FINISHED SOUTH 2 |  | START: | 44903412 |  | END: | 44915304 |  |  | Caustic | 6329 | 7875 | 7875
[73 empty] | TOTAL RAW | 29.225 |  | TOTAL MGD: |  | 4.4 |  |  | FINISHED CONWAY |  | START: | 10665454 |  | END: | 10669854 |  |  | Hypochlorite | 16 |  | 39
[76 empty] | TOTAL MGD: |  | 10.939 |  |  | FINISHED PERRY |  | START: | 34744656 |  | END: | 34755595 |  |  | Phosphate | 1258
[76 empty] | TOTAL MGD: |  | 9.67 |  |  | RAW PLANT 1 |  | START: | 31838790 |  | END: | 31848460 |  |  | Fluoride | 2650 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.773 |  |  | RAW PLANT 2 |  | START: | 31801227 |  | END: | 31811000 |  |  | Cal~Flo | 12 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.782 |  |  | RAW PLANT 3 |  | START: | 8434686 |  | END: | 8444468 |  |  | Zinc | 2466
[76 empty] | TOTAL MGD: |  | 0.674 |  |  | DECANT |  | START: | 1941786 |  | END: | 1942460 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.81549 |  |  | BLOW DOWN |  | START: | 9245.0022 |  | END: | 9245.8177 |  |  | NH3 | 10 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 492
23827676
44915304
10669854
34755595
31848460
31811000
8444468
1942460
9245.8177
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 8
DATE: | 2019-04-08 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-08 | [23 empty] | DATE: | 2019-04-08
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-08 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43563.0116 | 2,3,5 | 48 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 10.9656 | 1,3 | 12.5654 | 23.531 | 1.525 | 43563.0116 | 49.8977 | 3135.857 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4359 | 1.5316 | 1.5316 | 0.18628 | 0.18628 | 0.15523 | 0.15523 | 0.13195 | 0.13195 | 1.4077 | 5 | 0.070344 | 0.070344 | 0.070344 | 1.0505 | 0.50297 | 0.10099 | 3.8162 | 0.7235 | 5.0983 | 1.1371 | 0.50297 | 0.093217 | 3.9788 | 0.75538 | 9.7261 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.13 | 0.403 | 4 | 0.55 | 17 | 9.8 | 0.50522 |  | 6.12 | 0.308 | 4 | 0.54 | 17.5 | 9.8 | 0.50522 | 6.09 | 0.317 | 4 | 0.58 | 18 | 9.8 | 0.48296 | [13 empty] | 7.25 | 0.052 | 1 | 3.8 | 16.5 |  |  |  | 7.25 | 0.05 | 1 | 3.8 | 17 |  |  |  | 3.8 | 3.8 | 1.7 | [18 empty] | 6000 | [6 empty] | 0 | 0 | 0 | 300 | 320 | 320 | 480 | 480 | 400 | 400 | 340 | 340 | 740 |  | 1240 | 1240 | 1240 | 85 | 108 | 13 | 1450 | 295 | 325 | 46 | 54 | 6 | 750 | 154 | 310 |  | 1:00 | 0.55 | 9.8 | 25.9592 | 14.2776 | 6.13 | 17 | 10 | 1.4278 | 15 | 6.5 | 0.38522 | 1:00 | 0.54 | 9.8 | 25.9592 | 14.018 | 6.12 | 17.5 | 10 | 1.4018 | 15 | 6.5 | 0.38522 | 1:00 | 0.58 | 9.8 | 27.551 | 15.9796 | 6.09 | 18 | 10 | 1.598 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43563.3396 | 2,3,5 | 60 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3 | 8.3 | 1,3 | 15.3 | 23.6 | 1.5 | 8:09 | 50 | 3012 | 0 | 492 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1.6 | 1.5 | 0.2 | 0.22 | 0.17 | 0.16 | 0.14 | 0.14 | 1.41 | 5.5 | 0.07 | 0.07 | 0.07 | 1.1 | 0.5 | 0.1 | 3.8 | 0.7 | 5.1 | 1.1 | 0.56 | 0.1 | 4 | 0.8 | 9.7 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.6 | 21 | 20 | 5.9 | 75 | 107 | 18.5 | 0.292 |  | 6.07 | 12 | 0.046 | 6.08 | 12 |  | 6.01 | 12 | [8 empty] | 0.032 | [14 empty] | 0.032 | 1 | 0.2 |  | 0.035 | 0.038 | 1 | 0.3 |  | 0.032 | 1 | 0.25 | [38 empty] | 6160 | [6 empty] | 0 | 0 | 0 | 280 | 340 | 320 | 520 | 560 | 440 | 400 | 360 | 360 | 740 |  | 1240 | 1240 | 1240 | 90 | 107 | 13 | 1440 | 295 | 325 | 44 | 60 | 6 | 760 | 155 | 310 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43563.7895 | 2,3,5 | 60 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | 1,3,1,3 | 8.2642 | 1,3 | 15.3216 | 23.5858 | 1.4544 | 43563.7895 | 49.9661 | 3135.857 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5274 | 1.5274 | 1.5274 | 0.19904 | 0.19904 | 0.19904 | 0.17061 | 0.14217 | 0.14217 | 1.4077 | 2 | 0.069826 | 0.069826 | 0.069826 | 1.1043 | 0.50105 | 0.099158 | 3.7963 | 0.69991 | 5.0061 | 1.1269 | 0.50955 | 0.11332 | 4.0215 | 0.76923 | 9.44 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.35 | 0.05 | 1 | 3.8 | 16.5 |  |  |  | 7.31 | 0.048 | 1 | 3.7 | 17 |  |  |  | 3.7 | 3.7 | 2.1 | [18 empty] | 6560 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 560 | 560 | 560 | 480 | 400 | 400 | 740 |  | 1350 | 1350 | 1350 | 98 | 118 | 14 | 1530 | 313 | 350 | 50 | 60 | 8 | 850 | 172 | 330 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43563.9263 | 2,3,5 | 60 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | 1,3,1,3 | 8.2642 | 1,3 | 15.3216 | 23.5858 | 1.4544 | 43563.9263 | 49.9661 | 3135.857 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5274 | 1.5274 | 1.5274 | 0.19904 | 0.19904 | 0.19904 | 0.17061 | 0.14217 | 0.14217 | 1.4077 | 2 | 0.069826 | 0.069826 | 0.069826 | 1.1043 | 0.50105 | 0.099158 | 3.7963 | 0.69991 | 5.0061 | 1.1269 | 0.50955 | 0.11332 | 4.0215 | 0.76923 | 9.44 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.69 | 22 | 18 | 5.64 | 76 | 105 | 18.6 | 0.318 |  | 6.01 | 11 | 0.064 | 6 | 11 |  | 5.98 | 12 | [8 empty] | 0.038 | [14 empty] | 0.032 | 1 | 0.3 |  | 0.037 | 0.031 | 1 | 0.26 |  | 0.03 | 1 | 0.27 | [38 empty] | 6560 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 560 | 560 | 560 | 480 | 400 | 400 | 740 |  | 1350 | 1350 | 1350 | 98 | 118 | 14 | 1530 | 313 | 350 | 50 | 60 | 8 | 850 | 172 | 330 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.028 | [9 empty] | 6.01 | 0.315 | 4 | 0.63 | 17.7 | 9.6 | 0.49736 |  | 6.1 | 0.21 | 3 | 0.44 | 17.2 | 9.6 | 0.49736 | 6.07 | 0.313 | 4 | 0.43 | 17.2 | 9.9 | 0.48667 |  |  |  | 0.04 | [9 empty] | 7.31 | 0.058 | 1 | 4.2 | 17.2 | 26 | 30 | 0.013 | 7.25 | 0.06 | 1 | 3.2 | 18.7 | 23 | 32 | 0.013 | 4.1 | 3.7 | 3.7 | [55 empty] | 9:00 | 0.63 | 9.6 | 26.5 | 16.695 | 6.01 | 17.7 | 10 | 1.6695 | 15 | 6.5 | 0.37736 | 9:00 | 0.44 | 9.6 | 26.5 | 11.66 | 6.1 | 17.2 | 10 | 1.166 | 15 | 6.5 | 0.37736 | 9:00 | 0.43 | 9.9 | 27.2727 | 11.7273 | 6.07 | 17.2 | 10 | 1.1727 | 15 | 6.5 | 0.36667
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.6 | 20 | 19 | 6.09 | 80 | 111 | 18.4 | 0.329 |  | 5.98 | 11 | 0.056 | 5.96 | 12 |  | 5.95 | 12 | [8 empty] | 0.04 | [14 empty] | 0.028 | 1 | 0.37 |  | 0.038 | 0.037 | 1 | 0.39 |  | 0.035 | 1 | 0.29 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.99 | 0.298 | 4 | 0.67 | 17.8 | 9.7 | 0.42503 |  | 6.03 | 0.295 | 3 | 0.53 | 18.5 | 9.7 | 0.50129 | 6.05 | 0.254 | 3 | 0.46 | 17.5 | 9.9 | 0.48667 | [13 empty] | 7.3 | 0.054 | 1 | 4.9 | 17.4 |  |  |  | 7.24 | 0.055 | 1 | 4.2 | 18.9 |  |  |  | 3.9 | 3.9 | 3.8 | [55 empty] | 13:00 | 0.67 | 9.7 | 26.2268 | 17.572 | 5.99 | 17.8 | 8 | 2.1965 | 15 | 6 | 0.30503 | 13:00 | 0.53 | 9.7 | 26.2268 | 13.9002 | 6.03 | 18.5 | 10 | 1.39 | 15 | 6.5 | 0.38129 | 13:00 | 0.46 | 9.9 | 27.2727 | 12.5455 | 6.05 | 17.5 | 10 | 1.2545 | 15 | 6.5 | 0.36667
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.64 | 18 | 17 | 6.09 | 76 | 108 | 18.1 | 0.326 |  | 6.07 | 10 | 0.055 | 6.04 | 11 |  | 5.97 | 10 | [8 empty] | 0.039 | [14 empty] | 0.027 | 1 | 0.39 |  | 0.036 | 0.046 | 1 | 0.36 |  | 0.029 | 1 | 0.22 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.21 | 0.051 | 1 | 4.7 | 17.6 |  |  |  | 7.08 | 0.049 | 1 | 4.3 | 18.8 |  |  |  | 4.1 | 3.9 | 4.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.58 | 20 | 18 | 5.8 | 77 | 107 | 18.1 | 0.331 |  | 6.08 | 10 | 0.07 | 6.07 | 10 |  | 6 | 10 | [8 empty] | 0.041 | [14 empty] | 0.027 | 1 | 0.3 |  | 0.04 | 0.05 | 1 | 0.3 |  | 0.031 | 1 | 0.32 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.037 | [9 empty] | 6.06 | 0.449 | 4 | 0.6 | 17.7 | 10.7 | 0.5406 |  | 6.09 | 0.274 | 4 | 0.52 | 18.1 | 10.7 | 0.5406 | 6.08 | 0.32 | 3 | 0.48 | 18.5 | 10.7 | 0.5163 |  |  |  | 0.014 | [9 empty] | 7.2 | 0.06 | 1 | 4.7 | 17.3 | 24 | 32 | 0.014 | 7.29 | 0.051 | 1 | 4 | 17.7 | 22 | 32 | 0.017 | 4.4 | 3.8 | 3.7 | [55 empty] | 21:00 | 0.6 | 10.7 | 23.7757 | 14.2654 | 6.06 | 17.7 | 10 | 1.4265 | 15 | 6.5 | 0.4206 | 21:00 | 0.52 | 10.7 | 23.7757 | 12.3634 | 6.09 | 18.1 | 10 | 1.2363 | 15 | 6.5 | 0.4206 | 21:00 | 0.48 | 10.7 | 25.2336 | 12.1121 | 6.08 | 18.5 | 10 | 1.2112 | 15 | 6.5 | 0.3963
22:00 | [72 empty] | DOSE |  | TOTAL | 41 | 41 | 41 | 123 | 39 | 39 | 39 | 117 | 0 | 35.7939 | 0 | 58.5086 | 94.3026 | 5.9338 | TOTAL | 199.8299 | 12419.571 | 0 | 2030.326 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7907 | 6.1864 | 6.0864 | 0.78436 | 0.80436 | 0.72331 | 0.65644 | 0.55629 | 0.55629 | 5.633 | 14.5 | 0.28 | 0.28 | 0.28 | 4.3592 | 2.0051 | 0.3993 | 15.2088 | 2.8233 | 20.2105 | 4.4908 | 2.0821 | 0.41986 | 16.0217 | 3.0939 | 38.3061 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.74 | 21 | 18 | 6.2 | 82 | 115 | 18.6 | 0.344 |  | 6.07 | 10 | 0.071 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.041 | [14 empty] | 0.031 | 1 | 0.31 |  | 0.041 | 0.038 | 1 | 0.26 |  | 0.031 | 1 | 0.33 | [22 empty] | AVERAGE | 10.25 | 10.25 | 10.25 | 30.75 | 9.75 | 9.75 | 9.75 | 29.25 |  | 8.9485 |  | 14.6272 | 23.5756 | 1.4834 | AVERAGE | 49.9575 | 3104.8927 |  | 507.5815 | 0 | 0 | 0 |  |  |  | 1.4477 | 1.5466 | 1.5216 | 0.19609 | 0.20109 | 0.18083 | 0.16411 | 0.13907 | 0.13907 | 1.4082 | 3.625 | 0.069999 | 0.069999 | 0.069999 | 1.0898 | 0.50127 | 0.099825 | 3.8022 | 0.70583 | 5.0526 | 1.1227 | 0.52052 | 0.10497 | 4.0054 | 0.77346 | 9.5765 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.85 | 122 | 110 | 35.72 | 466 | 653 | 110.3 | 1.94 | 0.065 | 36.28 | 64 | 0.362 | 36.2 | 66 | 0 | 35.91 | 66 | 0 | 24.19 | 1.465 | 16 | 2.45 | 70.2 | 39.8 | 1.9682 | 0.231 | 24.34 | 1.087 | 14 | 2.03 | 71.3 | 39.8 | 2.0445 | 24.29 | 1.204 | 14 | 1.95 | 71.2 | 40.3 | 1.9726 | 0.177 | 6 | 1.87 | 0.054 | 0.227 | 0.24 | 6 | 1.87 | 0 | 0.188 | 6 | 1.68 | 0 | 43.62 | 0.325 | 6 | 26.1 | 102.5 | 50 | 62 | 0.027 | 43.42 | 0.313 | 6 | 23.2 | 108.1 | 45 | 64 | 0.03 | 24 | 22.8 | 19.3 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 8.2642 |  | 12.5654 | 23.531 | 1.4544 | MINIMUM | 49.8977 | 3012 |  | 491.63 | [6 empty] | 1.3 | 1.5274 | 1.5 | 0.18628 | 0.18628 | 0.15523 | 0.15523 | 0.13195 | 0.13195 | 1.4077 | 2 | 0.069826 | 0.069826 | 0.069826 | 1.0505 | 0.5 | 0.099158 | 3.7963 | 0.69991 | 5.0061 | 1.1 | 0.50297 | 0.093217 | 3.9788 | 0.75538 | 9.44 |  | MIN | 0.6 | 10.7 | 23.7757 | 14.2654 | 6.06 | 17.7 | 10 | 1.4265 |  |  |  | MIN | 0.44 | 9.6 | 26.5 | 11.66 | 6.1 | 17.2 | 10 | 1.166 |  |  |  | MIN | 0.43 | 9.9 | 27.2727 | 11.7273 | 6.07 | 17.2 | 10 | 1.1727 |  |  |  | 1.166
AVERAGE | 6.6417 | 20.3333 | 18.3333 | 5.9533 | 77.6667 | 108.8333 | 18.3833 | 0.32333 | 0.0325 | 6.0467 | 10.6667 | 0.060333 | 6.0333 | 11 |  | 5.985 | 11 |  | 6.0475 | 0.36625 | 4 | 0.6125 | 17.55 | 9.95 | 0.49205 | 0.0385 | 6.085 | 0.27175 | 3.5 | 0.5075 | 17.825 | 9.95 | 0.51112 | 6.0725 | 0.301 | 3.5 | 0.4875 | 17.8 | 10.075 | 0.49315 | 0.0295 | 1 | 0.31167 | 0.027 | 0.037833 | 0.04 | 1 | 0.31167 |  | 0.031333 | 1 | 0.28 |  | 7.27 | 0.054167 | 1 | 4.35 | 17.0833 | 25 | 31 | 0.0135 | 7.2367 | 0.052167 | 1 | 3.8667 | 18.0167 | 22.5 | 32 | 0.015 | 4 | 3.8 | 3.2167 |  |  | MAXIMUM | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 |  | 10.9656 |  | 15.3216 | 23.6 | 1.525 | MAXIMUM | 50 | 3135.857 |  | 523.348 | [6 empty] | 1.5274 | 1.6 | 1.5316 | 0.2 | 0.22 | 0.19904 | 0.17061 | 0.14217 | 0.14217 | 1.41 | 5.5 | 0.070344 | 0.070344 | 0.070344 | 1.1043 | 0.50297 | 0.10099 | 3.8162 | 0.7235 | 5.1 | 1.1371 | 0.56 | 0.11332 | 4.0215 | 0.8 | 9.7261
MINIMUM | 6.58 | 18 | 17 | 5.64 | 75 | 105 | 18.1 | 0.292 | 0.028 | 5.98 | 10 | 0.046 | 5.96 | 10 |  | 5.95 | 10 |  | 5.99 | 0.298 | 4 | 0.55 | 17 | 9.6 | 0.42503 | 0.032 | 6.03 | 0.21 | 3 | 0.44 | 17.2 | 9.6 | 0.49736 | 6.05 | 0.254 | 3 | 0.43 | 17.2 | 9.8 | 0.48296 | 0.027 | 1 | 0.2 | 0.014 | 0.035 | 0.031 | 1 | 0.26 |  | 0.029 | 1 | 0.22 |  | 7.2 | 0.05 | 1 | 3.8 | 16.5 | 24 | 30 | 0.013 | 7.08 | 0.048 | 1 | 3.2 | 17 | 22 | 32 | 0.013 | 3.7 | 3.7 | 1.7 | [15 empty] | MIL/MIN |  | TOTAL | 25280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1280 | 1360 | 1340 | 2120 | 2160 | 1960 | 1760 | 1500 | 1500 | 2960 | 0 | 5180 | 5180 | 5180 | 371 | 451 | 54 | 5950 | 1216 | 1350 | 190 | 234 | 28 | 3210 | 653 | 1280
MAXIMUM | 6.74 | 22 | 20 | 6.2 | 82 | 115 | 18.6 | 0.344 | 0.037 | 6.08 | 12 | 0.071 | 6.08 | 12 |  | 6.01 | 12 |  | 6.13 | 0.449 | 4 | 0.67 | 17.8 | 10.7 | 0.5406 | 0.041 | 6.12 | 0.308 | 4 | 0.54 | 18.5 | 10.7 | 0.5406 | 6.09 | 0.32 | 4 | 0.58 | 18.5 | 10.7 | 0.5163 | 0.032 | 1 | 0.39 | 0.04 | 0.041 | 0.05 | 1 | 0.39 |  | 0.035 | 1 | 0.33 |  | 7.35 | 0.06 | 1 | 4.9 | 17.6 | 26 | 32 | 0.014 | 7.31 | 0.06 | 1 | 4.3 | 18.9 | 23 | 32 | 0.017 | 4.4 | 3.9 | 4.3 | [17 empty] | AVERAGE | 6320 | [9 empty] | 320 | 340 | 335 | 530 | 540 | 490 | 440 | 375 | 375 | 740 |  | 1295 | 1295 | 1295 | 92.75 | 112.75 | 13.5 | 1487.5 | 304 | 337.5 | 47.5 | 58.5 | 7 | 802.5 | 163.25 | 320
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0217 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.449 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.43 | [5 empty] | 6.0683 |  |  |  |  | 0.05 |  |  |  |  | 0.43 | [6 empty] | 0.05 | [16 empty] | Pump Station MIN |  | 1.7 | [17 empty] | MINIMUM | 6000 | [9 empty] | 280 | 320 | 320 | 480 | 480 | 400 | 400 | 340 | 340 | 740 |  | 1240 | 1240 | 1240 | 85 | 107 | 13 | 1440 | 295 | 325 | 44 | 54 | 6 | 750 | 154 | 310
[90 empty] | MAXIMUM | 6560 | [9 empty] | 350 | 350 | 350 | 560 | 560 | 560 | 480 | 400 | 400 | 740 |  | 1350 | 1350 | 1350 | 98 | 118 | 14 | 1530 | 313 | 350 | 50 | 60 | 8 | 850 | 172 | 330
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.529 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23827676 |  | END: | 23827682 |  |  | Alum | 4871 | 8648 | 8648 | 7558 | 7558 | 0 | [44 empty] | 0.44 | 9.6 | 26.5 | 11.66 | 6.1 | 17.2 | 10 | 1.166
[73 empty] | FINISHED 2 | 16.876 |  | TOTAL MGD: |  | 9.523 |  |  | FINISHED SOUTH 2 |  | START: | 44915304 |  | END: | 44924827 |  |  | Caustic | 6240 | 7880 | 7880
[73 empty] | TOTAL RAW | 31.116 |  | TOTAL MGD: |  | 5.52 |  |  | FINISHED CONWAY |  | START: | 10669854 |  | END: | 10675374 |  |  | Hypochlorite | 21 |  | 32
[76 empty] | TOTAL MGD: |  | 11.356 |  |  | FINISHED PERRY |  | START: | 34755595 |  | END: | 34766951 |  |  | Phosphate | 1238
[76 empty] | TOTAL MGD: |  | 10.28 |  |  | RAW PLANT 1 |  | START: | 31848460 |  | END: | 31858740 |  |  | Fluoride | 2400 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.404 |  |  | RAW PLANT 2 |  | START: | 31811000 |  | END: | 31821404 |  |  | Cal~Flo | 10.5 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.432 |  |  | RAW PLANT 3 |  | START: | 8444468 |  | END: | 8454900 |  |  | Zinc | 2448
[76 empty] | TOTAL MGD: |  | 0.665 |  |  | DECANT |  | START: | 1942460 |  | END: | 1943125 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.79504 |  |  | BLOW DOWN |  | START: | 9245.8177 |  | END: | 9246.6127 |  |  | NH3 | 10 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 523
23827682
44924827
10675374
34766951
31858740
31821404
8454900
1943125
9246.6127
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 9
DATE: | 2019-04-09 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-09 | [23 empty] | DATE: | 2019-04-09
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-09 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43564.0096 | 2,3,5 | 60 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | 1,3,1,3 | 8.2642 | 1,3 | 15.3216 | 23.5858 | 1.4544 | 43564.0096 | 49.9661 | 3135.857 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5274 | 1.5274 | 1.5274 | 0.19904 | 0.19904 | 0.19904 | 0.17061 | 0.14217 | 0.14217 | 1.4077 | 2 | 0.069826 | 0.069826 | 0.069826 | 1.1043 | 0.50105 | 0.099158 | 3.7963 | 0.69991 | 5.0061 | 1.1269 | 0.50955 | 0.11332 | 4.0215 | 0.76923 | 9.44 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.39 | 4 | 0.58 | 17 | 10.8 | 0.54453 |  | 6.06 | 0.278 | 4 | 0.54 | 19 | 10.8 | 0.54453 | 6.05 | 0.327 | 3 | 0.5 | 19 | 10.8 | 0.52 | [13 empty] | 7.22 | 0.053 | 1 | 4 | 17.5 |  |  |  | 7.23 | 0.048 | 1 | 4 | 18 |  |  |  | 4.1 | 4.1 | 1.7 | [18 empty] | 6560 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 560 | 560 | 560 | 480 | 400 | 400 | 740 |  | 1350 | 1350 | 1350 | 98 | 118 | 14 | 1530 | 313 | 350 | 50 | 60 | 8 | 850 | 172 | 330 |  | 1:00 | 0.58 | 10.8 | 23.5556 | 13.6622 | 6.06 | 17 | 10 | 1.3662 | 15 | 6.5 | 0.42453 | 1:00 | 0.54 | 10.8 | 23.5556 | 12.72 | 6.06 | 19 | 10 | 1.272 | 15 | 6.5 | 0.42453 | 1:00 | 0.5 | 10.8 | 25 | 12.5 | 6.05 | 19 | 10 | 1.25 | 15 | 6.5 | 0.4
2:00 | [72 empty] | 43564.3495 | 2,3,5 | 41 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | 1,3,1,3 | 12.2155 | 1,3 | 17.0294 | 29.245 | 1.4544 | 43564.3495 | 49.9661 | 3873.7058 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 1.6583 | 1.6583 | 0.18482 | 0.18482 | 0.17061 | 0.14217 | 0.12796 | 0.12796 | 1.4077 | 3 | 0.068275 | 0.068275 | 0.070344 | 1.1269 | 0.50105 | 0.099158 | 3.8008 | 0.71557 | 5.0776 | 1.1269 | 0.50955 | 0.099158 | 3.9773 | 0.76029 | 9.44 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.69 | 22 | 20 | 6.15 | 80 | 115 | 19.2 | 0.315 |  | 6.01 | 11 | 0.047 | 6.03 | 11 |  | 6 | 11 | [8 empty] | 0.034 | [14 empty] | 0.031 | 1 | 0.28 |  | 0.035 | 0.027 | 1 | 0.25 |  | 0.031 | 1 | 0.3 | [38 empty] | 6560 | [6 empty] | 0 | 0 | 0 | 360 | 380 | 380 | 520 | 520 | 480 | 400 | 360 | 360 | 740 |  | 1320 | 1320 | 1360 | 100 | 118 | 14 | 1570 | 320 | 355 | 50 | 60 | 7 | 820 | 170 | 330 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43564.6285 | 2,3,5 | 41 | 10.2 | 10.2 | 10.2 | 30.6 | 9.7 | 9.7 | 9.7 | 29.1 | 1,3,1,3 | 14.4187 | 1,3 | 13.3819 | 27.8006 | 1.4544 | 43564.6285 | 52.4154 | 3566.2688 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6061 | 1.7438 | 1.652 | 0.19016 | 0.20507 | 0.17151 | 0.14914 | 0.13796 | 0.1305 | 1.4077 | 3 | 0.070706 | 0.070162 | 0.067443 | 1.1257 | 0.50009 | 0.10427 | 3.8171 | 0.71718 | 5.3393 | 1.0665 | 0.53581 | 0.10427 | 4.0152 | 0.75245 | 9.9266 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.18 | 0.055 | 1 | 4.2 | 17.5 |  |  |  | 7.25 | 0.049 | 1 | 4 | 18 |  |  |  | 4.4 | 4.1 | 1.8 | [18 empty] | 6560 | [6 empty] | 0 | 0 | 0 | 350 | 380 | 360 | 510 | 550 | 460 | 400 | 370 | 350 | 740 |  | 1300 | 1290 | 1240 | 95 | 112 | 14 | 1500 | 305 | 355 | 45 | 60 | 7 | 790 | 160 | 330 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43564.7933 | 2,3,5 | 41 | 10.2 | 10.2 | 10.2 | 30.6 | 9.7 | 9.7 | 9.7 | 29.1 | 1,3,1,3 | 14.4187 | 1,3 | 13.3819 | 27.8006 | 0.0014184 | 43564.7933 | 50.0184 | 3566.2688 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6061 | 1.6061 | 1.6061 | 0.19388 | 0.19388 | 0.16778 | 0.16778 | 0.1305 | 0.1305 | 1.4077 | 3 | 0.069619 | 0.069619 | 0.069619 | 1.0902 | 0.50009 | 0.10427 | 3.8136 | 0.71013 | 5.3393 | 1.0902 | 0.50009 | 0.11916 | 3.9952 | 0.75245 | 9.9266 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.6 | 20 | 18 | 5.51 | 81 | 111 | 19.5 | 0.32 |  | 5.93 | 10 | 0.054 | 5.92 | 11 |  | 5.89 | 10 | [8 empty] | 0.032 | [14 empty] | 0.026 | 1 | 0.27 |  | 0.029 | 0.022 | 1 | 0.31 |  | 0.029 | 1 | 0.31 | [38 empty] | 6260 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 520 | 520 | 450 | 450 | 350 | 350 | 740 |  | 1280 | 1280 | 1280 | 92 | 112 | 14 | 1490 | 302 | 355 | 46 | 56 | 8 | 790 | 160 | 330 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43564.9568 | 2,3,5 | 41 | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 | 1,3,1,3 | 14.4187 | 1,3 | 13.3819 | 27.8006 | 0.0014184 | 43564.9568 | 55.2094 | 3627.7562 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7704 | 1.7704 | 1.7704 | 0.20447 | 0.20447 | 0.18402 | 0.18402 | 0.14313 | 0.14313 | 1.4077 | 3 | 0.071942 | 0.071942 | 0.071942 | 1.1102 | 0.49217 | 0.098514 | 3.8091 | 0.71277 | 5.388 | 1.0972 | 0.49217 | 0.082095 | 4.0123 | 0.75165 | 10.1129 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.029 | [9 empty] | 6.03 | 0.418 | 5 | 0.59 | 18.6 | 10.8 | 0.54453 |  | 6.05 | 0.276 | 4 | 0.56 | 19.1 | 10.8 | 0.54453 | 6.04 | 0.312 | 4 | 0.55 | 19.3 | 10.9 | 0.5237 |  |  |  | 0.014 | [9 empty] | 7.19 | 0.059 | 1 | 4 | 18.4 | 21 | 29 | 0.018 | 7.21 | 0.058 | 1 | 3.7 | 18.7 | 23 | 35 | 0.014 | 4.3 | 4.2 | 4.2 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 500 | 500 | 450 | 450 | 350 | 350 | 740 |  | 1200 | 1200 | 1200 | 85 | 100 | 12 | 1350 | 275 | 325 | 42 | 50 | 5 | 720 | 145 | 305 |  | 9:00 | 0.59 | 10.8 | 23.5556 | 13.8978 | 6.03 | 18.6 | 10 | 1.3898 | 15 | 6.5 | 0.42453 | 9:00 | 0.56 | 10.8 | 23.5556 | 13.1911 | 6.05 | 19.1 | 10 | 1.3191 | 15 | 6.5 | 0.42453 | 9:00 | 0.55 | 10.9 | 24.7706 | 13.6239 | 6.04 | 19.3 | 10 | 1.3624 | 15 | 6.5 | 0.4037
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.58 | 20 | 18 | 5.74 | 78 | 112 | 19.8 | 0.327 |  | 5.98 | 10 | 0.064 | 5.99 | 10 |  | 5.99 | 10 | [8 empty] | 0.046 | [14 empty] | 0.031 | 1 | 0.24 |  | 0.044 | 0.039 | 1 | 0.34 |  | 0.031 | 1 | 0.3 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.02 | 0.371 | 3 | 0.54 | 18.5 | 10.5 | 0.53274 |  | 6.06 | 0.288 | 3 | 0.53 | 19 | 10.5 | 0.53274 | 6.05 | 0.214 | 3 | 0.48 | 19.2 | 10.6 | 0.51259 | [13 empty] | 7.35 | 0.057 | 1 | 4.3 | 18.4 |  |  |  | 7.36 | 0.056 | 1 | 3.9 | 18.6 |  |  |  | 4.4 | 4.1 | 4.5 | [55 empty] | 13:00 | 0.54 | 10.5 | 24.2286 | 13.0834 | 6.02 | 18.5 | 10 | 1.3083 | 15 | 6.5 | 0.41274 | 13:00 | 0.53 | 10.5 | 24.2286 | 12.8411 | 6.06 | 19 | 10 | 1.2841 | 15 | 6.5 | 0.41274 | 13:00 | 0.48 | 10.6 | 25.4717 | 12.2264 | 6.05 | 19.2 | 10 | 1.2226 | 15 | 6.5 | 0.39259
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.6 | 20 | 17 | 5.63 | 78 | 110 | 19.4 | 0.335 |  | 6 | 9 | 0.062 | 6.01 | 10 |  | 5.95 | 10 | [8 empty] | 0.047 | [14 empty] | 0.028 | 1 | 0.29 |  | 0.043 | 0.027 | 1 | 0.33 |  | 0.03 | 2 | 0.28 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.29 | 0.054 | 1 | 4.5 | 18.6 |  |  |  | 7.57 | 0.052 | 1 | 4.9 | 18.8 |  |  |  | 4.3 | 4 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.54 | 22 | 18 | 5.26 | 76 | 106 | 19.3 | 0.336 |  | 6.06 | 10 | 0.066 | 6.11 | 10 |  | 5.99 | 10 | [8 empty] | 0.044 | [14 empty] | 0.028 | 1 | 0.33 |  | 0.043 | 0.026 | 1 | 0.4 |  | 0.07 | 1 | 0.12 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.036 | [9 empty] | 6.06 | 0.33 | 3 | 0.66 | 18.7 | 10.2 | 0.52094 |  | 6.07 | 0.234 | 3 | 0.59 | 19.1 | 10.2 | 0.52094 | 6.04 | 0.177 | 3 | 0.48 | 19.3 | 10.2 | 0.49778 |  |  |  | 0.014 | [9 empty] | 7.38 | 0.061 | 1 | 4.7 | 18.3 | 21 | 35 | 0.026 | 7.43 | 0.06 | 1 | 4.6 | 18 | 20 | 32 | 0.02 | 4.3 | 3.9 | 3.8 | [55 empty] | 21:00 | 0.66 | 10.2 | 24.9412 | 16.4612 | 6.06 | 18.7 | 10 | 1.6461 | 15 | 6.5 | 0.40094 | 21:00 | 0.59 | 10.2 | 24.9412 | 14.7153 | 6.07 | 19.1 | 10 | 1.4715 | 15 | 6.5 | 0.40094 | 21:00 | 0.48 | 10.2 | 26.4706 | 12.7059 | 6.04 | 19.3 | 10 | 1.2706 | 15 | 6.5 | 0.37778
22:00 | [72 empty] | DOSE |  | TOTAL | 51.1 | 51.1 | 51.1 | 153.3 | 48.6 | 48.6 | 48.6 | 145.8 | 0 | 63.7358 | 0 | 72.4968 | 136.2326 | 4.366 | TOTAL | 257.5754 | 17769.8566 | 0 | 2553.304 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0811 | 8.306 | 8.2142 | 0.97238 | 0.98729 | 0.89297 | 0.81373 | 0.68171 | 0.67426 | 7.0383 | 14 | 0.35037 | 0.34982 | 0.34917 | 5.5574 | 2.4945 | 0.50537 | 19.0368 | 3.5556 | 26.1503 | 5.5076 | 2.5472 | 0.51801 | 20.0215 | 3.7861 | 48.8461 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.57 | 21 | 17 | 5.29 | 82 | 110 | 19.4 | 0.343 |  | 6.02 | 10 | 0.059 | 6 | 10 |  | 5.98 | 10 | [8 empty] | 0.041 | [14 empty] | 0.028 | 1 | 0.4 |  | 0.044 | 0.033 | 1 | 0.44 |  | 0.056 | 1 | 0.27 | [22 empty] | AVERAGE | 10.22 | 10.22 | 10.22 | 30.66 | 9.72 | 9.72 | 9.72 | 29.16 |  | 12.7472 |  | 14.4994 | 27.2465 | 0.87321 | AVERAGE | 51.5151 | 3553.9713 |  | 510.6608 | 0 | 0 | 0 |  |  |  | 1.6162 | 1.6612 | 1.6428 | 0.19448 | 0.19746 | 0.17859 | 0.16275 | 0.13634 | 0.13485 | 1.4077 | 2.8 | 0.070074 | 0.069965 | 0.069835 | 1.1115 | 0.49889 | 0.10107 | 3.8074 | 0.71111 | 5.2301 | 1.1015 | 0.50943 | 0.1036 | 4.0043 | 0.75722 | 9.7692 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.58 | 125 | 108 | 33.58 | 475 | 664 | 116.6 | 1.976 | 0.065 | 36 | 60 | 0.352 | 36.06 | 62 | 0 | 35.8 | 61 | 0 | 24.17 | 1.509 | 15 | 2.37 | 72.8 | 42.3 | 2.1427 | 0.244 | 24.24 | 1.076 | 14 | 2.22 | 76.2 | 42.3 | 2.1427 | 24.18 | 1.03 | 13 | 2.01 | 76.8 | 42.5 | 2.0541 | 0.172 | 6 | 1.81 | 0.028 | 0.238 | 0.174 | 6 | 2.07 | 0 | 0.247 | 7 | 1.58 | 0 | 43.61 | 0.339 | 6 | 25.7 | 108.7 | 42 | 64 | 0.044 | 44.05 | 0.323 | 6 | 25.1 | 110.1 | 43 | 67 | 0.034 | 25.8 | 24.4 | 19.8 |  |  | MINIMUM | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 |  | 8.2642 |  | 13.3819 | 23.5858 | 0.0014184 | MINIMUM | 49.9661 | 3135.857 |  | 475.7709 | [6 empty] | 1.5274 | 1.5274 | 1.5274 | 0.18482 | 0.18482 | 0.16778 | 0.14217 | 0.12796 | 0.12796 | 1.4077 | 2 | 0.068275 | 0.068275 | 0.067443 | 1.0902 | 0.49217 | 0.098514 | 3.7963 | 0.69991 | 5.0061 | 1.0665 | 0.49217 | 0.082095 | 3.9773 | 0.75165 | 9.44 |  | MIN | 0.54 | 10.5 | 24.2286 | 13.0834 | 6.02 | 18.5 | 10 | 1.3083 |  |  |  | MIN | 0.54 | 10.8 | 23.5556 | 12.72 | 6.06 | 19 | 10 | 1.272 |  |  |  | MIN | 0.48 | 10.6 | 25.4717 | 12.2264 | 6.05 | 19.2 | 10 | 1.2226 |  |  |  | 1.2226
AVERAGE | 6.5967 | 20.8333 | 18 | 5.5967 | 79.1667 | 110.6667 | 19.4333 | 0.32933 | 0.0325 | 6 | 10 | 0.058667 | 6.01 | 10.3333 |  | 5.9667 | 10.1667 |  | 6.0425 | 0.37725 | 3.75 | 0.5925 | 18.2 | 10.575 | 0.53568 | 0.040667 | 6.06 | 0.269 | 3.5 | 0.555 | 19.05 | 10.575 | 0.53568 | 6.045 | 0.2575 | 3.25 | 0.5025 | 19.2 | 10.625 | 0.51352 | 0.028667 | 1 | 0.30167 | 0.014 | 0.039667 | 0.029 | 1 | 0.345 |  | 0.041167 | 1.1667 | 0.26333 |  | 7.2683 | 0.0565 | 1 | 4.2833 | 18.1167 | 21 | 32 | 0.022 | 7.3417 | 0.053833 | 1 | 4.1833 | 18.35 | 21.5 | 33.5 | 0.017 | 4.3 | 4.0667 | 3.3 |  |  | MAXIMUM | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 |  | 14.4187 |  | 17.0294 | 29.245 | 1.4544 | MAXIMUM | 55.2094 | 3873.7058 |  | 523.348 | [6 empty] | 1.7704 | 1.7704 | 1.7704 | 0.20447 | 0.20507 | 0.19904 | 0.18402 | 0.14313 | 0.14313 | 1.4077 | 3 | 0.071942 | 0.071942 | 0.071942 | 1.1269 | 0.50105 | 0.10427 | 3.8171 | 0.71718 | 5.388 | 1.1269 | 0.53581 | 0.11916 | 4.0215 | 0.76923 | 10.1129
MINIMUM | 6.54 | 20 | 17 | 5.26 | 76 | 106 | 19.2 | 0.315 | 0.029 | 5.93 | 9 | 0.047 | 5.92 | 10 |  | 5.89 | 10 |  | 6.02 | 0.33 | 3 | 0.54 | 17 | 10.2 | 0.52094 | 0.032 | 6.05 | 0.234 | 3 | 0.53 | 19 | 10.2 | 0.52094 | 6.04 | 0.177 | 3 | 0.48 | 19 | 10.2 | 0.49778 | 0.026 | 1 | 0.24 | 0.014 | 0.029 | 0.022 | 1 | 0.25 |  | 0.029 | 1 | 0.12 |  | 7.18 | 0.053 | 1 | 4 | 17.5 | 21 | 29 | 0.018 | 7.21 | 0.048 | 1 | 3.7 | 18 | 20 | 32 | 0.014 | 4.1 | 3.9 | 1.7 | [15 empty] | MIL/MIN |  | TOTAL | 32240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 1810 | 1790 | 2610 | 2650 | 2400 | 2180 | 1830 | 1810 | 3700 | 0 | 6450 | 6440 | 6430 | 470 | 560 | 68 | 7440 | 1515 | 1740 | 233 | 286 | 35 | 3970 | 807 | 1625
MAXIMUM | 6.69 | 22 | 20 | 6.15 | 82 | 115 | 19.8 | 0.343 | 0.036 | 6.06 | 11 | 0.066 | 6.11 | 11 |  | 6 | 11 |  | 6.06 | 0.418 | 5 | 0.66 | 18.7 | 10.8 | 0.54453 | 0.047 | 6.07 | 0.288 | 4 | 0.59 | 19.1 | 10.8 | 0.54453 | 6.05 | 0.327 | 4 | 0.55 | 19.3 | 10.9 | 0.5237 | 0.031 | 1 | 0.4 | 0.014 | 0.044 | 0.039 | 1 | 0.44 |  | 0.07 | 2 | 0.31 |  | 7.38 | 0.061 | 1 | 4.7 | 18.6 | 21 | 35 | 0.026 | 7.57 | 0.06 | 1 | 4.9 | 18.8 | 23 | 35 | 0.02 | 4.4 | 4.2 | 4.5 | [17 empty] | AVERAGE | 6448 | [9 empty] | 352 | 362 | 358 | 522 | 530 | 480 | 436 | 366 | 362 | 740 |  | 1290 | 1288 | 1286 | 94 | 112 | 13.6 | 1488 | 303 | 348 | 46.6 | 57.2 | 7 | 794 | 161.4 | 325
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9922 |  | TOTAL AVG COAG ALK: |  |  |  | 10.1667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.418 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.48 | [5 empty] | 6.0492 |  |  |  |  | 0.07 |  |  |  |  | 0.48 | [6 empty] | 0.07 | [16 empty] | Pump Station MIN |  | 1.7 | [17 empty] | MINIMUM | 6260 | [9 empty] | 350 | 350 | 350 | 500 | 500 | 450 | 400 | 350 | 350 | 740 |  | 1200 | 1200 | 1200 | 85 | 100 | 12 | 1350 | 275 | 325 | 42 | 50 | 5 | 720 | 145 | 305
[90 empty] | MAXIMUM | 6560 | [9 empty] | 360 | 380 | 380 | 560 | 560 | 560 | 480 | 400 | 400 | 740 |  | 1350 | 1350 | 1360 | 100 | 118 | 14 | 1570 | 320 | 355 | 50 | 60 | 8 | 850 | 172 | 330
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.939 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827682 |  | END: | 23827683 |  |  | Alum | 4899 | 8020 | 8020 | 9077 | 9077 | 0 | [44 empty] | 0.48 | 10.6 | 25.4717 | 12.2264 | 6.05 | 19.2 | 10 | 1.2226
[73 empty] | FINISHED 2 | 15.844 |  | TOTAL MGD: |  | 11.938 |  |  | FINISHED SOUTH 2 |  | START: | 44924827 |  | END: | 44936765 |  |  | Caustic | 6126 | 7830 | 7830
[73 empty] | TOTAL RAW | 30.636 |  | TOTAL MGD: |  | 4.953 |  |  | FINISHED CONWAY |  | START: | 10675374 |  | END: | 10680327 |  |  | Hypochlorite | 18 |  | 30
[76 empty] | TOTAL MGD: |  | 10.891 |  |  | FINISHED PERRY |  | START: | 34766951 |  | END: | 34777842 |  |  | Phosphate | 1216
[76 empty] | TOTAL MGD: |  | 10.12 |  |  | RAW PLANT 1 |  | START: | 31858740 |  | END: | 31868860 |  |  | Fluoride | 2400 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.246 |  |  | RAW PLANT 2 |  | START: | 31821404 |  | END: | 31831650 |  |  | Cal~Flo | 8.75 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.27 |  |  | RAW PLANT 3 |  | START: | 8454900 |  | END: | 8465170 |  |  | Zinc | 2483
[76 empty] | TOTAL MGD: |  | 0.774 |  |  | DECANT |  | START: | 1943125 |  | END: | 1943899 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.89143 |  |  | BLOW DOWN |  | START: | 9246.6127 |  | END: | 9247.5041 |  |  | NH3 | 9 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 476
23827683
44936765
10680327
34777842
31868860
31831650
8465170
1943899
9247.5041
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 10
DATE: | 2019-04-10 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-10 | [23 empty] | DATE: | 2019-04-10
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-10 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43565.0037 | 2,3,5 | 41 | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 | 1,3,1,3 | 14.4187 | 1,3 | 13.3819 | 27.8006 | 0.0014184 | 43565.0037 | 55.2094 | 3627.7562 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7704 | 1.7704 | 1.7704 | 0.20447 | 0.20447 | 0.18402 | 0.18402 | 0.14313 | 0.14313 | 1.4077 | 3 | 0.071942 | 0.071942 | 0.071942 | 1.1102 | 0.49217 | 0.098514 | 3.8091 | 0.71277 | 5.388 | 1.0972 | 0.49217 | 0.082095 | 4.0123 | 0.75165 | 10.1129 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.04 | 0.366 | 3 | 0.58 | 19 | 9.3 | 0.48557 |  | 6.06 | 0.264 | 3 | 0.55 | 19.5 | 9.3 | 0.48557 | 6.02 | 0.315 | 3 | 0.5 | 19.5 | 9.3 | 0.46444 | [13 empty] | 7.24 | 0.055 | 1 | 4.4 | 18.5 |  |  |  | 7.24 | 0.058 | 1 | 4 | 18.5 |  |  |  | 4.4 | 3.9 | 1.9 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 500 | 500 | 450 | 450 | 350 | 350 | 740 |  | 1200 | 1200 | 1200 | 85 | 100 | 12 | 1350 | 275 | 325 | 42 | 50 | 5 | 720 | 145 | 305 |  | 1:00 | 0.58 | 9.3 | 27.3548 | 15.8658 | 6.04 | 19 | 10 | 1.5866 | 15 | 6.5 | 0.36557 | 1:00 | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.06 | 19.5 | 10 | 1.5045 | 15 | 6.5 | 0.36557 | 1:00 | 0.5 | 9.3 | 29.0323 | 14.5161 | 6.02 | 19.5 | 10 | 1.4516 | 15 | 6.5 | 0.34444
2:00 | [72 empty] | 43565.3297 | 2,3,5 | 45 | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 | 1,3,1,3 | 9.6926 | 1,3 | 13.8859 | 23.5786 | 1.0483 | 43565.3297 | 55.2094 | 3689.2436 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.5681 | 1.5175 | 0.20447 | 0.20447 | 0.18402 | 0.18402 | 0.1554 | 0.1554 | 1.4077 | 1.5 | 0.069544 | 0.069544 | 0.069544 | 1.0972 | 0.49217 | 0.098514 | 3.7993 | 0.71277 | 5.388 | 1.0972 | 0.49217 | 0.098514 | 3.9287 | 0.75165 | 10.1129 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.67 | 22 | 20 | 4.98 | 75 | 105 | 20 | 0.318 |  | 6.05 | 11 | 0.055 | 6.07 | 11 |  | 6 | 11 | [8 empty] | 0.035 | [14 empty] | 0.022 | 1 | 0.35 |  | 0.038 | 0.031 | 1 | 0.38 |  | 0.042 | 1 | 0.28 | [38 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 320 | 310 | 300 | 500 | 500 | 450 | 450 | 380 | 380 | 740 |  | 1160 | 1160 | 1160 | 84 | 100 | 12 | 1325 | 275 | 325 | 42 | 50 | 6 | 700 | 145 | 305 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43565.6193 | 2,3,5 | 45 | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 | 1,3,1,3 | 9.6926 | 1,3 | 13.8859 | 23.5786 | 1.0483 | 43565.6193 | 55.2094 | 3689.2436 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.5681 | 1.5175 | 0.20447 | 0.20447 | 0.18402 | 0.18402 | 0.1554 | 0.1554 | 1.4077 | 1.5 | 0.069544 | 0.069544 | 0.069544 | 1.0972 | 0.49217 | 0.098514 | 3.7993 | 0.71277 | 5.388 | 1.0972 | 0.49217 | 0.098514 | 3.9287 | 0.75165 | 10.1129 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.25 | 0.054 | 1 | 4.2 | 18.5 |  |  |  | 7.28 | 0.058 | 1 | 4 | 18.5 |  |  |  | 4.4 | 3.8 | 2 | [18 empty] | 6300 | [6 empty] | 0 | 0 | 0 | 320 | 310 | 300 | 500 | 500 | 450 | 450 | 380 | 380 | 740 |  | 1160 | 1160 | 1160 | 84 | 100 | 12 | 1325 | 275 | 325 | 42 | 50 | 6 | 700 | 145 | 305 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43565.8277 | 2,3,5 | 45 | 9.6 | 9.6 | 9.6 | 28.8 | 9.1 | 9.1 | 9.1 | 27.3 | 1,3,1,3 | 11.0707 | 1,3 | 17.2526 | 28.3234 | 1.0483 | 43565.8277 | 55.4197 | 4181.1428 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8588 | 1.8099 | 1.6142 | 0.19808 | 0.19016 | 0.17629 | 0.17431 | 0.15846 | 0.15846 | 1.4077 | 3.5 | 0.069571 | 0.069571 | 0.07015 | 1.1115 | 0.49975 | 0.095266 | 3.739 | 0.68927 | 5.4509 | 1.1115 | 0.52354 | 0.11114 | 3.789 | 0.67674 | 10.1001 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.57 | 19 | 20 | 5.31 | 81 | 108 | 19.2 | 0.342 |  | 5.96 | 10 | 0.05 | 6 | 10 |  | 5.98 | 10 | [8 empty] | 0.042 | [14 empty] | 0.03 | 1 | 0.32 |  | 0.044 | 0.032 | 1 | 0.37 |  | 0.059 | 1 | 0.38 | [38 empty] | 6528 | [6 empty] | 0 | 0 | 0 | 380 | 370 | 330 | 500 | 480 | 445 | 440 | 400 | 400 | 740 |  | 1200 | 1200 | 1210 | 88 | 105 | 12 | 1400 | 275 | 340 | 44 | 55 | 7 | 700 | 135 | 315 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.024 | [9 empty] | 5.99 | 0.487 | 6 | 0.65 | 19 | 9.3 | 0.41245 |  | 6.03 | 0.354 | 4 | 0.56 | 19.5 | 9.3 | 0.48557 | 6.03 | 0.311 | 4 | 0.53 | 19.8 | 9.3 | 0.46444 |  |  |  | 0.012 | [9 empty] | 7.26 | 0.058 | 1 | 4.4 | 18.7 | 21 | 45 | 0.017 | 7.18 | 0.062 | 1 | 3.9 | 18 | 25 | 40 | 0.012 | 4.2 | 3.8 | 3.8 | [55 empty] | 9:00 | 0.65 | 9.3 | 27.3548 | 17.7806 | 5.99 | 19 | 8 | 2.2226 | 15 | 6 | 0.29245 | 9:00 | 0.56 | 9.3 | 27.3548 | 15.3187 | 6.03 | 19.5 | 10 | 1.5319 | 15 | 6.5 | 0.36557 | 9:00 | 0.53 | 9.3 | 29.0323 | 15.3871 | 6.03 | 19.8 | 10 | 1.5387 | 15 | 6.5 | 0.34444
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.56 | 19 | 19 | 4.77 | 77 | 107 | 19.4 | 0.354 |  | 6.02 | 10 | 0.053 | 6 | 10 |  | 5.95 | 10 | [8 empty] | 0.043 | [14 empty] | 0.023 | 1 | 0.28 |  | 0.042 | 0.024 | 1 | 0.43 |  | 0.043 | 1 | 0.42 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.14 | 0.354 | 4 | 0.63 | 19.5 | 9.3 | 0.48557 |  | 6.08 | 0.269 | 5 | 0.49 | 20 | 9.3 | 0.3759 | 6.04 | 0.44 | 4 | 0.61 | 20 | 9.3 | 0.36111 | [13 empty] | 7.51 | 0.059 | 1 | 4.5 | 18.6 |  |  |  | 7.27 | 0.061 | 1 | 3.9 | 19.1 |  |  |  | 4.2 | 3.8 | 3.7 | [55 empty] | 13:00 | 0.63 | 9.3 | 27.3548 | 17.2335 | 6.14 | 19.5 | 10 | 1.7234 | 15 | 6.5 | 0.36557 | 13:00 | 0.49 | 9.3 | 27.3548 | 13.4039 | 6.08 | 20 | 7 | 1.9148 | 20 | 6.5 | 0.2559 | 13:00 | 0.61 | 9.3 | 29.0323 | 17.7097 | 6.04 | 20 | 7 | 2.53 | 20 | 6.5 | 0.24111
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 19 | 19 | 4.43 | 80 | 105 | 19.6 | 0.353 |  | 6.12 | 10 | 0.056 | 6 | 10 |  | 5.95 | 10 | [8 empty] | 0.045 | [14 empty] | 0.023 | 1 | 0.32 |  | 0.042 | 0.029 | 1 | 0.38 |  | 0.043 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.46 | 0.06 | 1 | 4.4 | 18.7 |  |  |  | 7.27 | 0.061 | 1 | 3.8 | 18.7 |  |  |  | 4.2 | 3.8 | 3.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.55 | 18 | 18 | 4.63 | 81 | 105 | 19.8 | 0.348 |  | 5.99 | 8 | 0.056 | 6.01 | 9 |  | 5.97 | 9 | [8 empty] | 0.046 | [14 empty] | 0.023 | 1 | 0.17 |  | 0.05 | 0.029 | 1 | 0.29 |  | 0.053 | 1 | 0.28 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.024 | [9 empty] | 6.06 | 0.653 | 6 | 0.77 | 19.2 | 9.6 | 0.49736 |  | 6.06 | 0.533 | 5 | 0.6 | 19.5 | 9.7 | 0.50129 | 6.06 | 0.449 | 4 | 0.6 | 19.8 | 9.8 | 0.48296 |  |  |  | 0.017 |  |  |  |  | 0.024 |  |  |  | 0.015 | 7.29 | 0.057 | 1 | 4.2 | 18.8 | 20 | 33 | 0.022 | 7.28 | 0.059 | 1 | 3.6 | 18.4 | 20 | 35 | 0.017 | 4.2 | 3.7 | 3.9 | [55 empty] | 21:00 | 0.77 | 9.6 | 26.5 | 20.405 | 6.06 | 19.2 | 10 | 2.0405 | 15 | 6.5 | 0.37736 | 21:00 | 0.6 | 9.7 | 26.2268 | 15.7361 | 6.06 | 19.5 | 10 | 1.5736 | 15 | 6.5 | 0.38129 | 21:00 | 0.6 | 9.8 | 27.551 | 16.5306 | 6.06 | 19.8 | 10 | 1.6531 | 15 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 37.5 | 37.5 | 37.5 | 112.5 | 35.5 | 35.5 | 35.5 | 106.5 | 0 | 44.8747 | 0 | 58.4064 | 103.2811 | 3.1464 | TOTAL | 221.0479 | 15187.3862 | 0 | 1903.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8664 | 6.7163 | 6.4195 | 0.81149 | 0.80356 | 0.72836 | 0.72638 | 0.61238 | 0.61238 | 5.6306 | 9.5 | 0.2806 | 0.2806 | 0.28118 | 4.4161 | 1.9763 | 0.39081 | 15.1466 | 2.8276 | 21.6149 | 4.4031 | 2.0001 | 0.39027 | 15.6587 | 2.9317 | 40.4388 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.57 | 20 | 19 | 4.7 | 82 | 107 | 19.7 | 0.349 |  | 6.02 | 10 | 0.058 | 6.09 | 11 |  | 5.96 | 10 | [8 empty] | 0.052 | [14 empty] | 0.029 | 1 | 0.27 |  | 0.048 | 0.044 | 1 | 0.3 |  | 0.042 | 1 | 0.34 | [22 empty] | AVERAGE | 9.375 | 9.375 | 9.375 | 28.125 | 8.875 | 8.875 | 8.875 | 26.625 |  | 11.2187 |  | 14.6016 | 25.8203 | 0.78659 | AVERAGE | 55.262 | 3796.8465 |  | 475.7709 | 0 | 0 | 0 |  |  |  | 1.7166 | 1.6791 | 1.6049 | 0.20287 | 0.20089 | 0.18209 | 0.18159 | 0.1531 | 0.1531 | 1.4077 | 2.375 | 0.07015 | 0.07015 | 0.070295 | 1.104 | 0.49407 | 0.097702 | 3.7867 | 0.7069 | 5.4037 | 1.1008 | 0.50002 | 0.097566 | 3.9147 | 0.73292 | 10.1097 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.46 | 117 | 115 | 28.82 | 476 | 637 | 117.7 | 2.064 | 0.048 | 36.16 | 59 | 0.328 | 36.17 | 61 | 0 | 35.81 | 60 | 0 | 24.23 | 1.86 | 19 | 2.63 | 76.7 | 37.5 | 1.8809 | 0.263 | 24.23 | 1.42 | 17 | 2.2 | 78.5 | 37.6 | 1.8483 | 24.15 | 1.515 | 15 | 2.24 | 79.1 | 37.7 | 1.773 | 0.15 | 6 | 1.71 | 0.029 | 0.264 | 0.189 | 6 | 2.15 | 0.024 | 0.282 | 6 | 2.1 | 0.015 | 44.01 | 0.343 | 6 | 26.1 | 111.8 | 41 | 78 | 0.039 | 43.52 | 0.359 | 6 | 23.2 | 111.2 | 45 | 75 | 0.029 | 25.6 | 22.8 | 19.2 |  |  | MINIMUM | 9.3 | 9.3 | 9.3 | 27.9 | 8.8 | 8.8 | 8.8 | 26.4 |  | 9.6926 |  | 13.3819 | 23.5786 | 0.0014184 | MINIMUM | 55.2094 | 3627.7562 |  | 475.7709 | [6 empty] | 1.6186 | 1.5681 | 1.5175 | 0.19808 | 0.19016 | 0.17629 | 0.17431 | 0.14313 | 0.14313 | 1.4077 | 1.5 | 0.069544 | 0.069544 | 0.069544 | 1.0972 | 0.49217 | 0.095266 | 3.739 | 0.68927 | 5.388 | 1.0972 | 0.49217 | 0.082095 | 3.789 | 0.67674 | 10.1001 |  | MIN | 0.58 | 9.3 | 27.3548 | 15.8658 | 6.04 | 19 | 10 | 1.5866 |  |  |  | MIN | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.06 | 19.5 | 10 | 1.5045 |  |  |  | MIN | 0.5 | 9.3 | 29.0323 | 14.5161 | 6.02 | 19.5 | 10 | 1.4516 |  |  |  | 1.4516
AVERAGE | 6.5767 | 19.5 | 19.1667 | 4.8033 | 79.3333 | 106.1667 | 19.6167 | 0.344 | 0.024 | 6.0267 | 9.8333 | 0.054667 | 6.0283 | 10.1667 |  | 5.9683 | 10 |  | 6.0575 | 0.465 | 4.75 | 0.6575 | 19.175 | 9.375 | 0.47024 | 0.043833 | 6.0575 | 0.355 | 4.25 | 0.55 | 19.625 | 9.4 | 0.46208 | 6.0375 | 0.37875 | 3.75 | 0.56 | 19.775 | 9.425 | 0.44324 | 0.025 | 1 | 0.285 | 0.0145 | 0.044 | 0.0315 | 1 | 0.35833 | 0.024 | 0.047 | 1 | 0.35 | 0.015 | 7.335 | 0.057167 | 1 | 4.35 | 18.6333 | 20.5 | 39 | 0.0195 | 7.2533 | 0.059833 | 1 | 3.8667 | 18.5333 | 22.5 | 37.5 | 0.0145 | 4.2667 | 3.8 | 3.2 |  |  | MAXIMUM | 9.6 | 9.6 | 9.6 | 28.8 | 9.1 | 9.1 | 9.1 | 27.3 |  | 14.4187 |  | 17.2526 | 28.3234 | 1.0483 | MAXIMUM | 55.4197 | 4181.1428 |  | 475.7709 | [6 empty] | 1.8588 | 1.8099 | 1.7704 | 0.20447 | 0.20447 | 0.18402 | 0.18402 | 0.15846 | 0.15846 | 1.4077 | 3.5 | 0.071942 | 0.071942 | 0.071942 | 1.1115 | 0.49975 | 0.098514 | 3.8091 | 0.71277 | 5.4509 | 1.1115 | 0.52354 | 0.11114 | 4.0123 | 0.75165 | 10.1129
MINIMUM | 6.54 | 18 | 18 | 4.43 | 75 | 105 | 19.2 | 0.318 | 0.024 | 5.96 | 8 | 0.05 | 6 | 9 |  | 5.95 | 9 |  | 5.99 | 0.354 | 3 | 0.58 | 19 | 9.3 | 0.41245 | 0.035 | 6.03 | 0.264 | 3 | 0.49 | 19.5 | 9.3 | 0.3759 | 6.02 | 0.311 | 3 | 0.5 | 19.5 | 9.3 | 0.36111 | 0.022 | 1 | 0.17 | 0.012 | 0.038 | 0.024 | 1 | 0.29 | 0.024 | 0.042 | 1 | 0.28 | 0.015 | 7.24 | 0.054 | 1 | 4.2 | 18.5 | 20 | 33 | 0.017 | 7.18 | 0.058 | 1 | 3.6 | 18 | 20 | 35 | 0.012 | 4.2 | 3.7 | 1.9 | [15 empty] | MIL/MIN |  | TOTAL | 25428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1370 | 1340 | 1280 | 2000 | 1980 | 1795 | 1790 | 1510 | 1510 | 2960 | 0 | 4720 | 4720 | 4730 | 341 | 405 | 48 | 5400 | 1100 | 1315 | 170 | 205 | 24 | 2820 | 570 | 1230
MAXIMUM | 6.67 | 22 | 20 | 5.31 | 82 | 108 | 20 | 0.354 | 0.024 | 6.12 | 11 | 0.058 | 6.09 | 11 |  | 6 | 11 |  | 6.14 | 0.653 | 6 | 0.77 | 19.5 | 9.6 | 0.49736 | 0.052 | 6.08 | 0.533 | 5 | 0.6 | 20 | 9.7 | 0.50129 | 6.06 | 0.449 | 4 | 0.61 | 20 | 9.8 | 0.48296 | 0.03 | 1 | 0.35 | 0.017 | 0.05 | 0.044 | 1 | 0.43 | 0.024 | 0.059 | 1 | 0.42 | 0.015 | 7.51 | 0.06 | 1 | 4.5 | 18.8 | 21 | 45 | 0.022 | 7.28 | 0.062 | 1 | 4 | 19.1 | 25 | 40 | 0.017 | 4.4 | 3.9 | 3.9 | [17 empty] | AVERAGE | 6357 | [9 empty] | 342.5 | 335 | 320 | 500 | 495 | 448.75 | 447.5 | 377.5 | 377.5 | 740 |  | 1180 | 1180 | 1182.5 | 85.25 | 101.25 | 12 | 1350 | 275 | 328.75 | 42.5 | 51.25 | 6 | 705 | 142.5 | 307.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0078 |  | TOTAL AVG COAG ALK: |  |  |  | 10 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.653 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.49 | [5 empty] | 6.0508 |  |  |  |  | 0.059 |  |  |  |  | 0.49 | [6 empty] | 0.059 | [16 empty] | Pump Station MIN |  | 1.9 | [17 empty] | MINIMUM | 6300 | [9 empty] | 320 | 310 | 300 | 500 | 480 | 445 | 440 | 350 | 350 | 740 |  | 1160 | 1160 | 1160 | 84 | 100 | 12 | 1325 | 275 | 325 | 42 | 50 | 5 | 700 | 135 | 305
[90 empty] | MAXIMUM | 6528 | [9 empty] | 380 | 370 | 350 | 500 | 500 | 450 | 450 | 400 | 400 | 740 |  | 1200 | 1200 | 1210 | 88 | 105 | 12 | 1400 | 275 | 340 | 44 | 55 | 7 | 720 | 145 | 315
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.757 |  | TOTAL MGD: |  | 0.003 |  |  | FINISHED SOUTH 1 |  | START: | 23827683 |  | END: | 23827686 |  |  | Alum | 4888 | 9750 | 9750 | 8550 | 8550 | 0 | [44 empty] | 0.5 | 9.3 | 29.0323 | 14.5161 | 6.02 | 19.5 | 10 | 1.4516
[73 empty] | FINISHED 2 | 16.067 |  | TOTAL MGD: |  | 11.754 |  |  | FINISHED SOUTH 2 |  | START: | 44936765 |  | END: | 44948519 |  |  | Caustic | 5973 | 7768 | 7768
[73 empty] | TOTAL RAW | 29.183 |  | TOTAL MGD: |  | 4.619 |  |  | FINISHED CONWAY |  | START: | 10680327 |  | END: | 10684946 |  |  | Hypochlorite | 16 |  | 39
[76 empty] | TOTAL MGD: |  | 11.448 |  |  | FINISHED PERRY |  | START: | 34777842 |  | END: | 34789290 |  |  | Phosphate | 1044
[76 empty] | TOTAL MGD: |  | 9.609 |  |  | RAW PLANT 1 |  | START: | 31868860 |  | END: | 31878469 |  |  | Fluoride | 2250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.73 |  |  | RAW PLANT 2 |  | START: | 31831650 |  | END: | 31841380 |  |  | Cal~Flo | 7.15 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.844 |  |  | RAW PLANT 3 |  | START: | 8465170 |  | END: | 8475014 |  |  | Zinc | 2471
[76 empty] | TOTAL MGD: |  | 0.59 |  |  | DECANT |  | START: | 1943899 |  | END: | 1944489 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.81052 |  |  | BLOW DOWN |  | START: | 9247.5041 |  | END: | 9248.3146 |  |  | NH3 | 9.2 |  | BI-SUL | 1150
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 700
23827686
44948519
10684946
34789290
31878469
31841380
8475014
1944489
9248.3146
1 | 1,5,6 |  |  | 28 | 8.8 | 8 |  | 9.6 |  | 26.4 | 8.3 | 7.5 | 9.1 | 24.9 | 7 | 19.4256 | 0 | 0.02772 | 19.4533 | 1 | 0 | 1900 | 650 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | [5 empty] | 0 | 0 |  | 0 | 0.3 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.4 | #DIV/0! | 0
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 11
DATE: | 2019-04-11 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-11 | [23 empty] | DATE: | 2019-04-11
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-11 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43566.0173 | 2,3,5 | 45 | 9.6 | 9.6 | 9.6 | 28.8 | 9.1 | 9.1 | 9.1 | 27.3 | 1,3,1,3 | 9.5933 | 1,3 | 16.5082 | 26.1014 | 1.722 | 43566.0173 | 55.4197 | 4181.1428 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7609 | 1.8099 | 1.6142 | 0.19808 | 0.19016 | 0.17629 | 0.17431 | 0.15846 | 0.15846 | 1.4077 | 3.5 | 0.069571 | 0.069571 | 0.07015 | 1.1115 | 0.49975 | 0.095266 | 3.739 | 0.68927 | 5.4509 | 1.1115 | 0.52354 | 0.11114 | 3.789 | 0.67674 | 10.1001 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.681 | 5 | 0.72 | 19.2 | 9.7 | 0.50129 |  | 6.14 | 0.503 | 6 | 0.53 | 19.3 | 9.8 | 0.50522 | 6.09 | 0.484 | 6 | 0.6 | 19.8 | 9.8 | 0.48296 | [13 empty] | 7.35 | 0.059 | 1 | 4.1 | 18.9 |  |  |  | 7.31 | 0.067 | 1 | 3.8 | 18.2 |  |  |  | 4.1 | 3.6 | 3.8 | [18 empty] | 6528 | [6 empty] | 0 | 0 | 0 | 360 | 370 | 330 | 500 | 480 | 445 | 440 | 400 | 400 | 740 |  | 1200 | 1200 | 1210 | 88 | 105 | 12 | 1400 | 275 | 340 | 44 | 55 | 7 | 700 | 135 | 315 |  | 1:00 | 0.72 | 9.7 | 26.2268 | 18.8833 | 6.14 | 19.2 | 10 | 1.8883 | 15 | 6.5 | 0.38129 | 1:00 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.14 | 19.3 | 10 | 1.3758 | 15 | 6.5 | 0.38522 | 1:00 | 0.6 | 9.8 | 27.551 | 16.5306 | 6.09 | 19.8 | 10 | 1.6531 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43566.3641 | 2,3,5 | 53 | 9.6 | 9.6 | 9.6 | 28.8 | 9.1 | 9.1 | 9.1 | 27.3 | 1,3,1,3 | 13.4582 | 1,3 | 14.9054 | 28.3637 | 1.6762 | 43566.3641 | 55.182 | 4181.1428 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6631 | 1.6631 | 1.6142 | 0.19808 | 0.19808 | 0.18025 | 0.17827 | 0.16243 | 0.16243 | 1.4077 | 3 | 0.069571 | 0.069571 | 0.069571 | 1.1115 | 0.49975 | 0.1032 | 3.779 | 0.72687 | 5.4509 | 1.1115 | 0.50451 | 0.095266 | 3.8893 | 0.75194 | 10.1001 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.59 | 19 | 18 | 4.36 | 82 | 110 | 19.7 | 0.348 |  | 5.99 | 10 | 0.056 | 6.07 | 10 |  | 5.99 | 10 | [8 empty] | 0.05 | [14 empty] | 0.024 | 1 | 0.28 |  | 0.051 | 0.053 | 1 | 0.26 |  | 0.042 | 1 | 0.33 | [38 empty] | 6500 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 330 | 500 | 500 | 455 | 450 | 410 | 410 | 740 |  | 1200 | 1200 | 1200 | 88 | 105 | 13 | 1400 | 290 | 340 | 44 | 53 | 6 | 720 | 150 | 315 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43566.5842 | 2,3,5 | 53 | 9.6 | 9.6 | 9.6 | 28.8 | 9.1 | 9.1 | 9.1 | 27.3 | 1,3,1,3 | 13.4582 | 1,3 | 14.9054 | 28.3637 | 1.6762 | 43566.5842 | 59.7664 | 4181.1428 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6631 | 1.6631 | 1.6142 | 0.19808 | 0.19808 | 0.18025 | 0.17827 | 0.16243 | 0.16243 | 1.4077 | 3 | 0.069571 | 0.069571 | 0.069571 | 1.1115 | 0.49975 | 0.1032 | 3.779 | 0.72687 | 5.4509 | 1.1115 | 0.50451 | 0.095266 | 3.8893 | 0.75194 | 10.1001 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.29 | 0.057 | 1 | 4 | 18.8 |  |  |  | 7.27 | 0.067 | 1 | 4 | 18.1 |  |  |  | 4.1 | 3.6 | 3.9 | [18 empty] | 7040 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 330 | 500 | 500 | 455 | 450 | 410 | 410 | 740 |  | 1200 | 1200 | 1200 | 88 | 105 | 13 | 1400 | 290 | 340 | 44 | 53 | 6 | 720 | 150 | 315 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43566.7007 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 12.4618 | 1,3 | 15.6499 | 28.1117 | 1.6762 | 43566.7007 | 59.9416 | 4918.9916 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5443 | 1.5443 | 1.5287 | 0.19939 | 0.19939 | 0.18462 | 0.18462 | 0.16456 | 0.16456 | 1.4077 | 3 | 0.069985 | 0.069985 | 0.069278 | 1.1025 | 0.50825 | 0.095833 | 3.7611 | 0.069823 | 5.4039 | 1.0914 | 0.48124 | 0.10216 | 3.9663 | 0.69117 | 10.1092 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.56 | 19 | 18 | 4.56 | 80 | 102 | 19.7 | 0.37 |  | 6.02 | 10 | 0.058 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.049 | [14 empty] | 0.03 | 1 | 0.27 |  | 0.057 | 0.03 | 1 | 0.29 |  | 0.049 | 1 | 0.3 | [38 empty] | 7600 | [6 empty] | 0 | 0 | 0 | 340 | 340 | 340 | 540 | 540 | 500 | 500 | 450 | 450 | 740 |  | 1300 | 1300 | 1300 | 94 | 115 | 13 | 1500 | 30 | 363 | 47 | 55 | 7 | 800 | 150 | 343 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43566.8206 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 12.8794 | 1,3 | 18.7603 | 31.6397 | 1.6762 | 43566.8206 | 59.7839 | 5041.9664 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.726 | 1.726 | 1.5287 | 0.19939 | 0.20308 | 0.18462 | 0.16985 | 0.16456 | 0.16456 | 1.4077 | 5.5 | 0.069985 | 0.069985 | 0.070024 | 1.1025 | 0.49941 | 0.095833 | 3.8561 | 0.66331 | 5.0615 | 1.1146 | 0.52499 | 0.10216 | 3.8884 | 0.64509 | 10.0208 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.019 | [9 empty] | 6.07 | 0.642 | 5 | 0.66 | 18.9 | 9.7 | 0.50129 |  | 6.1 | 0.458 | 5 | 0.53 | 19.1 | 9.8 | 0.50522 | 6.07 | 0.408 | 5 | 0.6 | 19.7 | 9.8 | 0.48296 |  |  |  | 0.006 | [9 empty] | 7.31 | 0.062 | 1 | 4.2 | 19.1 | 25 | 38 | 0.018 | 7.29 | 0.062 | 1 | 4 | 18.4 | 23 | 41 | 0.011 | 4 | 3.6 | 3.1 | [18 empty] | 7580 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 340 | 540 | 550 | 500 | 460 | 450 | 450 | 740 |  | 1300 | 1300 | 1314 | 94 | 113 | 13 | 1500 | 285 | 340 | 48 | 60 | 7 | 820 | 140 | 340 |  | 9:00 | 0.66 | 9.7 | 26.2268 | 17.3097 | 6.07 | 18.9 | 10 | 1.731 | 15 | 6.5 | 0.38129 | 9:00 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.1 | 19.1 | 10 | 1.3758 | 15 | 6.5 | 0.38522 | 9:00 | 0.6 | 9.8 | 27.551 | 16.5306 | 6.07 | 19.7 | 10 | 1.6531 | 15 | 6.5 | 0.36296
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.53 | 18 | 18 | 4.15 | 85 | 106 | 19.8 | 0.368 |  | 6.06 | 10 | 0.06 | 6.02 | 10 |  | 6 | 10 | [8 empty] | 0.049 | [14 empty] | 0.039 | 1 | 0.28 |  | 0.051 | 0.036 | 1 | 0.23 |  | 0.046 | 1 | 0.31 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.623 | 6 | 0.51 | 19.8 | 9.7 | 0.50129 |  | 6.14 | 0.496 | 5 | 0.43 | 20.1 | 9.8 | 0.38965 | 6.11 | 0.456 | 5 | 0.52 | 20 | 9.8 | 0.37407 | [13 empty] | 7.33 | 0.057 | 1 | 4.5 | 19.1 |  |  |  | 7.24 | 0.064 | 1 | 3.8 | 19.5 |  |  |  | 4.1 | 3.6 | 3.5 | [55 empty] | 13:00 | 0.51 | 9.7 | 26.2268 | 13.3757 | 6.12 | 19.8 | 10 | 1.3376 | 15 | 6.5 | 0.38129 | 13:00 | 0.43 | 9.8 | 25.9592 | 11.1624 | 6.14 | 20.1 | 7 | 1.5946 | 20 | 6.5 | 0.26965 | 13:00 | 0.52 | 9.8 | 27.551 | 14.3265 | 6.11 | 20 | 7 | 2.0466 | 20 | 6.5 | 0.25407
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.51 | 18 | 18 | 3.89 | 92 | 108 | 20.1 | 0.381 |  | 6.07 | 10 | 0.062 | 6.1 | 10 |  | 6.04 | 10 | [8 empty] | 0.048 | [14 empty] | 0.048 | 1 | 0.32 |  | 0.052 | 0.054 | 1 | 0.28 |  | 0.05 | 1 | 0.34 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.61 | 0.062 | 1 | 4.1 | 19.2 |  |  |  | 7.4 | 0.064 | 1 | 3.7 | 19.1 |  |  |  | 4.2 | 3.6 | 3.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.54 | 20 | 18 | 3.85 | 88 | 109 | 20.4 | 0.38 |  | 6.02 | 10 | 0.061 | 6.07 | 10 |  | 6.03 | 10 | [8 empty] | 0.052 | [14 empty] | 0.07 | 1 | 0.23 |  | 0.056 | 0.05 | 1 | 0.14 |  | 0.05 | 1 | 0.11 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.024 | [9 empty] | 6.16 | 0.612 | 6 | 0.64 | 19.7 | 10.3 | 0.52487 |  | 6.13 | 0.533 | 6 | 0.44 | 20 | 10.3 | 0.40341 | 6.14 | 0.48 | 6 | 0.43 | 20.2 | 10.4 | 0.38963 |  |  |  | 0.014 |  |  |  |  | 0.024 |  |  |  | 0.01 | 7.32 | 0.057 | 1 | 4.2 | 19.3 | 22 | 35 | 0.018 | 7.33 | 0.065 | 1 | 3.8 | 18.9 | 21 | 36 | 0.018 | 4.1 | 3.5 | 3.7 | [55 empty] | 21:00 | 0.64 | 10.3 | 24.699 | 15.8074 | 6.16 | 19.7 | 10 | 1.5807 | 15 | 6.5 | 0.40487 | 21:00 | 0.44 | 10.3 | 24.699 | 10.8676 | 6.13 | 20 | 7 | 1.5525 | 20 | 6.5 | 0.28341 | 21:00 | 0.43 | 10.4 | 25.9615 | 11.1635 | 6.14 | 20.2 | 7 | 1.5948 | 20 | 6.5 | 0.26963
22:00 | [72 empty] | DOSE |  | TOTAL | 49.4 | 49.4 | 49.6 | 148.4 | 46.9 | 46.9 | 47.1 | 140.9 | 0 | 61.8509 | 0 | 80.7293 | 142.5802 | 8.4266 | TOTAL | 290.0936 | 22504.3864 | 0 | 2410.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3575 | 8.4064 | 7.9 | 0.99301 | 0.98878 | 0.90603 | 0.88532 | 0.81243 | 0.81243 | 7.0383 | 18 | 0.34868 | 0.34868 | 0.34859 | 5.5396 | 2.5069 | 0.49334 | 18.9143 | 2.8762 | 26.818 | 5.5406 | 2.5388 | 0.506 | 19.4223 | 3.5169 | 50.4304 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 20 | 18 | 3.99 | 99 | 119 | 20.4 | 0.384 |  | 6.11 | 11 | 0.066 | 6.12 | 12 |  | 6.02 | 11 | [8 empty] | 0.056 | [14 empty] | 0.055 | 1 | 0.36 |  | 0.049 | 0.066 | 1 | 0.25 |  | 0.044 | 1 | 0.3 | [22 empty] | AVERAGE | 9.88 | 9.88 | 9.92 | 29.68 | 9.38 | 9.38 | 9.42 | 28.18 |  | 12.3702 |  | 16.1459 | 28.516 | 1.6853 | AVERAGE | 58.0187 | 4500.8773 |  | 482.1145 | 0 | 0 | 0 |  |  |  | 1.6715 | 1.6813 | 1.58 | 0.1986 | 0.19776 | 0.18121 | 0.17706 | 0.16249 | 0.16249 | 1.4077 | 3.6 | 0.069736 | 0.069736 | 0.069719 | 1.1079 | 0.50138 | 0.098668 | 3.7829 | 0.57523 | 5.3636 | 1.1081 | 0.50776 | 0.1012 | 3.8845 | 0.70338 | 10.0861 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.26 | 114 | 108 | 24.8 | 526 | 654 | 120.1 | 2.231 | 0.043 | 36.27 | 61 | 0.363 | 36.43 | 62 | 0 | 36.08 | 61 | 0 | 24.49 | 2.558 | 22 | 2.53 | 77.6 | 39.4 | 2.0287 | 0.304 | 24.51 | 1.99 | 22 | 1.93 | 78.5 | 39.7 | 1.8035 | 24.41 | 1.828 | 22 | 2.15 | 79.7 | 39.8 | 1.7296 | 0.266 | 6 | 1.74 | 0.02 | 0.316 | 0.289 | 6 | 1.45 | 0.024 | 0.281 | 6 | 1.69 | 0.01 | 44.21 | 0.354 | 6 | 25.1 | 114.4 | 47 | 73 | 0.036 | 43.84 | 0.389 | 6 | 23.1 | 112.2 | 44 | 77 | 0.029 | 24.6 | 21.5 | 21.7 |  |  | MINIMUM | 9.6 | 9.6 | 9.6 | 28.8 | 9.1 | 9.1 | 9.1 | 27.3 |  | 9.5933 |  | 14.9054 | 26.1014 | 1.6762 | MINIMUM | 55.182 | 4181.1428 |  | 475.7709 | [6 empty] | 1.5443 | 1.5443 | 1.5287 | 0.19808 | 0.19016 | 0.17629 | 0.16985 | 0.15846 | 0.15846 | 1.4077 | 3 | 0.069571 | 0.069571 | 0.069278 | 1.1025 | 0.49941 | 0.095266 | 3.739 | 0.069823 | 5.0615 | 1.0914 | 0.48124 | 0.095266 | 3.789 | 0.64509 | 10.0208 |  | MIN | 0.51 | 9.7 | 26.2268 | 13.3757 | 6.12 | 19.8 | 10 | 1.3376 |  |  |  | MIN | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.14 | 19.3 | 10 | 1.3758 |  |  |  | MIN | 0.43 | 10.4 | 25.9615 | 11.1635 | 6.14 | 20.2 | 7 | 1.5948 |  |  |  | 1.3376
AVERAGE | 6.5433 | 19 | 18 | 4.1333 | 87.6667 | 109 | 20.0167 | 0.37183 | 0.0215 | 6.045 | 10.1667 | 0.0605 | 6.0717 | 10.3333 |  | 6.0133 | 10.1667 |  | 6.1225 | 0.6395 | 5.5 | 0.6325 | 19.4 | 9.85 | 0.50719 | 0.050667 | 6.1275 | 0.4975 | 5.5 | 0.4825 | 19.625 | 9.925 | 0.45088 | 6.1025 | 0.457 | 5.5 | 0.5375 | 19.925 | 9.95 | 0.43241 | 0.044333 | 1 | 0.29 | 0.01 | 0.052667 | 0.048167 | 1 | 0.24167 | 0.024 | 0.046833 | 1 | 0.28167 |  | 7.3683 | 0.059 | 1 | 4.1833 | 19.0667 | 23.5 | 36.5 | 0.018 | 7.3067 | 0.064833 | 1 | 3.85 | 18.7 | 22 | 38.5 | 0.0145 | 4.1 | 3.5833 | 3.6167 |  |  | MAXIMUM | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 |  | 13.4582 |  | 18.7603 | 31.6397 | 1.722 | MAXIMUM | 59.9416 | 5041.9664 |  | 507.489 | [6 empty] | 1.7609 | 1.8099 | 1.6142 | 0.19939 | 0.20308 | 0.18462 | 0.18462 | 0.16456 | 0.16456 | 1.4077 | 5.5 | 0.069985 | 0.069985 | 0.07015 | 1.1115 | 0.50825 | 0.1032 | 3.8561 | 0.72687 | 5.4509 | 1.1146 | 0.52499 | 0.11114 | 3.9663 | 0.75194 | 10.1092
MINIMUM | 6.51 | 18 | 18 | 3.85 | 80 | 102 | 19.7 | 0.348 | 0.019 | 5.99 | 10 | 0.056 | 6.02 | 10 |  | 5.99 | 10 |  | 6.07 | 0.612 | 5 | 0.51 | 18.9 | 9.7 | 0.50129 | 0.048 | 6.1 | 0.458 | 5 | 0.43 | 19.1 | 9.8 | 0.38965 | 6.07 | 0.408 | 5 | 0.43 | 19.7 | 9.8 | 0.37407 | 0.024 | 1 | 0.23 | 0.006 | 0.049 | 0.03 | 1 | 0.14 | 0.024 | 0.042 | 1 | 0.11 |  | 7.29 | 0.057 | 1 | 4 | 18.8 | 22 | 35 | 0.018 | 7.24 | 0.062 | 1 | 3.7 | 18.1 | 21 | 36 | 0.011 | 4 | 3.5 | 3.1 | [15 empty] | MIL/MIN |  | TOTAL | 35248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 1770 | 1670 | 2580 | 2570 | 2355 | 2300 | 2120 | 2120 | 3700 | 0 | 6200 | 6200 | 6224 | 452 | 543 | 64 | 7200 | 1170 | 1723 | 227 | 276 | 33 | 3760 | 725 | 1628
MAXIMUM | 6.59 | 20 | 18 | 4.56 | 99 | 119 | 20.4 | 0.384 | 0.024 | 6.11 | 11 | 0.066 | 6.12 | 12 |  | 6.04 | 11 |  | 6.16 | 0.681 | 6 | 0.72 | 19.8 | 10.3 | 0.52487 | 0.056 | 6.14 | 0.533 | 6 | 0.53 | 20.1 | 10.3 | 0.50522 | 6.14 | 0.484 | 6 | 0.6 | 20.2 | 10.4 | 0.48296 | 0.07 | 1 | 0.36 | 0.014 | 0.057 | 0.066 | 1 | 0.29 | 0.024 | 0.05 | 1 | 0.34 |  | 7.61 | 0.062 | 1 | 4.5 | 19.3 | 25 | 38 | 0.018 | 7.4 | 0.067 | 1 | 4 | 19.5 | 23 | 41 | 0.018 | 4.2 | 3.6 | 3.9 | [17 empty] | AVERAGE | 7049.6 | [9 empty] | 352 | 354 | 334 | 516 | 514 | 471 | 460 | 424 | 424 | 740 |  | 1240 | 1240 | 1244.8 | 90.4 | 108.6 | 12.8 | 1440 | 234 | 344.6 | 45.4 | 55.2 | 6.6 | 752 | 145 | 325.6
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0433 |  | TOTAL AVG COAG ALK: |  |  |  | 10.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.681 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.43 | [5 empty] | 6.1175 |  |  |  |  | 0.07 |  |  |  |  | 0.43 | [6 empty] | 0.07 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 6500 | [9 empty] | 340 | 340 | 330 | 500 | 480 | 445 | 440 | 400 | 400 | 740 |  | 1200 | 1200 | 1200 | 88 | 105 | 12 | 1400 | 30 | 340 | 44 | 53 | 6 | 700 | 135 | 315
[90 empty] | MAXIMUM | 7600 | [9 empty] | 380 | 380 | 340 | 540 | 550 | 500 | 500 | 450 | 450 | 740 |  | 1300 | 1300 | 1314 | 94 | 115 | 13 | 1500 | 290 | 363 | 48 | 60 | 7 | 820 | 150 | 343
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.592 |  | TOTAL MGD: |  | 0.004 |  |  | FINISHED SOUTH 1 |  | START: | 23827686 |  | END: | 23827690 |  |  | Alum | 4892 | 8933 | 8933 | 7804 | 7804 | 0 | [44 empty] | 0.51 | 9.7 | 26.2268 | 13.3757 | 6.12 | 19.8 | 10 | 1.3376
[73 empty] | FINISHED 2 | 15.681 |  | TOTAL MGD: |  | 11.588 |  |  | FINISHED SOUTH 2 |  | START: | 44948519 |  | END: | 44960107 |  |  | Caustic | 5853 | 7731 | 7731
[73 empty] | TOTAL RAW | 29.659 |  | TOTAL MGD: |  | 4.434 |  |  | FINISHED CONWAY |  | START: | 10684946 |  | END: | 10689380 |  |  | Hypochlorite | 19 |  | 31
[76 empty] | TOTAL MGD: |  | 11.247 |  |  | FINISHED PERRY |  | START: | 34789290 |  | END: | 34800537 |  |  | Phosphate | 998
[76 empty] | TOTAL MGD: |  | 9.794 |  |  | RAW PLANT 1 |  | START: | 31878469 |  | END: | 31888263 |  |  | Fluoride | 2150 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.917 |  |  | RAW PLANT 2 |  | START: | 31841380 |  | END: | 31851297 |  |  | Cal~Flo | 13.75 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.948 |  |  | RAW PLANT 3 |  | START: | 8475014 |  | END: | 8484962 |  |  | Zinc | 2467
[76 empty] | TOTAL MGD: |  | 0.77 |  |  | DECANT |  | START: | 1944489 |  | END: | 1945259 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 1.1043 |  |  | BLOW DOWN |  | START: | 9248.3146 |  | END: | 9249.4189 |  |  | NH3 | 9 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 490
23827690
44960107
10689380
34800537
31888263
31851297
8484962
1945259
9249.4189
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 12
DATE: | 2019-04-12 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-12 | [23 empty] | DATE: | 2019-04-12
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-12 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43567.0065 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 10.6891 | 1,3 | 16.9733 | 27.6624 | 1.6762 | 43567.0065 | 60.1782 | 5041.9664 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.726 | 1.726 | 1.5287 | 0.19939 | 0.20308 | 0.18462 | 0.16985 | 0.16456 | 0.16456 | 1.4077 | 5.5 | 0.069985 | 0.069985 | 0.070024 | 1.1025 | 0.49941 | 0.095833 | 3.8561 | 0.66331 | 5.2104 | 1.1146 | 0.52499 | 0.10216 | 3.8884 | 0.64509 | 10.0208 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.23 | 0.702 | 6 | 0.59 | 19.7 | 10.3 | 0.52487 |  | 6.2 | 0.553 | 6 | 0.45 | 19.9 | 10.3 | 0.52487 | 6.15 | 0.531 | 6 | 0.5 | 20.3 | 10.4 | 0.38963 | [13 empty] | 7.21 | 0.056 | 1 | 4.2 | 19.3 |  |  |  | 7.23 | 0.059 | 1 | 3.9 | 18.8 |  |  |  | 4.1 | 3.5 | 3.7 | [18 empty] | 7630 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 340 | 540 | 550 | 500 | 460 | 450 | 450 | 740 |  | 1300 | 1300 | 1314 | 94 | 113 | 13 | 1500 | 285 | 350 | 48 | 60 | 7 | 820 | 140 | 340 |  | 1:00 | 0.59 | 10.3 | 24.699 | 14.5724 | 6.23 | 19.7 | 10 | 1.4572 | 15 | 6.5 | 0.40487 | 1:00 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.2 | 19.9 | 10 | 1.1115 | 15 | 6.5 | 0.40487 | 1:00 | 0.5 | 10.4 | 25.9615 | 12.9808 | 6.15 | 20.3 | 7 | 1.8544 | 20 | 6.5 | 0.26963
2:00 | [72 empty] | 43567.3854 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 11.4091 | 1,3 | 17.3117 | 28.7208 | 0.90864 | 43567.3854 | 63.0965 | 4980.479 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.4989 | 1.4 | 0.19939 | 0.19939 | 0.18093 | 0.18093 | 0.1609 | 0.1609 | 1.4077 | 3 | 0.069985 | 0.069985 | 0.069278 | 1.1025 | 0.49941 | 0.1032 | 3.7993 | 0.72615 | 5.2104 | 1.1146 | 0.49874 | 0.10216 | 4.0284 | 0.77411 | 10.0208 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.54 | 20 | 18 | 3.81 | 89 | 111 | 20.5 | 0.379 |  | 6 | 10 | 0.064 | 6.01 | 10 |  | 6 | 10 | [8 empty] | 0.058 | [14 empty] | 0.044 | 1 | 0.29 |  | 0.054 | 0.078 | 1 | 0.24 |  | 0.045 | 1 | 0.25 | [38 empty] | 8000 | [6 empty] | 0 | 0 | 0 | 330 | 330 | 340 | 540 | 540 | 490 | 490 | 440 | 440 | 740 |  | 1300 | 1300 | 1300 | 94 | 113 | 14 | 1525 | 312 | 350 | 48 | 57 | 7 | 820 | 168 | 340 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43567.5367 | 2,3,5 | 80 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | 1,3,1,3 | 11.4091 | 1,3 | 17.3117 | 28.7208 | 0.90864 | 43567.5367 | 64.7427 | 4980.479 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3092 | 1.4401 | 1.4838 | 0.19193 | 0.19193 | 0.17416 | 0.17416 | 0.15639 | 0.15639 | 1.4077 | 3 | 0.06724 | 0.06724 | 0.06724 | 1.0593 | 0.47982 | 0.099158 | 3.8278 | 0.72675 | 5.4352 | 1.1043 | 0.48407 | 0.099158 | 4.0067 | 0.76476 | 10.1265 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.2 | 0.057 | 1 | 4.2 | 19.4 |  |  |  | 7.24 | 0.061 | 1 | 3.8 | 18.8 |  |  |  | 4.1 | 3.5 | 3.6 | [18 empty] | 8500 | [6 empty] | 0 | 0 | 0 | 300 | 330 | 340 | 540 | 540 | 490 | 490 | 440 | 440 | 740 |  | 1300 | 1300 | 1300 | 94 | 113 | 14 | 1600 | 325 | 380 | 49 | 57 | 7 | 840 | 171 | 354 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43567.8204 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 11.6122 | 1,3 | 18.4018 | 30.0139 | 0.90864 | 43567.8204 | 65.4626 | 5533.8656 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6352 | 1.6352 | 1.4838 | 0.19939 | 0.20677 | 0.16985 | 0.16246 | 0.15724 | 0.15724 | 1.4077 | 3 | 0.069985 | 0.069985 | 0.070344 | 1.1025 | 0.49941 | 0.095833 | 3.6663 | 0.66331 | 5.4337 | 1.1146 | 0.50749 | 0.10216 | 4.0806 | 0.69117 | 10.1092 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.54 | 19 | 18 | 3.92 | 91 | 112 | 20.5 | 0.389 |  | 6.01 | 10 | 0.059 | 6.02 | 10 |  | 6 | 10 | [8 empty] | 0.049 | [14 empty] | 0.04 | 1 | 0.28 |  | 0.056 | 0.063 | 1 | 0.26 |  | 0.042 | 1 | 0.25 | [38 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 360 | 360 | 330 | 540 | 560 | 460 | 440 | 430 | 430 | 740 |  | 1300 | 1300 | 1320 | 94 | 113 | 13 | 1470 | 285 | 365 | 48 | 58 | 7 | 840 | 150 | 343 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.025 | [9 empty] | 6.06 | 0.525 | 6 | 0.61 | 19.6 | 10.3 | 0.52487 |  | 6.05 | 0.444 | 7 | 0.49 | 19.8 | 10.3 | 0.52487 | 6.06 | 0.394 | 7 | 0.36 | 20.3 | 10.4 | 0.38963 |  |  |  | 0.011 | [9 empty] | 7.16 | 0.061 | 2 | 4.2 | 19.6 | 27 | 42 | 0.02 | 7.17 | 0.066 | 2 | 3.8 | 18.8 | 29 | 41 | 0.015 | 3.9 | 3.5 | 3.8 | [55 empty] | 9:00 | 0.61 | 10.3 | 24.699 | 15.0664 | 6.06 | 19.6 | 10 | 1.5066 | 15 | 6.5 | 0.40487 | 9:00 | 0.49 | 10.3 | 24.699 | 12.1025 | 6.05 | 19.8 | 10 | 1.2103 | 15 | 6.5 | 0.40487 | 9:00 | 0.36 | 10.4 | 25.9615 | 9.3462 | 6.06 | 20.3 | 7 | 1.3352 | 20 | 6.5 | 0.26963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.52 | 18 | 18 | 3.61 | 92 | 111 | 21 | 0.4 |  | 6.09 | 10 | 0.069 | 6.02 | 10 |  | 6 | 10 | [8 empty] | 0.05 | [14 empty] | 0.042 | 1 | 0.26 |  | 0.051 | 0.042 | 1 | 0.27 |  | 0.042 | 1 | 0.25 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.08 | 0.271 | 6 | 0.44 | 20.8 | 10.3 | 0.40341 |  | 6.1 | 0.337 | 5 | 0.45 | 21 | 10.3 | 0.40341 | 6.06 | 0.634 | 5 | 0.34 | 21 | 10.4 | 0.38963 | [13 empty] | 7.41 | 0.064 | 1 | 4.3 | 19.5 |  |  |  | 7.27 | 0.068 | 1 | 3.9 | 19.5 |  |  |  | 4 | 2.7 | 3.3 | [55 empty] | 13:00 | 0.44 | 10.3 | 24.699 | 10.8676 | 6.08 | 20.8 | 7 | 1.5525 | 20 | 6.5 | 0.28341 | 13:00 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.1 | 21 | 7 | 1.5878 | 20 | 6.5 | 0.28341 | 13:00 | 0.34 | 10.4 | 25.9615 | 8.8269 | 6.06 | 21 | 7 | 1.261 | 20 | 6.5 | 0.26963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.52 | 19 | 18 | 3.62 | 93 | 112 | 21.2 | 0.397 |  | 6.06 | 10 | 0.067 | 6.1 | 10 |  | 6 | 10 | [8 empty] | 0.05 | [14 empty] | 0.049 | 1 | 0.28 |  | 0.051 | 0.068 | 1 | 0.24 |  | 0.047 | 1 | 0.27 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.82 | 0.066 | 1 | 4.8 | 20 |  |  |  | 7.45 | 0.071 | 1 | 4 | 19.8 |  |  |  | 3.9 | 3.5 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.46 | 19 | 18 | 3.74 | 94 | 113 | 21.1 | 0.399 |  | 6.04 | 10 | 0.067 | 6.04 | 10 |  | 5.98 | 9 | [8 empty] | 0.055 | [14 empty] | 0.048 | 1 | 0.27 |  | 0.055 | 0.053 | 1 | 0.22 |  | 0.047 | 1 | 0.21 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.024 | [9 empty] | 6.09 | 0.3 | 6 | 0.49 | 20.5 | 10.3 | 0.40341 |  | 6.09 | 0.375 | 6 | 0.44 | 20.8 | 10.3 | 0.40341 | 6.1 | 0.41 | 6 | 0.44 | 20.8 | 10.4 | 0.38963 |  |  |  | 0.008 |  |  |  |  | 0.024 |  |  |  | 0.014 | 7.32 | 0.063 | 1 | 4.6 | 19.1 | 21 | 39 | 0.02 | 7.26 | 0.065 | 1 | 4 | 19.3 | 23 | 37 | 0.014 | 4 | 3.9 | 3.5 | [55 empty] | 21:00 | 0.49 | 10.3 | 24.699 | 12.1025 | 6.09 | 20.5 | 7 | 1.7289 | 20 | 6.5 | 0.28341 | 21:00 | 0.44 | 10.3 | 24.699 | 10.8676 | 6.09 | 20.8 | 7 | 1.5525 | 20 | 6.5 | 0.28341 | 21:00 | 0.44 | 10.4 | 25.9615 | 11.4231 | 6.1 | 20.8 | 7 | 1.6319 | 20 | 6.5 | 0.26963
22:00 | [72 empty] | DOSE |  | TOTAL | 41.6 | 41.6 | 41.9 | 125.1 | 39.6 | 39.6 | 39.9 | 119.1 | 0 | 45.1195 | 0 | 69.9984 | 115.1179 | 4.4021 | TOTAL | 253.4799 | 20536.79 | 0 | 2045.815 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1703 | 6.3002 | 5.8962 | 0.79009 | 0.80117 | 0.70955 | 0.6874 | 0.63909 | 0.63909 | 5.6306 | 14.5 | 0.27719 | 0.27719 | 0.27689 | 4.3668 | 1.978 | 0.39403 | 15.1496 | 2.7795 | 21.2896 | 4.4481 | 2.0153 | 0.40564 | 16.0041 | 2.8751 | 40.2773 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.5 | 20 | 17 | 3.76 | 88 | 114 | 20.5 | 0.369 |  | 6 | 10 | 0.057 | 6.03 | 10 |  | 5.94 | 10 | [8 empty] | 0.053 | [14 empty] | 0.046 | 1 | 0.25 |  | 0.051 | 0.044 | 1 | 0.27 |  | 0.042 | 1 | 0.28 | [22 empty] | AVERAGE | 10.4 | 10.4 | 10.475 | 31.275 | 9.9 | 9.9 | 9.975 | 29.775 |  | 11.2799 |  | 17.4996 | 28.7795 | 1.1005 | AVERAGE | 63.37 | 5134.1975 |  | 511.4537 | 0 | 0 | 0 |  |  |  | 1.5426 | 1.575 | 1.4741 | 0.19752 | 0.20029 | 0.17739 | 0.17185 | 0.15977 | 0.15977 | 1.4077 | 3.625 | 0.069299 | 0.069299 | 0.069221 | 1.0917 | 0.49451 | 0.098507 | 3.7874 | 0.69488 | 5.3224 | 1.112 | 0.50382 | 0.10141 | 4.001 | 0.71879 | 10.0693 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.08 | 115 | 107 | 22.46 | 547 | 673 | 124.8 | 2.333 | 0.049 | 36.2 | 60 | 0.383 | 0 | 60 | 0 | 35.92 | 59 | 0 | 24.46 | 1.798 | 24 | 2.13 | 80.6 | 41.2 | 1.8566 | 0.315 | 24.44 | 1.709 | 24 | 1.83 | 81.5 | 41.2 | 1.8566 | 24.37 | 1.969 | 24 | 1.64 | 82.4 | 41.6 | 1.5585 | 0.269 | 6 | 1.63 | 0.019 | 0.318 | 0.348 | 6 | 1.5 | 0.024 | 0.265 | 6 | 1.51 | 0.014 | 44.12 | 0.367 | 7 | 26.3 | 116.9 | 48 | 81 | 0.04 | 43.62 | 0.39 | 7 | 23.4 | 115 | 52 | 78 | 0.029 | 24 | 20.6 | 21.3 |  |  | MINIMUM | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 |  | 10.6891 |  | 16.9733 | 27.6624 | 0.90864 | MINIMUM | 60.1782 | 4980.479 |  | 507.489 | [6 empty] | 1.3092 | 1.4401 | 1.4 | 0.19193 | 0.19193 | 0.16985 | 0.16246 | 0.15639 | 0.15639 | 1.4077 | 3 | 0.06724 | 0.06724 | 0.06724 | 1.0593 | 0.47982 | 0.095833 | 3.6663 | 0.66331 | 5.2104 | 1.1043 | 0.48407 | 0.099158 | 3.8884 | 0.64509 | 10.0208 |  | MIN | 0.59 | 10.3 | 24.699 | 14.5724 | 6.23 | 19.7 | 10 | 1.4572 |  |  |  | MIN | 0.45 | 10.3 | 24.699 | 11.1146 | 6.2 | 19.9 | 10 | 1.1115 |  |  |  | MIN | 0.34 | 10.4 | 25.9615 | 8.8269 | 6.06 | 21 | 7 | 1.261 |  |  |  | 1.1115
AVERAGE | 6.5133 | 19.1667 | 17.8333 | 3.7433 | 91.1667 | 112.1667 | 20.8 | 0.38883 | 0.0245 | 6.0333 | 10 | 0.063833 |  | 10 |  | 5.9867 | 9.8333 |  | 6.115 | 0.4495 | 6 | 0.5325 | 20.15 | 10.3 | 0.46414 | 0.0525 | 6.11 | 0.42725 | 6 | 0.4575 | 20.375 | 10.3 | 0.46414 | 6.0925 | 0.49225 | 6 | 0.41 | 20.6 | 10.4 | 0.38963 | 0.044833 | 1 | 0.27167 | 0.0095 | 0.053 | 0.058 | 1 | 0.25 | 0.024 | 0.044167 | 1 | 0.25167 | 0.014 | 7.3533 | 0.061167 | 1.1667 | 4.3833 | 19.4833 | 24 | 40.5 | 0.02 | 7.27 | 0.065 | 1.1667 | 3.9 | 19.1667 | 26 | 39 | 0.0145 | 4 | 3.4333 | 3.55 |  |  | MAXIMUM | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 |  | 11.6122 |  | 18.4018 | 30.0139 | 1.6762 | MAXIMUM | 65.4626 | 5533.8656 |  | 523.348 | [6 empty] | 1.726 | 1.726 | 1.5287 | 0.19939 | 0.20677 | 0.18462 | 0.18093 | 0.16456 | 0.16456 | 1.4077 | 5.5 | 0.069985 | 0.069985 | 0.070344 | 1.1025 | 0.49941 | 0.1032 | 3.8561 | 0.72675 | 5.4352 | 1.1146 | 0.52499 | 0.10216 | 4.0806 | 0.77411 | 10.1265
MINIMUM | 6.46 | 18 | 17 | 3.61 | 88 | 111 | 20.5 | 0.369 | 0.024 | 6 | 10 | 0.057 |  | 10 |  | 5.94 | 9 |  | 6.06 | 0.271 | 6 | 0.44 | 19.6 | 10.3 | 0.40341 | 0.049 | 6.05 | 0.337 | 5 | 0.44 | 19.8 | 10.3 | 0.40341 | 6.06 | 0.394 | 5 | 0.34 | 20.3 | 10.4 | 0.38963 | 0.04 | 1 | 0.25 | 0.008 | 0.051 | 0.042 | 1 | 0.22 | 0.024 | 0.042 | 1 | 0.21 | 0.014 | 7.16 | 0.056 | 1 | 4.2 | 19.1 | 21 | 39 | 0.02 | 7.17 | 0.059 | 1 | 3.8 | 18.8 | 23 | 37 | 0.014 | 3.9 | 2.7 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 32430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1370 | 1400 | 1350 | 2160 | 2190 | 1940 | 1880 | 1760 | 1760 | 2960 | 0 | 5200 | 5200 | 5234 | 376 | 452 | 54 | 6095 | 1207 | 1445 | 193 | 232 | 28 | 3320 | 629 | 1377
MAXIMUM | 6.54 | 20 | 18 | 3.92 | 94 | 114 | 21.2 | 0.4 | 0.025 | 6.09 | 10 | 0.069 |  | 10 |  | 6 | 10 |  | 6.23 | 0.702 | 6 | 0.61 | 20.8 | 10.3 | 0.52487 | 0.058 | 6.2 | 0.553 | 7 | 0.49 | 21 | 10.3 | 0.52487 | 6.15 | 0.634 | 7 | 0.5 | 21 | 10.4 | 0.38963 | 0.049 | 1 | 0.29 | 0.011 | 0.056 | 0.078 | 1 | 0.27 | 0.024 | 0.047 | 1 | 0.28 | 0.014 | 7.82 | 0.066 | 2 | 4.8 | 20 | 27 | 42 | 0.02 | 7.45 | 0.071 | 2 | 4 | 19.8 | 29 | 41 | 0.015 | 4.1 | 3.9 | 3.8 | [17 empty] | AVERAGE | 8107.5 | [9 empty] | 342.5 | 350 | 337.5 | 540 | 547.5 | 485 | 470 | 440 | 440 | 740 |  | 1300 | 1300 | 1308.5 | 94 | 113 | 13.5 | 1523.75 | 301.75 | 361.25 | 48.25 | 58 | 7 | 830 | 157.25 | 344.25
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.01 |  | TOTAL AVG COAG ALK: |  |  |  | 9.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.702 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.34 | [5 empty] | 6.1058 |  |  |  |  | 0.078 |  |  |  |  | 0.34 | [6 empty] | 0.078 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 7630 | [9 empty] | 300 | 330 | 330 | 540 | 540 | 460 | 440 | 430 | 430 | 740 |  | 1300 | 1300 | 1300 | 94 | 113 | 13 | 1470 | 285 | 350 | 48 | 57 | 7 | 820 | 140 | 340
[90 empty] | MAXIMUM | 8500 | [9 empty] | 380 | 380 | 340 | 540 | 560 | 500 | 490 | 450 | 450 | 740 |  | 1300 | 1300 | 1320 | 94 | 113 | 14 | 1600 | 325 | 380 | 49 | 60 | 7 | 840 | 171 | 354
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.823 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827690 |  | END: | 23827691 |  |  | Alum | 4873 | 7930 | 7930 | 9688 | 9688 | 0 | [44 empty] | 0.45 | 10.3 | 24.699 | 11.1146 | 6.2 | 19.9 | 10 | 1.1115
[73 empty] | FINISHED 2 | 16.398 |  | TOTAL MGD: |  | 11.822 |  |  | FINISHED SOUTH 2 |  | START: | 44960107 |  | END: | 44971929 |  |  | Caustic | 5698 | 7695 | 7695
[73 empty] | TOTAL RAW | 31.356 |  | TOTAL MGD: |  | 4.727 |  |  | FINISHED CONWAY |  | START: | 10689380 |  | END: | 10694107 |  |  | Hypochlorite | 18 |  | 42
[76 empty] | TOTAL MGD: |  | 11.671 |  |  | FINISHED PERRY |  | START: | 34800537 |  | END: | 34812208 |  |  | Phosphate | 4025
[76 empty] | TOTAL MGD: |  | 10.37 |  |  | RAW PLANT 1 |  | START: | 31888263 |  | END: | 31898633 |  |  | Fluoride | 2100 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.5 |  |  | RAW PLANT 2 |  | START: | 31851297 |  | END: | 31861797 |  |  | Cal~Flo | 11.4 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.486 |  |  | RAW PLANT 3 |  | START: | 8484962 |  | END: | 8495448 |  |  | Zinc | 2454
[76 empty] | TOTAL MGD: |  | 0.711 |  |  | DECANT |  | START: | 1945259 |  | END: | 1945970 |  |  | Polymer | 24
[76 empty] | TOTAL MGD: |  | 0.57281 |  |  | BLOW DOWN |  | START: | 9249.4189 |  | END: | 9249.9917 |  |  | NH3 | 8.82 |  | BI-SUL | 1090
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 550
23827691
44971929
10694107
34812208
31898633
31861797
8495448
1945970
9249.9917
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 13
DATE: | 2019-04-13 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-13 | [23 empty] | DATE: | 2019-04-13
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-13 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43568.0022 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 12.4301 | 1,3 | 16.4635 | 28.8936 | 1.7389 | 43568.0022 | 65.4626 | 5533.8656 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6352 | 1.6352 | 1.4838 | 0.19939 | 0.20677 | 0.16985 | 0.16246 | 0.15724 | 0.15724 | 1.4077 | 3 | 0.069985 | 0.069985 | 0.070344 | 1.1025 | 0.49941 | 0.095833 | 3.5965 | 0.66331 | 5.4337 | 1.1146 | 0.50749 | 0.10216 | 3.9884 | 0.69117 | 10.1092 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.315 | 4 | 0.58 | 20.1 | 10.2 | 0.40066 |  | 6.11 | 0.377 | 4 | 0.5 | 20.5 | 10.2 | 0.40066 | 6.04 | 0.417 | 4 | 0.52 | 20.9 | 10.3 | 0.38704 | [13 empty] | 7.29 | 0.068 | 1 | 4.3 | 19.8 |  |  |  | 7.22 | 0.069 | 1 | 4 | 19.2 |  |  |  | 4 | 3.5 | 1.6 | [18 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 360 | 360 | 330 | 540 | 560 | 460 | 440 | 430 | 430 | 740 |  | 1300 | 1300 | 1320 | 94 | 113 | 13 | 1440 | 285 | 365 | 48 | 58 | 7 | 820 | 150 | 343 |  | 1:00 | 0.58 | 10.2 | 24.9412 | 14.4659 | 6.1 | 20.1 | 7 | 2.0666 | 20 | 6.5 | 0.28066 | 1:00 | 0.5 | 10.2 | 24.9412 | 12.4706 | 6.11 | 20.5 | 7 | 1.7815 | 20 | 6.5 | 0.28066 | 1:00 | 0.52 | 10.3 | 26.2136 | 13.6311 | 6.04 | 20.9 | 7 | 1.9473 | 20 | 6.5 | 0.26704
2:00 | [72 empty] | 43568.3701 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 10.283 | 1,3 | 18.72 | 29.003 | 0 | 43568.3701 | 65.4626 | 5534 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5897 | 1.6352 | 1.5287 | 0.19939 | 0.21046 | 0.16911 | 0.15877 | 0.1609 | 0.1609 | 1.4077 | 0 | 0.069985 | 0.069985 | 0.069278 | 1.1025 | 0.49941 | 0.1032 | 3.816 | 0.72383 | 5.4039 | 1.0914 | 0.49874 | 0.10216 | 4.0093 | 0.75568 | 10.1092 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.55 | 19 | 18 | 3.71 | 89 | 115 | 20.4 | 0.38 |  | 6.01 | 10 | 0.06 | 6.06 | 10 |  | 6 | 10 | [8 empty] | 0.055 | [14 empty] | 0.044 | 1 | 0.25 |  | 0.054 | 0.039 | 1 | 0.26 |  | 0.042 | 1 | 0.3 | [38 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 350 | 360 | 340 | 540 | 570 | 458 | 430 | 440 | 440 | 740 |  | 1300 | 1300 | 1300 | 94 | 113 | 14 | 1530 | 311 | 363 | 47 | 57 | 7 | 805 | 164 | 343 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43568.6988 | 2,3,5 | 80 | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 | 1,3,1,3 | 10.283 | 1,3 | 18.72 | 29.003 | 0 | 43568.6988 | 65.4626 | 5534 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5897 | 1.6352 | 1.5287 | 0.19939 | 0.21046 | 0.16911 | 0.15877 | 0.1609 | 0.1609 | 1.4077 | 3 | 0.069985 | 0.069985 | 0.069278 | 1.1 | 0.49941 | 0.1032 | 3.816 | 0.72383 | 5.4039 | 1.0914 | 0.49874 | 0.10216 | 4.0093 | 0.75568 | 10.1092 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.25 | 0.065 | 1 | 4.4 | 19.6 |  |  |  | 7.31 | 0.067 | 1 | 4 | 19.1 |  |  |  | 3.9 | 3.5 | 3.9 | [18 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 350 | 360 | 340 | 540 | 570 | 458 | 430 | 440 | 440 | 740 |  | 1300 | 1300 | 1300 | 94 | 113 | 14 | 1530 | 311 | 363 | 47 | 57 | 7 | 805 | 164 | 343 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43568.7935 | 2,3,5 | 80 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 11.052 | 1,3 | 15.9192 | 26.9712 | 1.6301 | 43568.7935 | 64.867 | 5902.79 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6752 | 1.6752 | 1.6752 | 0.2018 | 0.2018 | 0.16687 | 0.16687 | 0.15911 | 0.15911 | 1.4077 | 5 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8026 | 0.71124 | 5.4121 | 1.1371 | 0.50297 | 0.093217 | 3.9879 | 0.7652 | 10.1967 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.53 | 18 | 18 | 4.45 | 97 | 122 | 20.3 | 0.407 |  | 6.06 | 10 | 0.068 | 6.07 | 10 |  | 6 | 10 | [8 empty] | 0.053 | [14 empty] | 0.043 | 1 | 0.27 |  | 0.053 | 0.04 | 1 | 0.29 |  | 0.046 | 1 | 0.3 | [38 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 350 | 350 | 350 | 520 | 520 | 430 | 430 | 410 | 410 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1420 | 290 | 345 | 46 | 54 | 6 | 760 | 156 | 325 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.025 | [9 empty] | 6.05 | 0.317 | 4 | 0.48 | 20.5 | 10.3 | 0.40341 |  | 6.11 | 0.293 | 4 | 0.51 | 21 | 10.3 | 0.40341 | 6.08 | 0.363 | 4 | 0.54 | 21 | 10.4 | 0.38963 |  |  |  | 0.008 | [9 empty] | 7.46 | 0.071 | 1 | 4.2 | 19.6 | 20 | 36 | 0.018 | 7.36 | 0.08 | 1 | 3.8 | 19 | 20 | 38 | 0.016 | 4 | 3.1 | 3.8 | [55 empty] | 9:00 | 0.48 | 10.3 | 24.699 | 11.8555 | 6.05 | 20.5 | 7 | 1.6936 | 20 | 6.5 | 0.28341 | 9:00 | 0.51 | 10.3 | 24.699 | 12.5965 | 6.11 | 21 | 7 | 1.7995 | 20 | 6.5 | 0.28341 | 9:00 | 0.54 | 10.4 | 25.9615 | 14.0192 | 6.08 | 21 | 7 | 2.0027 | 20 | 6.5 | 0.26963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 18 | 18 | 4.61 | 97 | 121 | 20.5 | 0.4 |  | 6.02 | 10 | 0.059 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.042 | [14 empty] | 0.042 | 1 | 0.26 |  | 0.043 | 0.039 | 1 | 0.28 |  | 0.042 | 1 | 0.32 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.09 | 0.332 | 4 | 0.43 | 20.6 | 10.3 | 0.40341 |  | 6.13 | 0.316 | 4 | 0.49 | 21.2 | 10.3 | 0.40341 | 6.1 | 0.339 | 4 | 0.49 | 21.2 | 10.4 | 0.38963 | [13 empty] | 7.23 | 0.069 | 1 | 4.4 | 19.8 |  |  |  | 7.24 | 0.073 | 1 | 3.7 | 19.9 |  |  |  | 3.9 | 3.5 | 3.5 | [55 empty] | 13:00 | 0.43 | 10.3 | 24.699 | 10.6206 | 6.09 | 20.6 | 7 | 1.5172 | 20 | 6.5 | 0.28341 | 13:00 | 0.49 | 10.3 | 24.699 | 12.1025 | 6.13 | 21.2 | 7 | 1.7289 | 20 | 6.5 | 0.28341 | 13:00 | 0.49 | 10.4 | 25.9615 | 12.7212 | 6.1 | 21.2 | 7 | 1.8173 | 20 | 6.5 | 0.26963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.49 | 19 | 18 | 4.56 | 97 | 121 | 20.3 | 0.412 |  | 6.1 | 10 | 0.074 | 6.18 | 10 |  | 6 | 10 | [8 empty] | 0.053 | [14 empty] | 0.048 | 1 | 0.18 |  | 0.052 | 0.05 | 1 | 0.46 |  | 0.052 | 1 | 0.26 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.47 | 0.071 | 1 | 4.4 | 20 |  |  |  | 7.52 | 0.075 | 1 | 4 | 19.7 |  |  |  | 4 | 3.4 | 3.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.46 | 19 | 18 | 4.4 | 93 | 118 | 20.8 | 0.39 |  | 6.06 | 10 | 0.07 | 6.12 | 10 |  | 6.04 | 10 | [8 empty] | 0.048 | [14 empty] | 0.04 | 1 | 0.21 |  | 0.058 | 0.043 | 1 | 0.44 |  | 0.066 | 1 | 0.37 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.026 | [9 empty] | 6.13 | 0.481 | 5 | 0.38 | 20.7 | 9.8 | 0.38965 |  | 6.11 | 0.414 | 5 | 0.42 | 20.9 | 9.8 | 0.38965 | 6.09 | 0.473 | 5 | 0.32 | 21.1 | 9.8 | 0.37407 |  |  |  | 0.008 |  |  |  |  | 0.02 |  |  |  | 0.015 | 7.28 | 0.073 | 1 | 4.3 | 20 | 21 | 35 | 0.02 | 7.26 | 0.08 | 1 | 3.9 | 19.6 | 20 | 36 | 0.017 | 4 | 3.4 | 3.3 | [55 empty] | 21:00 | 0.38 | 9.8 | 25.9592 | 9.8645 | 6.13 | 20.7 | 7 | 1.4092 | 20 | 6.5 | 0.26965 | 21:00 | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.11 | 20.9 | 7 | 1.5576 | 20 | 6.5 | 0.26965 | 21:00 | 0.32 | 9.8 | 27.551 | 8.8163 | 6.09 | 21.1 | 7 | 1.2595 | 20 | 6.5 | 0.25407
22:00 | [72 empty] | DOSE |  | TOTAL | 40.7 | 40.7 | 41 | 122.4 | 38.7 | 38.7 | 39 | 116.4 | 0 | 44.0482 | 0 | 69.8227 | 113.8709 | 3.369 | TOTAL | 261.2548 | 22504.6556 | 0 | 2093.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4898 | 6.5807 | 6.2164 | 0.79996 | 0.8295 | 0.67494 | 0.64688 | 0.63816 | 0.63816 | 5.6306 | 11 | 0.2803 | 0.2803 | 0.27924 | 4.4174 | 2.0012 | 0.40323 | 15.031 | 2.8222 | 21.6536 | 4.4344 | 2.0079 | 0.3997 | 15.9949 | 2.9677 | 40.5243 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.48 | 19 | 18 | 4.68 | 97 | 125 | 20.8 | 0.4 |  | 6 | 10 | 0.066 | 6.16 | 10 |  | 6.1 | 10 | [8 empty] | 0.054 | [14 empty] | 0.059 | 1 | 0.12 |  | 0.055 | 0.049 | 1 | 0.17 |  | 0.065 | 1 | 0.12 | [22 empty] | AVERAGE | 10.175 | 10.175 | 10.25 | 30.6 | 9.675 | 9.675 | 9.75 | 29.1 |  | 11.012 |  | 17.4557 | 28.4677 | 0.84226 | AVERAGE | 65.3137 | 5626.1639 |  | 523.348 | 0 | 0 | 0 |  |  |  | 1.6225 | 1.6452 | 1.5541 | 0.19999 | 0.20737 | 0.16873 | 0.16172 | 0.15954 | 0.15954 | 1.4077 | 2.75 | 0.070075 | 0.070075 | 0.069811 | 1.1043 | 0.5003 | 0.10081 | 3.7578 | 0.70555 | 5.4134 | 1.1086 | 0.50198 | 0.099926 | 3.9987 | 0.74193 | 10.1311 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.01 | 112 | 108 | 26.41 | 570 | 722 | 123.1 | 2.389 | 0.051 | 36.25 | 60 | 0.397 | 36.64 | 60 | 0 | 36.14 | 60 | 0 | 24.37 | 1.445 | 17 | 1.87 | 81.9 | 40.6 | 1.5971 | 0.305 | 24.46 | 1.4 | 17 | 1.92 | 83.6 | 40.6 | 1.5971 | 24.31 | 1.592 | 17 | 1.87 | 84.2 | 40.9 | 1.5404 | 0 | 6 | 1.29 | 0.016 | 0.315 | 0.26 | 6 | 1.9 | 0.02 | 0.313 | 6 | 1.67 | 0.015 | 43.98 | 0.417 | 6 | 26 | 118.8 | 41 | 71 | 0.038 | 43.91 | 0.444 | 6 | 23.4 | 116.5 | 40 | 74 | 0.033 | 23.8 | 20.4 | 19.8 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 10.283 |  | 15.9192 | 26.9712 | 0 | MINIMUM | 64.867 | 5533.8656 |  | 523.348 | [6 empty] | 1.5897 | 1.6352 | 1.4838 | 0.19939 | 0.2018 | 0.16687 | 0.15877 | 0.15724 | 0.15724 | 1.4077 | 0 | 0.069985 | 0.069985 | 0.069278 | 1.1 | 0.49941 | 0.095833 | 3.5965 | 0.66331 | 5.4039 | 1.0914 | 0.49874 | 0.093217 | 3.9879 | 0.69117 | 10.1092 |  | MIN | 0.38 | 9.8 | 25.9592 | 9.8645 | 6.13 | 20.7 | 7 | 1.4092 |  |  |  | MIN | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.11 | 20.9 | 7 | 1.5576 |  |  |  | MIN | 0.32 | 9.8 | 27.551 | 8.8163 | 6.09 | 21.1 | 7 | 1.2595 |  |  |  | 1.2595
AVERAGE | 6.5017 | 18.6667 | 18 | 4.4017 | 95 | 120.3333 | 20.5167 | 0.39817 | 0.0255 | 6.0417 | 10 | 0.066167 | 6.1067 | 10 |  | 6.0233 | 10 |  | 6.0925 | 0.36125 | 4.25 | 0.4675 | 20.475 | 10.15 | 0.39928 | 0.050833 | 6.115 | 0.35 | 4.25 | 0.48 | 20.9 | 10.15 | 0.39928 | 6.0775 | 0.398 | 4.25 | 0.4675 | 21.05 | 10.225 | 0.38509 |  | 1 | 0.215 | 0.008 | 0.0525 | 0.043333 | 1 | 0.31667 | 0.02 | 0.052167 | 1 | 0.27833 | 0.015 | 7.33 | 0.0695 | 1 | 4.3333 | 19.8 | 20.5 | 35.5 | 0.019 | 7.3183 | 0.074 | 1 | 3.9 | 19.4167 | 20 | 37 | 0.0165 | 3.9667 | 3.4 | 3.3 |  |  | MAXIMUM | 10.3 | 10.3 | 10.4 | 31 | 9.8 | 9.8 | 9.9 | 29.5 |  | 12.4301 |  | 18.72 | 29.003 | 1.7389 | MAXIMUM | 65.4626 | 5902.79 |  | 523.348 | [6 empty] | 1.6752 | 1.6752 | 1.6752 | 0.2018 | 0.21046 | 0.16985 | 0.16687 | 0.1609 | 0.1609 | 1.4077 | 5 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.1032 | 3.816 | 0.72383 | 5.4337 | 1.1371 | 0.50749 | 0.10216 | 4.0093 | 0.7652 | 10.1967
MINIMUM | 6.46 | 18 | 18 | 3.71 | 89 | 115 | 20.3 | 0.38 | 0.025 | 6 | 10 | 0.059 | 6.05 | 10 |  | 6 | 10 |  | 6.05 | 0.315 | 4 | 0.38 | 20.1 | 9.8 | 0.38965 | 0.042 | 6.11 | 0.293 | 4 | 0.42 | 20.5 | 9.8 | 0.38965 | 6.04 | 0.339 | 4 | 0.32 | 20.9 | 9.8 | 0.37407 |  | 1 | 0.12 | 0.008 | 0.043 | 0.039 | 1 | 0.17 | 0.02 | 0.042 | 1 | 0.12 | 0.015 | 7.23 | 0.065 | 1 | 4.2 | 19.6 | 20 | 35 | 0.018 | 7.22 | 0.067 | 1 | 3.7 | 19 | 20 | 36 | 0.016 | 3.9 | 3.1 | 1.6 | [15 empty] | MIL/MIN |  | TOTAL | 32700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1410 | 1430 | 1360 | 2140 | 2220 | 1806 | 1730 | 1720 | 1720 | 2960 | 0 | 5140 | 5140 | 5160 | 372 | 447 | 54 | 5920 | 1197 | 1436 | 188 | 226 | 27 | 3190 | 634 | 1354
MAXIMUM | 6.55 | 19 | 18 | 4.68 | 97 | 125 | 20.8 | 0.412 | 0.026 | 6.1 | 10 | 0.074 | 6.18 | 10 |  | 6.1 | 10 |  | 6.13 | 0.481 | 5 | 0.58 | 20.7 | 10.3 | 0.40341 | 0.055 | 6.13 | 0.414 | 5 | 0.51 | 21.2 | 10.3 | 0.40341 | 6.1 | 0.473 | 5 | 0.54 | 21.2 | 10.4 | 0.38963 |  | 1 | 0.27 | 0.008 | 0.058 | 0.05 | 1 | 0.46 | 0.02 | 0.066 | 1 | 0.37 | 0.015 | 7.47 | 0.073 | 1 | 4.4 | 20 | 21 | 36 | 0.02 | 7.52 | 0.08 | 1 | 4 | 19.9 | 20 | 38 | 0.017 | 4 | 3.5 | 3.9 | [17 empty] | AVERAGE | 8175 | [9 empty] | 352.5 | 357.5 | 340 | 535 | 555 | 451.5 | 432.5 | 430 | 430 | 740 |  | 1285 | 1285 | 1290 | 93 | 111.75 | 13.5 | 1480 | 299.25 | 359 | 47 | 56.5 | 6.75 | 797.5 | 158.5 | 338.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0572 |  | TOTAL AVG COAG ALK: |  |  |  | 10 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.481 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.32 | [5 empty] | 6.095 |  |  |  |  | 0.066 |  |  |  |  | 0.32 | [23 empty] | Pump Station MIN |  | 1.6 | [17 empty] | MINIMUM | 7800 | [9 empty] | 350 | 350 | 330 | 520 | 520 | 430 | 430 | 410 | 410 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1420 | 285 | 345 | 46 | 54 | 6 | 760 | 150 | 325
[90 empty] | MAXIMUM | 8300 | [9 empty] | 360 | 360 | 350 | 540 | 570 | 460 | 440 | 440 | 440 | 740 |  | 1300 | 1300 | 1320 | 94 | 113 | 14 | 1530 | 311 | 365 | 48 | 58 | 7 | 820 | 164 | 343
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.721 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827691 |  | END: | 23827691 |  |  | Alum | 4853 | 7392 | 7932 | 8895 | 8895 | 0 | [44 empty] | 0.32 | 9.8 | 27.551 | 8.8163 | 6.09 | 21.1 | 7 | 1.2595
[73 empty] | FINISHED 2 | 14.7 |  | TOTAL MGD: |  | 12.721 |  |  | FINISHED SOUTH 2 |  | START: | 44971929 |  | END: | 44984650 |  |  | Caustic | 5567 | 7658 | 7658
[73 empty] | TOTAL RAW | 29.827 |  | TOTAL MGD: |  | 4.123 |  |  | FINISHED CONWAY |  | START: | 10694107 |  | END: | 10698230 |  |  | Hypochlorite | 19 |  | 40
[76 empty] | TOTAL MGD: |  | 10.577 |  |  | FINISHED PERRY |  | START: | 34812208 |  | END: | 34822785 |  |  | Phosphate | 3978
[76 empty] | TOTAL MGD: |  | 9.837 |  |  | RAW PLANT 1 |  | START: | 31898633 |  | END: | 31908470 |  |  | Fluoride | 2100 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.953 |  |  | RAW PLANT 2 |  | START: | 31861797 |  | END: | 31871750 |  |  | Cal~Flo | 8.8 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.037 |  |  | RAW PLANT 3 |  | START: | 8495448 |  | END: | 8505485 |  |  | Zinc | 2458
[76 empty] | TOTAL MGD: |  | 0.741 |  |  | DECANT |  | START: | 1945970 |  | END: | 1946711 |  |  | Polymer | 23
[76 empty] | TOTAL MGD: |  | 0.85084 |  |  | BLOW DOWN |  | START: | 9249.9917 |  | END: | 9250.8425 |  |  | NH3 | 8.65 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 520
23827691
44984650
10698230
34822785
31908470
31871750
8505485
1946711
9250.8425
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 14
DATE: | 2019-04-14 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-14 | [23 empty] | DATE: | 2019-04-14
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-14 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43569.0024 | 2,3,5 | 80 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 11.052 | 1,3 | 15.9192 | 26.9712 | 1.1246 | 43569.0024 | 64.867 | 5902.79 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7949 | 1.7949 | 1.7949 | 0.2018 | 0.2018 | 0.16687 | 0.16687 | 0.15911 | 0.15911 | 1.4077 | 5 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10099 | 3.8026 | 0.71124 | 5.4121 | 1.1371 | 0.50297 | 0.093217 | 3.9879 | 0.7652 | 10.1967 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.516 | 5 | 0.46 | 19.8 | 9.8 | 0.50522 |  | 6.16 | 0.52 | 5 | 0.47 | 20.7 | 9.8 | 0.38965 | 6.17 | 0.588 | 5 | 0.37 | 21.1 | 9.8 | 0.37407 | [13 empty] | 7.57 | 0.077 | 1 | 4.5 | 20.2 |  |  |  | 7.61 | 0.081 | 1 | 4 | 19.3 |  |  |  | 3.4 | 3.4 | 1.6 | [18 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 375 | 375 | 375 | 520 | 520 | 430 | 430 | 410 | 410 | 740 |  | 1240 | 1240 | 1240 | 90 | 108 | 13 | 1420 | 290 | 345 | 46 | 54 | 6 | 760 | 156 | 325 |  | 1:00 | 0.46 | 9.8 | 25.9592 | 11.9412 | 6.14 | 19.8 | 10 | 1.1941 | 15 | 6.5 | 0.38522 | 1:00 | 0.47 | 9.8 | 25.9592 | 12.2008 | 6.16 | 20.7 | 7 | 1.743 | 20 | 6.5 | 0.26965 | 1:00 | 0.37 | 9.8 | 27.551 | 10.1939 | 6.17 | 21.1 | 7 | 1.4563 | 20 | 6.5 | 0.25407
2:00 | [72 empty] | 43569.3737 | 1,2,3 | 52 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 12.4862 | 1,3 | 16.9085 | 29.3947 | 1.0987 | 43569.3737 | 71.5201 | 5902.79 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8188 | 1.8188 | 1.8188 | 0.2018 | 0.20568 | 0.16687 | 0.15911 | 0.15911 | 0.15911 | 1.5218 | 6 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.49366 | 0.10099 | 3.7676 | 0.73576 | 5.4121 | 1.1123 | 0.50297 | 0.093217 | 4.056 | 0.78482 | 10.1967 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.45 | 18 | 18 | 4.75 | 99 | 127 | 20.8 | 0.409 |  | 6.06 | 10 | 0.06 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.058 | [14 empty] | 0.049 | 1 | 0.2 |  | 0.065 | 0.067 | 1 | 0.37 |  | 0.065 | 1 | 0.23 | [38 empty] | 8600 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 380 | 520 | 530 | 430 | 410 | 410 | 410 | 800 |  | 1240 | 1240 | 1240 | 90 | 106 | 13 | 1420 | 300 | 345 | 45 | 54 | 6 | 780 | 160 | 325 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43569.6345 | 1,2,3 | 52 | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 | 1,3,1,3 | 12.4862 | 1,3 | 16.9085 | 29.3947 | 1.0987 | 43569.6345 | 71.5201 | 5902.79 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8188 | 1.8188 | 1.8188 | 0.2018 | 0.20568 | 0.16687 | 0.15911 | 0.15911 | 0.15911 | 1.5218 | 6 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.49366 | 0.10099 | 3.7676 | 0.73576 | 5.4121 | 1.1123 | 0.50297 | 0.093217 | 4.056 | 0.78482 | 10.1967 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.16 | 0.067 | 1 | 4.3 | 20 |  |  |  | 7.15 | 0.072 | 1 | 4.1 | 19.3 |  |  |  | 3.2 | 3.2 | 2.6 | [18 empty] | 8600 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 380 | 520 | 530 | 430 | 410 | 410 | 410 | 800 |  | 1240 | 1240 | 1240 | 90 | 106 | 13 | 1420 | 300 | 345 | 45 | 54 | 6 | 780 | 160 | 325 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43569.7772 | 1,2,3 | 65 | 10.5 | 10.5 | 10.5 | 31.5 | 10 | 10 | 10 | 30 | 1,3,1,3 | 9.2794 | 1,3 | 14.8032 | 24.0826 | 1.2442 | 43569.7772 | 66.752 | 6394.6892 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.7805 | 0.18835 | 0.18835 | 0.15575 | 0.15212 | 0.1485 | 0.1485 | 1.5218 | 8 | 0.070168 | 0.070168 | 0.070168 | 1.1034 | 0.49375 | 0.10114 | 3.7975 | 0.72075 | 5.398 | 1.1034 | 0.50241 | 0.11559 | 4.0162 | 0.7755 | 10.2124 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.44 | 18 | 18 | 4.8 | 94 | 125 | 20.6 | 0.431 |  | 6.04 | 10 | 0.07 | 6.12 | 10 |  | 6 | 9 | [8 empty] | 0.06 | [14 empty] | 0.039 | 1 | 0.19 |  | 0.066 | 0.062 | 1 | 0.34 |  | 0.062 | 1 | 0.24 | [38 empty] | 8600 | [6 empty] | 0 | 0 | 0 | 400 | 400 | 400 | 520 | 520 | 430 | 420 | 410 | 410 | 800 |  | 1330 | 1330 | 1330 | 96 | 114 | 14 | 1540 | 316 | 370 | 48 | 58 | 8 | 830 | 170 | 350 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.025 | [9 empty] | 6.13 | 0.396 | 4 | 0.44 | 19.8 | 9.8 | 0.50522 |  | 6.14 | 0.391 | 4 | 0.38 | 20 | 9.8 | 0.38965 | 6.11 | 0.541 | 5 | 0.41 | 21.2 | 9.8 | 0.37407 |  |  |  | 0.005 | [9 empty] | 7.5 | 0.071 | 1 | 4.5 | 20.1 | 20 | 36 | 0.012 | 7.41 | 0.08 | 1 | 3.9 | 19.2 | 20 | 38 | 0.006 | 3.5 | 3.3 | 3.4 | [55 empty] | 9:00 | 0.44 | 9.8 | 25.9592 | 11.422 | 6.13 | 19.8 | 10 | 1.1422 | 15 | 6.5 | 0.38522 | 9:00 | 0.38 | 9.8 | 25.9592 | 9.8645 | 6.14 | 20 | 7 | 1.4092 | 20 | 6.5 | 0.26965 | 9:00 | 0.41 | 9.8 | 27.551 | 11.2959 | 6.11 | 21.2 | 7 | 1.6137 | 20 | 6.5 | 0.25407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 18 | 18 | 4.64 | 103 | 124 | 20.7 | 0.431 |  | 6.05 | 10 | 0.069 | 6.1 | 10 |  | 5.99 | 10 | [8 empty] | 0.056 | [14 empty] | 0.038 | 1 | 0.2 |  | 0.07 | 0.056 | 1 | 0.27 |  | 0.055 | 1 | 0.23 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.249 | 4 | 0.44 | 20.1 | 9.8 | 0.38965 |  | 6.09 | 0.322 | 4 | 0.49 | 21.4 | 9.8 | 0.38965 | 6.1 | 0.535 | 4 | 0.38 | 21.5 | 9.8 | 0.37407 | [13 empty] | 7.58 | 0.068 | 1 | 4.3 | 20.2 |  |  |  | 7.2 | 0.071 | 1 | 3.6 | 19.4 |  |  |  | 3.7 | 3.2 | 3.8 | [55 empty] | 13:00 | 0.44 | 9.8 | 25.9592 | 11.422 | 6.12 | 20.1 | 7 | 1.6317 | 20 | 6.5 | 0.26965 | 13:00 | 0.49 | 9.8 | 25.9592 | 12.72 | 6.09 | 21.4 | 7 | 1.8171 | 20 | 6.5 | 0.26965 | 13:00 | 0.38 | 9.8 | 27.551 | 10.4694 | 6.1 | 21.5 | 7 | 1.4956 | 20 | 6.5 | 0.25407
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.45 | 18 | 18 | 4.58 | 103 | 126 | 20.9 | 0.425 |  | 6.1 | 11 | 0.067 | 6.16 | 11 |  | 6.03 | 11 | [8 empty] | 0.054 | [14 empty] | 0.036 | 1 | 0.2 |  | 0.053 | 0.053 | 1 | 0.23 |  | 0.053 | 1 | 0.23 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.62 | 0.064 | 1 | 4.5 | 20.1 |  |  |  | 7.4 | 0.07 | 1 | 3.8 | 19.8 |  |  |  | 3.4 | 2.8 | 3.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.54 | 19 | 18 | 4.75 | 100 | 128 | 22 | 0.378 |  | 6.04 | 12 | 0.044 | 6.06 | 12 |  | 6 | 12 | [8 empty] | 0.026 | [14 empty] | 0.035 | 1 | 0.22 |  | 0.029 | 0.051 | 1 | 0.26 |  | 0.062 | 1 | 0.25 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.021 | [9 empty] | 6.07 | 0.435 | 5 | 0.33 | 21.3 | 10.5 | 0.40892 |  | 6.17 | 0.585 | 5 | 0.36 | 21.2 | 10.5 | 0.40892 | 6.214 | 0.576 | 5 | 0.31 | 21.5 | 10.5 | 0.39222 |  |  |  | 0.007 | [9 empty] | 7.36 | 0.073 | 1 | 4.2 | 20.4 | 20 | 34 | 0.013 | 7.5 | 0.076 | 1 | 3.8 | 19.9 | 21 | 36 | 0.009 | 3.9 | 3.3 | 3.4 | [55 empty] | 21:00 | 0.33 | 10.5 | 24.2286 | 7.9954 | 6.07 | 21.3 | 7 | 1.1422 | 20 | 6.5 | 0.28892 | 21:00 | 0.36 | 10.5 | 24.2286 | 8.7223 | 6.17 | 21.2 | 7 | 1.246 | 20 | 6.5 | 0.28892 | 21:00 | 0.31 | 10.5 | 25.7143 | 7.9714 | 6.214 | 21.5 | 7 | 1.1388 | 20 | 6.5 | 0.27222
22:00 | [72 empty] | DOSE |  | TOTAL | 39.9 | 39.9 | 39.9 | 119.7 | 37.9 | 37.9 | 37.9 | 113.7 | 0 | 45.3038 | 0 | 64.5394 | 109.8432 | 4.5662 | TOTAL | 274.6592 | 24103.0592 | 0 | 2093.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2129 | 7.2129 | 7.2129 | 0.79374 | 0.8015 | 0.65636 | 0.63722 | 0.62583 | 0.62583 | 5.9731 | 25 | 0.2812 | 0.2812 | 0.2812 | 4.4405 | 1.984 | 0.4041 | 15.1354 | 2.9035 | 21.6342 | 4.4652 | 2.0113 | 0.39524 | 16.1161 | 3.1103 | 40.8024 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.45 | 18 | 18 | 4.66 | 101 | 130 | 21.1 | 0.417 |  | 6 | 10 | 0.051 | 6 | 10 |  | 6.02 | 10 | [8 empty] | 0.032 | [14 empty] | 0.051 | 1 | 0.1 |  | 0.03 | 0.034 | 1 | 0.15 |  | 0.08 | 1 | 0.02 | [22 empty] | AVERAGE | 9.975 | 9.975 | 9.975 | 29.925 | 9.475 | 9.475 | 9.475 | 28.425 |  | 11.326 |  | 16.1348 | 27.4608 | 1.1416 | AVERAGE | 68.6648 | 6025.7648 |  | 523.348 | 0 | 0 | 0 |  |  |  | 1.8032 | 1.8032 | 1.8032 | 0.19844 | 0.20038 | 0.16409 | 0.1593 | 0.15646 | 0.15646 | 1.4933 | 6.25 | 0.0703 | 0.0703 | 0.0703 | 1.1101 | 0.49601 | 0.10102 | 3.7838 | 0.72588 | 5.4086 | 1.1163 | 0.50283 | 0.09881 | 4.029 | 0.77758 | 10.2006 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.83 | 109 | 108 | 28.18 | 600 | 760 | 126.1 | 2.491 | 0.046 | 36.29 | 63 | 0.361 | 36.49 | 63 | 0 | 36.04 | 62 | 0 | 24.46 | 1.596 | 18 | 1.67 | 81 | 39.9 | 1.809 | 0.286 | 24.56 | 1.818 | 18 | 1.7 | 83.3 | 39.9 | 1.5779 | 24.594 | 2.24 | 19 | 1.47 | 85.3 | 39.9 | 1.5144 | 0.248 | 6 | 1.11 | 0.012 | 0.313 | 0.323 | 6 | 1.62 | 0 | 0.377 | 6 | 1.2 | 0 | 44.79 | 0.42 | 6 | 26.3 | 121 | 40 | 70 | 0.025 | 44.27 | 0.45 | 6 | 23.2 | 116.9 | 41 | 74 | 0.015 | 21.1 | 19.2 | 18.4 |  |  | MINIMUM | 9.8 | 9.8 | 9.8 | 29.4 | 9.3 | 9.3 | 9.3 | 27.9 |  | 9.2794 |  | 14.8032 | 24.0826 | 1.0987 | MINIMUM | 64.867 | 5902.79 |  | 523.348 | [6 empty] | 1.7805 | 1.7805 | 1.7805 | 0.18835 | 0.18835 | 0.15575 | 0.15212 | 0.1485 | 0.1485 | 1.4077 | 5 | 0.070168 | 0.070168 | 0.070168 | 1.1034 | 0.49366 | 0.10099 | 3.7676 | 0.71124 | 5.398 | 1.1034 | 0.50241 | 0.093217 | 3.9879 | 0.7652 | 10.1967 |  | MIN | 0.44 | 9.8 | 25.9592 | 11.422 | 6.13 | 19.8 | 10 | 1.1422 |  |  |  | MIN | 0.36 | 10.5 | 24.2286 | 8.7223 | 6.17 | 21.2 | 7 | 1.246 |  |  |  | MIN | 0.31 | 10.5 | 25.7143 | 7.9714 | 6.214 | 21.5 | 7 | 1.1388 |  |  |  | 1.1388
AVERAGE | 6.4717 | 18.1667 | 18 | 4.6967 | 100 | 126.6667 | 21.0167 | 0.41517 | 0.023 | 6.0483 | 10.5 | 0.060167 | 6.0817 | 10.5 |  | 6.0067 | 10.3333 |  | 6.115 | 0.399 | 4.5 | 0.4175 | 20.25 | 9.975 | 0.45225 | 0.047667 | 6.14 | 0.4545 | 4.5 | 0.425 | 20.825 | 9.975 | 0.39447 | 6.1485 | 0.56 | 4.75 | 0.3675 | 21.325 | 9.975 | 0.37861 | 0.041333 | 1 | 0.185 | 0.006 | 0.052167 | 0.053833 | 1 | 0.27 |  | 0.062833 | 1 | 0.2 |  | 7.465 | 0.07 | 1 | 4.3833 | 20.1667 | 20 | 35 | 0.0125 | 7.3783 | 0.075 | 1 | 3.8667 | 19.4833 | 20.5 | 37 | 0.0075 | 3.5167 | 3.2 | 3.0667 |  |  | MAXIMUM | 10.5 | 10.5 | 10.5 | 31.5 | 10 | 10 | 10 | 30 |  | 12.4862 |  | 16.9085 | 29.3947 | 1.2442 | MAXIMUM | 71.5201 | 6394.6892 |  | 523.348 | [6 empty] | 1.8188 | 1.8188 | 1.8188 | 0.2018 | 0.20568 | 0.16687 | 0.16687 | 0.15911 | 0.15911 | 1.5218 | 8 | 0.070344 | 0.070344 | 0.070344 | 1.1123 | 0.50297 | 0.10114 | 3.8026 | 0.73576 | 5.4121 | 1.1371 | 0.50297 | 0.11559 | 4.056 | 0.78482 | 10.2124
MINIMUM | 6.44 | 18 | 18 | 4.58 | 94 | 124 | 20.6 | 0.378 | 0.021 | 6 | 10 | 0.044 | 6 | 10 |  | 5.99 | 9 |  | 6.07 | 0.249 | 4 | 0.33 | 19.8 | 9.8 | 0.38965 | 0.026 | 6.09 | 0.322 | 4 | 0.36 | 20 | 9.8 | 0.38965 | 6.1 | 0.535 | 4 | 0.31 | 21.1 | 9.8 | 0.37407 | 0.035 | 1 | 0.1 | 0.005 | 0.029 | 0.034 | 1 | 0.15 |  | 0.053 | 1 | 0.02 |  | 7.16 | 0.064 | 1 | 4.2 | 20 | 20 | 34 | 0.012 | 7.15 | 0.07 | 1 | 3.6 | 19.2 | 20 | 36 | 0.006 | 3.2 | 2.8 | 1.6 | [15 empty] | MIL/MIN |  | TOTAL | 33600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1535 | 1535 | 1535 | 2080 | 2100 | 1720 | 1670 | 1640 | 1640 | 3140 | 0 | 5050 | 5050 | 5050 | 366 | 434 | 53 | 5800 | 1206 | 1405 | 184 | 220 | 26 | 3150 | 646 | 1325
MAXIMUM | 6.54 | 19 | 18 | 4.8 | 103 | 130 | 22 | 0.431 | 0.025 | 6.1 | 12 | 0.07 | 6.16 | 12 |  | 6.03 | 12 |  | 6.14 | 0.516 | 5 | 0.46 | 21.3 | 10.5 | 0.50522 | 0.06 | 6.17 | 0.585 | 5 | 0.49 | 21.4 | 10.5 | 0.40892 | 6.214 | 0.588 | 5 | 0.41 | 21.5 | 10.5 | 0.39222 | 0.051 | 1 | 0.22 | 0.007 | 0.07 | 0.067 | 1 | 0.37 |  | 0.08 | 1 | 0.25 |  | 7.62 | 0.077 | 1 | 4.5 | 20.4 | 20 | 36 | 0.013 | 7.61 | 0.081 | 1 | 4.1 | 19.9 | 21 | 38 | 0.009 | 3.9 | 3.4 | 3.8 | [17 empty] | AVERAGE | 8400 | [9 empty] | 383.75 | 383.75 | 383.75 | 520 | 525 | 430 | 417.5 | 410 | 410 | 785 |  | 1262.5 | 1262.5 | 1262.5 | 91.5 | 108.5 | 13.25 | 1450 | 301.5 | 351.25 | 46 | 55 | 6.5 | 787.5 | 161.5 | 331.25
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0456 |  | TOTAL AVG COAG ALK: |  |  |  | 10.4444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.588 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.31 | [5 empty] | 6.1345 |  |  |  |  | 0.08 |  |  |  |  | 0.31 | [6 empty] | 0.08 | [16 empty] | Pump Station MIN |  | 1.6 | [17 empty] | MINIMUM | 7800 | [9 empty] | 375 | 375 | 375 | 520 | 520 | 430 | 410 | 410 | 410 | 740 |  | 1240 | 1240 | 1240 | 90 | 106 | 13 | 1420 | 290 | 345 | 45 | 54 | 6 | 760 | 156 | 325
[90 empty] | MAXIMUM | 8600 | [9 empty] | 400 | 400 | 400 | 520 | 530 | 430 | 430 | 410 | 410 | 800 |  | 1330 | 1330 | 1330 | 96 | 114 | 14 | 1540 | 316 | 370 | 48 | 58 | 8 | 830 | 170 | 350
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.69 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827691 |  | END: | 23827691 |  |  | Alum | 4883 | 6480 | 6480 | 7905 | 7905 | 0 | [44 empty] | 0.31 | 10.5 | 25.7143 | 7.9714 | 6.214 | 21.5 | 7 | 1.1388
[73 empty] | FINISHED 2 | 15.62 |  | TOTAL MGD: |  | 12.69 |  |  | FINISHED SOUTH 2 |  | START: | 44984650 |  | END: | 44997340 |  |  | Caustic | 5445 | 7615 | 7615
[73 empty] | TOTAL RAW | 30.345 |  | TOTAL MGD: |  | 4.865 |  |  | FINISHED CONWAY |  | START: | 10698230 |  | END: | 10703095 |  |  | Hypochlorite | 19 |  | 35
[76 empty] | TOTAL MGD: |  | 10.755 |  |  | FINISHED PERRY |  | START: | 34822785 |  | END: | 34833540 |  |  | Phosphate | 3932
[76 empty] | TOTAL MGD: |  | 10.04 |  |  | RAW PLANT 1 |  | START: | 31908470 |  | END: | 31918510 |  |  | Fluoride | 1900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.12 |  |  | RAW PLANT 2 |  | START: | 31871750 |  | END: | 31881870 |  |  | Cal~Flo | 6.3 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.185 |  |  | RAW PLANT 3 |  | START: | 8505485 |  | END: | 8515670 |  |  | Zinc | 2470
[76 empty] | TOTAL MGD: |  | 0.623 |  |  | DECANT |  | START: | 1946711 |  | END: | 1947334 |  |  | Polymer | 23
[76 empty] | TOTAL MGD: |  | 0.94004 |  |  | BLOW DOWN |  | START: | 9250.8425 |  | END: | 9251.7826 |  |  | NH3 | 8.45 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 520
23827691
44997340
10703095
34833540
31918510
31881870
8515670
1947334
9251.7826
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 15
DATE: | 2019-04-15 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [33 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-15 | [23 empty] | DATE: | 2019-04-15
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-15 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43570.0128 | 1,2,3 | 98 | 10.5 | 10.5 | 10.5 | 31.5 | 10 | 10 | 10 | 30 | 1,3,1,3 | 12.3754 | 1,3 | 16.8653 | 29.2406 | 1.7971 | 43570.0128 | 69.8568 | 6640.6388 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8918 | 1.8918 | 1.8918 | 0.18835 | 0.18835 | 0.15575 | 0.15212 | 0.1485 | 0.1485 | 1.5218 | 8 | 0.070168 | 0.070168 | 0.070168 | 1.1034 | 0.49375 | 0.10114 | 3.7975 | 0.72075 | 5.398 | 1.1034 | 0.50241 | 0.11559 | 4.0162 | 0.7755 | 10.2124 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6 | 0.424 | 5 | 0.41 | 20.8 | 10.3 | 0.36292 |  | 6.02 | 0.487 | 5 | 0.37 | 21.1 | 10.3 | 0.40341 | 6.12 | 0.536 | 5 | 0.35 | 21.5 | 10.7 | 0.39741 | [13 empty] | 7.37 | 0.074 | 1 | 4.1 | 20.5 |  |  |  | 7.45 | 0.078 | 1 | 3.8 | 19.8 |  |  |  | 3.9 | 3.3 | 2.2 | [18 empty] | 9000 | [6 empty] | 0 | 0 | 0 | 425 | 425 | 425 | 520 | 520 | 430 | 420 | 410 | 410 | 800 |  | 1330 | 1330 | 1330 | 96 | 114 | 14 | 1540 | 316 | 370 | 48 | 58 | 8 | 830 | 170 | 350 |  | 1:00 | 0.41 | 10.3 | 24.699 | 10.1266 | 6 | 20.8 | 6 | 1.6878 | 20 | 6 | 0.24292 | 1:00 | 0.37 | 10.3 | 24.699 | 9.1386 | 6.02 | 21.1 | 7 | 1.3055 | 20 | 6.5 | 0.28341 | 1:00 | 0.35 | 10.7 | 25.2336 | 8.8318 | 6.12 | 21.5 | 7 | 1.2617 | 20 | 6.5 | 0.27741
2:00 | [72 empty] | 8:00 | 1,2,3 | 98 | 10.5 | 10.5 | 10.5 | 31.5 | 10 | 10 | 10 | 30 | 1,3,1,3 | 12.8117 | 1,3 | 14.3323 | 27.144 | 0 | 8:00 | 72.9615 | 7009.5632 | 0 | 523.348 | 0 | 0 | 0 | 1.3894 | 1.3894 | 1.1115 | 1.914 | 1.914 | 1.9942 | 0.19559 | 0.19559 | 0.15937 | 0.1485 | 0.15212 | 0.15212 | 1.52 | 0 | 0.070168 | 0.070168 | 0.070168 | 1.1264 | 0.49808 | 0.10114 | 3.7981 | 0.74813 | 5.4 | 1.1034 | 0.51974 | 0.10114 | 4.0003 | 0.79374 | 10.21 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.45 | 19 | 18 | 4.77 | 104 | 131 | 21 | 0.43 |  | 6.02 | 10 | 0.047 | 6.03 | 10 |  | 5.99 | 10 | [8 empty] | 0.04 | [14 empty] | 0.035 | 1 | 0.1 |  | 0.046 | 0.077 | 1 | 0.17 |  | 0.063 | 1 | 0.03 | [38 empty] | 9400 | [6 empty] | 50 | 50 | 40 | 430 | 430 | 448 | 540 | 540 | 440 | 410 | 420 | 420 | 800 |  | 1330 | 1330 | 1330 | 98 | 115 | 14 | 1606 | 328 | 370 | 48 | 60 | 7 | 855 | 174 | 350 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43570.4723 | 1,2,3 | 98 | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 | 1,3,1,3 | 12.8117 | 1,3 | 14.3323 | 27.144 | 1.8274 | 43570.4723 | 72.6087 | 7009.5632 | 0 | 523.348 | 0 | 0 | 0 | 2.9709 | 2.9709 | 2.3873 | 1.9077 | 1.9077 | 1.9077 | 0.19016 | 0.19016 | 0.1625 | 0.1625 | 0.15558 | 0.15558 | 1.52 | 6 | 0.070344 | 0.070344 | 0.070344 | 1.0947 | 0.49499 | 0.1032 | 3.8061 | 0.74726 | 5.4049 | 1.0947 | 0.49499 | 0.096324 | 4.0101 | 0.79505 | 10.1985 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.24 | 0.078 | 1 | 4.3 | 20.3 |  |  |  | 7.52 | 0.081 | 1 | 4.2 | 19.6 |  |  |  | 3.8 | 3.3 | 3.4 | [18 empty] | 9800 | [6 empty] | 112 | 112 | 90 | 450 | 450 | 450 | 550 | 550 | 470 | 470 | 450 | 450 | 800 |  | 1400 | 1400 | 1400 | 100 | 120 | 15 | 1690 | 344 | 389 | 50 | 60 | 7 | 900 | 183 | 367 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43570.6163 | 1,2,3 | 98 | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 | 1,3,1,3 | 14.8118 | 1,3 | 16.6709 | 31.4827 | 1.8274 | 43570.6163 | 72.6087 | 6271.7144 | 0 | 523.348 | 0 | 0 | 0 | 2.9709 | 2.9709 | 2.3873 | 1.9077 | 1.9077 | 1.9077 | 0.19016 | 0.19016 | 0.1625 | 0.1625 | 0.15558 | 0.15558 | 1.46 | 6 | 0.070344 | 0.070344 | 0.070344 | 1.0947 | 0.49499 | 0.1032 | 3.8061 | 0.74726 | 5.4049 | 1.0947 | 0.49499 | 0.096324 | 4.0101 | 0.79505 | 10.1985 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.45 | 19 | 18 | 4.7 | 107 | 132 | 21 | 0.435 |  | 6.02 | 10 | 0.064 | 6.04 | 11 |  | 5.97 | 10 | [8 empty] | 0.059 | [14 empty] | 0.035 | 1 | 0.14 |  | 0.057 | 0.048 | 1 | 0.15 |  | 0.059 | 1 | 0.09 | [38 empty] | 9800 | [6 empty] | 112 | 112 | 90 | 450 | 450 | 450 | 550 | 550 | 470 | 470 | 450 | 450 | 770 |  | 1400 | 1400 | 1400 | 100 | 120 | 15 | 1690 | 344 | 389 | 50 | 60 | 7 | 900 | 183 | 367 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43570.8355 | 1,2,3 | 98 | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 | 1,3,1,3 | 14.2344 | 1,3 | 18.1008 | 32.3352 | 1.8274 | 43570.8355 | 73.4978 | 7194.0254 | 0 | 555.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.9501 | 0.19016 | 0.17978 | 0.16595 | 0.16941 | 0.15558 | 0.15558 | 1.4647 | 0 | 0.069841 | 0.070344 | 0.070344 | 1.0947 | 0.49911 | 0.096324 | 3.6341 | 0.6734 | 5.3493 | 1.1385 | 0.49499 | 0.096324 | 3.8659 | 0.69512 | 10.1985 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.027 | [9 empty] | 6.14 | 0.47 | 5 | 0.37 | 21 | 10.5 | 0.40892 |  | 6.17 | 0.521 | 5 | 0.35 | 21.1 | 10.5 | 0.40892 | 6.14 | 0.71 | 7 | 0.3 | 21.5 | 10.5 | 0.39222 |  |  |  | 0.014 | [9 empty] | 7.23 | 0.067 | 1 | 4.3 | 20.2 | 26 | 50 | 0.011 | 7.73 | 0.084 | 1 | 3.9 | 20.2 | 28 | 50 | 0.007 | 4.12 | 3.3 | 3.2 | [18 empty] | 9920 | [6 empty] | 0 | 0 | 0 | 420 | 420 | 460 | 550 | 520 | 480 | 490 | 450 | 450 | 770 |  | 1390 | 1400 | 1400 | 100 | 121 | 14 | 1620 | 310 | 385 | 52 | 60 | 7 | 830 | 160 | 367 |  | 9:00 | 0.37 | 10.5 | 24.2286 | 8.9646 | 6.14 | 21 | 7 | 1.2807 | 20 | 6.5 | 0.28892 | 9:00 | 0.35 | 10.5 | 24.2286 | 8.48 | 6.17 | 21.1 | 7 | 1.2114 | 20 | 6.5 | 0.28892 | 9:00 | 0.3 | 10.5 | 25.7143 | 7.7143 | 6.14 | 21.5 | 7 | 1.102 | 20 | 6.5 | 0.27222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.47 | 19 | 19 | 4.46 | 107 | 130 | 20.8 | 0.45 |  | 6.13 | 10 | 0.074 | 6.19 | 10 |  | 6.08 | 10 | [8 empty] | 0.057 | [14 empty] | 0.033 | 1 | 0.17 |  | 0.061 | 0.051 | 1 | 0.21 |  | 0.079 | 1 | 0.27 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.14 | 0.432 | 5 | 0.42 | 21.3 | 11 | 0.42267 |  | 6.18 | 0.396 | 5 | 0.42 | 21.1 | 11 | 0.42267 | 6.16 | 0.497 | 5 | 0.4 | 21.1 | 11 | 0.40519 | [13 empty] | 7.53 | 0.069 | 14.2 | 4.2 | 20.4 |  |  |  | 7.62 | 0.083 | 2 | 3.8 | 20.4 |  |  |  | 4.12 | 3.3 | 4.8 | [55 empty] | 13:00 | 0.42 | 11 | 23.1273 | 9.7135 | 6.14 | 21.3 | 7 | 1.3876 | 20 | 6.5 | 0.30267 | 13:00 | 0.42 | 11 | 23.1273 | 9.7135 | 6.18 | 21.1 | 7 | 1.3876 | 20 | 6.5 | 0.30267 | 13:00 | 0.4 | 11 | 24.5455 | 9.8182 | 6.16 | 21.1 | 7 | 1.4026 | 20 | 6.5 | 0.28519
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.35 | 18 | 18 | 4.47 | 111 | 138 | 20.8 | 0.446 |  | 6.02 | 9 | 0.066 | 6.12 | 10 |  | 6 | 10 | [8 empty] | 0.055 | [14 empty] | 0.032 | 1 | 0.1 |  | 0.052 | 0.045 | 1 | 0.11 |  | 0.068 | 1 | 0.17 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.64 | 0.059 | 1 | 4.4 | 20.5 |  |  |  | 7.44 | 0.073 | 1 | 4 | 20.1 |  |  |  | 3.7 | 3.4 | 3.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.45 | 19 | 18 | 4.76 | 110 | 135 | 21.1 | 0.444 |  | 6.01 | 10 | 0.067 | 6.1 | 10 |  | 5.96 | 9 | [8 empty] | 0.057 | [14 empty] | 0.032 | 1 | 0.1 |  | 0.051 | 0.055 | 1 | 0.13 |  | 0.063 | 1 | 0.26 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.031 | [9 empty] | 6.09 | 0.483 | 6 | 0.48 | 21.1 | 11 | 0.42267 |  | 6.08 | 0.583 | 6 | 0.42 | 21.3 | 11 | 0.42267 | 6.09 | 0.633 | 6 | 0.57 | 21.4 | 11 | 0.40519 |  |  |  | 0.018 |  |  |  |  | 0.029 |  |  |  | 0.014 | 7.38 | 0.063 | 1 | 4.4 | 19.9 | 21 | 41 | 0.024 | 7.42 | 0.07 | 1 | 4 | 19.9 | 21 | 43 | 0.02 | 3.9 | 3.1 | 3.6 | [55 empty] | 21:00 | 0.48 | 11 | 23.1273 | 11.1011 | 6.09 | 21.1 | 7 | 1.5859 | 20 | 6.5 | 0.30267 | 21:00 | 0.42 | 11 | 23.1273 | 9.7135 | 6.08 | 21.3 | 7 | 1.3876 | 20 | 6.5 | 0.30267 | 21:00 | 0.57 | 11 | 24.5455 | 13.9909 | 6.09 | 21.4 | 7 | 1.9987 | 20 | 6.5 | 0.28519
22:00 | [72 empty] | DOSE |  | TOTAL | 54 | 54 | 54 | 162 | 51.5 | 51.5 | 51.5 | 154.5 | 0 | 67.045 | 0 | 80.3016 | 147.3466 | 7.2792 | TOTAL | 361.5336 | 34125.505 | 0 | 2648.4581 | 0 | 0 | 0 | 7.3312 | 7.3312 | 5.8862 | 9.4017 | 9.4017 | 9.6514 | 0.9544 | 0.94403 | 0.80606 | 0.79503 | 0.76738 | 0.76738 | 7.4865 | 20 | 0.35086 | 0.35137 | 0.35137 | 5.514 | 2.4809 | 0.50502 | 18.8419 | 3.6368 | 26.9571 | 5.5348 | 2.5071 | 0.5057 | 19.9026 | 3.8545 | 51.0178 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.49 | 20 | 17 | 4.66 | 108 | 134 | 19.9 | 0.442 |  | 6.03 | 10 | 0.067 | 6.12 | 11 |  | 5.99 | 10 | [8 empty] | 0.057 | [14 empty] | 0.031 | 1 | 0.19 |  | 0.056 | 0.062 | 1 | 0.23 |  | 0.058 | 1 | 0.31 | [22 empty] | AVERAGE | 10.8 | 10.8 | 10.8 | 32.4 | 10.3 | 10.3 | 10.3 | 30.9 |  | 13.409 |  | 16.0603 | 29.4693 | 1.4558 | AVERAGE | 72.3067 | 6825.101 |  | 529.6916 | 0 | 0 | 0 | 1.4662 | 1.4662 | 1.1772 | 1.8803 | 1.8803 | 1.9303 | 0.19088 | 0.18881 | 0.16121 | 0.15901 | 0.15348 | 0.15348 | 1.4973 | 4 | 0.070173 | 0.070273 | 0.070273 | 1.1028 | 0.49618 | 0.101 | 3.7684 | 0.72736 | 5.3914 | 1.107 | 0.50142 | 0.10114 | 3.9805 | 0.77089 | 10.2036 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.66 | 114 | 108 | 27.82 | 647 | 800 | 124.6 | 2.647 | 0.058 | 36.23 | 59 | 0.385 | 36.6 | 62 | 0 | 35.99 | 59 | 0 | 24.37 | 1.809 | 21 | 1.68 | 84.2 | 42.8 | 1.6172 | 0.325 | 24.45 | 1.987 | 21 | 1.56 | 84.6 | 42.8 | 1.6577 | 24.51 | 2.376 | 23 | 1.62 | 85.5 | 43.2 | 1.6 | 0.198 | 6 | 0.8 | 0.032 | 0.323 | 0.338 | 6 | 1 | 0.029 | 0.39 | 6 | 1.13 | 0.014 | 44.39 | 0.41 | 19.2 | 25.7 | 121.8 | 47 | 91 | 0.035 | 45.18 | 0.469 | 7 | 23.7 | 120 | 49 | 93 | 0.027 | 23.54 | 19.7 | 20.7 |  |  | MINIMUM | 10.5 | 10.5 | 10.5 | 31.5 | 10 | 10 | 10 | 30 |  | 12.3754 |  | 14.3323 | 27.144 | 0 | MINIMUM | 69.8568 | 6271.7144 |  | 523.348 |  |  |  | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.8918 | 0.18835 | 0.17978 | 0.15575 | 0.1485 | 0.1485 | 0.1485 | 1.46 | 0 | 0.069841 | 0.070168 | 0.070168 | 1.0947 | 0.49375 | 0.096324 | 3.6341 | 0.6734 | 5.3493 | 1.0947 | 0.49499 | 0.096324 | 3.8659 | 0.69512 | 10.1985 |  | MIN | 0.37 | 10.5 | 24.2286 | 8.9646 | 6.14 | 21 | 7 | 1.2807 |  |  |  | MIN | 0.35 | 10.5 | 24.2286 | 8.48 | 6.17 | 21.1 | 7 | 1.2114 |  |  |  | MIN | 0.3 | 10.5 | 25.7143 | 7.7143 | 6.14 | 21.5 | 7 | 1.102 |  |  |  | 1.102
AVERAGE | 6.4433 | 19 | 18 | 4.6367 | 107.8333 | 133.3333 | 20.7667 | 0.44117 | 0.029 | 6.0383 | 9.8333 | 0.064167 | 6.1 | 10.3333 |  | 5.9983 | 9.8333 |  | 6.0925 | 0.45225 | 5.25 | 0.42 | 21.05 | 10.7 | 0.4043 | 0.054167 | 6.1125 | 0.49675 | 5.25 | 0.39 | 21.15 | 10.7 | 0.41442 | 6.1275 | 0.594 | 5.75 | 0.405 | 21.375 | 10.8 | 0.4 | 0.033 | 1 | 0.13333 | 0.016 | 0.053833 | 0.056333 | 1 | 0.16667 | 0.029 | 0.065 | 1 | 0.18833 | 0.014 | 7.3983 | 0.068333 | 3.2 | 4.2833 | 20.3 | 23.5 | 45.5 | 0.0175 | 7.53 | 0.078167 | 1.1667 | 3.95 | 20 | 24.5 | 46.5 | 0.0135 | 3.9233 | 3.2833 | 3.45 |  |  | MAXIMUM | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 |  | 14.8118 |  | 18.1008 | 32.3352 | 1.8274 | MAXIMUM | 73.4978 | 7194.0254 |  | 555.0661 |  |  |  | 2.9709 | 2.9709 | 2.3873 | 1.914 | 1.914 | 1.9942 | 0.19559 | 0.19559 | 0.16595 | 0.16941 | 0.15558 | 0.15558 | 1.5218 | 8 | 0.070344 | 0.070344 | 0.070344 | 1.1264 | 0.49911 | 0.1032 | 3.8061 | 0.74813 | 5.4049 | 1.1385 | 0.51974 | 0.11559 | 4.0162 | 0.79505 | 10.2124
MINIMUM | 6.35 | 18 | 17 | 4.46 | 104 | 130 | 19.9 | 0.43 | 0.027 | 6.01 | 9 | 0.047 | 6.03 | 10 |  | 5.96 | 9 |  | 6 | 0.424 | 5 | 0.37 | 20.8 | 10.3 | 0.36292 | 0.04 | 6.02 | 0.396 | 5 | 0.35 | 21.1 | 10.3 | 0.40341 | 6.09 | 0.497 | 5 | 0.3 | 21.1 | 10.5 | 0.39222 | 0.031 | 1 | 0.1 | 0.014 | 0.046 | 0.045 | 1 | 0.11 | 0.029 | 0.058 | 1 | 0.03 | 0.014 | 7.23 | 0.059 | 1 | 4.1 | 19.9 | 21 | 41 | 0.011 | 7.42 | 0.07 | 1 | 3.8 | 19.6 | 21 | 43 | 0.007 | 3.7 | 3.1 | 2.2 | [15 empty] | MIL/MIN |  | TOTAL | 47920 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 274 | 220 | 2175 | 2175 | 2233 | 2710 | 2680 | 2290 | 2260 | 2180 | 2180 | 3940 | 0 | 6850 | 6860 | 6860 | 494 | 590 | 72 | 8146 | 1642 | 1903 | 248 | 298 | 36 | 4315 | 870 | 1801
MAXIMUM | 6.49 | 20 | 19 | 4.77 | 111 | 138 | 21.1 | 0.45 | 0.031 | 6.13 | 10 | 0.074 | 6.19 | 11 |  | 6.08 | 10 |  | 6.14 | 0.483 | 6 | 0.48 | 21.3 | 11 | 0.42267 | 0.059 | 6.18 | 0.583 | 6 | 0.42 | 21.3 | 11 | 0.42267 | 6.16 | 0.71 | 7 | 0.57 | 21.5 | 11 | 0.40519 | 0.035 | 1 | 0.19 | 0.018 | 0.061 | 0.077 | 1 | 0.23 | 0.029 | 0.079 | 1 | 0.31 | 0.014 | 7.64 | 0.078 | 14.2 | 4.4 | 20.5 | 26 | 50 | 0.024 | 7.73 | 0.084 | 2 | 4.2 | 20.4 | 28 | 50 | 0.02 | 4.12 | 3.4 | 4.8 | [17 empty] | AVERAGE | 9584 | [6 empty] | 54.8 | 54.8 | 44 | 435 | 435 | 446.6 | 542 | 536 | 458 | 452 | 436 | 436 | 788 |  | 1370 | 1372 | 1372 | 98.8 | 118 | 14.4 | 1629.2 | 328.4 | 380.6 | 49.6 | 59.6 | 7.2 | 863 | 174 | 360.2
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0456 |  | TOTAL AVG COAG ALK: |  |  |  | 10 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.71 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.3 | [5 empty] | 6.1108 |  |  |  |  | 0.079 |  |  |  |  | 0.3 | [6 empty] | 0.079 | [16 empty] | Pump Station MIN |  | 2.2 | [17 empty] | MINIMUM | 9000 | [6 empty] | 0 | 0 | 0 | 420 | 420 | 425 | 520 | 520 | 430 | 410 | 410 | 410 | 770 |  | 1330 | 1330 | 1330 | 96 | 114 | 14 | 1540 | 310 | 370 | 48 | 58 | 7 | 830 | 160 | 350
[90 empty] | MAXIMUM | 9920 | [6 empty] | 112 | 112 | 90 | 450 | 450 | 460 | 550 | 550 | 480 | 490 | 450 | 450 | 800 |  | 1400 | 1400 | 1400 | 100 | 121 | 15 | 1690 | 344 | 389 | 52 | 60 | 8 | 900 | 183 | 367
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.849 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827691 |  | END: | 23827692 |  |  | Alum | 4887 | 5557 | 5557 | 7072 | 7072 | 0 | [44 empty] | 0.3 | 10.5 | 25.7143 | 7.7143 | 6.14 | 21.5 | 7 | 1.102
[73 empty] | FINISHED 2 | 15.926 |  | TOTAL MGD: |  | 13.848 |  |  | FINISHED SOUTH 2 |  | START: | 44997340 |  | END: | 45011188 |  |  | Caustic | 5279 | 7578 | 7578
[73 empty] | TOTAL RAW | 32.17 |  | TOTAL MGD: |  | 4.673 |  |  | FINISHED CONWAY |  | START: | 10703095 |  | END: | 10707768 |  |  | Hypochlorite | 16 |  | 31
[76 empty] | TOTAL MGD: |  | 11.253 |  |  | FINISHED PERRY |  | START: | 34833540 |  | END: | 34844793 |  |  | Phosphate | 3878
[76 empty] | TOTAL MGD: |  | 10.646 |  |  | RAW PLANT 1 |  | START: | 31918510 |  | END: | 31929156 |  |  | Fluoride | 1750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.655 |  |  | RAW PLANT 2 |  | START: | 31881870 |  | END: | 31892525 |  |  | Cal~Flo | 11.8 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.869 |  |  | RAW PLANT 3 |  | START: | 8515670 |  | END: | 8526539 |  |  | Zinc | 2475
[76 empty] | TOTAL MGD: |  | 0.701 |  |  | DECANT |  | START: | 1947334 |  | END: | 1948035 |  |  | Polymer | 23
[76 empty] | TOTAL MGD: |  | 0.85782 |  |  | BLOW DOWN |  | START: | 9251.7826 |  | END: | 9252.6404 |  |  | NH3 | 8.21 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 500
23827692
45011188
10707768
34844793
31929156
31892525
8526539
1948035
9252.6404
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 16
DATE: | 2019-04-16 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-16 | [23 empty] | DATE: | 2019-04-16
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-16 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43571.0095 | 1,2,3 | 98 | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 | 1,3,1,3 | 14.2344 | 1,3 | 18.1008 | 32.3352 | 1.2908 | 43571.0095 | 73.4978 | 7194.0254 | 0 | 555.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.9501 | 0.19534 | 0.1867 | 0.17287 | 0.17633 | 0.16077 | 0.16077 | 1.4647 | 0 | 0.069841 | 0.070344 | 0.070344 | 1.0947 | 0.49911 | 0.096324 | 3.6341 | 0.6734 | 5.3493 | 1.1385 | 0.49499 | 0.096324 | 3.8659 | 0.69512 | 10.1985 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.16 | 0.388 | 5 | 0.51 | 19.9 | 10.9 | 0.54846 |  | 6.13 | 0.508 | 6 | 0.42 | 20.6 | 10.9 | 0.41992 | 6.11 | 0.409 | 6 | 0.57 | 21.2 | 11.1 | 0.40778 | [13 empty] | 7.28 | 0.061 | 1 | 4.2 | 20.3 |  |  |  | 7.27 | 0.067 | 1 | 4 | 19.5 |  |  |  | 4 | 3.5 | 4.1 | [18 empty] | 9920 | [6 empty] | 0 | 0 | 0 | 420 | 420 | 460 | 565 | 540 | 500 | 510 | 465 | 465 | 770 |  | 1390 | 1400 | 1400 | 100 | 121 | 14 | 1620 | 310 | 385 | 52 | 60 | 7 | 830 | 160 | 367 |  | 1:00 | 0.51 | 10.9 | 23.3394 | 11.9031 | 6.16 | 19.9 | 10 | 1.1903 | 15 | 6.5 | 0.42846 | 1:00 | 0.42 | 10.9 | 23.3394 | 9.8026 | 6.13 | 20.6 | 7 | 1.4004 | 20 | 6.5 | 0.29992 | 1:00 | 0.57 | 11.1 | 24.3243 | 13.8649 | 6.11 | 21.2 | 7 | 1.9807 | 20 | 6.5 | 0.28778
2:00 | [72 empty] | 43571.4051 | 1,2,3,5 | 41 | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 | 1,3,1,3 | 8.7696 | 1,3 | 19.0123 | 27.7819 | 1.607 | 43571.4051 | 73.3496 | 7378.4876 | 0 | 555.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8017 | 1.8017 | 2.0349 | 0.20053 | 0.19016 | 0.16941 | 0.17978 | 0.15904 | 0.15904 | 1.46 | 3 | 0.070344 | 0.070344 | 0.070344 | 1.0947 | 0.49499 | 0.099765 | 3.8059 | 0.73422 | 4.0155 | 1.0947 | 0.49499 | 0.096324 | 4.0028 | 0.73857 | 10.1985 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.45 | 19 | 17 | 4.63 | 104 | 134 | 20.8 | 0.424 |  | 6.07 | 10 | 0.065 | 6.11 | 10 |  | 6.04 | 10 | [8 empty] | 0.054 | [14 empty] | 0.031 | 1 | 0.22 |  | 0.053 | 0.035 | 1 | 0.18 |  | 0.056 | 1 | 0.31 | [38 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 425 | 425 | 480 | 580 | 550 | 490 | 520 | 460 | 460 | 770 |  | 1400 | 1400 | 1400 | 100 | 120 | 14.5 | 1660 | 338 | 289 | 50 | 60 | 7 | 850 | 170 | 367 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43571.8314 | 1,2,3 | 41 | 10.4 | 10.4 | 10.4 | 31.2 | 9.9 | 9.9 | 9.9 | 29.7 | 1,3,1,3 | 14.1653 | 0 | 17.5925 | 31.7578 | 1.607 | 43571.8314 | 75.5439 | 7071.0506 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9783 | 1.9783 | 1.9109 | 0.20113 | 0.2121 | 0.18284 | 0.19016 | 0.15907 | 0.15907 | 2.9295 | 6 | 0.069811 | 0.069811 | 0.070344 | 1.1146 | 0.49874 | 0.10216 | 3.713 | 0.65661 | 5.0104 | 1.1146 | 0.52499 | 0.10216 | 4.0306 | 0.69117 | 9.5787 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.29 | 0.07 | 1 | 4.4 | 19.9 |  |  |  | 7.38 | 0.069 | 1 | 4.2 | 19.2 |  |  |  | 3.9 | 3.4 | 4 | [18 empty] | 9640 | [6 empty] | 0 | 0 | 0 | 440 | 440 | 425 | 550 | 580 | 500 | 520 | 435 | 435 | 1540 |  | 1310 | 1310 | 1320 | 96 | 114 | 14 | 1540 | 285 | 340 | 48 | 60 | 7 | 840 | 150 | 325 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.44 | 19 | 18 | 4.55 | 113 | 133 | 20.7 | 0.455 |  | 6.03 | 10 | 0.072 | 6.08 | 10 |  | 6 | 10 | [8 empty] | 0.056 | [14 empty] | 0.033 | 1 | 0.23 |  | 0.054 | 0.036 | 1 | 0.22 |  | 0.056 | 1 | 0.3 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.029 | [9 empty] | 6.15 | 0.474 | 5 | 0.51 | 20.5 | 11 | 0.42267 |  | 6.16 | 0.529 | 5 | 0.4 | 20.5 | 11 | 0.42267 | 6.19 | 0.495 | 6 | 0.74 | 20.3 | 11 | 0.40519 |  |  |  | 0.013 | [9 empty] | 7.39 | 0.079 | 2 | 4.3 | 19.9 | 28 | 52 | 0.024 | 7.39 | 0.071 | 1 | 4.1 | 19.3 | 29 | 47 | 0.01 | 4 | 3.5 | 3.7 | [55 empty] | 9:00 | 0.51 | 11 | 23.1273 | 11.7949 | 6.15 | 20.5 | 7 | 1.685 | 20 | 6.5 | 0.30267 | 9:00 | 0.4 | 11 | 23.1273 | 9.2509 | 6.16 | 20.5 | 7 | 1.3216 | 20 | 6.5 | 0.30267 | 9:00 | 0.74 | 11 | 24.5455 | 18.1636 | 6.19 | 20.3 | 7 | 2.5948 | 20 | 6.5 | 0.28519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.36 | 19 | 19 | 4.56 | 111 | 132 | 20.5 | 0.45 |  | 6.14 | 10 | 0.068 | 6.16 | 10 |  | 6.1 | 10 | [8 empty] | 0.055 | [14 empty] | 0.052 | 1 | 0.26 |  | 0.055 | 0.046 | 1 | 0.17 |  | 0.052 | 1 | 0.37 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.18 | 0.324 | 4 | 0.37 | 21 | 11 | 0.42267 |  | 6.14 | 0.393 | 5 | 0.36 | 21 | 11 | 0.42267 | 6.11 | 0.395 | 4 | 0.7 | 20.2 | 11 | 0.40519 | [13 empty] | 7.82 | 0.078 | 1 | 4.6 | 19.6 |  |  |  | 7.56 | 0.077 | 1 | 3.8 | 19.8 |  |  |  | 4 | 2.7 | 3.3 | [55 empty] | 13:00 | 0.37 | 11 | 23.1273 | 8.5571 | 6.18 | 21 | 7 | 1.2224 | 20 | 6.5 | 0.30267 | 13:00 | 0.36 | 11 | 23.1273 | 8.3258 | 6.14 | 21 | 7 | 1.1894 | 20 | 6.5 | 0.30267 | 13:00 | 0.7 | 11 | 24.5455 | 17.1818 | 6.11 | 20.2 | 7 | 2.4545 | 20 | 6.5 | 0.28519
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.48 | 19 | 18 | 4.43 | 109 | 131 | 20.4 | 0.449 |  | 6.19 | 11 | 0.07 | 6.27 | 11 |  | 6.1 | 11 | [8 empty] | 0.055 | [14 empty] | 0.066 | 1 | 0.29 |  | 0.056 | 0.042 | 1 | 0.2 |  | 0.058 | 1 | 0.34 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.42 | 0.074 | 1 | 4.6 | 20 |  |  |  | 7.6 | 0.069 | 1 | 4.1 | 19.3 |  |  |  | 4.3 | 3.5 | 3.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.43 | 19 | 19 | 4.16 | 108 | 131 | 20.7 | 0.44 |  | 6.14 | 11 | 0.067 | 6.23 | 12 |  | 6.19 | 11 | [8 empty] | 0.057 | [14 empty] | 0.07 | 1 | 0.19 |  | 0.054 | 0.038 | 1 | 0.14 |  | 0.058 | 1 | 0.16 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.027 | [9 empty] | 6.28 | 0.478 | 6 | 0.43 | 20.3 | 10.3 | 0.40341 |  | 6.26 | 0.639 | 6 | 0.38 | 20.6 | 10.4 | 0.40616 | 6.32 | 0.476 | 6 | 0.71 | 20.2 | 10.6 | 0.39481 |  |  |  | 0.005 |  |  |  |  | 0.024 |  |  |  | 0.015 | 7.88 | 0.08 | 1 | 4.4 | 19.8 | 21 | 44 | 0.019 | 7.75 | 0.079 | 1 | 4 | 19.4 | 21 | 46 | 0.019 | 4.3 | 3.4 | 3.8 | [55 empty] | 21:00 | 0.43 | 10.3 | 24.699 | 10.6206 | 6.28 | 20.3 | 7 | 1.5172 | 20 | 6.5 | 0.28341 | 21:00 | 0.38 | 10.4 | 24.4615 | 9.2954 | 6.26 | 20.6 | 7 | 1.3279 | 20 | 6.5 | 0.28616 | 21:00 | 0.71 | 10.6 | 25.4717 | 18.0849 | 6.32 | 20.2 | 7 | 2.5836 | 20 | 6.5 | 0.27481
22:00 | [72 empty] | DOSE |  | TOTAL | 32.4 | 32.4 | 32.4 | 97.2 | 30.9 | 30.9 | 30.9 | 92.7 | 0 | 37.1693 | 0 | 54.7056 | 91.8749 | 4.5049 | TOTAL | 222.3913 | 21643.5636 | 0 | 1617.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5605 | 5.5605 | 5.8958 | 0.597 | 0.58895 | 0.52512 | 0.54627 | 0.47888 | 0.47888 | 5.8542 | 9 | 0.21 | 0.2105 | 0.21103 | 3.304 | 1.4928 | 0.29825 | 11.153 | 2.0642 | 14.3752 | 3.3478 | 1.515 | 0.29481 | 11.8994 | 2.1249 | 29.9756 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.46 | 19 | 19 | 4.27 | 106 | 133 | 20.2 | 0.442 |  | 6.11 | 12 | 0.067 | 6.19 | 13 |  | 6.08 | 11 | [8 empty] | 0.055 | [14 empty] | 0.057 | 1 | 0.3 |  | 0.057 | 0.05 | 1 | 0.27 |  | 0.045 | 1 | 0.28 | [22 empty] | AVERAGE | 10.8 | 10.8 | 10.8 | 32.4 | 10.3 | 10.3 | 10.3 | 30.9 |  | 12.3898 |  | 18.2352 | 30.625 | 1.5016 | AVERAGE | 74.1304 | 7214.5212 |  | 539.207 | 0 | 0 | 0 |  |  |  | 1.8535 | 1.8535 | 1.9653 | 0.199 | 0.19632 | 0.17504 | 0.18209 | 0.15963 | 0.15963 | 1.9514 | 3 | 0.069999 | 0.070166 | 0.070344 | 1.1013 | 0.49761 | 0.099417 | 3.7177 | 0.68808 | 4.7917 | 1.1159 | 0.50499 | 0.09827 | 3.9665 | 0.70829 | 9.9919 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.62 | 114 | 110 | 26.6 | 651 | 794 | 123.3 | 2.66 | 0.056 | 36.68 | 64 | 0.409 | 37.04 | 66 | 0 | 36.51 | 63 | 0 | 24.77 | 1.664 | 20 | 1.82 | 81.7 | 43.2 | 1.7972 | 0.332 | 24.69 | 2.069 | 22 | 1.56 | 82.7 | 43.3 | 1.6714 | 24.73 | 1.775 | 22 | 2.72 | 81.9 | 43.7 | 1.613 | 0.309 | 6 | 1.49 | 0.018 | 0.329 | 0.247 | 6 | 1.18 | 0.024 | 0.325 | 6 | 1.76 | 0.015 | 45.08 | 0.442 | 7 | 26.5 | 119.5 | 49 | 96 | 0.043 | 44.95 | 0.432 | 6 | 24.2 | 116.5 | 50 | 93 | 0.029 | 24.5 | 20 | 22.2 |  |  | MINIMUM | 10.4 | 10.4 | 10.4 | 31.2 | 9.9 | 9.9 | 9.9 | 29.7 |  | 8.7696 |  | 17.5925 | 27.7819 | 1.2908 | MINIMUM | 73.3496 | 7071.0506 |  | 507.489 | [6 empty] | 1.7805 | 1.7805 | 1.9109 | 0.19534 | 0.1867 | 0.16941 | 0.17633 | 0.15904 | 0.15904 | 1.46 | 0 | 0.069811 | 0.069811 | 0.070344 | 1.0947 | 0.49499 | 0.096324 | 3.6341 | 0.65661 | 4.0155 | 1.0947 | 0.49499 | 0.096324 | 3.8659 | 0.69117 | 9.5787 |  | MIN | 0.51 | 10.9 | 23.3394 | 11.9031 | 6.16 | 19.9 | 10 | 1.1903 |  |  |  | MIN | 0.36 | 11 | 23.1273 | 8.3258 | 6.14 | 21 | 7 | 1.1894 |  |  |  | MIN | 0.57 | 11.1 | 24.3243 | 13.8649 | 6.11 | 21.2 | 7 | 1.9807 |  |  |  | 1.1894
AVERAGE | 6.4367 | 19 | 18.3333 | 4.4333 | 108.5 | 132.3333 | 20.55 | 0.44333 | 0.028 | 6.1133 | 10.6667 | 0.068167 | 6.1733 | 11 |  | 6.085 | 10.5 |  | 6.1925 | 0.416 | 5 | 0.455 | 20.425 | 10.8 | 0.4493 | 0.055333 | 6.1725 | 0.51725 | 5.5 | 0.39 | 20.675 | 10.825 | 0.41786 | 6.1825 | 0.44375 | 5.5 | 0.68 | 20.475 | 10.925 | 0.40324 | 0.0515 | 1 | 0.24833 | 0.009 | 0.054833 | 0.041167 | 1 | 0.19667 | 0.024 | 0.054167 | 1 | 0.29333 | 0.015 | 7.5133 | 0.073667 | 1.1667 | 4.4167 | 19.9167 | 24.5 | 48 | 0.0215 | 7.4917 | 0.072 | 1 | 4.0333 | 19.4167 | 25 | 46.5 | 0.0145 | 4.0833 | 3.3333 | 3.7 |  |  | MAXIMUM | 11 | 11 | 11 | 33 | 10.5 | 10.5 | 10.5 | 31.5 |  | 14.2344 |  | 19.0123 | 32.3352 | 1.607 | MAXIMUM | 75.5439 | 7378.4876 |  | 555.0661 | [6 empty] | 1.9783 | 1.9783 | 2.0349 | 0.20113 | 0.2121 | 0.18284 | 0.19016 | 0.16077 | 0.16077 | 2.9295 | 6 | 0.070344 | 0.070344 | 0.070344 | 1.1146 | 0.49911 | 0.10216 | 3.8059 | 0.73422 | 5.3493 | 1.1385 | 0.52499 | 0.10216 | 4.0306 | 0.73857 | 10.1985
MINIMUM | 6.36 | 19 | 17 | 4.16 | 104 | 131 | 20.2 | 0.424 | 0.027 | 6.03 | 10 | 0.065 | 6.08 | 10 |  | 6 | 10 |  | 6.15 | 0.324 | 4 | 0.37 | 19.9 | 10.3 | 0.40341 | 0.054 | 6.13 | 0.393 | 5 | 0.36 | 20.5 | 10.4 | 0.40616 | 6.11 | 0.395 | 4 | 0.57 | 20.2 | 10.6 | 0.39481 | 0.031 | 1 | 0.19 | 0.005 | 0.053 | 0.035 | 1 | 0.14 | 0.024 | 0.045 | 1 | 0.16 | 0.015 | 7.28 | 0.061 | 1 | 4.2 | 19.6 | 21 | 44 | 0.019 | 7.27 | 0.067 | 1 | 3.8 | 19.2 | 21 | 46 | 0.01 | 3.9 | 2.7 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 29460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1285 | 1285 | 1365 | 1695 | 1670 | 1490 | 1550 | 1360 | 1360 | 3080 | 0 | 4100 | 4110 | 4120 | 296 | 355 | 42.5 | 4820 | 933 | 1014 | 150 | 180 | 21 | 2520 | 480 | 1059
MAXIMUM | 6.48 | 19 | 19 | 4.63 | 113 | 134 | 20.8 | 0.455 | 0.029 | 6.19 | 12 | 0.072 | 6.27 | 13 |  | 6.19 | 11 |  | 6.28 | 0.478 | 6 | 0.51 | 21 | 11 | 0.54846 | 0.057 | 6.26 | 0.639 | 6 | 0.42 | 21 | 11 | 0.42267 | 6.32 | 0.495 | 6 | 0.74 | 21.2 | 11.1 | 0.40778 | 0.07 | 1 | 0.3 | 0.013 | 0.057 | 0.05 | 1 | 0.27 | 0.024 | 0.058 | 1 | 0.37 | 0.015 | 7.88 | 0.08 | 2 | 4.6 | 20.3 | 28 | 52 | 0.024 | 7.75 | 0.079 | 1 | 4.2 | 19.8 | 29 | 47 | 0.019 | 4.3 | 3.5 | 4.1 | [17 empty] | AVERAGE | 9820 | [9 empty] | 428.3333 | 428.3333 | 455 | 565 | 556.6667 | 496.6667 | 516.6667 | 453.3333 | 453.3333 | 1026.6667 |  | 1366.6667 | 1370 | 1373.3333 | 98.6667 | 118.3333 | 14.1667 | 1606.6667 | 311 | 338 | 50 | 60 | 7 | 840 | 160 | 353
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1239 |  | TOTAL AVG COAG ALK: |  |  |  | 10.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.639 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.36 | [5 empty] | 6.1825 |  |  |  |  | 0.07 |  |  |  |  | 0.36 | [6 empty] | 0.07 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 9640 | [9 empty] | 420 | 420 | 425 | 550 | 540 | 490 | 510 | 435 | 435 | 770 |  | 1310 | 1310 | 1320 | 96 | 114 | 14 | 1540 | 285 | 289 | 48 | 60 | 7 | 830 | 150 | 325
[90 empty] | MAXIMUM | 9920 | [9 empty] | 440 | 440 | 480 | 580 | 580 | 500 | 520 | 465 | 465 | 1540 |  | 1400 | 1400 | 1400 | 100 | 121 | 14.5 | 1660 | 338 | 385 | 52 | 60 | 7 | 850 | 170 | 367
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.444 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23827692 |  | END: | 23827698 |  |  | Alum | 4898 | 4841 | 4841 | 5742 | 5742 | 0 | [44 empty] | 0.36 | 11 | 23.1273 | 8.3258 | 6.14 | 21 | 7 | 1.1894
[73 empty] | FINISHED 2 | 16.431 |  | TOTAL MGD: |  | 13.438 |  |  | FINISHED SOUTH 2 |  | START: | 45011188 |  | END: | 45024626 |  |  | Caustic | 5133 | 7533 | 7533
[73 empty] | TOTAL RAW | 32.464 |  | TOTAL MGD: |  | 4.857 |  |  | FINISHED CONWAY |  | START: | 10707768 |  | END: | 10712625 |  |  | Hypochlorite | 19 |  | 22.5
[76 empty] | TOTAL MGD: |  | 11.574 |  |  | FINISHED PERRY |  | START: | 34844793 |  | END: | 34856367 |  |  | Phosphate | 3827
[76 empty] | TOTAL MGD: |  | 10.758 |  |  | RAW PLANT 1 |  | START: | 31929156 |  | END: | 31939914 |  |  | Fluoride | 1700 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.75 |  |  | RAW PLANT 2 |  | START: | 31892525 |  | END: | 31903275 |  |  | Cal~Flo | 8.28 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.956 |  |  | RAW PLANT 3 |  | START: | 8526539 |  | END: | 8537495 |  |  | Zinc | 2488
[76 empty] | TOTAL MGD: |  | 0.753 |  |  | DECANT |  | START: | 1948035 |  | END: | 1948788 |  |  | Polymer | 23
[76 empty] | TOTAL MGD: |  | 0.78677 |  |  | BLOW DOWN |  | START: | 9252.6404 |  | END: | 9253.4272 |  |  | NH3 | 7.95 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 500
23827698
45024626
10712625
34856367
31939914
31903275
8537495
1948788
9253.4272
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 17
DATE: | 2019-04-17 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-17 | [23 empty] | DATE: | 2019-04-17
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-17 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43572.0044 | 1,2,3 | 41 | 10.4 | 10.4 | 10.4 | 31.2 | 9.9 | 9.9 | 9.9 | 29.7 | 1,3,1,3 | 12.4978 | 0 | 17.9914 | 30.4891 | 1.2634 | 43572.0044 | 75.5439 | 7009.5632 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9783 | 1.9783 | 1.9109 | 0.20113 | 0.2121 | 0.18284 | 0.19016 | 0.15907 | 0.15907 | 2.9295 | 6 | 0.069811 | 0.069811 | 0.070344 | 1.1146 | 0.49874 | 0.10216 | 3.6669 | 0.65661 | 5.0104 | 1.1146 | 0.52499 | 0.10216 | 4.0306 | 0.69117 | 9.5787 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.23 | 0.424 | 6 | 0.53 | 19.6 | 10.4 | 0.52881 |  | 6.23 | 0.529 | 6 | 0.43 | 19.9 | 10.4 | 0.52881 | 6.26 | 0.543 | 6 | 0.73 | 19.8 | 10.6 | 0.51259 | [13 empty] | 7.335 | 0.064 | 1 | 4.2 | 19.8 |  |  |  | 7.32 | 0.059 | 1 | 4 | 19.1 |  |  |  | 4.1 | 3.5 | 3.8 | [18 empty] | 9640 | [6 empty] | 0 | 0 | 0 | 440 | 440 | 425 | 550 | 580 | 500 | 520 | 435 | 435 | 1540 |  | 1310 | 1310 | 1320 | 96 | 114 | 14 | 1520 | 285 | 340 | 48 | 60 | 7 | 840 | 150 | 325 |  | 1:00 | 0.53 | 10.4 | 24.4615 | 12.9646 | 6.23 | 19.6 | 10 | 1.2965 | 15 | 6.5 | 0.40881 | 1:00 | 0.43 | 10.4 | 24.4615 | 10.5185 | 6.23 | 19.9 | 10 | 1.0518 | 15 | 6.5 | 0.40881 | 1:00 | 0.73 | 10.6 | 25.4717 | 18.5943 | 6.26 | 19.8 | 10 | 1.8594 | 15 | 6.5 | 0.39259
2:00 | [72 empty] | 43572.3146 | 1,2,3 | 80 | 10.4 | 10.4 | 10.4 | 31.2 | 9.9 | 9.9 | 9.9 | 29.7 | 1,3,1,3 | 12.4978 | 0 | 17.9914 | 30.4891 | #VALUE! | 43572.3146 | 76.7977 | 7009.5632 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0233 | 2.0233 | 1.9783 | 0.20478 | 0.21941 | 0.19016 | 0.2121 | 0.1609 | 0.1609 | 3.6713 | 4.5 | 0.069278 | 0.069278 | 0.069278 | 1.103 | 0.49874 | 0.10216 | 3.8069 | 0.71421 | 5.2314 | 1.0914 | 0.52499 | 0.10216 | 3.9363 | 0.76029 | 9.6082 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.42 | 18 | 18 | 4.22 | 105 | 133 | 20.2 | 0.434 |  | 6.07 | 11 | 0.069 | 6.11 | 11 |  | 6.02 | 11 | [8 empty] | 0.056 | [14 empty] | 0.048 | 1 | 0.3 |  | 0.055 | 0.023 | 1 | 0.26 |  | 0.039 | 1 | 0.24 | [38 empty] | 9800 | [6 empty] | 0 | 0 | 0 | 450 | 450 | 440 | 560 | 600 | 520 | 580 | 440 | 440 | 1930 |  | 1300 | 1300 | 1300 | 95 | 114 | 14 | 1520 | 310 | 355 | 47 | 60 | 7 | 800 | 165 | 326 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 14:00 | 1,2,3,5 | 42 | 11.3 | 11.3 | 11.3 | 33.9 | 10.8 | 10.8 | 10.8 | 32.4 | 1,3,1,3 | 12.4978 | 0 | 17.9914 | 30.4891 | #VALUE! | 43572.667 | 75.0085 | 7255.5128 | 0 | 555.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0608 | 2.0608 | 1.9783 | 0.20194 | 0.20194 | 0.18511 | 0.1952 | 0.15987 | 0.15987 | 2.6631 | 4.5 | 0.070832 | 0.070832 | 0.070832 | 1.0962 | 0.50129 | 0.093649 | 3.7897 | 0.71383 | 5.0657 | 1.1069 | 0.49728 | 0.093649 | 3.967 | 0.76029 | 9.3208 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.16 | 0.067 | 1 | 4.4 | 19.5 |  |  |  | 7.24 | 0.063 | 1 | 4.1 | 19 |  |  |  | 4 | 3.5 | 3.6 | [18 empty] | 10400 | [6 empty] | 0 | 0 | 0 | 500 | 500 | 480 | 600 | 600 | 550 | 580 | 475 | 475 | 1400 |  | 1450 | 1450 | 1450 | 103 | 125 | 14 | 1650 | 338 | 375 | 52 | 62 | 7 | 880 | 180 | 345 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43572.8771 | 1,2,3,5 | 50 | 11.8 | 11.8 | 11.8 | 35.4 | 11.3 | 11.3 | 11.3 | 33.9 | ,1,3 | 15.3605 | 1,2 | 16.7026 | 32.063 | #VALUE! | 43572.8771 | 74.8691 | 7310 | 0 | 555.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9696 | 2.0484 | 1.812 | 0.20627 | 0.21916 | 0.18049 | 0.19338 | 0.1547 | 0.1547 | 2.3778 | 8 | 0.069099 | 0.070966 | 0.070032 | 1.0986 | 0.49827 | 0.10229 | 3.802 | 0.71656 | 4.8415 | 1.0986 | 0.49827 | 0.10229 | 3.984 | 0.76702 | 8.9084 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.4 | 20 | 18 | 4.4 | 107 | 137 | 20.2 | 0.44 |  | 6.03 | 14 | 0.072 | 6.09 | 14 |  | 6.01 | 13 | [8 empty] | 0.052 | [14 empty] | 0.045 | 1 | 0.32 |  | 0.057 | 0.065 | 1 | 0.29 |  | 0.039 | 1 | 0.25 | [38 empty] | 10840 | [6 empty] | 0 | 0 | 0 | 500 | 520 | 460 | 640 | 680 | 560 | 600 | 480 | 480 | 1250 |  | 1480 | 1520 | 1500 | 108 | 130 | 16 | 1730 | 355 | 375 | 54 | 65 | 8 | 920 | 190 | 345 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.05 | [9 empty] | 6.11 | 0.342 | 4 | 0.55 | 19.6 | 10.4 | 0.52881 |  | 6.15 | 0.331 | 4 | 0.54 | 19.3 | 10.4 | 0.52881 | 6.15 | 0.4 | 3 | 0.76 | 19.5 | 10.4 | 0.50519 |  |  |  | 0.049 | [9 empty] | 7.27 | 0.066 | 1 | 4.3 | 19.5 | 30 | 54 | 0.066 | 7.26 | 0.065 | 1 | 3.9 | 19.1 | 26 | 49 | 0.059 | 4 | 3.5 | 3.4 | [55 empty] | 9:00 | 0.55 | 10.4 | 24.4615 | 13.4538 | 6.11 | 19.6 | 10 | 1.3454 | 15 | 6.5 | 0.40881 | 9:00 | 0.54 | 10.4 | 24.4615 | 13.2092 | 6.15 | 19.3 | 10 | 1.3209 | 15 | 6.5 | 0.40881 | 9:00 | 0.76 | 10.4 | 25.9615 | 19.7308 | 6.15 | 19.5 | 10 | 1.9731 | 15 | 6.5 | 0.38519
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.47 | 20 | 18 | 4.26 | 109 | 133 | 20 | 0.444 |  | 6.07 | 10 | 0.07 | 6.14 | 10 |  | 6.03 | 10 | [8 empty] | 0.052 | [14 empty] | 0.044 | 1 | 0.61 |  | 0.056 | 0.051 | 1 | 0.57 |  | 0.037 | 1 | 0.25 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.11 | 0.278 | 4 | 0.52 | 20.8 | 10.4 | 0.40616 |  | 6.17 | 0.225 | 4 | 0.55 | 20.8 | 10.4 | 0.40616 | 6.19 | 0.414 | 3 | 0.72 | 20 | 10.4 | 0.38963 | [13 empty] | 7.24 | 0.06 | 1 | 4.2 | 20 |  |  |  | 7.27 | 0.061 | 1 | 4 | 21 |  |  |  | 4.1 | 2.7 | 1.9 | [55 empty] | 13:00 | 0.52 | 10.4 | 24.4615 | 12.72 | 6.11 | 20.8 | 7 | 1.8171 | 20 | 6.5 | 0.28616 | 13:00 | 0.55 | 10.4 | 24.4615 | 13.4538 | 6.17 | 20.8 | 7 | 1.922 | 20 | 6.5 | 0.28616 | 13:00 | 0.72 | 10.4 | 25.9615 | 18.6923 | 6.19 | 20 | 7 | 2.6703 | 20 | 6.5 | 0.26963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.46 | 21 | 18 | 4.52 | 105 | 135 | 21.5 | 0.427 |  | 6.03 | 11 | 0.068 | 6.07 | 11 |  | 6.01 | 11 | [8 empty] | 0.052 | [14 empty] | 0.04 | 1 | 0.55 |  | 0.055 | 0.046 | 1 | 0.58 |  | 0.039 | 1 | 0.22 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.19 | 0.062 | 1 | 4 | 20 |  |  |  | 7.22 | 0.058 | 1 | 4 | 21 |  |  |  | 4.1 | 3.4 | 3.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.52 | 20 | 15 | 4.49 | 108 | 134 | 21.3 | 0.433 |  | 5.92 | 11 | 0.087 | 5.94 | 12 |  | 5.93 | [9 empty] | 0.054 | [14 empty] | 0.038 | 1 | 0.24 |  | 0.074 | 0.043 | 1 | 0.38 |  | 0.078 | 1 | 0.27 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.033 | [9 empty] | 6.04 | 0.375 | 5 | 0.47 | 20.9 | 11.6 | 0.43918 |  | 6.03 | 0.283 | 5 | 0.54 | 20.9 | 11.7 | 0.44193 | 6.05 | 0.469 | 5 | 0.6 | 20.2 | 11.9 | 0.42852 |  |  |  | 0.009 | [9 empty] | 7.13 | 0.057 | 2 | 3.9 | 20.4 | 20 | 35 | 0.016 | 7.3 | 0.061 | 2 | 4.5 | 20.6 | 21 | 35 | 0.01 | 4 | 3.4 | 3.2 | [55 empty] | 21:00 | 0.47 | 11.6 | 21.931 | 10.3076 | 6.04 | 20.9 | 7 | 1.4725 | 20 | 6.5 | 0.31918 | 21:00 | 0.54 | 11.7 | 21.7436 | 11.7415 | 6.03 | 20.9 | 7 | 1.6774 | 20 | 6.5 | 0.32193 | 21:00 | 0.6 | 11.9 | 22.6891 | 13.6134 | 6.05 | 20.2 | 7 | 1.9448 | 20 | 6.5 | 0.30852
22:00 | [72 empty] | DOSE |  | TOTAL | 43.9 | 43.9 | 43.9 | 131.7 | 41.9 | 41.9 | 41.9 | 125.7 | 0 | 52.8538 | 0 | 70.6766 | 123.5304 | #VALUE! | TOTAL | 302.2191 | 28584.6392 | 0 | 2125.1101 | 0 | 0 | 0 | 0 | 0 | 0 | 8.032 | 8.1108 | 7.6796 | 0.81412 | 0.85261 | 0.73859 | 0.79084 | 0.63454 | 0.63454 | 11.6417 | 23 | 0.27902 | 0.28089 | 0.28049 | 4.4124 | 1.997 | 0.40026 | 15.0655 | 2.8012 | 20.149 | 4.4114 | 2.0455 | 0.40026 | 15.9178 | 2.9788 | 37.4161 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.5 | 18 | 16 | 4.66 | 106 | 136 | 21.4 | 0.415 |  | 5.99 | 11 | 0.075 | 6.01 | 12 |  | 5.94 | 12 | [8 empty] | 0.055 | [14 empty] | 0.034 | 1 | 0.27 |  | 0.048 | 0.039 | 1 | 0.43 |  | 0.064 | 1 | 0.34 | [22 empty] | AVERAGE | 10.975 | 10.975 | 10.975 | 32.925 | 10.475 | 10.475 | 10.475 | 31.425 |  | 13.2134 |  | 17.6692 | 30.8826 | #VALUE! | AVERAGE | 75.5548 | 7146.1598 |  | 531.2775 | 0 | 0 | 0 |  |  |  | 2.008 | 2.0277 | 1.9199 | 0.20353 | 0.21315 | 0.18465 | 0.19771 | 0.15864 | 0.15864 | 2.9104 | 5.75 | 0.069755 | 0.070222 | 0.070122 | 1.1031 | 0.49926 | 0.10007 | 3.7664 | 0.7003 | 5.0373 | 1.1028 | 0.51138 | 0.10007 | 3.9794 | 0.74469 | 9.354 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.77 | 117 | 103 | 26.55 | 640 | 808 | 124.6 | 2.593 | 0.083 | 36.11 | 68 | 0.441 | 36.36 | 70 | 0 | 5.942 | 5 | 0 | 24.49 | 1.419 | 19 | 2.07 | 80.9 | 42.8 | 1.903 | 0.321 | 24.58 | 1.368 | 19 | 2.06 | 80.9 | 42.9 | 1.9057 | 24.65 | 1.826 | 17 | 2.81 | 79.5 | 43.3 | 1.8359 | 0.249 | 6 | 2.29 | 0.058 | 0.345 | 0.267 | 6 | 2.51 | 0 | 0.1 | 6 | 1.57 | 0 | 43.325 | 0.376 | 7 | 25 | 119.2 | 50 | 89 | 0.082 | 43.61 | 0.367 | 7 | 24.5 | 119.8 | 47 | 84 | 0.069 | 24.3 | 20 | 19.1 |  |  | MINIMUM | 10.4 | 10.4 | 10.4 | 31.2 | 9.9 | 9.9 | 9.9 | 29.7 |  | 12.4978 |  | 16.7026 | 30.4891 | #VALUE! | MINIMUM | 74.8691 | 7009.5632 |  | 507.489 | [6 empty] | 1.9696 | 1.9783 | 1.812 | 0.20113 | 0.20194 | 0.18049 | 0.19016 | 0.1547 | 0.1547 | 2.3778 | 4.5 | 0.069099 | 0.069278 | 0.069278 | 1.0962 | 0.49827 | 0.093649 | 3.6669 | 0.65661 | 4.8415 | 1.0914 | 0.49728 | 0.093649 | 3.9363 | 0.69117 | 8.9084 |  | MIN | 0.53 | 10.4 | 24.4615 | 12.9646 | 6.23 | 19.6 | 10 | 1.2965 |  |  |  | MIN | 0.43 | 10.4 | 24.4615 | 10.5185 | 6.23 | 19.9 | 10 | 1.0518 |  |  |  | MIN | 0.73 | 10.6 | 25.4717 | 18.5943 | 6.26 | 19.8 | 10 | 1.8594 |  |  |  | 1.0518
AVERAGE | 6.4617 | 19.5 | 17.1667 | 4.425 | 106.6667 | 134.6667 | 20.7667 | 0.43217 | 0.0415 | 6.0183 | 11.3333 | 0.0735 | 6.06 | 11.6667 |  | 5.99 | 11.4 |  | 6.1225 | 0.35475 | 4.75 | 0.5175 | 20.225 | 10.7 | 0.47574 | 0.0535 | 6.145 | 0.342 | 4.75 | 0.515 | 20.225 | 10.725 | 0.47643 | 6.1625 | 0.4565 | 4.25 | 0.7025 | 19.875 | 10.825 | 0.45898 | 0.0415 | 1 | 0.38167 | 0.029 | 0.0575 | 0.0445 | 1 | 0.41833 |  | 0.049333 | 1 | 0.26167 |  | 7.2208 | 0.062667 | 1.1667 | 4.1667 | 19.8667 | 25 | 44.5 | 0.041 | 7.2683 | 0.061167 | 1.1667 | 4.0833 | 19.9667 | 23.5 | 42 | 0.0345 | 4.05 | 3.3333 | 3.1833 |  |  | MAXIMUM | 11.8 | 11.8 | 11.8 | 35.4 | 11.3 | 11.3 | 11.3 | 33.9 |  | 15.3605 |  | 17.9914 | 32.063 | #VALUE! | MAXIMUM | 76.7977 | 7310 |  | 555.0661 | [6 empty] | 2.0608 | 2.0608 | 1.9783 | 0.20627 | 0.21941 | 0.19016 | 0.2121 | 0.1609 | 0.1609 | 3.6713 | 8 | 0.070832 | 0.070966 | 0.070832 | 1.1146 | 0.50129 | 0.10229 | 3.8069 | 0.71656 | 5.2314 | 1.1146 | 0.52499 | 0.10229 | 4.0306 | 0.76702 | 9.6082
MINIMUM | 6.4 | 18 | 15 | 4.22 | 105 | 133 | 20 | 0.415 | 0.033 | 5.92 | 10 | 0.068 | 5.94 | 10 |  | 5.93 | 10 |  | 6.04 | 0.278 | 4 | 0.47 | 19.6 | 10.4 | 0.40616 | 0.052 | 6.03 | 0.225 | 4 | 0.43 | 19.3 | 10.4 | 0.40616 | 6.05 | 0.4 | 3 | 0.6 | 19.5 | 10.4 | 0.38963 | 0.034 | 1 | 0.24 | 0.009 | 0.048 | 0.023 | 1 | 0.26 |  | 0.037 | 1 | 0.22 |  | 7.13 | 0.057 | 1 | 3.9 | 19.5 | 20 | 35 | 0.016 | 7.22 | 0.058 | 1 | 3.9 | 19 | 21 | 35 | 0.01 | 4 | 2.7 | 1.9 | [15 empty] | MIL/MIN |  | TOTAL | 40680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1890 | 1910 | 1805 | 2350 | 2460 | 2130 | 2280 | 1830 | 1830 | 6120 | 0 | 5540 | 5580 | 5570 | 402 | 483 | 58 | 6420 | 1288 | 1445 | 201 | 247 | 29 | 3440 | 685 | 1341
MAXIMUM | 6.52 | 21 | 18 | 4.66 | 109 | 137 | 21.5 | 0.444 | 0.05 | 6.07 | 14 | 0.087 | 6.14 | 14 |  | 6.03 | 13 |  | 6.23 | 0.424 | 6 | 0.55 | 20.9 | 11.6 | 0.52881 | 0.056 | 6.23 | 0.529 | 6 | 0.55 | 20.9 | 11.7 | 0.52881 | 6.26 | 0.543 | 6 | 0.76 | 20.2 | 11.9 | 0.51259 | 0.048 | 1 | 0.61 | 0.049 | 0.074 | 0.065 | 1 | 0.58 |  | 0.078 | 1 | 0.34 |  | 7.335 | 0.067 | 2 | 4.4 | 20.4 | 30 | 54 | 0.066 | 7.32 | 0.065 | 2 | 4.5 | 21 | 26 | 49 | 0.059 | 4.1 | 3.5 | 3.8 | [17 empty] | AVERAGE | 10170 | [9 empty] | 472.5 | 477.5 | 451.25 | 587.5 | 615 | 532.5 | 570 | 457.5 | 457.5 | 1530 |  | 1385 | 1395 | 1392.5 | 100.5 | 120.75 | 14.5 | 1605 | 322 | 361.25 | 50.25 | 61.75 | 7.25 | 860 | 171.25 | 335.25
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0228 |  | TOTAL AVG COAG ALK: |  |  |  | 11.4667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.543 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.43 | [5 empty] | 6.1433 |  |  |  |  | 0.078 |  |  |  |  | 0.43 | [6 empty] | 0.078 | [16 empty] | Pump Station MIN |  | 1.9 | [17 empty] | MINIMUM | 9640 | [9 empty] | 440 | 440 | 425 | 550 | 580 | 500 | 520 | 435 | 435 | 1250 |  | 1300 | 1300 | 1300 | 95 | 114 | 14 | 1520 | 285 | 340 | 47 | 60 | 7 | 800 | 150 | 325
[90 empty] | MAXIMUM | 10840 | [9 empty] | 500 | 520 | 480 | 640 | 680 | 560 | 600 | 480 | 480 | 1930 |  | 1480 | 1520 | 1500 | 108 | 130 | 16 | 1730 | 355 | 375 | 54 | 65 | 8 | 920 | 190 | 345
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.635 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23827698 |  | END: | 23827704 |  |  | Alum | 4885 | 6369 | 6369 | 6794 | 6794 | 0 | [44 empty] | 0.43 | 10.4 | 24.4615 | 10.5185 | 6.23 | 19.9 | 10 | 1.0518
[73 empty] | FINISHED 2 | 15.684 |  | TOTAL MGD: |  | 13.629 |  |  | FINISHED SOUTH 2 |  | START: | 45024626 |  | END: | 45038255 |  |  | Caustic | 4988 | 7518 | 7518
[73 empty] | TOTAL RAW | 32.662 |  | TOTAL MGD: |  | 4.365 |  |  | FINISHED CONWAY |  | START: | 10712625 |  | END: | 10716990 |  |  | Hypochlorite | 12 |  | 20.5
[76 empty] | TOTAL MGD: |  | 11.319 |  |  | FINISHED PERRY |  | START: | 34856367 |  | END: | 34867686 |  |  | Phosphate | 3814
[76 empty] | TOTAL MGD: |  | 10.857 |  |  | RAW PLANT 1 |  | START: | 31939914 |  | END: | 31950771 |  |  | Fluoride | 1750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.852 |  |  | RAW PLANT 2 |  | START: | 31903275 |  | END: | 31914127 |  |  | Cal~Flo | 13.3 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.953 |  |  | RAW PLANT 3 |  | START: | 8537495 |  | END: | 8548448 |  |  | Zinc | 2470
[76 empty] | TOTAL MGD: |  | 0.623 |  |  | DECANT |  | START: | 1948788 |  | END: | 1949411 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 0.80548 |  |  | BLOW DOWN |  | START: | 9253.4272 |  | END: | 9254.2327 |  |  | NH3 | 7.69 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 555
23827704
45038255
10716990
34867686
31950771
31914127
8548448
1949411
9254.2327
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 18
DATE: | 2019-04-18 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-18 | [23 empty] | DATE: | 2019-04-18
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-18 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [7 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  | 5.625 |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43573.0013 | 1,2,3,5 | 50 | 11.8 | 11.8 | 11.8 | 35.4 | 11.3 | 11.3 | 11.3 | 33.9 | ,1,3 | 15.3605 | 1,2 | 16.7026 | 32.063 | 2.1135 | 43573.0013 | 74.8691 | 7624.4372 | 0 | 555.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9696 | 2.0484 | 1.812 | 0.20627 | 0.21916 | 0.18049 | 0.19338 | 0.1547 | 0.1547 | 2.3778 | 8 | 0.069099 | 0.070966 | 0.070032 | 1.0986 | 0.49827 | 0.10229 | 3.802 | 0.71656 | 4.8415 | 1.0986 | 0.49827 | 0.10229 | 3.984 | 0.76702 | 8.9084 |  |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.384 | 5 | 0.69 | 20.7 | 12 | 0.45019 |  | 6.03 | 0.315 | 5 | 0.59 | 20.9 | 12 | 0.45019 | 6.04 | 0.358 | 5 | 0.77 | 20.4 | 12.3 | 0.43889 | [13 empty] | 7.25 | 0.055 | 1 | 4 | 20.3 |  |  |  | 7.22 | 0.059 | 1 | 4.1 | 20.2 |  |  |  | 3.9 | 3.3 | 3.9 | [18 empty] | 10840 | [6 empty] | 0 | 0 | 0 | 500 | 520 | 460 | 640 | 680 | 560 | 600 | 480 | 480 | 1250 |  | 1480 | 1520 | 1500 | 108 | 130 | 16 | 1730 | 355 | 375 | 54 | 65 | 8 | 920 | 190 | 345 |  |  | 1:00 | 0.69 | 12 | 21.2 | 14.628 | 6.01 | 20.7 | 7 | 2.0897 | 20 | 6.5 | 0.33019 | 1:00 | 0.59 | 12 | 21.2 | 12.508 | 6.03 | 20.9 | 7 | 1.7869 | 20 | 6.5 | 0.33019 | 1:00 | 0.77 | 12.3 | 21.9512 | 16.9024 | 6.04 | 20.4 | 7 | 2.4146 | 20 | 6.5 | 0.31889
2:00 | [72 empty] | 43573.2957 | 1,2,3,5 | 50 | 11.8 | 11.8 | 11.8 | 35.4 | 11.3 | 11.3 | 11.3 | 33.9 | ,1,3 | 15.3605 | 1,2 | 16.7026 | 32.063 | #VALUE! | 43573.2957 | 74.0403 | 7685.9246 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8908 | 1.9696 | 1.812 | 0.19983 | 0.22561 | 0.17404 | 0.18693 | 0.1547 | 0.1547 | 1.4077 | 6.5 | 0.070032 | 0.070499 | 0.068165 | 1.0986 | 0.49827 | 0.10229 | 3.8875 | 0.70646 | 4.8415 | 1.0986 | 0.52127 | 0.10229 | 3.671 | 0.72665 | 8.9084 |  |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.54 | 18 | 17 | 4.69 | 102 | 137 | 19.8 | 0.42 |  | 6.05 | 11 | 0.096 | 6.1 | 11 |  | 6 | 11 | [8 empty] | 0.054 | [14 empty] | 0.037 | 1 | 0.28 |  | 0.051 | 0.059 | 1 | 0.39 |  | 0.063 | 1 | 0.28 | [38 empty] | 10720 | [6 empty] | 0 | 0 | 0 | 480 | 500 | 460 | 620 | 700 | 540 | 580 | 480 | 480 | 740 |  | 1500 | 1510 | 1460 | 108 | 130 | 16 | 1760 | 350 | 375 | 54 | 68 | 8 | 840 | 180 | 345 |  |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43573.8517 | 1,2,3,5 | 48 | 11.2 | 11.2 | 11.2 | 33.6 | 10.7 | 10.7 | 10.7 | 32.1 | ,1,3 | 14.0558 | 1,2 | 15.804 | 29.8598 | #VALUE! | 43573.8517 | 75.0233 | 7808.8994 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9968 | 2.08 | 1.9136 | 0.20374 | 0.21732 | 0.17657 | 0.19016 | 0.14941 | 0.14941 | 1.9974 | 1.5 | 0.069029 | 0.071001 | 0.069029 | 1.0742 | 0.50193 | 0.10128 | 3.802 | 0.70345 | 4.8403 | 1.0742 | 0.52621 | 0.10803 | 4.0264 | 0.74608 | 8.8625 |  |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.36 | 0.062 | 1 | 4.3 | 20.4 |  |  |  | 7.28 | 0.063 | 1 | 4.1 | 20.1 |  |  |  | 3.9 | 3.6 | 4.1 | [18 empty] | 10310 | [6 empty] | 0 | 0 | 0 | 480 | 500 | 460 | 600 | 640 | 520 | 560 | 440 | 440 | 1050 |  | 1400 | 1440 | 1400 | 100 | 124 | 15 | 1610 | 330 | 355 | 50 | 65 | 8 | 860 | 175 | 325 |  |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [128 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.45 | 20 | 18 | 4.68 | 108 | 139 | 20.4 | 0.445 |  | 6 | 12 | 0.089 | 6.04 | 12 |  | 5.99 | 11 | [8 empty] | 0.054 | [14 empty] | 0.035 | 1 | 0.26 |  | 0.053 | 0.045 | 1 | 0.44 |  | 0.047 | 1 | 0.35 | [76 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [128 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.081 | [9 empty] | 6.12 | 0.433 | 5 | 0.5 | 19.8 | 11.8 | 0.58384 |  | 6.15 | 0.461 | 5 | 0.59 | 19.8 | 11.8 | 0.58384 | 6.14 | 0.483 | 4 | 0.64 | 19.7 | 11.8 | 0.55704 |  |  |  | 0.044 | [9 empty] | 7.21 | 0.071 | 2 | 4.5 | 19.6 | 28 | 53 | 0.053 | 7.55 | 0.071 | 2 | 4.9 | 19.1 | 28 | 53 | 0.04 | 4.2 | 3.6 | 4 | [56 empty] | 9:00 | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.12 | 19.8 | 10 | 1.078 | 15 | 6.5 | 0.46384 | 9:00 | 0.59 | 11.8 | 21.5593 | 12.72 | 6.15 | 19.8 | 10 | 1.272 | 15 | 6.5 | 0.46384 | 9:00 | 0.64 | 11.8 | 22.8814 | 14.6441 | 6.14 | 19.7 | 10 | 1.4644 | 15 | 6.5 | 0.43704
10:00 | [128 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 20 | 18 | 4.7 | 111 | 137 | 20.3 | 0.447 |  | 6.04 | 12 | 0.091 | 6.08 | 12 |  | 6.02 | 12 | [8 empty] | 0.056 | [14 empty] | 0.036 | 1 | 0.3 |  | 0.055 | 0.051 | 2 | 0.46 |  | 0.057 | 2 | 0.29 | [76 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [128 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.13 | 0.332 | 4 | 0.52 | 20.2 | 11.4 | 0.43368 |  | 6.15 | 0.269 | 4 | 0.57 | 20.5 | 11.4 | 0.43368 | 6.15 | 0.487 | 5 | 0.6 | 20 | 11.4 | 0.41556 | [13 empty] | 7.19 | 0.07 | 2 | 4.2 | 19.7 |  |  |  | 7.19 | 0.071 | 2 | 3.9 | 19.9 |  |  |  | 4.1 | 3.6 | 4.5 | [56 empty] | 13:00 | 0.52 | 11.4 | 22.3158 | 11.6042 | 6.13 | 20.2 | 7 | 1.6577 | 20 | 6.5 | 0.31368 | 13:00 | 0.57 | 11.4 | 22.3158 | 12.72 | 6.15 | 20.5 | 7 | 1.8171 | 20 | 6.5 | 0.31368 | 13:00 | 0.6 | 11.4 | 23.6842 | 14.2105 | 6.15 | 20 | 7 | 2.0301 | 20 | 6.5 | 0.29556
14:00 | [126 empty] | #REF! |  | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.58 | 19 | 18 | 4.49 | 111 | 141 | 20.3 | 0.446 |  | 6.07 | 11 | 0.082 | 6.07 | 11 |  | 6.04 | 11 | [8 empty] | 0.053 | [14 empty] | 0.035 | 1 | 0.27 |  | 0.051 | 0.055 | 1 | 0.49 |  | 0.065 | 2 | 0.31 | [76 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [128 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.41 | 0.064 | 2 | 4.8 | 19.8 |  |  |  | 7.49 | 0.07 | 2 | 4.5 | 19.9 |  |  |  | 4.1 | 3.7 | 4.2 | [56 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [128 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.49 | 20 | 17 | 6.15 | 112 | 150 | 21.4 | 0.448 |  | 6.03 | 10 | 0.08 | 6.07 | 12 |  | 6.03 | 11 | [8 empty] | 0.05 | [14 empty] | 0.029 | 1 | 0.34 |  | 0.049 | 0.033 | 1 | 0.4 |  | 0.044 | 1 | 0.36 | [76 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [128 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.034 | [9 empty] | 6.11 | 0.285 | 4 | 0.64 | 21.1 | 11.2 | 0.42818 |  | 6.13 | 0.259 | 5 | 0.65 | 21.1 | 11 | 0.42267 | 6.15 | 0.391 | 4 | 0.77 | 20.6 | 11.4 | 0.41556 |  |  |  | 0.014 | [9 empty] | 7.22 | 0.055 | 1 | 4.4 | 20.5 | 21 | 39 | 0.019 | 7.26 | 0.061 | 1 | 3.9 | 20.9 | 22 | 41 | 0.015 | 4 | 3.5 | 3.9 | [56 empty] | 21:00 | 0.64 | 11.2 | 22.7143 | 14.5371 | 6.11 | 21.1 | 7 | 2.0767 | 20 | 6.5 | 0.30818 | 21:00 | 0.65 | 11 | 23.1273 | 15.0327 | 6.13 | 21.1 | 7 | 2.1475 | 20 | 6.5 | 0.30267 | 21:00 | 0.77 | 11.4 | 23.6842 | 18.2368 | 6.15 | 20.6 | 7 | 2.6053 | 20 | 6.5 | 0.29556
22:00 | [72 empty] | DOSE |  | TOTAL | 34.8 | 34.8 | 34.8 | 104.4 | 33.3 | 33.3 | 33.3 | 99.9 | 0 | 44.7768 | 0 | 49.2091 | 93.9859 | #VALUE! | TOTAL | 223.9327 | 23119.2612 | 0 | 1728.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8572 | 6.098 | 5.5377 | 0.60984 | 0.66209 | 0.5311 | 0.57047 | 0.45882 | 0.45882 | 5.7828 | 16 | 0.20816 | 0.21247 | 0.20723 | 3.2714 | 1.4985 | 0.30586 | 11.4914 | 2.1265 | 14.5233 | 3.2714 | 1.5458 | 0.31261 | 11.6815 | 2.2397 | 26.6793 |  |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.51 | 21 | 17 | 5.59 | 106 | 140 | 21.4 | 0.403 |  | 6.04 | 11 | 0.068 | 6.02 | 11 |  | 6.01 | 12 | [8 empty] | 0.052 | [14 empty] | 0.036 | 1 | 0.33 |  | 0.052 | 0.044 | 1 | 0.45 |  | 0.047 | 1 | 0.31 | [22 empty] | AVERAGE | 11.6 | 11.6 | 11.6 | 34.8 | 11.1 | 11.1 | 11.1 | 33.3 |  | 14.9256 |  | 16.403 | 31.3286 | #VALUE! | AVERAGE | 74.6442 | 7706.4204 |  | 576.2115 | 0 | 0 | 0 |  |  |  | 1.9524 | 2.0327 | 1.8459 | 0.20328 | 0.2207 | 0.17703 | 0.19016 | 0.15294 | 0.15294 | 1.9276 | 5.3333 | 0.069387 | 0.070822 | 0.069075 | 1.0905 | 0.49949 | 0.10195 | 3.8305 | 0.70882 | 4.8411 | 1.0905 | 0.51525 | 0.1042 | 3.8938 | 0.74658 | 8.8931 |  |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.07 | 118 | 105 | 30.3 | 650 | 844 | 123.6 | 2.609 | 0.115 | 36.23 | 67 | 0.506 | 36.38 | 69 | 0 | 36.09 | 68 | 0 | 24.37 | 1.434 | 18 | 2.35 | 81.8 | 46.4 | 1.8959 | 0.319 | 24.46 | 1.304 | 19 | 2.4 | 82.3 | 46.2 | 1.8904 | 24.48 | 1.719 | 18 | 2.78 | 80.7 | 46.9 | 1.827 | 0.208 | 6 | 1.78 | 0.058 | 0.311 | 0.287 | 7 | 2.63 | 0 | 0.323 | 8 | 1.9 | 0 | 43.64 | 0.377 | 9 | 26.2 | 120.3 | 49 | 92 | 0.072 | 43.99 | 0.395 | 9 | 25.4 | 120.1 | 50 | 94 | 0.055 | 24.2 | 21.3 | 24.6 |  |  | MINIMUM | 11.2 | 11.2 | 11.2 | 33.6 | 10.7 | 10.7 | 10.7 | 32.1 |  | 14.0558 |  | 15.804 | 29.8598 | #VALUE! | MINIMUM | 74.0403 | 7624.4372 |  | 555.0661 | [6 empty] | 1.8908 | 1.9696 | 1.812 | 0.19983 | 0.21732 | 0.17404 | 0.18693 | 0.14941 | 0.14941 | 1.4077 | 1.5 | 0.069029 | 0.070499 | 0.068165 | 1.0742 | 0.49827 | 0.10128 | 3.802 | 0.70345 | 4.8403 | 1.0742 | 0.49827 | 0.10229 | 3.671 | 0.72665 | 8.8625 |  |  | MIN | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.12 | 19.8 | 10 | 1.078 |  |  |  | MIN | 0.59 | 11.8 | 21.5593 | 12.72 | 6.15 | 19.8 | 10 | 1.272 |  |  |  | MIN | 0.64 | 11.8 | 22.8814 | 14.6441 | 6.14 | 19.7 | 10 | 1.4644 |  |  |  | 1.078
AVERAGE | 6.5117 | 19.6667 | 17.5 | 5.05 | 108.3333 | 140.6667 | 20.6 | 0.43483 | 0.0575 | 6.0383 | 11.1667 | 0.084333 | 6.0633 | 11.5 |  | 6.015 | 11.3333 |  | 6.0925 | 0.3585 | 4.5 | 0.5875 | 20.45 | 11.6 | 0.47397 | 0.053167 | 6.115 | 0.326 | 4.75 | 0.6 | 20.575 | 11.55 | 0.47259 | 6.12 | 0.42975 | 4.5 | 0.695 | 20.175 | 11.725 | 0.45676 | 0.034667 | 1 | 0.29667 | 0.029 | 0.051833 | 0.047833 | 1.1667 | 0.43833 |  | 0.053833 | 1.3333 | 0.31667 |  | 7.2733 | 0.062833 | 1.5 | 4.3667 | 20.05 | 24.5 | 46 | 0.036 | 7.3317 | 0.065833 | 1.5 | 4.2333 | 20.0167 | 25 | 47 | 0.0275 | 4.0333 | 3.55 | 4.1 |  |  | MAXIMUM | 11.8 | 11.8 | 11.8 | 35.4 | 11.3 | 11.3 | 11.3 | 33.9 |  | 15.3605 |  | 16.7026 | 32.063 | #VALUE! | MAXIMUM | 75.0233 | 7808.8994 |  | 586.7841 | [6 empty] | 1.9968 | 2.08 | 1.9136 | 0.20627 | 0.22561 | 0.18049 | 0.19338 | 0.1547 | 0.1547 | 2.3778 | 8 | 0.070032 | 0.071001 | 0.070032 | 1.0986 | 0.50193 | 0.10229 | 3.8875 | 0.71656 | 4.8415 | 1.0986 | 0.52621 | 0.10803 | 4.0264 | 0.76702 | 8.9084
MINIMUM | 6.45 | 18 | 17 | 4.49 | 102 | 137 | 19.8 | 0.403 | 0.034 | 6 | 10 | 0.068 | 6.02 | 11 |  | 5.99 | 11 |  | 6.01 | 0.285 | 4 | 0.5 | 19.8 | 11.2 | 0.42818 | 0.05 | 6.03 | 0.259 | 4 | 0.57 | 19.8 | 11 | 0.42267 | 6.04 | 0.358 | 4 | 0.6 | 19.7 | 11.4 | 0.41556 | 0.029 | 1 | 0.26 | 0.014 | 0.049 | 0.033 | 1 | 0.39 |  | 0.044 | 1 | 0.28 |  | 7.19 | 0.055 | 1 | 4 | 19.6 | 21 | 39 | 0.019 | 7.19 | 0.059 | 1 | 3.9 | 19.1 | 22 | 41 | 0.015 | 3.9 | 3.3 | 3.9 | [15 empty] | MIL/MIN |  | TOTAL | 31870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1460 | 1520 | 1380 | 1860 | 2020 | 1620 | 1740 | 1400 | 1400 | 3040 | 0 | 4380 | 4470 | 4360 | 316 | 384 | 47 | 5100 | 1035 | 1105 | 158 | 198 | 24 | 2620 | 545 | 1015
MAXIMUM | 6.58 | 21 | 18 | 6.15 | 112 | 150 | 21.4 | 0.448 | 0.081 | 6.07 | 12 | 0.096 | 6.1 | 12 |  | 6.04 | 12 |  | 6.13 | 0.433 | 5 | 0.69 | 21.1 | 12 | 0.58384 | 0.056 | 6.15 | 0.461 | 5 | 0.65 | 21.1 | 12 | 0.58384 | 6.15 | 0.487 | 5 | 0.77 | 20.6 | 12.3 | 0.55704 | 0.037 | 1 | 0.34 | 0.044 | 0.055 | 0.059 | 2 | 0.49 |  | 0.065 | 2 | 0.36 |  | 7.41 | 0.071 | 2 | 4.8 | 20.5 | 28 | 53 | 0.053 | 7.55 | 0.071 | 2 | 4.9 | 20.9 | 28 | 53 | 0.04 | 4.2 | 3.7 | 4.5 | [17 empty] | AVERAGE | 10623.3333 | [9 empty] | 486.6667 | 506.6667 | 460 | 620 | 673.3333 | 540 | 580 | 466.6667 | 466.6667 | 1013.3333 |  | 1460 | 1490 | 1453.3333 | 105.3333 | 128 | 15.6667 | 1700 | 345 | 368.3333 | 52.6667 | 66 | 8 | 873.3333 | 181.6667 | 338.3333
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0389 |  | TOTAL AVG COAG ALK: |  |  |  | 11.3333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.487 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.5 | [5 empty] | 6.1092 |  |  |  |  | 0.065 |  |  |  |  | 0.5 | [6 empty] | 0.065 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 10310 | [9 empty] | 480 | 500 | 460 | 600 | 640 | 520 | 560 | 440 | 440 | 740 |  | 1400 | 1440 | 1400 | 100 | 124 | 15 | 1610 | 330 | 355 | 50 | 65 | 8 | 840 | 175 | 325
[90 empty] | MAXIMUM | 10840 | [9 empty] | 500 | 520 | 460 | 640 | 700 | 560 | 600 | 480 | 480 | 1250 |  | 1500 | 1520 | 1500 | 108 | 130 | 16 | 1760 | 355 | 375 | 54 | 68 | 8 | 920 | 190 | 345
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [51 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.945 |  | TOTAL MGD: |  | 0.003 |  |  | FINISHED SOUTH 1 |  | START: | 23827704 |  | END: | 23827707 |  |  | Alum | 4882 | 8287 | 8287 | 5502 | 5502 | 0 | [45 empty] | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.12 | 19.8 | 10 | 1.078
[73 empty] | FINISHED 2 | 17.706 |  | TOTAL MGD: |  | 13.942 |  |  | FINISHED SOUTH 2 |  | START: | 45038255 |  | END: | 45052197 |  |  | Caustic | 4865 | 7461 | 7461
[73 empty] | TOTAL RAW | 34.596 |  | TOTAL MGD: |  | 5.391 |  |  | FINISHED CONWAY |  | START: | 10716990 |  | END: | 10722381 |  |  | Hypochlorite | 9 |  | 20.5
[76 empty] | TOTAL MGD: |  | 12.315 |  |  | FINISHED PERRY |  | START: | 34867686 |  | END: | 34880001 |  |  | Phosphate | 3719
[76 empty] | TOTAL MGD: |  | 11.446 |  |  | RAW PLANT 1 |  | START: | 31950771 |  | END: | 31962217 |  |  | Fluoride | 1750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.408 |  |  | RAW PLANT 2 |  | START: | 31914127 |  | END: | 31925535 |  |  | Cal~Flo | 9.78 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.742 |  |  | RAW PLANT 3 |  | START: | 8548448 |  | END: | 8560190 |  |  | Zinc | 2466
[76 empty] | TOTAL MGD: |  | 0.907 |  |  | DECANT |  | START: | 1949411 |  | END: | 1950318 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.1752 |  |  | BLOW DOWN |  | START: | 9254.2327 |  | END: | 9255.4079 |  |  | NH3 | 7.45 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 587
23827707
45052197
10722381
34880001
31962217
31925535
8560190
1950318
9255.4079
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 19
DATE: | 2019-04-19 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-19 | [23 empty] | DATE: | 2019-04-19
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-19 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43574.0095 | 1,2,3,5 | 48 | 10.6 | 10.6 | 10.6 | 31.8 | 10.1 | 10.1 | 10.1 | 30.3 | ,1,3 | 14.0558 | 1,2 | 15.804 | 29.8598 | 1.531 | 43574.0095 | 75.0411 | 7300 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0273 | 2.1154 | 1.9392 | 0.20092 | 0.21527 | 0.17222 | 0.17222 | 0.14351 | 0.14351 | 1.9974 | 1.5 | 0.07104 | 0.07104 | 0.07104 | 1.1153 | 0.50173 | 0.10014 | 3.8026 | 0.70007 | 4.9112 | 1.0925 | 0.51459 | 0.10014 | 3.9733 | 0.74523 | 8.9557 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.274 | 4 | 0.77 | 21.1 | 10.2 | 0.40066 |  | 6.15 | 0.255 | 5 | 0.72 | 21.1 | 10.2 | 0.40066 | 6.19 | 0.31 | 4 | 0.73 | 20.7 | 10.4 | 0.38963 | [13 empty] | 7.53 | 0.054 | 1 | 4.4 | 20.4 |  |  |  | 7.24 | 0.059 | 1 | 3.9 | 20.5 |  |  |  | 4.2 | 3.7 | 1.8 | [18 empty] | 9760 | [6 empty] | 0 | 0 | 0 | 460 | 480 | 440 | 560 | 600 | 480 | 480 | 400 | 400 | 1050 |  | 1360 | 1360 | 1360 | 98 | 117 | 14 | 1520 | 310 | 340 | 48 | 60 | 7 | 800 | 165 | 310 |  | 1:00 | 0.77 | 10.2 | 24.9412 | 19.2047 | 6.14 | 21.1 | 7 | 2.7435 | 20 | 6.5 | 0.28066 | 1:00 | 0.72 | 10.2 | 24.9412 | 17.9576 | 6.15 | 21.1 | 7 | 2.5654 | 20 | 6.5 | 0.28066 | 1:00 | 0.73 | 10.4 | 25.9615 | 18.9519 | 6.19 | 20.7 | 7 | 2.7074 | 20 | 6.5 | 0.26963
2:00 | [72 empty] | 43574.3467 | 1,2,3,5 | 48 | 11.3 | 11.3 | 11.3 | 33.9 | 10.8 | 10.8 | 10.8 | 32.4 | ,1,3 | 14.0558 | 1,2 | 15.804 | 29.8598 | 1.531 | 43574.3467 | 75.7297 | 7255.5128 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9783 | 2.0608 | 1.8959 | 0.20194 | 0.20194 | 0.17165 | 0.17501 | 0.15482 | 0.13799 | 1.5218 | 7 | 0.06839 | 0.068878 | 0.06839 | 1.0856 | 0.50129 | 0.10034 | 3.6935 | 0.63358 | 4.9711 | 1.1069 | 0.48124 | 0.093649 | 3.8335 | 0.67581 | 9.1857 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.55 | 18 | 15 | 5.44 | 109 | 141 | 20.7 | 0.44 |  | 6.12 | 12 | 0.072 | 6.14 | 12 |  | 6.11 | 10 | [8 empty] | 0.053 | [14 empty] | 0.034 | 1 | 0.38 |  | 0.052 | 0.036 | 1 | 0.47 |  | 0.051 | 1 | 0.36 | [38 empty] | 10500 | [6 empty] | 0 | 0 | 0 | 480 | 500 | 460 | 600 | 600 | 510 | 520 | 460 | 410 | 800 |  | 1400 | 1410 | 1400 | 102 | 125 | 15 | 1550 | 300 | 368 | 52 | 60 | 7 | 820 | 160 | 340 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43574.5061 | 2,3,5 | 48 | 10 | 10 | 10 | 30 | 9.5 | 9.5 | 9.5 | 28.5 | ,1,3 | 14.0558 | 1,2 | 15.804 | 29.8598 | 1.531 | 43574.5061 | 74.9796 | 7132.538 | 0 | 507.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1085 | 2.1085 | 2.0616 | 0.21297 | 0.21297 | 0.19016 | 0.19776 | 0.17114 | 0.15593 | 1.5218 | 0 | 0.069418 | 0.069418 | 0.069418 | 1.0889 | 0.5015 | 0.10646 | 3.5892 | 0.60023 | 5.2214 | 1.0889 | 0.5015 | 0.10646 | 3.9714 | 0.62424 | 9.8284 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.32 | 0.055 | 1 | 4.2 | 20.6 |  |  |  | 7.33 | 0.06 | 1 | 4 | 20.5 |  |  |  | 4.2 | 3.7 | 2 | [18 empty] | 9200 | [6 empty] | 0 | 0 | 0 | 450 | 450 | 440 | 560 | 560 | 500 | 520 | 450 | 410 | 800 |  | 1250 | 1250 | 1250 | 90 | 110 | 14 | 1320 | 250 | 340 | 45 | 55 | 7 | 750 | 130 | 320 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43574.6416 | 2,3,5 | 48 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | ,1,3 | 14.0558 | 1,2 | 15.804 | 29.8598 | 1.531 | 43574.6416 | 76.0663 | 7009.5632 | 0 | 459.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0947 | 2.0947 | 2.3042 | 0.20283 | 0.21128 | 0.20072 | 0.19016 | 0.17959 | 0.16903 | 1.5218 | 0 | 0.070758 | 0.070758 | 0.068275 | 1.0818 | 0.49935 | 0.10199 | 3.5572 | 0.61718 | 5.4924 | 1.1089 | 0.50955 | 0.10199 | 4.0321 | 0.64401 | 10.2982 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.51 | 20 | 17 | 5.9 | 112 | 146 | 20.7 | 0.444 |  | 6.02 | 12 | 0.07 | 6.01 | 12 |  | 5.99 | 11 | [8 empty] | 0.049 | [14 empty] | 0.066 | 2 | 0.42 |  | 0.048 | 0.068 | 2 | 0.57 |  | 0.073 | 2 | 0.41 | [38 empty] | 8400 | [6 empty] | 0 | 0 | 0 | 400 | 400 | 440 | 480 | 500 | 475 | 450 | 425 | 400 | 800 |  | 1140 | 1140 | 1100 | 80 | 98 | 12 | 1130 | 230 | 320 | 41 | 50 | 6 | 660 | 120 | 300 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43574.8429 | 2,3,5 | 40 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | ,1,3 | 9.3974 | 1,2 | 15.4598 | 24.8573 | 1.531 | 43574.8429 | 75.1607 | 6271.7144 | 0 | 459.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0947 | 2.3042 | 2.0947 | 0.20283 | 0.21974 | 0.16903 | 0.16903 | 0.16903 | 0.16903 | 2.1876 | 6 | 0.069516 | 0.069516 | 0.069516 | 1.0818 | 0.49935 | 0.10199 | 3.8124 | 0.67084 | 5.4924 | 1.0818 | 0.50955 | 0.11899 | 4.0094 | 0.75135 | 10.2982 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.057 | [9 empty] | 6.16 | 0.31 | 5 | 0.68 | 20.6 | 11.3 | 0.43093 |  | 6.2 | 0.352 | 5 | 0.75 | 20.6 | 11.3 | 0.43093 | 6.2 | 0.45 | 5 | 0.85 | 20.4 | 11.3 | 0.41296 |  |  |  | 0.036 | [9 empty] | 7.37 | 0.068 | 2 | 4.4 | 19.9 | 30 | 55 | 0.036 | 7.35 | 0.07 | 2 | 4.1 | 19.7 | 29 | 50 | 0.029 | 4.2 | 3.5 | 3 | [18 empty] | 8300 | [6 empty] | 0 | 0 | 0 | 400 | 440 | 400 | 480 | 520 | 400 | 400 | 400 | 400 | 1150 |  | 1120 | 1120 | 1120 | 80 | 98 | 12 | 1240 | 250 | 320 | 40 | 50 | 7 | 680 | 140 | 300 |  | 9:00 | 0.68 | 11.3 | 22.5133 | 15.309 | 6.16 | 20.6 | 7 | 2.187 | 20 | 6.5 | 0.31093 | 9:00 | 0.75 | 11.3 | 22.5133 | 16.885 | 6.2 | 20.6 | 7 | 2.4121 | 20 | 6.5 | 0.31093 | 9:00 | 0.85 | 11.3 | 23.8938 | 20.3097 | 6.2 | 20.4 | 7 | 2.9014 | 20 | 6.5 | 0.29296
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.51 | 20 | 18 | 5.79 | 112 | 145 | 20.7 | 0.452 |  | 6.01 | 14 | 0.071 | 6.05 | 14 |  | 5.98 | 13 | [8 empty] | 0.049 | [14 empty] | 0.062 | 1 | 0.45 |  | 0.049 | 0.033 | 1 | 0.56 |  | 0.04 | 1 | 0.43 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.06 | 0.242 | 3 | 0.83 | 20.5 | 10 | 0.39516 |  | 6.16 | 0.205 | 3 | 0.82 | 20.2 | 10 | 0.39516 | 6.19 | 0.404 | 3 | 0.68 | 20.6 | 10 | 0.37926 | [13 empty] | 7.27 | 0.059 | 1 | 4.6 | 20.2 |  |  |  | 7.2 | 0.054 | 1 | 3.7 | 19.9 |  |  |  | 4.2 | 3.5 | 4 | [55 empty] | 13:00 | 0.83 | 10 | 25.44 | 21.1152 | 6.06 | 20.5 | 7 | 3.0165 | 20 | 6.5 | 0.27516 | 13:00 | 0.82 | 10 | 25.44 | 20.8608 | 6.16 | 20.2 | 7 | 2.9801 | 20 | 6.5 | 0.27516 | 13:00 | 0.68 | 10 | 27 | 18.36 | 6.19 | 20.6 | 7 | 2.6229 | 20 | 6.5 | 0.25926
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.64 | 20 | 17 | 5.46 | 107 | 137 | 20.7 | 0.46 |  | 6.2 | 12 | 0.064 | 6.13 | 12 |  | 6.06 | 12 | [8 empty] | 0.045 | [14 empty] | 0.067 | 1 | 0.49 |  | 0.046 | 0.051 | 1 | 0.56 |  | 0.032 | 1 | 0.49 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.43 | 0.053 | 1 | 4.5 | 19.9 |  |  |  | 7.33 | 0.057 | 1 | 3.9 | 19.8 |  |  |  | 4.2 | 3.5 | 3.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.55 | 19 | 19 | 5.34 | 110 | 141 | 21.7 | 0.444 |  | 6.09 | 12 | 0.066 | 6.08 | 11 |  | 6.06 | 11 | [8 empty] | 0.046 | [14 empty] | 0.074 | 2 | 0.56 |  | 0.045 | 0.038 | 1 | 0.41 |  | 0.048 | 1 | 0.36 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.028 | [9 empty] | 6.21 | 0.344 | 4 | 0.76 | 21.2 | 8.4 | 0.35113 |  | 6.2 | 0.274 | 5 | 0.79 | 21.1 | 8.5 | 0.35388 | 6.21 | 0.359 | 5 | 0.94 | 20.8 | 8.8 | 0.34815 |  |  |  | 0.015 | [9 empty] | 7.98 | 0.061 | 2 | 3.6 | 20.7 | 23 | 38 | 0.013 | 7.66 | 0.06 | 2 | 3.7 | 20.4 | 22 | 43 | 0.006 | 4.1 | 3.6 | 4.2 | [55 empty] | 21:00 | 0.76 | 8.4 | 30.2857 | 23.0171 | 6.21 | 21.2 | 7 | 3.2882 | 20 | 6.5 | 0.23113 | 21:00 | 0.79 | 8.5 | 29.9294 | 23.6442 | 6.2 | 21.1 | 7 | 3.3777 | 20 | 6.5 | 0.23388 | 21:00 | 0.94 | 8.8 | 30.6818 | 28.8409 | 6.21 | 20.8 | 7 | 4.1201 | 20 | 6.5 | 0.22815
22:00 | [72 empty] | DOSE |  | TOTAL | 49.9 | 49.9 | 49.9 | 149.7 | 47.4 | 47.4 | 47.4 | 142.2 | 0 | 65.6208 | 0 | 78.6758 | 144.2966 | 7.655 | TOTAL | 376.9775 | 34969.3284 | 0 | 2585.022 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3035 | 10.6836 | 10.2956 | 1.0215 | 1.0612 | 0.90377 | 0.90417 | 0.81809 | 0.77549 | 8.7503 | 14.5 | 0.34912 | 0.34961 | 0.34664 | 5.4534 | 2.5032 | 0.51092 | 18.4549 | 3.2219 | 26.0884 | 5.479 | 2.5164 | 0.52123 | 19.8196 | 3.4406 | 48.5662 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.52 | 18 | 19 | 5.26 | 111 | 144 | 21.6 | 0.417 |  | 6.16 | 11 | 0.081 | 6.15 | 10 |  | 6.12 | 10 | [8 empty] | 0.054 | [14 empty] | 0.065 | 1 | 0.46 |  | 0.05 | 0.032 | 1 | 0.44 |  | 0.048 | 1 | 0.28 | [22 empty] | AVERAGE | 9.98 | 9.98 | 9.98 | 29.94 | 9.48 | 9.48 | 9.48 | 28.44 |  | 13.1242 |  | 15.7352 | 28.8593 | 1.531 | AVERAGE | 75.3955 | 6993.8657 |  | 517.0044 | 0 | 0 | 0 |  |  |  | 2.0607 | 2.1367 | 2.0591 | 0.2043 | 0.21224 | 0.18075 | 0.18083 | 0.16362 | 0.1551 | 1.7501 | 2.9 | 0.069824 | 0.069922 | 0.069328 | 1.0907 | 0.50064 | 0.10218 | 3.691 | 0.64438 | 5.2177 | 1.0958 | 0.50328 | 0.10425 | 3.9639 | 0.68813 | 9.7132 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.28 | 115 | 105 | 33.19 | 661 | 854 | 126.1 | 2.657 | 0.085 | 36.6 | 73 | 0.424 | 36.56 | 71 | 0 | 36.32 | 67 | 0 | 24.57 | 1.17 | 16 | 3.04 | 83.4 | 39.9 | 1.5779 | 0.296 | 24.71 | 1.086 | 18 | 3.08 | 83 | 40 | 1.5806 | 24.79 | 1.523 | 17 | 3.2 | 82.5 | 40.5 | 1.53 | 0.368 | 8 | 2.76 | 0.051 | 0.29 | 0.258 | 7 | 3.01 | 0 | 0.292 | 7 | 2.33 | 0 | 44.9 | 0.35 | 8 | 25.7 | 121.7 | 53 | 93 | 0.049 | 44.11 | 0.36 | 8 | 23.3 | 120.8 | 51 | 93 | 0.035 | 25.1 | 21.5 | 18.9 |  |  | MINIMUM | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 |  | 9.3974 |  | 15.4598 | 24.8573 | 1.531 | MINIMUM | 74.9796 | 6271.7144 |  | 459.9119 | [6 empty] | 1.9783 | 2.0608 | 1.8959 | 0.20092 | 0.20194 | 0.16903 | 0.16903 | 0.14351 | 0.13799 | 1.5218 | 0 | 0.06839 | 0.068878 | 0.068275 | 1.0818 | 0.49935 | 0.10014 | 3.5572 | 0.60023 | 4.9112 | 1.0818 | 0.48124 | 0.093649 | 3.8335 | 0.62424 | 8.9557 |  | MIN | 0.68 | 11.3 | 22.5133 | 15.309 | 6.16 | 20.6 | 7 | 2.187 |  |  |  | MIN | 0.75 | 11.3 | 22.5133 | 16.885 | 6.2 | 20.6 | 7 | 2.4121 |  |  |  | MIN | 0.68 | 10 | 27 | 18.36 | 6.19 | 20.6 | 7 | 2.6229 |  |  |  | 2.187
AVERAGE | 6.5467 | 19.1667 | 17.5 | 5.5317 | 110.1667 | 142.3333 | 21.0167 | 0.44283 | 0.0425 | 6.1 | 12.1667 | 0.070667 | 6.0933 | 11.8333 |  | 6.0533 | 11.1667 |  | 6.1425 | 0.2925 | 4 | 0.76 | 20.85 | 9.975 | 0.39447 | 0.049333 | 6.1775 | 0.2715 | 4.5 | 0.77 | 20.75 | 10 | 0.39516 | 6.1975 | 0.38075 | 4.25 | 0.8 | 20.625 | 10.125 | 0.3825 | 0.061333 | 1.3333 | 0.46 | 0.0255 | 0.048333 | 0.043 | 1.1667 | 0.50167 |  | 0.048667 | 1.1667 | 0.38833 |  | 7.4833 | 0.058333 | 1.3333 | 4.2833 | 20.2833 | 26.5 | 46.5 | 0.0245 | 7.3517 | 0.06 | 1.3333 | 3.8833 | 20.1333 | 25.5 | 46.5 | 0.0175 | 4.1833 | 3.5833 | 3.15 |  |  | MAXIMUM | 11.3 | 11.3 | 11.3 | 33.9 | 10.8 | 10.8 | 10.8 | 32.4 |  | 14.0558 |  | 15.804 | 29.8598 | 1.531 | MAXIMUM | 76.0663 | 7300 |  | 586.7841 | [6 empty] | 2.1085 | 2.3042 | 2.3042 | 0.21297 | 0.21974 | 0.20072 | 0.19776 | 0.17959 | 0.16903 | 2.1876 | 7 | 0.07104 | 0.07104 | 0.07104 | 1.1153 | 0.50173 | 0.10646 | 3.8124 | 0.70007 | 5.4924 | 1.1089 | 0.51459 | 0.11899 | 4.0321 | 0.75135 | 10.2982
MINIMUM | 6.51 | 18 | 15 | 5.26 | 107 | 137 | 20.7 | 0.417 | 0.028 | 6.01 | 11 | 0.064 | 6.01 | 10 |  | 5.98 | 10 |  | 6.06 | 0.242 | 3 | 0.68 | 20.5 | 8.4 | 0.35113 | 0.045 | 6.15 | 0.205 | 3 | 0.72 | 20.2 | 8.5 | 0.35388 | 6.19 | 0.31 | 3 | 0.68 | 20.4 | 8.8 | 0.34815 | 0.034 | 1 | 0.38 | 0.015 | 0.045 | 0.032 | 1 | 0.41 |  | 0.032 | 1 | 0.28 |  | 7.27 | 0.053 | 1 | 3.6 | 19.9 | 23 | 38 | 0.013 | 7.2 | 0.054 | 1 | 3.7 | 19.7 | 22 | 43 | 0.006 | 4.1 | 3.5 | 1.8 | [15 empty] | MIL/MIN |  | TOTAL | 46160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2190 | 2270 | 2180 | 2680 | 2780 | 2365 | 2370 | 2135 | 2020 | 4600 | 0 | 6270 | 6280 | 6230 | 450 | 548 | 67 | 6760 | 1340 | 1688 | 226 | 275 | 34 | 3710 | 715 | 1570
MAXIMUM | 6.64 | 20 | 19 | 5.9 | 112 | 146 | 21.7 | 0.46 | 0.057 | 6.2 | 14 | 0.081 | 6.15 | 14 |  | 6.12 | 13 |  | 6.21 | 0.344 | 5 | 0.83 | 21.2 | 11.3 | 0.43093 | 0.054 | 6.2 | 0.352 | 5 | 0.82 | 21.1 | 11.3 | 0.43093 | 6.21 | 0.45 | 5 | 0.94 | 20.8 | 11.3 | 0.41296 | 0.074 | 2 | 0.56 | 0.036 | 0.052 | 0.068 | 2 | 0.57 |  | 0.073 | 2 | 0.49 |  | 7.98 | 0.068 | 2 | 4.6 | 20.7 | 30 | 55 | 0.036 | 7.66 | 0.07 | 2 | 4.1 | 20.5 | 29 | 50 | 0.029 | 4.2 | 3.7 | 4.2 | [17 empty] | AVERAGE | 9232 | [9 empty] | 438 | 454 | 436 | 536 | 556 | 473 | 474 | 427 | 404 | 920 |  | 1254 | 1256 | 1246 | 90 | 109.6 | 13.4 | 1352 | 268 | 337.6 | 45.2 | 55 | 6.8 | 742 | 143 | 314
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0822 |  | TOTAL AVG COAG ALK: |  |  |  | 11.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.45 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.68 | [5 empty] | 6.1725 |  |  |  |  | 0.074 |  |  |  |  | 0.68 | [6 empty] | 0.074 | [16 empty] | Pump Station MIN |  | 1.8 | [17 empty] | MINIMUM | 8300 | [9 empty] | 400 | 400 | 400 | 480 | 500 | 400 | 400 | 400 | 400 | 800 |  | 1120 | 1120 | 1100 | 80 | 98 | 12 | 1130 | 230 | 320 | 40 | 50 | 6 | 660 | 120 | 300
[90 empty] | MAXIMUM | 10500 | [9 empty] | 480 | 500 | 460 | 600 | 600 | 510 | 520 | 460 | 410 | 1150 |  | 1400 | 1410 | 1400 | 102 | 125 | 15 | 1550 | 310 | 368 | 52 | 60 | 7 | 820 | 165 | 340
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.224 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827707 |  | END: | 23827708 |  |  | Alum | 4905 | 7017 | 7017 | 7044 | 7044 | 0 | [44 empty] | 0.68 | 11.3 | 22.5133 | 15.309 | 6.16 | 20.6 | 7 | 2.187
[73 empty] | FINISHED 2 | 15.664 |  | TOTAL MGD: |  | 11.223 |  |  | FINISHED SOUTH 2 |  | START: | 45052197 |  | END: | 45063420 |  |  | Caustic | 4697 | 7461 | 7461
[73 empty] | TOTAL RAW | 29.5 |  | TOTAL MGD: |  | 5.345 |  |  | FINISHED CONWAY |  | START: | 10722381 |  | END: | 10727726 |  |  | Hypochlorite | 11 |  | 24
[76 empty] | TOTAL MGD: |  | 10.319 |  |  | FINISHED PERRY |  | START: | 34880001 |  | END: | 34890320 |  |  | Phosphate | 3742
[76 empty] | TOTAL MGD: |  | 9.78 |  |  | RAW PLANT 1 |  | START: | 31962217 |  | END: | 31971997 |  |  | Fluoride | 1550 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.744 |  |  | RAW PLANT 2 |  | START: | 31925535 |  | END: | 31935279 |  |  | Cal~Flo | 6.54 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.976 |  |  | RAW PLANT 3 |  | START: | 8560190 |  | END: | 8570166 |  |  | Zinc | 2502
[76 empty] | TOTAL MGD: |  | 0.894 |  |  | DECANT |  | START: | 1950318 |  | END: | 1951212 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.2488 |  |  | BLOW DOWN |  | START: | 9255.4079 |  | END: | 9256.6567 |  |  | NH3 | 7.27 |  | BI-SUL | 1025
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 460
23827708
45063420
10727726
34890320
31971997
31935279
8570166
1951212
9256.6567
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 20
DATE: | 2019-04-20 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-20 | [23 empty] | DATE: | 2019-04-20
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-20 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43575.0021 | 2,3,5 | 40 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | ,1,3 | 8.6026 | 1,2 | 14.5613 | 23.1638 | 1.7555 | 43575.0021 | 74.7879 | 6148.7396 | 0 | 459.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1143 | 2.2256 | 2.0031 | 0.19687 | 0.21476 | 0.16107 | 0.16107 | 0.14318 | 0.16107 | 2.1305 | 6 | 0.071223 | 0.069904 | 0.071223 | 1.092 | 0.53056 | 0.10837 | 3.7923 | 0.68426 | 5.1974 | 1.1494 | 0.54139 | 0.12643 | 4.0164 | 0.74128 | 9.4829 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.16 | 0.295 | 4 | 0.74 | 21.2 | 7.8 | 0.33462 |  | 6.2 | 0.269 | 4 | 0.83 | 21.1 | 8.1 | 0.34288 | 6.23 | 0.305 | 4 | 0.93 | 20.7 | 8.3 | 0.33519 | [13 empty] | 7.64 | 0.059 | 1 | 4 | 20.8 |  |  |  | 7.5 | 0.058 | 1 | 3.8 | 20.6 |  |  |  | 3.7 | 3.3 | 3.6 | [18 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 380 | 400 | 360 | 440 | 480 | 360 | 360 | 320 | 360 | 1120 |  | 1080 | 1060 | 1080 | 76 | 98 | 12 | 1160 | 240 | 285 | 40 | 50 | 7 | 650 | 130 | 260 |  | 1:00 | 0.74 | 7.8 | 32.6154 | 24.1354 | 6.16 | 21.2 | 7 | 3.4479 | 20 | 6.5 | 0.21462 | 1:00 | 0.83 | 8.1 | 31.4074 | 26.0681 | 6.2 | 21.1 | 7 | 3.724 | 20 | 6.5 | 0.22288 | 1:00 | 0.93 | 8.3 | 32.5301 | 30.253 | 6.23 | 20.7 | 7 | 4.3219 | 20 | 6.5 | 0.21519
2:00 | [72 empty] | 43575.3616 | 2,3,5 | 40 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | ,1,3 | 8.6026 | 1,2 | 14.5613 | 23.1638 | 0.0013176 | 43575.3616 | 74.7879 | 5964.2774 | 0 | 428.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2256 | 2.2256 | 2.2256 | 0.23266 | 0.20134 | 0.1566 | 0.1566 | 0.14318 | 0.15212 | 2.1305 | 3 | 0.070564 | 0.069904 | 0.070564 | 1.092 | 0.49808 | 0.10837 | 3.7308 | 0.69567 | 5.1974 | 1.1494 | 0.49808 | 0.10837 | 4.0394 | 0.74128 | 9.4829 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.48 | 17 | 17 | 5.12 | 110 | 143 | 20.4 | 0.451 |  | 6.07 | 11 | 0.086 | 6.02 | 11 |  | 6.02 | 12 | [8 empty] | 0.052 | [14 empty] | 0.063 | 1 | 0.42 |  | 0.051 | 0.053 | 1 | 0.37 |  | 0.048 | 1 | 0.39 | [38 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 400 | 400 | 400 | 520 | 450 | 350 | 350 | 320 | 340 | 1120 |  | 1070 | 1060 | 1070 | 76 | 92 | 12 | 1170 | 244 | 285 | 40 | 46 | 6 | 640 | 130 | 260 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43575.8049 | 2,3,5 | 35 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | ,1,3 | 10.5725 | 1,2 | 13.667 | 24.2395 | 0.0013176 | 43575.8049 | 74.7879 | 5841.3026 | 0 | 428.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1143 | 2.1143 | 1.8918 | 0.19687 | 0.21476 | 0.19687 | 0.14318 | 0.16107 | 0.17897 | 2.1876 | 8 | 0.068585 | 0.068585 | 0.067266 | 1.1207 | 0.53056 | 0.10837 | 3.8011 | 0.71277 | 5.1974 | 1.1494 | 0.54139 | 0.12643 | 3.9834 | 0.76979 | 9.4829 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.58 | 0.058 | 1 | 3.9 | 20.7 |  |  |  | 7.46 | 0.059 | 1 | 3.8 | 20.6 |  |  |  | 4 | 3.2 | 2.7 | [18 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 340 | 440 | 480 | 440 | 320 | 360 | 400 | 1150 |  | 1040 | 1040 | 1020 | 78 | 98 | 12 | 1235 | 250 | 285 | 40 | 50 | 7 | 660 | 135 | 260 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.48 | 20 | 17 | 4.74 | 120 | 144 | 20.6 | 0.469 |  | 6.03 | 10 | 0.081 | 6.02 | 10 |  | 6.01 | 10 | [8 empty] | 0.05 | [14 empty] | 0.053 | 1 | 0.41 |  | 0.05 | 0.034 | 1 | 0.39 |  | 0.041 | 1 | 0.33 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.057 | [9 empty] | 6.11 | 0.337 | 4 | 0.71 | 20 | 10.6 | 0.41167 |  | 6.16 | 0.352 | 4 | 0.64 | 20 | 10.6 | 0.41167 | 6.14 | 0.491 | 5 | 0.77 | 19.9 | 10.6 | 0.51259 |  |  |  | 0.036 | [9 empty] | 7.41 | 0.059 | 2 | 4.3 | 19.9 | 21 | 36 | 0.033 | 7.34 | 0.058 | 2 | 4 | 19.1 | 21 | 39 | 0.031 | 3.9 | 3.3 | 2.8 | [55 empty] | 9:00 | 0.71 | 10.6 | 24 | 17.04 | 6.11 | 20 | 7 | 2.4343 | 20 | 6.5 | 0.29167 | 9:00 | 0.64 | 10.6 | 24 | 15.36 | 6.16 | 20 | 7 | 2.1943 | 20 | 6.5 | 0.29167 | 9:00 | 0.77 | 10.6 | 25.4717 | 19.6132 | 6.14 | 19.9 | 10 | 1.9613 | 15 | 6.5 | 0.39259
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.49 | 20 | 18 | 5.19 | 114 | 144 | 20.4 | 0.468 |  | 6.04 | 10 | 0.084 | 6.02 | 10 |  | 5.98 | 10 | [8 empty] | 0.051 | [14 empty] | 0.05 | 1 | 0.46 |  | 0.05 | 0.041 | 1 | 0.41 |  | 0.043 | 1 | 0.39 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.256 | 4 | 0.7 | 21 | 8.6 | 0.35664 |  | 6.13 | 0.22 | 4 | 0.65 | 21 | 8.6 | 0.35664 | 6.12 | 0.386 | 4 | 0.74 | 20.4 | 8.6 | 0.34296 | [13 empty] | 7.48 | 0.056 | 2 | 4.2 | 20 |  |  |  | 7.31 | 0.054 | 1 | 4 | 20.4 |  |  |  | 4 | 3.2 | 3.6 | [55 empty] | 13:00 | 0.7 | 8.6 | 29.5814 | 20.707 | 6.1 | 21 | 7 | 2.9581 | 20 | 6.5 | 0.23664 | 13:00 | 0.65 | 8.6 | 29.5814 | 19.2279 | 6.13 | 21 | 7 | 2.7468 | 20 | 6.5 | 0.23664 | 13:00 | 0.74 | 8.6 | 31.3953 | 23.2326 | 6.12 | 20.4 | 7 | 3.3189 | 20 | 6.5 | 0.22296
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.51 | 20 | 18 | 5.47 | 110 | 143 | 21.4 | 0.427 |  | 6.05 | 11 | 0.072 | 6.1 | 11 |  | 6.05 | 11 | [8 empty] | 0.049 | [14 empty] | 0.038 | 1 | 0.44 |  | 0.055 | 0.031 | 1 | 0.4 |  | 0.041 | 1 | 0.4 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.4 | 0.054 | 2 | 4.2 | 20 |  |  |  | 7.35 | 0.052 | 1 | 3.9 | 20.8 |  |  |  | 3.9 | 3.4 | 3.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.56 | 19 | 17 | 5.36 | 119 | 148 | 21.1 | 0.456 |  | 6.04 | 10 | 0.071 | 6.02 | 11 |  | 6 | 12 | [8 empty] | 0.048 | [14 empty] | 0.048 | 1 | 0.33 |  | 0.048 | 0.023 | 2 | 0.23 |  | 0.041 | 1 | 0.22 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.033 | [9 empty] | 6.09 | 0.374 | 5 | 0.59 | 20.9 | 8.7 | 0.35939 |  | 6.12 | 0.386 | 5 | 0.52 | 20.7 | 8.6 | 0.35664 | 6.14 | 0.385 | 5 | 0.56 | 20.2 | 8.9 | 0.35074 |  |  |  | 0.01 | [9 empty] | 7.38 | 0.059 | 2 | 3.8 | 20.5 | 22 | 40 | 0.015 | 7.29 | 0.056 | 2 | 3.5 | 20.4 | 23 | 37 | 0.009 | 3.9 | 3.3 | 3.5 | [55 empty] | 21:00 | 0.59 | 8.7 | 29.2414 | 17.2524 | 6.09 | 20.9 | 7 | 2.4646 | 20 | 6.5 | 0.23939 | 21:00 | 0.52 | 8.6 | 29.5814 | 15.3823 | 6.12 | 20.7 | 7 | 2.1975 | 20 | 6.5 | 0.23664 | 21:00 | 0.56 | 8.9 | 30.3371 | 16.9888 | 6.14 | 20.2 | 7 | 2.427 | 20 | 6.5 | 0.23074
22:00 | [72 empty] | DOSE |  | TOTAL | 25.5 | 25.5 | 25.5 | 76.5 | 24 | 24 | 24 | 72 | 0 | 27.7776 | 0 | 42.7896 | 70.5672 | 1.7581 | TOTAL | 224.3636 | 17954.3196 | 0 | 1316.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4543 | 6.5656 | 6.1205 | 0.6264 | 0.63087 | 0.51454 | 0.46085 | 0.44743 | 0.49217 | 6.4486 | 17 | 0.21037 | 0.20839 | 0.20905 | 3.3046 | 1.5592 | 0.3251 | 11.3241 | 2.0927 | 15.5921 | 3.4483 | 1.5809 | 0.36122 | 12.0392 | 2.2524 | 28.4487 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.5 | 18 | 18 | 5.63 | 115 | 150 | 21.1 | 0.434 |  | 6.05 | 12 | 0.079 | 6.07 | 11 |  | 6.05 | 12 | [8 empty] | 0.057 | [14 empty] | 0.047 | 1 | 0.28 |  | 0.049 | 0.035 | 1 | 0.26 |  | 0.047 | 1 | 0.18 | [22 empty] | AVERAGE | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 |  | 9.2592 |  | 14.2632 | 23.5224 | 0.58605 | AVERAGE | 74.7879 | 5984.7732 |  | 438.7665 | 0 | 0 | 0 |  |  |  | 2.1514 | 2.1885 | 2.0402 | 0.2088 | 0.21029 | 0.17151 | 0.15362 | 0.14914 | 0.16406 | 2.1495 | 5.6667 | 0.070124 | 0.069464 | 0.069684 | 1.1015 | 0.51974 | 0.10837 | 3.7747 | 0.69757 | 5.1974 | 1.1494 | 0.52695 | 0.12041 | 4.0131 | 0.75079 | 9.4829 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.02 | 114 | 105 | 31.51 | 688 | 872 | 125 | 2.705 | 0.09 | 36.28 | 64 | 0.473 | 36.25 | 64 | 0 | 36.11 | 67 | 0 | 24.46 | 1.262 | 17 | 2.74 | 83.1 | 35.7 | 1.4623 | 0.307 | 24.61 | 1.227 | 17 | 2.64 | 82.8 | 35.9 | 1.4678 | 24.63 | 1.567 | 18 | 3 | 81.2 | 36.4 | 1.5415 | 0.299 | 6 | 2.34 | 0.046 | 0.303 | 0.217 | 7 | 2.06 | 0 | 0.261 | 6 | 1.91 | 0 | 44.89 | 0.345 | 10 | 24.4 | 121.9 | 43 | 76 | 0.048 | 44.25 | 0.337 | 8 | 23 | 121.9 | 44 | 76 | 0.04 | 23.4 | 19.7 | 19.8 |  |  | MINIMUM | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 |  | 8.6026 |  | 13.667 | 23.1638 | 0.0013176 | MINIMUM | 74.7879 | 5841.3026 |  | 428.1938 | [6 empty] | 2.1143 | 2.1143 | 1.8918 | 0.19687 | 0.20134 | 0.1566 | 0.14318 | 0.14318 | 0.15212 | 2.1305 | 3 | 0.068585 | 0.068585 | 0.067266 | 1.092 | 0.49808 | 0.10837 | 3.7308 | 0.68426 | 5.1974 | 1.1494 | 0.49808 | 0.10837 | 3.9834 | 0.74128 | 9.4829 |  | MIN | 0.71 | 10.6 | 24 | 17.04 | 6.11 | 20 | 7 | 2.4343 |  |  |  | MIN | 0.64 | 10.6 | 24 | 15.36 | 6.16 | 20 | 7 | 2.1943 |  |  |  | MIN | 0.77 | 10.6 | 25.4717 | 19.6132 | 6.14 | 19.9 | 10 | 1.9613 |  |  |  | 1.9613
AVERAGE | 6.5033 | 19 | 17.5 | 5.2517 | 114.6667 | 145.3333 | 20.8333 | 0.45083 | 0.045 | 6.0467 | 10.6667 | 0.078833 | 6.0417 | 10.6667 |  | 6.0183 | 11.1667 |  | 6.115 | 0.3155 | 4.25 | 0.685 | 20.775 | 8.925 | 0.36558 | 0.051167 | 6.1525 | 0.30675 | 4.25 | 0.66 | 20.7 | 8.975 | 0.36695 | 6.1575 | 0.39175 | 4.5 | 0.75 | 20.3 | 9.1 | 0.38537 | 0.049833 | 1 | 0.39 | 0.023 | 0.0505 | 0.036167 | 1.1667 | 0.34333 |  | 0.0435 | 1 | 0.31833 |  | 7.4817 | 0.0575 | 1.6667 | 4.0667 | 20.3167 | 21.5 | 38 | 0.024 | 7.375 | 0.056167 | 1.3333 | 3.8333 | 20.3167 | 22 | 38 | 0.02 | 3.9 | 3.2833 | 3.3 |  |  | MAXIMUM | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 |  | 10.5725 |  | 14.5613 | 24.2395 | 1.7555 | MAXIMUM | 74.7879 | 6148.7396 |  | 459.9119 | [6 empty] | 2.2256 | 2.2256 | 2.2256 | 0.23266 | 0.21476 | 0.19687 | 0.16107 | 0.16107 | 0.17897 | 2.1876 | 8 | 0.071223 | 0.069904 | 0.071223 | 1.1207 | 0.53056 | 0.10837 | 3.8011 | 0.71277 | 5.1974 | 1.1494 | 0.54139 | 0.12643 | 4.0394 | 0.76979 | 9.4829
MINIMUM | 6.48 | 17 | 17 | 4.74 | 110 | 143 | 20.4 | 0.427 | 0.033 | 6.03 | 10 | 0.071 | 6.02 | 10 |  | 5.98 | 10 |  | 6.09 | 0.256 | 4 | 0.59 | 20 | 7.8 | 0.33462 | 0.048 | 6.12 | 0.22 | 4 | 0.52 | 20 | 8.1 | 0.34288 | 6.12 | 0.305 | 4 | 0.56 | 19.9 | 8.3 | 0.33519 | 0.038 | 1 | 0.28 | 0.01 | 0.048 | 0.023 | 1 | 0.23 |  | 0.041 | 1 | 0.18 |  | 7.38 | 0.054 | 1 | 3.8 | 19.9 | 21 | 36 | 0.015 | 7.29 | 0.052 | 1 | 3.5 | 19.1 | 21 | 37 | 0.009 | 3.7 | 3.2 | 2.7 | [15 empty] | MIL/MIN |  | TOTAL | 23400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 1180 | 1100 | 1400 | 1410 | 1150 | 1030 | 1000 | 1100 | 3390 | 0 | 3190 | 3160 | 3170 | 230 | 288 | 36 | 3565 | 734 | 855 | 120 | 146 | 20 | 1950 | 395 | 780
MAXIMUM | 6.56 | 20 | 18 | 5.63 | 120 | 150 | 21.4 | 0.469 | 0.057 | 6.07 | 12 | 0.086 | 6.1 | 11 |  | 6.05 | 12 |  | 6.16 | 0.374 | 5 | 0.74 | 21.2 | 10.6 | 0.41167 | 0.057 | 6.2 | 0.386 | 5 | 0.83 | 21.1 | 10.6 | 0.41167 | 6.23 | 0.491 | 5 | 0.93 | 20.7 | 10.6 | 0.51259 | 0.063 | 1 | 0.46 | 0.036 | 0.055 | 0.053 | 2 | 0.41 |  | 0.048 | 1 | 0.4 |  | 7.64 | 0.059 | 2 | 4.3 | 20.8 | 22 | 40 | 0.033 | 7.5 | 0.059 | 2 | 4 | 20.8 | 23 | 39 | 0.031 | 4 | 3.4 | 3.6 | [17 empty] | AVERAGE | 7800 | [9 empty] | 386.6667 | 393.3333 | 366.6667 | 466.6667 | 470 | 383.3333 | 343.3333 | 333.3333 | 366.6667 | 1130 |  | 1063.3333 | 1053.3333 | 1056.6667 | 76.6667 | 96 | 12 | 1188.3333 | 244.6667 | 285 | 40 | 48.6667 | 6.6667 | 650 | 131.6667 | 260
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0356 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.491 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.52 | [5 empty] | 6.1417 |  |  |  |  | 0.063 |  |  |  |  | 0.52 | [6 empty] | 0.063 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 7800 | [9 empty] | 380 | 380 | 340 | 440 | 450 | 350 | 320 | 320 | 340 | 1120 |  | 1040 | 1040 | 1020 | 76 | 92 | 12 | 1160 | 240 | 285 | 40 | 46 | 6 | 640 | 130 | 260
[90 empty] | MAXIMUM | 7800 | [9 empty] | 400 | 400 | 400 | 520 | 480 | 440 | 360 | 360 | 400 | 1150 |  | 1080 | 1060 | 1080 | 78 | 98 | 12 | 1235 | 250 | 285 | 40 | 50 | 7 | 660 | 135 | 260
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.444 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23827708 |  | END: | 23827714 |  |  | Alum | 4916 | 6220 | 6220 | 6376 | 6376 | 0 | [44 empty] | 0.77 | 10.6 | 25.4717 | 19.6132 | 6.14 | 19.9 | 10 | 1.9613
[73 empty] | FINISHED 2 | 13.312 |  | TOTAL MGD: |  | 10.438 |  |  | FINISHED SOUTH 2 |  | START: | 45063420 |  | END: | 45073858 |  |  | Caustic | 4618 | 7422 | 7422
[73 empty] | TOTAL RAW | 25.901 |  | TOTAL MGD: |  | 4.256 |  |  | FINISHED CONWAY |  | START: | 10727726 |  | END: | 10731982 |  |  | Hypochlorite | 10 |  | 24
[76 empty] | TOTAL MGD: |  | 9.056 |  |  | FINISHED PERRY |  | START: | 34890320 |  | END: | 34899376 |  |  | Phosphate | 3760
[76 empty] | TOTAL MGD: |  | 8.565 |  |  | RAW PLANT 1 |  | START: | 31971997 |  | END: | 31980562 |  |  | Fluoride | 1550 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.542 |  |  | RAW PLANT 2 |  | START: | 31935279 |  | END: | 31943821 |  |  | Cal~Flo | 12.38 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 8.794 |  |  | RAW PLANT 3 |  | START: | 8570166 |  | END: | 8578960 |  |  | Zinc | 2522
[76 empty] | TOTAL MGD: |  | 0.63 |  |  | DECANT |  | START: | 1951212 |  | END: | 1951842 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 1.1688 |  |  | BLOW DOWN |  | START: | 9256.6567 |  | END: | 9257.8255 |  |  | NH3 | 7.08 |  | BI-SUL | 1025
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 428
23827714
45073858
10731982
34899376
31980562
31943821
8578960
1951842
9257.8255
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 21
DATE: | 2019-04-21 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-21 | [23 empty] | DATE: | 2019-04-21
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-21 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43576.0017 | 2,3,5 | 35 | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 | ,1,3 | 10.5725 | 1,2 | 13.667 | 24.2395 | 1.171 | 43576.0017 | 74.7879 | 5841.3026 | 0 | 428.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1143 | 2.1143 | 1.8918 | 0.19687 | 0.21476 | 0.19687 | 0.14318 | 0.16107 | 0.17897 | 2.1876 | 8 | 0.068585 | 0.068585 | 0.067266 | 1.1207 | 0.53056 | 0.10837 | 3.8011 | 0.71277 | 5.1974 | 1.1494 | 0.54139 | 0.12643 | 3.9834 | 0.76979 | 9.4829 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.13 | 0.454 | 5 | 0.44 | 20.6 | 8.4 | 0.35113 |  | 6.17 | 0.41 | 5 | 0.54 | 20.2 | 8.5 | 0.35388 | 6.18 | 0.415 | 5 | 0.64 | 19.9 | 8.7 | 0.44222 | [13 empty] | 7.48 | 0.057 | 2 | 3.9 | 20.4 |  |  |  | 7.37 | 0.056 | 2 | 3.6 | 19.7 |  |  |  | 3.8 | 3.2 | 3.8 | [18 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 340 | 440 | 480 | 440 | 320 | 360 | 400 | 1150 |  | 1040 | 1040 | 1020 | 78 | 98 | 12 | 1235 | 250 | 285 | 40 | 50 | 7 | 660 | 135 | 260 |  | 1:00 | 0.44 | 8.4 | 30.2857 | 13.3257 | 6.13 | 20.6 | 7 | 1.9037 | 20 | 6.5 | 0.23113 | 1:00 | 0.54 | 8.5 | 29.9294 | 16.1619 | 6.17 | 20.2 | 7 | 2.3088 | 20 | 6.5 | 0.23388 | 1:00 | 0.64 | 8.7 | 31.0345 | 19.8621 | 6.18 | 19.9 | 10 | 1.9862 | 15 | 6.5 | 0.32222
2:00 | [72 empty] | 43576.3481 | 2,3,5 | 35 | 9 | 9 | 9 | 27 | 8.5 | 8.5 | 8.5 | 25.5 | ,1,3 | 10.5725 | 1,2 | 13.667 | 24.2395 | 1.3363 | 43576.3481 | 74.6174 | 5533.8656 | 0 | 475.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 1.99 | 1.99 | 1.7805 | 0.20072 | 0.20072 | 0.18593 | 0.17959 | 0.16903 | 0.16903 | 2.1686 | 6 | 0.070137 | 0.070137 | 0.070137 | 1.1089 | 0.49935 | 0.10199 | 3.7952 | 0.71914 | 5.2349 | 1.0818 | 0.50955 | 0.10199 | 4.0036 | 0.77281 | 9.44 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.51 | 18 | 19 | 5.54 | 119 | 150 | 20 | 0.468 |  | 6.11 | 12 | 0.087 | 6.11 | 12 |  | 6.09 | 11 | [8 empty] | 0.056 | [14 empty] | 0.048 | 1 | 0.21 |  | 0.053 | 0.058 | 1 | 0.12 |  | 0.049 | 1 | 0.2 | [38 empty] | 8240 | [6 empty] | 0 | 0 | 0 | 380 | 380 | 340 | 475 | 475 | 440 | 425 | 400 | 400 | 1140 |  | 1130 | 1130 | 1130 | 82 | 98 | 12 | 1310 | 268 | 305 | 40 | 50 | 6 | 705 | 144 | 275 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43576.4712 | 2,3,5 | 50 | 10 | 10 | 10 | 30 | 9.5 | 9.5 | 9.5 | 28.5 | ,1,3 | 10.5725 | 1,2 | 13.667 | 24.2395 | 1.3363 | 43576.4712 | 74.9796 | 6148.7396 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8742 | 1.8742 | 1.7571 | 0.19776 | 0.19776 | 0.17114 | 0.15212 | 0.15212 | 0.15212 | 2.1686 | 0 | 0.070807 | 0.070807 | 0.069418 | 1.1373 | 0.5015 | 0.10646 | 3.8093 | 0.72027 | 4.991 | 1.0889 | 0.51062 | 0.10646 | 4.0615 | 0.76829 | 9.2142 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.58 | 0.059 | 1 | 3.9 | 20.2 |  |  |  | 7.38 | 0.058 | 1 | 3.9 | 19.4 |  |  |  | 3.7 | 3.3 | 2.8 | [18 empty] | 9200 | [6 empty] | 0 | 0 | 0 | 400 | 400 | 375 | 520 | 520 | 450 | 400 | 400 | 400 | 1140 |  | 1275 | 1275 | 1250 | 94 | 110 | 14 | 1470 | 300 | 325 | 45 | 56 | 7 | 800 | 160 | 300 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 20:57 | 2,3,5 | 50 | 10 | 10 | 10 | 30 | 9.5 | 9.5 | 9.5 | 28.5 | ,1,3 | 9.0086 | 1,2 | 16.2965 | 25.3051 | 1.3363 | 43576.9378 | 74.6536 | 6517.664 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8742 | 1.8742 | 1.6868 | 0.19776 | 0.19776 | 0.16734 | 0.16734 | 0.18255 | 0.18255 | 2.1876 | 9 | 0.068863 | 0.068863 | 0.071084 | 1.1131 | 0.5015 | 0.098859 | 3.8014 | 0.72027 | 4.991 | 1.0647 | 0.5015 | 0.10646 | 3.9854 | 0.76829 | 9.2142 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.5 | 20 | 18 | 5.74 | 120 | 150 | 19.8 | 0.48 |  | 5.99 | 12 | 0.088 | 6 | 12 |  | 5.98 | 12 | [8 empty] | 0.054 | [14 empty] | 0.042 | 1 | 0.33 |  | 0.052 | 0.04 | 1 | 0.36 |  | 0.035 | 1 | 0.23 | [38 empty] | 9160 | [6 empty] | 0 | 0 | 0 | 400 | 400 | 360 | 520 | 520 | 440 | 440 | 480 | 480 | 1150 |  | 1240 | 1240 | 1280 | 92 | 110 | 13 | 1475 | 300 | 325 | 44 | 55 | 7 | 780 | 160 | 300 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.054 | [9 empty] | 6.16 | 0.359 | 4 | 0.66 | 19.1 | 9 | 0.47377 |  | 6.17 | 0.391 | 6 | 0.57 | 19.1 | 9 | 0.47377 | 6.16 | 0.471 | 6 | 0.65 | 19.1 | 9 | 0.45333 |  |  |  | 0.029 | [9 empty] | 7.44 | 0.056 | 1 | 4.3 | 19.2 | 21 | 40 | 0.034 | 7.37 | 0.054 | 1 | 4.1 | 18.6 | 21 | 43 | 0.031 | 3.9 | 3.1 | 2.6 | [55 empty] | 9:00 | 0.66 | 9 | 28.2667 | 18.656 | 6.16 | 19.1 | 10 | 1.8656 | 15 | 6.5 | 0.35377 | 9:00 | 0.57 | 9 | 28.2667 | 16.112 | 6.17 | 19.1 | 10 | 1.6112 | 15 | 6.5 | 0.35377 | 9:00 | 0.65 | 9 | 30 | 19.5 | 6.16 | 19.1 | 10 | 1.95 | 15 | 6.5 | 0.33333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 17 | 17 | 6.11 | 124 | 155 | 19.7 | 0.485 |  | 6 | 10 | 0.084 | 6.01 | 10 |  | 5.97 | 10 | [8 empty] | 0.054 | [14 empty] | 0.038 | 1 | 0.3 |  | 0.055 | 0.02 | 1 | 0.31 |  | 0.039 | 1 | 0.25 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.13 | 0.298 | 4 | 0.6 | 20.2 | 10 | 0.39516 |  | 6.08 | 0.269 | 4 | 0.58 | 20.2 | 10 | 0.39516 | 6.03 | 0.369 | 4 | 0.6 | 20 | 10 | 0.37926 | [13 empty] | 7.26 | 0.054 | 1 | 4.2 | 20 |  |  |  | 7.16 | 0.055 | 1 | 4 | 20.5 |  |  |  | 4 | 3 | 3 | [55 empty] | 13:00 | 0.6 | 10 | 25.44 | 15.264 | 6.13 | 20.2 | 7 | 2.1806 | 20 | 6.5 | 0.27516 | 13:00 | 0.58 | 10 | 25.44 | 14.7552 | 6.08 | 20.2 | 7 | 2.1079 | 20 | 6.5 | 0.27516 | 13:00 | 0.6 | 10 | 27 | 16.2 | 6.03 | 20 | 7 | 2.3143 | 20 | 6.5 | 0.25926
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 20 | 18 | 6.24 | 115 | 154 | 20.5 | 0.44 |  | 6.03 | 12 | 0.074 | 6.02 | 12 |  | 6 | 12 | [8 empty] | 0.048 | [14 empty] | 0.035 | 1 | 0.28 |  | 0.05 | 0.04 | 1 | 0.26 |  | 0.052 | 1 | 0.26 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17;00 | [53 empty] | 7.28 | 0.048 | 1 | 4 | 20 |  |  |  | 7.21 | 0.052 | 1 | 3.8 | 20.5 |  |  |  | 3.9 | 3.4 | 3.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.58 | 18 | 16 | 5.98 | 116 | 152 | 20.4 | 0.45 |  | 5.99 | 11 | 0.077 | 5.95 | 11 |  | 5.96 | 10 | [8 empty] | 0.055 | [14 empty] | 0.036 | 2 | 0.17 |  | 0.053 | 0.058 | 2 | 0.35 |  | 0.063 | 2 | 0.24 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.033 | [9 empty] | 6.05 | 0.381 | 5 | 0.54 | 20.2 | 9.7 | 0.3869 |  | 6.07 | 0.352 | 6 | 0.42 | 20.1 | 9.8 | 0.38965 | 6.04 | 0.395 | 5 | 0.59 | 19.4 | 10.1 | 0.49407 |  |  |  | 0.014 | [9 empty] | 7.11 | 0.056 | 2 | 4.4 | 20 | 22 | 37 | 0.019 | 7.23 | 0.058 | 2 | 3.8 | 20.1 | 21 | 35 | 0.014 | 3.8 | 2.9 | 3.6 | [55 empty] | 21:00 | 0.54 | 9.7 | 26.2268 | 14.1625 | 6.05 | 20.2 | 7 | 2.0232 | 20 | 6.5 | 0.2669 | 21:00 | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.07 | 20.1 | 7 | 1.5576 | 20 | 6.5 | 0.26965 | 21:00 | 0.59 | 10.1 | 26.7327 | 15.7723 | 6.04 | 19.4 | 10 | 1.5772 | 15 | 6.5 | 0.37407
22:00 | [72 empty] | DOSE |  | TOTAL | 37.5 | 37.5 | 37.5 | 112.5 | 35.5 | 35.5 | 35.5 | 106.5 | 0 | 40.7261 | 0 | 57.2976 | 98.0237 | 5.18 | TOTAL | 299.0385 | 24041.5718 | 0 | 1887.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8527 | 7.8527 | 7.1162 | 0.79311 | 0.81101 | 0.72128 | 0.64223 | 0.66478 | 0.68267 | 8.7123 | 23 | 0.27839 | 0.27839 | 0.27791 | 4.48 | 2.0329 | 0.41568 | 15.207 | 2.8725 | 20.4143 | 4.3849 | 2.0631 | 0.44134 | 16.0339 | 3.0792 | 37.3512 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.52 | 19 | 17 | 6.1 | 118 | 153 | 20.4 | 0.457 |  | 6.01 | 12 | 0.072 | 6.02 | 11 |  | 5.99 | 11 | [8 empty] | 0.05 | [14 empty] | 0.034 | 2 | 0.25 |  | 0.049 | 0.043 | 1 | 0.42 |  | 0.06 | 1 | 0.25 | [22 empty] | AVERAGE | 9.375 | 9.375 | 9.375 | 28.125 | 8.875 | 8.875 | 8.875 | 26.625 |  | 10.1815 |  | 14.3244 | 24.5059 | 1.295 | AVERAGE | 74.7596 | 6010.393 |  | 471.8062 | 0 | 0 | 0 |  |  |  | 1.9632 | 1.9632 | 1.779 | 0.19828 | 0.20275 | 0.18032 | 0.16056 | 0.16619 | 0.17067 | 2.1781 | 5.75 | 0.069598 | 0.069598 | 0.069476 | 1.12 | 0.50823 | 0.10392 | 3.8018 | 0.71812 | 5.1036 | 1.0962 | 0.51576 | 0.11034 | 4.0085 | 0.7698 | 9.3378 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.15 | 112 | 105 | 35.71 | 712 | 914 | 120.8 | 2.78 | 0.087 | 36.13 | 69 | 0.482 | 36.11 | 68 | 0 | 35.99 | 66 | 0 | 24.47 | 1.492 | 18 | 2.24 | 80.1 | 37.1 | 1.607 | 0.317 | 24.49 | 1.422 | 21 | 2.11 | 79.6 | 37.3 | 1.6125 | 24.41 | 1.65 | 20 | 2.48 | 78.4 | 37.8 | 1.7689 | 0.233 | 8 | 1.54 | 0.043 | 0.312 | 0.259 | 7 |  | 0 | 0.298 | 7 | 1.43 | 0 | 44.15 | 0.33 | 8 | 24.7 | 119.8 | 43 | 77 | 0.053 | 43.72 | 0.333 | 8 | 23.2 | 118.8 | 42 | 78 | 0.045 | 23.1 | 18.9 | 18.9 |  |  | MINIMUM | 8.5 | 8.5 | 8.5 | 25.5 | 8 | 8 | 8 | 24 |  | 9.0086 |  | 13.667 | 24.2395 | 1.171 | MINIMUM | 74.6174 | 5533.8656 |  | 428.1938 | [6 empty] | 1.8742 | 1.8742 | 1.6868 | 0.19687 | 0.19776 | 0.16734 | 0.14318 | 0.15212 | 0.15212 | 2.1686 | 0 | 0.068585 | 0.068585 | 0.067266 | 1.1089 | 0.49935 | 0.098859 | 3.7952 | 0.71277 | 4.991 | 1.0647 | 0.5015 | 0.10199 | 3.9834 | 0.76829 | 9.2142 |  | MIN | 0.66 | 9 | 28.2667 | 18.656 | 6.16 | 19.1 | 10 | 1.8656 |  |  |  | MIN | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.07 | 20.1 | 7 | 1.5576 |  |  |  | MIN | 0.59 | 10.1 | 26.7327 | 15.7723 | 6.04 | 19.4 | 10 | 1.5772 |  |  |  | 1.5576
AVERAGE | 6.525 | 18.6667 | 17.5 | 5.9517 | 118.6667 | 152.3333 | 20.1333 | 0.46333 | 0.0435 | 6.0217 | 11.5 | 0.080333 | 6.0183 | 11.3333 |  | 5.9983 | 11 |  | 6.1175 | 0.373 | 4.5 | 0.56 | 20.025 | 9.275 | 0.40174 | 0.052833 | 6.1225 | 0.3555 | 5.25 | 0.5275 | 19.9 | 9.325 | 0.40312 | 6.1025 | 0.4125 | 5 | 0.62 | 19.6 | 9.45 | 0.44222 | 0.038833 | 1.3333 | 0.25667 | 0.0215 | 0.052 | 0.043167 | 1.1667 |  |  | 0.049667 | 1.1667 | 0.23833 |  | 7.3583 | 0.055 | 1.3333 | 4.1167 | 19.9667 | 21.5 | 38.5 | 0.0265 | 7.2867 | 0.0555 | 1.3333 | 3.8667 | 19.8 | 21 | 39 | 0.0225 | 3.85 | 3.15 | 3.15 |  |  | MAXIMUM | 10 | 10 | 10 | 30 | 9.5 | 9.5 | 9.5 | 28.5 |  | 10.5725 |  | 16.2965 | 25.3051 | 1.3363 | MAXIMUM | 74.9796 | 6517.664 |  | 491.63 | [6 empty] | 2.1143 | 2.1143 | 1.8918 | 0.20072 | 0.21476 | 0.19687 | 0.17959 | 0.18255 | 0.18255 | 2.1876 | 9 | 0.070807 | 0.070807 | 0.071084 | 1.1373 | 0.53056 | 0.10837 | 3.8093 | 0.72027 | 5.2349 | 1.1494 | 0.54139 | 0.12643 | 4.0615 | 0.77281 | 9.4829
MINIMUM | 6.5 | 17 | 16 | 5.54 | 115 | 150 | 19.7 | 0.44 | 0.033 | 5.99 | 10 | 0.072 | 5.95 | 10 |  | 5.96 | 10 |  | 6.05 | 0.298 | 4 | 0.44 | 19.1 | 8.4 | 0.35113 | 0.048 | 6.07 | 0.269 | 4 | 0.42 | 19.1 | 8.5 | 0.35388 | 6.03 | 0.369 | 4 | 0.59 | 19.1 | 8.7 | 0.37926 | 0.034 | 1 | 0.17 | 0.014 | 0.049 | 0.02 | 1 |  |  | 0.035 | 1 | 0.2 |  | 7.11 | 0.048 | 1 | 3.9 | 19.2 | 21 | 37 | 0.019 | 7.16 | 0.052 | 1 | 3.6 | 18.6 | 21 | 35 | 0.014 | 3.7 | 2.9 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 34400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560 | 1560 | 1415 | 1955 | 1995 | 1770 | 1585 | 1640 | 1680 | 4580 | 0 | 4685 | 4685 | 4680 | 346 | 416 | 51 | 5490 | 1118 | 1240 | 169 | 211 | 27 | 2945 | 599 | 1135
MAXIMUM | 6.58 | 20 | 19 | 6.24 | 124 | 155 | 20.5 | 0.485 | 0.054 | 6.11 | 12 | 0.088 | 6.11 | 12 |  | 6.09 | 12 |  | 6.16 | 0.454 | 5 | 0.66 | 20.6 | 10 | 0.47377 | 0.056 | 6.17 | 0.41 | 6 | 0.58 | 20.2 | 10 | 0.47377 | 6.18 | 0.471 | 6 | 0.65 | 20 | 10.1 | 0.49407 | 0.048 | 2 | 0.33 | 0.029 | 0.055 | 0.058 | 2 |  |  | 0.063 | 2 | 0.26 |  | 7.58 | 0.059 | 2 | 4.4 | 20.4 | 22 | 40 | 0.034 | 7.38 | 0.058 | 2 | 4.1 | 20.5 | 21 | 43 | 0.031 | 4 | 3.4 | 3.8 | [17 empty] | AVERAGE | 8600 | [9 empty] | 390 | 390 | 353.75 | 488.75 | 498.75 | 442.5 | 396.25 | 410 | 420 | 1145 |  | 1171.25 | 1171.25 | 1170 | 86.5 | 104 | 12.75 | 1372.5 | 279.5 | 310 | 42.25 | 52.75 | 6.75 | 736.25 | 149.75 | 283.75
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0128 |  | TOTAL AVG COAG ALK: |  |  |  | 11.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.471 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.42 | [5 empty] | 6.1142 |  |  |  |  | 0.063 |  |  |  |  | 0.42 | [6 empty] | 0.063 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 7800 | [9 empty] | 380 | 380 | 340 | 440 | 475 | 440 | 320 | 360 | 400 | 1140 |  | 1040 | 1040 | 1020 | 78 | 98 | 12 | 1235 | 250 | 285 | 40 | 50 | 6 | 660 | 135 | 260
[90 empty] | MAXIMUM | 9200 | [9 empty] | 400 | 400 | 375 | 520 | 520 | 450 | 440 | 480 | 480 | 1150 |  | 1275 | 1275 | 1280 | 94 | 110 | 14 | 1475 | 300 | 325 | 45 | 56 | 7 | 800 | 160 | 300
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.795 |  | TOTAL MGD: |  | 0.01 |  |  | FINISHED SOUTH 1 |  | START: | 23827714 |  | END: | 23827724 |  |  | Alum | 4924 | 5279 | 5279 | 5564 | 5564 | 0 | [44 empty] | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.07 | 20.1 | 7 | 1.5576
[73 empty] | FINISHED 2 | 14.789 |  | TOTAL MGD: |  | 10.785 |  |  | FINISHED SOUTH 2 |  | START: | 45073858 |  | END: | 45084643 |  |  | Caustic | 4501 | 7364 | 7365
[73 empty] | TOTAL RAW | 28.486 |  | TOTAL MGD: |  | 4.489 |  |  | FINISHED CONWAY |  | START: | 10731982 |  | END: | 10736471 |  |  | Hypochlorite | 7.5 |  | 23
[76 empty] | TOTAL MGD: |  | 10.3 |  |  | FINISHED PERRY |  | START: | 34899376 |  | END: | 34909676 |  |  | Phosphate | 3647
[76 empty] | TOTAL MGD: |  | 9.429 |  |  | RAW PLANT 1 |  | START: | 31980562 |  | END: | 31989991 |  |  | Fluoride | 1550 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.411 |  |  | RAW PLANT 2 |  | START: | 31943821 |  | END: | 31953232 |  |  | Cal~Flo | 9.43 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.646 |  |  | RAW PLANT 3 |  | START: | 8578960 |  | END: | 8588606 |  |  | Zinc | 2509
[76 empty] | TOTAL MGD: |  | 0.784 |  |  | DECANT |  | START: | 1951842 |  | END: | 1952626 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 0.89261 |  |  | BLOW DOWN |  | START: | 9257.8255 |  | END: | 9258.7181 |  |  | NH3 | 6.86 |  | BI-SUL | 1025
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 492
23827724
45084643
10736471
34909676
31989991
31953232
8588606
1952626
9258.7181
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 22
DATE: | 2019-04-22 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-22 | [23 empty] | DATE: | 2019-04-22
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-22 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43577.0033 | 2,3,5 | 50 | 10 | 10 | 10 | 30 | 9.5 | 9.5 | 9.5 | 28.5 | ,1,3 | 9.0086 | 1,2 | 16.2965 | 25.3051 | 2.0557 | 43577.0033 | 74.6536 | 6517.664 | 0 | 491.63 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8742 | 1.8742 | 1.6868 | 0.19776 | 0.19776 | 0.16734 | 0.16734 | 0.18255 | 0.18255 | 2.1876 | 9 | 0.068863 | 0.068863 | 0.071084 | 1.1131 | 0.5015 | 0.098859 | 3.8014 | 0.72027 | 4.991 | 1.0647 | 0.5015 | 0.10646 | 3.9854 | 0.76829 | 9.2142 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.371 | 5 | 0.57 | 20.1 | 9.7 | 0.3869 |  | 6.03 | 0.312 | 4 | 0.55 | 19.7 | 9.8 | 0.50522 | 6.05 | 0.345 | 5 | 0.57 | 19.3 | 10 | 0.49037 | [13 empty] | 7.77 | 0.055 | 2 | 4.1 | 19.7 |  |  |  | 7.31 | 0.059 | 1 | 4.3 | 19.3 |  |  |  | 4 | 3.3 | 4.2 | [18 empty] | 9160 | [6 empty] | 0 | 0 | 0 | 400 | 400 | 360 | 520 | 520 | 440 | 440 | 480 | 480 | 1150 |  | 1240 | 1240 | 1280 | 92 | 110 | 13 | 1475 | 300 | 325 | 44 | 55 | 7 | 780 | 160 | 300 |  | 1:00 | 0.57 | 9.7 | 26.2268 | 14.9493 | 6.01 | 20.1 | 7 | 2.1356 | 20 | 6.5 | 0.2669 | 1:00 | 0.55 | 9.8 | 25.9592 | 14.2776 | 6.03 | 19.7 | 10 | 1.4278 | 15 | 6.5 | 0.38522 | 1:00 | 0.57 | 10 | 27 | 15.39 | 6.05 | 19.3 | 10 | 1.539 | 15 | 6.5 | 0.37037
2:00 | [72 empty] | 43577.3063 | 2,3,5 | 50 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | ,1,3 | 9.0086 | 1,2 | 16.2965 | 25.3051 | 1.62 | 43577.3063 | 74.9492 | 6640.6388 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8329 | 1.8329 | 1.9638 | 0.19549 | 0.18838 | 0.17061 | 0.17061 | 0.17061 | 0.17061 | 2.1876 | 7 | 0.069826 | 0.069826 | 0.069826 | 1.1043 | 0.50105 | 0.099158 | 3.7996 | 0.71557 | 5.2921 | 1.1269 | 0.59447 | 0.11332 | 4.0067 | 0.76029 | 9.583 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.49 | 19 | 16 | 5.87 | 124 | 155 | 19.5 | 0.473 |  | 6.1 | 10 | 0.066 | 6.1 | 10 |  | 6.1 | 12 | [8 empty] | 0.057 | [14 empty] | 0.036 | 2 | 0.22 |  | 0.051 | 0.056 | 1 | 0.38 |  | 0.056 | 2 | 0.25 | [38 empty] | 9840 | [6 empty] | 0 | 0 | 0 | 420 | 420 | 450 | 550 | 530 | 480 | 480 | 480 | 480 | 1150 |  | 1350 | 1350 | 1350 | 98 | 118 | 14 | 1565 | 320 | 370 | 50 | 70 | 8 | 840 | 170 | 335 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43577.5287 | 2,3,5 | 50 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | ,1,3 | 9.0086 | 1,2 | 16.2965 | 25.3051 | 1.62 | 43577.5287 | 79.9762 | 6640.6388 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8329 | 1.8329 | 1.9638 | 0.19549 | 0.18838 | 0.17061 | 0.17061 | 0.17061 | 0.17061 | 2.1876 | 7 | 0.069826 | 0.069826 | 0.069826 | 1.1043 | 0.50105 | 0.099158 | 3.7996 | 0.71557 | 5.2921 | 1.1269 | 0.59447 | 0.11332 | 4.0067 | 0.76029 | 9.583 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.25 | 0.055 | 1 | 3.9 | 18.8 |  |  |  | 7.55 | 0.054 | 1 | 4.3 | 18.3 |  |  |  | 3.9 | 3.3 | 2.5 | [18 empty] | 10500 | [6 empty] | 0 | 0 | 0 | 420 | 420 | 450 | 550 | 530 | 480 | 480 | 480 | 480 | 1150 |  | 1350 | 1350 | 1350 | 98 | 118 | 14 | 1565 | 320 | 370 | 50 | 70 | 8 | 840 | 170 | 335 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 20:43 | 2,3,4,6 | 45 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | ,1,3 | 13.5936 | 1,2 | 17.8963 | 31.4899 | 1.62 | 43577.8915 | 82.1089 | 7747.412 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8329 | 2.0074 | 1.7456 | 0.21326 | 0.22748 | 0.18482 | 0.18482 | 0.17061 | 0.15639 | 2.1876 | 10 | 0.068275 | 0.068275 | 0.070344 | 1.1269 | 0.50105 | 0.10624 | 3.8058 | 0.71557 | 5.2921 | 1.1269 | 0.50955 | 0.099158 | 3.9915 | 0.78265 | 9.583 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.51 | 20 | 16 | 5.86 | 124 | 157 | 19.4 | 0.488 |  | 5.94 | 10 | 0.077 | 5.94 | 10 |  | 5.93 | 10 | [8 empty] | 0.055 | [14 empty] | 0.032 | 1 | 0.3 |  | 0.052 | 0.04 | 1 | 0.45 |  | 0.033 | 1 | 0.28 | [38 empty] | 10780 | [6 empty] | 0 | 0 | 0 | 420 | 460 | 400 | 600 | 640 | 520 | 520 | 480 | 440 | 1150 |  | 1320 | 1320 | 1360 | 100 | 118 | 15 | 1570 | 320 | 370 | 50 | 60 | 7 | 850 | 175 | 335 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.091 | [9 empty] | 6.06 | 0.352 | 4 | 0.55 | 18.6 | 10.7 | 0.5406 |  | 6.08 | 0.317 | 5 | 0.49 | 18.6 | 10.7 | 0.5406 | 6.06 | 0.418 | 5 | 0.7 | 18.4 | 10.7 | 0.5163 |  |  |  | 0.059 | [9 empty] | 7.37 | 0.064 | 2 | 4.4 | 18.5 | 25 | 52 | 0.059 | 7.33 | 0.07 | 2 | 4.2 | 18.7 | 23 | 52 | 0.041 | 4.1 | 3.6 | 4.1 | [55 empty] | 9:00 | 0.55 | 10.7 | 23.7757 | 13.0766 | 6.06 | 18.6 | 10 | 1.3077 | 15 | 6.5 | 0.4206 | 9:00 | 0.49 | 10.7 | 23.7757 | 11.6501 | 6.08 | 18.6 | 10 | 1.165 | 15 | 6.5 | 0.4206 | 9:00 | 0.7 | 10.7 | 25.2336 | 17.6636 | 6.06 | 18.4 | 10 | 1.7664 | 15 | 6.5 | 0.3963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 20 | 17 | 5.9 | 130 | 147 | 19.3 | 0.499 |  | 6 | 10 | 0.073 | 6.02 | 10 |  | 5.96 | 10 | [8 empty] | 0.055 | [14 empty] | 0.03 | 1 | 0.27 |  | 0.053 | 0.038 | 1 | 0.29 |  | 0.046 | 1 | 0.28 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.303 | 6 | 0.57 | 20 | 10.7 | 0.41442 |  | 6.08 | 0.269 | 6 | 0.52 | 20 | 10.7 | 0.41442 | 6.1 | 0.409 | 6 | 0.58 | 19.8 | 10.7 | 0.5163 | [13 empty] | 7.33 | 0.06 | 2 | 4.2 | 19 |  |  |  | 7.19 | 0.065 | 2 | 4 | 20 |  |  |  | 3.8 | 3.6 | 4.3 | [55 empty] | 13:00 | 0.57 | 10.7 | 23.7757 | 13.5521 | 6.1 | 20 | 7 | 1.936 | 20 | 6.5 | 0.29442 | 13:00 | 0.52 | 10.7 | 23.7757 | 12.3634 | 6.08 | 20 | 7 | 1.7662 | 20 | 6.5 | 0.29442 | 13:00 | 0.58 | 10.7 | 25.2336 | 14.6355 | 6.1 | 19.8 | 10 | 1.4636 | 15 | 6.5 | 0.3963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.59 | 20 | 18 | 6.21 | 118 | 159 | 20 | 0.455 |  | 6.05 | 11 | 0.075 | 6.07 | 12 |  | 6.01 | 11 | [8 empty] | 0.058 | [14 empty] | 0.031 | 1 | 0.28 |  | 0.062 | 0.042 | 1 | 0.3 |  | 0.038 | 1 | 0.25 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.28 | 0.056 | 2 | 4.2 | 19 |  |  |  | 7.21 | 0.06 | 2 | 3.8 | 20 |  |  |  | 3.8 | 3.7 | 3.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.53 | 21 | 19 | 6.08 | 125 | 158 | 20.3 | 0.484 |  | 5.93 | 10 | 0.07 | 5.91 | 10 |  | 5.89 | 10 | [8 empty] | 0.052 | [14 empty] | 0.03 | 2 | 0.25 |  | 0.048 | 0.036 | 1 | 0.34 |  | 0.041 | 1 | 0.19 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.038 | [9 empty] | 6.01 | 0.391 | 6 | 0.51 | 20.1 | 10.9 | 0.41992 |  | 6.03 | 0.332 | 6 | 0.53 | 20.1 | 10.9 | 0.41992 | 6.08 | 0.3 | 7 | 0.54 | 19.3 | 11.2 | 0.53481 |  |  |  | 0.018 | [9 empty] | 7.1 | 0.057 | 2 | 3.9 | 19.4 | 21 | 45 | 0.022 | 7.17 | 0.054 | 2 | 3.6 | 19.9 | 22 | 41 | 0.017 | 4.2 | 3.4 | 3.8 | [55 empty] | 21:00 | 0.51 | 10.9 | 23.3394 | 11.9031 | 6.01 | 20.1 | 7 | 1.7004 | 20 | 6.5 | 0.29992 | 21:00 | 0.53 | 10.9 | 23.3394 | 12.3699 | 6.03 | 20.1 | 7 | 1.7671 | 20 | 6.5 | 0.29992 | 21:00 | 0.54 | 11.2 | 24.1071 | 13.0179 | 6.08 | 19.3 | 10 | 1.3018 | 15 | 6.5 | 0.41481
22:00 | [72 empty] | DOSE |  | TOTAL | 42.1 | 42.1 | 42.1 | 126.3 | 40.1 | 40.1 | 40.1 | 120.3 | 0 | 40.6195 | 0 | 66.7858 | 107.4053 | 6.9157 | TOTAL | 311.688 | 27546.3536 | 0 | 2061.674 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3728 | 7.5474 | 7.36 | 0.802 | 0.802 | 0.69338 | 0.69338 | 0.69437 | 0.68016 | 8.7503 | 33 | 0.27679 | 0.27679 | 0.28108 | 4.4487 | 2.0047 | 0.40341 | 15.2062 | 2.867 | 20.8674 | 4.4454 | 2.2 | 0.43227 | 15.9903 | 3.0715 | 37.9632 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.51 | 21 | 19 | 6.41 | 127 | 159 | 20.2 | 0.456 |  | 6 | 12 | 0.076 | 6.01 | 12 |  | 5.98 | 11 | [8 empty] | 0.054 | [14 empty] | 0.031 | 2 | 0.27 |  | 0.049 | 0.04 | 2 | 0.4 |  | 0.041 | 1 | 0.24 | [22 empty] | AVERAGE | 10.525 | 10.525 | 10.525 | 31.575 | 10.025 | 10.025 | 10.025 | 30.075 |  | 10.1549 |  | 16.6964 | 26.8513 | 1.7289 | AVERAGE | 77.922 | 6886.5884 |  | 515.4185 | 0 | 0 | 0 |  |  |  | 1.8432 | 1.8868 | 1.84 | 0.2005 | 0.2005 | 0.17334 | 0.17334 | 0.17359 | 0.17004 | 2.1876 | 8.25 | 0.069198 | 0.069198 | 0.07027 | 1.1122 | 0.50116 | 0.10085 | 3.8016 | 0.71674 | 5.2168 | 1.1113 | 0.55 | 0.10807 | 3.9976 | 0.76788 | 9.4908 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.13 | 121 | 105 | 36.33 | 748 | 935 | 118.7 | 2.855 | 0.129 | 36.02 | 63 | 0.437 | 36.05 | 64 | 0 | 35.87 | 64 | 0 | 24.18 | 1.417 | 21 | 2.2 | 78.8 | 42 | 1.7618 | 0.331 | 24.22 | 1.23 | 21 | 2.09 | 78.4 | 42.1 | 1.8802 | 24.29 | 1.472 | 23 | 2.39 | 76.8 | 42.6 | 2.0578 | 0.19 | 9 | 1.59 | 0.077 | 0.315 | 0.252 | 7 | 2.16 | 0 | 0.255 | 7 | 1.49 | 0 | 44.1 | 0.347 | 11 | 24.7 | 114.4 | 46 | 97 | 0.081 | 43.76 | 0.362 | 10 | 24.2 | 116.2 | 45 | 93 | 0.058 | 23.8 | 20.9 | 22.8 |  |  | MINIMUM | 10 | 10 | 10 | 30 | 9.5 | 9.5 | 9.5 | 28.5 |  | 9.0086 |  | 16.2965 | 25.3051 | 1.62 | MINIMUM | 74.6536 | 6517.664 |  | 491.63 | [6 empty] | 1.8329 | 1.8329 | 1.6868 | 0.19549 | 0.18838 | 0.16734 | 0.16734 | 0.17061 | 0.15639 | 2.1876 | 7 | 0.068275 | 0.068275 | 0.069826 | 1.1043 | 0.50105 | 0.098859 | 3.7996 | 0.71557 | 4.991 | 1.0647 | 0.5015 | 0.099158 | 3.9854 | 0.76029 | 9.2142 |  | MIN | 0.55 | 10.7 | 23.7757 | 13.0766 | 6.06 | 18.6 | 10 | 1.3077 |  |  |  | MIN | 0.49 | 10.7 | 23.7757 | 11.6501 | 6.08 | 18.6 | 10 | 1.165 |  |  |  | MIN | 0.54 | 11.2 | 24.1071 | 13.0179 | 6.08 | 19.3 | 10 | 1.3018 |  |  |  | 1.165
AVERAGE | 6.5217 | 20.1667 | 17.5 | 6.055 | 124.6667 | 155.8333 | 19.7833 | 0.47583 | 0.0645 | 6.0033 | 10.5 | 0.072833 | 6.0083 | 10.6667 |  | 5.9783 | 10.6667 |  | 6.045 | 0.35425 | 5.25 | 0.55 | 19.7 | 10.5 | 0.44046 | 0.055167 | 6.055 | 0.3075 | 5.25 | 0.5225 | 19.6 | 10.525 | 0.47004 | 6.0725 | 0.368 | 5.75 | 0.5975 | 19.2 | 10.65 | 0.51444 | 0.031667 | 1.5 | 0.265 | 0.0385 | 0.0525 | 0.042 | 1.1667 | 0.36 |  | 0.0425 | 1.1667 | 0.24833 |  | 7.35 | 0.057833 | 1.8333 | 4.1167 | 19.0667 | 23 | 48.5 | 0.0405 | 7.2933 | 0.060333 | 1.6667 | 4.0333 | 19.3667 | 22.5 | 46.5 | 0.029 | 3.9667 | 3.4833 | 3.8 |  |  | MAXIMUM | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 |  | 13.5936 |  | 17.8963 | 31.4899 | 2.0557 | MAXIMUM | 82.1089 | 7747.412 |  | 523.348 | [6 empty] | 1.8742 | 2.0074 | 1.9638 | 0.21326 | 0.22748 | 0.18482 | 0.18482 | 0.18255 | 0.18255 | 2.1876 | 10 | 0.069826 | 0.069826 | 0.071084 | 1.1269 | 0.5015 | 0.10624 | 3.8058 | 0.72027 | 5.2921 | 1.1269 | 0.59447 | 0.11332 | 4.0067 | 0.78265 | 9.583
MINIMUM | 6.49 | 19 | 16 | 5.86 | 118 | 147 | 19.3 | 0.455 | 0.038 | 5.93 | 10 | 0.066 | 5.91 | 10 |  | 5.89 | 10 |  | 6.01 | 0.303 | 4 | 0.51 | 18.6 | 9.7 | 0.3869 | 0.052 | 6.03 | 0.269 | 4 | 0.49 | 18.6 | 9.8 | 0.41442 | 6.05 | 0.3 | 5 | 0.54 | 18.4 | 10 | 0.49037 | 0.03 | 1 | 0.22 | 0.018 | 0.048 | 0.036 | 1 | 0.29 |  | 0.033 | 1 | 0.19 |  | 7.1 | 0.055 | 1 | 3.9 | 18.5 | 21 | 45 | 0.022 | 7.17 | 0.054 | 1 | 3.6 | 18.3 | 22 | 41 | 0.017 | 3.8 | 3.3 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 40280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1660 | 1700 | 1660 | 2220 | 2220 | 1920 | 1920 | 1920 | 1880 | 4600 | 0 | 5260 | 5260 | 5340 | 388 | 464 | 56 | 6175 | 1260 | 1435 | 194 | 255 | 30 | 3310 | 675 | 1305
MAXIMUM | 6.59 | 21 | 19 | 6.41 | 130 | 159 | 20.3 | 0.499 | 0.091 | 6.1 | 12 | 0.077 | 6.1 | 12 |  | 6.1 | 12 |  | 6.1 | 0.391 | 6 | 0.57 | 20.1 | 10.9 | 0.5406 | 0.058 | 6.08 | 0.332 | 6 | 0.55 | 20.1 | 10.9 | 0.5406 | 6.1 | 0.418 | 7 | 0.7 | 19.8 | 11.2 | 0.53481 | 0.036 | 2 | 0.3 | 0.059 | 0.062 | 0.056 | 2 | 0.45 |  | 0.056 | 2 | 0.28 |  | 7.77 | 0.064 | 2 | 4.4 | 19.7 | 25 | 52 | 0.059 | 7.55 | 0.07 | 2 | 4.3 | 20 | 23 | 52 | 0.041 | 4.2 | 3.7 | 4.3 | [17 empty] | AVERAGE | 10070 | [9 empty] | 415 | 425 | 415 | 555 | 555 | 480 | 480 | 480 | 470 | 1150 |  | 1315 | 1315 | 1335 | 97 | 116 | 14 | 1543.75 | 315 | 358.75 | 48.5 | 63.75 | 7.5 | 827.5 | 168.75 | 326.25
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9967 |  | TOTAL AVG COAG ALK: |  |  |  | 10.6111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.418 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.49 | [5 empty] | 6.0575 |  |  |  |  | 0.056 |  |  |  |  | 0.49 | [6 empty] | 0.056 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 9160 | [9 empty] | 400 | 400 | 360 | 520 | 520 | 440 | 440 | 480 | 440 | 1150 |  | 1240 | 1240 | 1280 | 92 | 110 | 13 | 1475 | 300 | 325 | 44 | 55 | 7 | 780 | 160 | 300
[90 empty] | MAXIMUM | 10780 | [9 empty] | 420 | 460 | 450 | 600 | 640 | 520 | 520 | 480 | 480 | 1150 |  | 1350 | 1350 | 1360 | 100 | 118 | 15 | 1570 | 320 | 370 | 50 | 70 | 8 | 850 | 175 | 335
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.613 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23827724 |  | END: | 23827733 |  |  | Alum | 4889 | 6631 | 6631 | 4715 | 4715 | 0 | [44 empty] | 0.49 | 10.7 | 23.7757 | 11.6501 | 6.08 | 18.6 | 10 | 1.165
[73 empty] | FINISHED 2 | 16.191 |  | TOTAL MGD: |  | 12.604 |  |  | FINISHED SOUTH 2 |  | START: | 45084643 |  | END: | 45097247 |  |  | Caustic | 4387 | 7365 | 7365
[73 empty] | TOTAL RAW | 30.993 |  | TOTAL MGD: |  | 4.92 |  |  | FINISHED CONWAY |  | START: | 10736471 |  | END: | 10741391 |  |  | Hypochlorite | 6 |  | 23
[76 empty] | TOTAL MGD: |  | 11.271 |  |  | FINISHED PERRY |  | START: | 34909676 |  | END: | 34920947 |  |  | Phosphate | 3549
[76 empty] | TOTAL MGD: |  | 10.241 |  |  | RAW PLANT 1 |  | START: | 31989991 |  | END: | 32000232 |  |  | Fluoride | 1550 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.227 |  |  | RAW PLANT 2 |  | START: | 31953232 |  | END: | 31963459 |  |  | Cal~Flo | 6.19 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.525 |  |  | RAW PLANT 3 |  | START: | 8588606 |  | END: | 8599131 |  |  | Zinc | 2465
[76 empty] | TOTAL MGD: |  | 0.842 |  |  | DECANT |  | START: | 1952626 |  | END: | 1953468 |  |  | Polymer | 22
[76 empty] | TOTAL MGD: |  | 0.90338 |  |  | BLOW DOWN |  | START: | 9258.7181 |  | END: | 9259.6215 |  |  | NH3 | 6.61 |  | BI-SUL | 1010
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 523
23827733
45097247
10741391
34920947
32000232
31963459
8599131
1953468
9259.6215
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 23
DATE: | 2019-04-23 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-23 | [23 empty] | DATE: | 2019-04-23
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-23 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43578.0014 | 2,3,4,6 | 45 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | ,1,3 | 13.5936 | 1,2 | 17.8963 | 31.4899 | 1.5 | 43578.0014 | 82.1089 | 7747.412 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8329 | 2.0074 | 1.7456 | 0.21326 | 0.22748 | 0.18482 | 0.18482 | 0.17061 | 0.15639 | 2.1876 | 10 | 0.068275 | 0.068275 | 0.070344 | 1.1269 | 0.50105 | 0.10624 | 3.8058 | 0.71557 | 5.2921 | 1.1269 | 0.50955 | 0.099158 | 3.9915 | 0.78265 | 9.583 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.03 | 0.361 | 6 | 0.52 | 19.9 | 10.6 | 0.53667 |  | 6.07 | 0.388 | 6 | 0.51 | 19.8 | 10.6 | 0.53667 | 6.13 | 0.303 | 6 | 0.71 | 19.2 | 10.7 | 0.5163 | [13 empty] | 7.28 | 0.056 | 2 | 3.8 | 19.4 |  |  |  | 7.3 | 0.054 | 2 | 3.3 | 19.4 |  |  |  | 4.1 | 3.6 | 4.3 | [18 empty] | 10780 | [6 empty] | 0 | 0 | 0 | 420 | 460 | 400 | 600 | 640 | 520 | 520 | 480 | 440 | 1150 |  | 1320 | 1320 | 1360 | 100 | 118 | 15 | 1570 | 320 | 370 | 50 | 60 | 7 | 850 | 175 | 335 |  | 1:00 | 0.52 | 10.6 | 24 | 12.48 | 6.03 | 19.9 | 10 | 1.248 | 15 | 6.5 | 0.41667 | 1:00 | 0.51 | 10.6 | 24 | 12.24 | 6.07 | 19.8 | 10 | 1.224 | 15 | 6.5 | 0.41667 | 1:00 | 0.71 | 10.7 | 25.2336 | 17.9159 | 6.13 | 19.2 | 10 | 1.7916 | 15 | 6.5 | 0.3963
2:00 | [72 empty] | 43578.3288 | 2,3,4,6 | 45 | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 | ,1,3 | 13.5936 | 1,2 | 17.8963 | 31.4899 | 1.4544 | 43578.3288 | 79.9762 | 8054.849 | 0 | 523.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8329 | 1.9201 | 1.9638 | 0.21326 | 0.22037 | 0.18482 | 0.18482 | 0.15639 | 0.15639 | 2.1876 | 9 | 0.069826 | 0.069826 | 0.069826 | 1.0818 | 0.50105 | 0.099158 | 3.8089 | 0.69321 | 5.2921 | 1.1269 | 0.50955 | 0.11332 | 4.0215 | 0.76923 | 9.583 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.55 | 19 | 18 | 6.28 | 126 | 162 | 19.4 | 0.483 |  | 6.01 | 8 | 0.075 | 6.01 | 9 |  | 5.99 | 9 | [8 empty] | 0.053 | [14 empty] | 0.031 | 2 | 0.37 |  | 0.05 | 0.053 | 1 | 0.45 |  | 0.039 | 1 | 0.24 | [38 empty] | 10500 | [6 empty] | 0 | 0 | 0 | 420 | 440 | 450 | 600 | 620 | 520 | 520 | 440 | 440 | 1150 |  | 1350 | 1350 | 1350 | 96 | 118 | 14 | 1520 | 310 | 370 | 50 | 60 | 8 | 850 | 172 | 335 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43578.5078 | 2,3,4,6 | 55 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 13.5936 | 1,2 | 17.8963 | 31.4899 | 1.4544 | 43578.5078 | 80.803 | 8120 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7487 | 1.7487 | 1.9872 | 0.21128 | 0.20153 | 0.16903 | 0.16903 | 0.15603 | 0.15603 | 2.1686 | 0 | 0.069716 | 0.069716 | 0.070658 | 1.1289 | 0.50272 | 0.090304 | 3.8109 | 0.69241 | 5.1453 | 1.1084 | 0.50272 | 0.090304 | 4.0079 | 0.77387 | 9.1182 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.17 | 0.052 | 2 | 3.9 | 19.3 |  |  |  | 7.19 | 0.053 | 2 | 3.2 | 19.3 |  |  |  | 3.9 | 3.6 | 4.1 | [18 empty] | 11600 | [6 empty] | 0 | 0 | 0 | 440 | 440 | 500 | 650 | 620 | 520 | 520 | 480 | 480 | 1140 |  | 1480 | 1480 | 1500 | 110 | 130 | 14 | 1670 | 340 | 395 | 54 | 65 | 7 | 930 | 190 | 350 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43578.8385 | 2,3,4,6 | 52 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 15.2496 | 1,2 | 15.7306 | 30.9802 | 1.4544 | 43578.8385 | 81.9175 | 8239.3112 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8282 | 1.9872 | 1.7487 | 0.22104 | 0.23404 | 0.16903 | 0.20803 | 0.16903 | 0.16903 | 2.1876 | 6 | 0.069716 | 0.069716 | 0.069716 | 1.1084 | 0.49885 | 0.1032 | 3.7978 | 0.71277 | 5.1453 | 1.0673 | 0.54139 | 0.1032 | 4.0086 | 0.77387 | 9.1182 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.53 | 22 | 19 | 6.11 | 130 | 164 | 19.1 | 0.503 |  | 6 | 13 | 0.077 | 6.02 | 13 |  | 6.02 | 12 | [8 empty] | 0.052 | [14 empty] | 0.028 | 1 | 0.31 |  | 0.05 | 0.054 | 1 | 0.46 |  | 0.031 | 1 | 0.28 | [38 empty] | 11760 | [6 empty] | 0 | 0 | 0 | 460 | 500 | 440 | 680 | 720 | 520 | 640 | 520 | 520 | 1150 |  | 1480 | 1480 | 1480 | 108 | 129 | 16 | 1720 | 350 | 395 | 52 | 70 | 8 | 940 | 190 | 350 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.074 | [9 empty] | 6.08 | 0.415 | 5 | 0.47 | 18.8 | 10.7 | 0.5406 |  | 6.11 | 0.492 | 5 | 0.63 | 18.8 | 10.7 | 0.5406 | 6.13 | 0.433 | 5 | 0.61 | 18.6 | 10.7 | 0.5163 |  |  |  | 0.029 | [9 empty] | 7.29 | 0.06 | 2 | 4.3 | 18.3 | 26 | 50 | 0.033 | 7.23 | 0.066 | 2 | 4.1 | 18.9 | 24 | 57 | 0.027 | 4.1 | 3.5 | 3.7 | [55 empty] | 9:00 | 0.47 | 10.7 | 23.7757 | 11.1746 | 6.08 | 18.8 | 10 | 1.1175 | 15 | 6.5 | 0.4206 | 9:00 | 0.63 | 10.7 | 23.7757 | 14.9787 | 6.11 | 18.8 | 10 | 1.4979 | 15 | 6.5 | 0.4206 | 9:00 | 0.61 | 10.7 | 25.2336 | 15.3925 | 6.13 | 18.6 | 10 | 1.5393 | 15 | 6.5 | 0.3963
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.49 | 16 | 17 | 6.42 | 129 | 163 | 19.3 | 0.505 |  | 6.02 | 10 | 0.075 | 6.05 | 10 |  | 6.04 | 10 | [8 empty] | 0.055 | [14 empty] | 0.029 | 1 | 0.33 |  | 0.055 | 0.038 | 1 | 0.4 |  | 0.046 | 1 | 0.24 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.05 | 0.335 | 6 | 0.5 | 20.2 | 11.7 | 0.44193 |  | 6.12 | 0.254 | 6 | 0.62 | 20.2 | 11.7 | 0.44193 | 6.15 | 0.458 | 6 | 0.6 | 19.4 | 11.7 | 0.55333 | [13 empty] | 7.18 | 0.056 | 2 | 4.2 | 19 |  |  |  | 7.26 | 0.06 | 2 | 4 | 20.3 |  |  |  | 4 | 3.4 | 4.2 | [55 empty] | 13:00 | 0.5 | 11.7 | 21.7436 | 10.8718 | 6.05 | 20.2 | 7 | 1.5531 | 20 | 6.5 | 0.32193 | 13:00 | 0.62 | 11.7 | 21.7436 | 13.481 | 6.12 | 20.2 | 7 | 1.9259 | 20 | 6.5 | 0.32193 | 13:00 | 0.6 | 11.7 | 23.0769 | 13.8462 | 6.15 | 19.4 | 10 | 1.3846 | 15 | 6.5 | 0.43333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.55 | 20 | 18 | 6.58 | 125 | 164 | 20 | 0.463 |  | 6.03 | 11 | 0.072 | 6.07 | 11 |  | 6.02 | 11 | [8 empty] | 0.05 | [14 empty] | 0.027 | 1 | 0.32 |  | 0.055 | 0.031 | 1 | 0.42 |  | 0.041 | 1 | 0.28 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.21 | 0.058 | 2 | 4 | 19 |  |  |  | 7.25 | 0.055 | 2 | 4.2 | 20.4 |  |  |  | 3.9 | 3.5 | 4.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.53 | 21 | 17 | 5.6 | 129 | 162 | 20.1 | 0.477 |  | 6.08 | 12 | 0.068 | 6.11 | 12 |  | 6.05 | 12 | [8 empty] | 0.046 | [14 empty] | 0.03 | 2 | 0.26 |  | 0.063 | 0.056 | 2 | 0.33 |  | 0.042 | 2 | 0.18 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.041 | [9 empty] | 6.11 | 0.42 | 6 | 0.48 | 20.4 | 11.7 | 0.44193 |  | 6.13 | 0.405 | 6 | 0.5 | 20.4 | 11.8 | 0.44469 | 6.18 | 0.439 | 7 | 0.59 | 19.7 | 11.9 | 0.56074 |  |  |  | 0.014 | [9 empty] | 7.25 | 0.057 | 2 | 4.2 | 19.7 | 22 | 40 | 0.016 | 7.3 | 0.062 | 2 | 3.7 | 20.3 | 23 | 49 | 0.014 | 3.9 | 3.6 | 5 | [55 empty] | 21:00 | 0.48 | 11.7 | 21.7436 | 10.4369 | 6.11 | 20.4 | 7 | 1.491 | 20 | 6.5 | 0.32193 | 21:00 | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.13 | 20.4 | 7 | 1.54 | 20 | 6.5 | 0.32469 | 21:00 | 0.59 | 11.9 | 22.6891 | 13.3866 | 6.18 | 19.7 | 10 | 1.3387 | 15 | 6.5 | 0.44074
22:00 | [72 empty] | DOSE |  | TOTAL | 44.8 | 44.8 | 44.8 | 134.4 | 42.8 | 42.8 | 42.8 | 128.4 | 0 | 56.0304 | 0 | 69.4195 | 125.4499 | 5.8632 | TOTAL | 324.8057 | 32161.5722 | 0 | 2188.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2426 | 7.6635 | 7.4453 | 0.85884 | 0.88342 | 0.70771 | 0.74671 | 0.65205 | 0.63783 | 8.7313 | 25 | 0.27753 | 0.27753 | 0.28054 | 4.446 | 2.0037 | 0.39891 | 15.2234 | 2.814 | 20.8748 | 4.4295 | 2.0632 | 0.40599 | 16.0294 | 3.0996 | 37.4024 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.5 | 19 | 18 | 6.48 | 132 | 160 | 20.4 | 0.471 |  | 6 | 12 | 0.057 | 5.96 | 11 |  | 5.95 | 12 | [8 empty] | 0.042 | [14 empty] | 0.029 | 2 | 0.22 |  | 0.05 | 0.037 | 2 | 0.31 |  | 0.041 | 2 | 0.17 | [22 empty] | AVERAGE | 11.2 | 11.2 | 11.2 | 33.6 | 10.7 | 10.7 | 10.7 | 32.1 |  | 14.0076 |  | 17.3549 | 31.3625 | 1.4658 | AVERAGE | 81.2014 | 8040.393 |  | 547.1366 | 0 | 0 | 0 |  |  |  | 1.8107 | 1.9159 | 1.8613 | 0.21471 | 0.22085 | 0.17693 | 0.18668 | 0.16301 | 0.15946 | 2.1828 | 6.25 | 0.069383 | 0.069383 | 0.070136 | 1.1115 | 0.50092 | 0.099727 | 3.8059 | 0.70349 | 5.2187 | 1.1074 | 0.5158 | 0.1015 | 4.0073 | 0.7749 | 9.3506 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.15 | 117 | 107 | 37.47 | 771 | 975 | 118.3 | 2.902 | 0.115 | 36.14 | 66 | 0.424 | 36.22 | 66 | 0 | 36.07 | 66 | 0 | 24.27 | 1.531 | 23 | 1.97 | 79.3 | 44.7 | 1.9611 | 0.298 | 24.43 | 1.539 | 23 | 2.26 | 79.2 | 44.8 | 1.9639 | 24.59 | 1.633 | 24 | 2.51 | 76.9 | 45 | 2.1467 | 0.174 | 9 | 1.81 | 0.043 | 0.323 | 0.269 | 8 | 2.37 | 0 | 0.24 | 8 | 1.39 | 0 | 43.38 | 0.339 | 12 | 24.4 | 114.7 | 48 | 90 | 0.049 | 43.53 | 0.35 | 12 | 22.5 | 118.6 | 47 | 106 | 0.041 | 23.9 | 21.2 | 25.6 |  |  | MINIMUM | 10.7 | 10.7 | 10.7 | 32.1 | 10.2 | 10.2 | 10.2 | 30.6 |  | 13.5936 |  | 15.7306 | 30.9802 | 1.4544 | MINIMUM | 79.9762 | 7747.412 |  | 523.348 | [6 empty] | 1.7487 | 1.7487 | 1.7456 | 0.21128 | 0.20153 | 0.16903 | 0.16903 | 0.15603 | 0.15603 | 2.1686 | 0 | 0.068275 | 0.068275 | 0.069716 | 1.0818 | 0.49885 | 0.090304 | 3.7978 | 0.69241 | 5.1453 | 1.0673 | 0.50272 | 0.090304 | 3.9915 | 0.76923 | 9.1182 |  | MIN | 0.47 | 10.7 | 23.7757 | 11.1746 | 6.08 | 18.8 | 10 | 1.1175 |  |  |  | MIN | 0.51 | 10.6 | 24 | 12.24 | 6.07 | 19.8 | 10 | 1.224 |  |  |  | MIN | 0.59 | 11.9 | 22.6891 | 13.3866 | 6.18 | 19.7 | 10 | 1.3387 |  |  |  | 1.1175
AVERAGE | 6.525 | 19.5 | 17.8333 | 6.245 | 128.5 | 162.5 | 19.7167 | 0.48367 | 0.0575 | 6.0233 | 11 | 0.070667 | 6.0367 | 11 |  | 6.0117 | 11 |  | 6.0675 | 0.38275 | 5.75 | 0.4925 | 19.825 | 11.175 | 0.49028 | 0.049667 | 6.1075 | 0.38475 | 5.75 | 0.565 | 19.8 | 11.2 | 0.49097 | 6.1475 | 0.40825 | 6 | 0.6275 | 19.225 | 11.25 | 0.53667 | 0.029 | 1.5 | 0.30167 | 0.0215 | 0.053833 | 0.044833 | 1.3333 | 0.395 |  | 0.04 | 1.3333 | 0.23167 |  | 7.23 | 0.0565 | 2 | 4.0667 | 19.1167 | 24 | 45 | 0.0245 | 7.255 | 0.058333 | 2 | 3.75 | 19.7667 | 23.5 | 53 | 0.0205 | 3.9833 | 3.5333 | 4.2667 |  |  | MAXIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 15.2496 |  | 17.8963 | 31.4899 | 1.5 | MAXIMUM | 82.1089 | 8239.3112 |  | 570.9251 | [6 empty] | 1.8329 | 2.0074 | 1.9872 | 0.22104 | 0.23404 | 0.18482 | 0.20803 | 0.17061 | 0.16903 | 2.1876 | 10 | 0.069826 | 0.069826 | 0.070658 | 1.1289 | 0.50272 | 0.10624 | 3.8109 | 0.71557 | 5.2921 | 1.1269 | 0.54139 | 0.11332 | 4.0215 | 0.78265 | 9.583
MINIMUM | 6.49 | 16 | 17 | 5.6 | 125 | 160 | 19.1 | 0.463 | 0.041 | 6 | 8 | 0.057 | 5.96 | 9 |  | 5.95 | 9 |  | 6.03 | 0.335 | 5 | 0.47 | 18.8 | 10.6 | 0.44193 | 0.042 | 6.07 | 0.254 | 5 | 0.5 | 18.8 | 10.6 | 0.44193 | 6.13 | 0.303 | 5 | 0.59 | 18.6 | 10.7 | 0.5163 | 0.027 | 1 | 0.22 | 0.014 | 0.05 | 0.031 | 1 | 0.31 |  | 0.031 | 1 | 0.17 |  | 7.17 | 0.052 | 2 | 3.8 | 18.3 | 22 | 40 | 0.016 | 7.19 | 0.053 | 2 | 3.2 | 18.9 | 23 | 49 | 0.014 | 3.9 | 3.4 | 3.7 | [15 empty] | MIL/MIN |  | TOTAL | 44640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1740 | 1840 | 1790 | 2530 | 2600 | 2080 | 2200 | 1920 | 1880 | 4590 | 0 | 5630 | 5630 | 5690 | 414 | 495 | 59 | 6480 | 1320 | 1530 | 206 | 255 | 30 | 3570 | 727 | 1370
MAXIMUM | 6.55 | 22 | 19 | 6.58 | 132 | 164 | 20.4 | 0.505 | 0.074 | 6.08 | 13 | 0.077 | 6.11 | 13 |  | 6.05 | 12 |  | 6.11 | 0.42 | 6 | 0.52 | 20.4 | 11.7 | 0.5406 | 0.055 | 6.13 | 0.492 | 6 | 0.63 | 20.4 | 11.8 | 0.5406 | 6.18 | 0.458 | 7 | 0.71 | 19.7 | 11.9 | 0.56074 | 0.031 | 2 | 0.37 | 0.029 | 0.063 | 0.056 | 2 | 0.46 |  | 0.046 | 2 | 0.28 |  | 7.29 | 0.06 | 2 | 4.3 | 19.7 | 26 | 50 | 0.033 | 7.3 | 0.066 | 2 | 4.2 | 20.4 | 24 | 57 | 0.027 | 4.1 | 3.6 | 5 | [17 empty] | AVERAGE | 11160 | [9 empty] | 435 | 460 | 447.5 | 632.5 | 650 | 520 | 550 | 480 | 470 | 1147.5 |  | 1407.5 | 1407.5 | 1422.5 | 103.5 | 123.75 | 14.75 | 1620 | 330 | 382.5 | 51.5 | 63.75 | 7.5 | 892.5 | 181.75 | 342.5
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0239 |  | TOTAL AVG COAG ALK: |  |  |  | 11 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.492 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.1075 |  |  |  |  | 0.056 |  |  |  |  | 0.47 | [6 empty] | 0.056 | [16 empty] | Pump Station MIN |  | 3.4 | [17 empty] | MINIMUM | 10500 | [9 empty] | 420 | 440 | 400 | 600 | 620 | 520 | 520 | 440 | 440 | 1140 |  | 1320 | 1320 | 1350 | 96 | 118 | 14 | 1520 | 310 | 370 | 50 | 60 | 7 | 850 | 172 | 335
[90 empty] | MAXIMUM | 11760 | [9 empty] | 460 | 500 | 500 | 680 | 720 | 520 | 640 | 520 | 520 | 1150 |  | 1480 | 1480 | 1500 | 110 | 130 | 16 | 1720 | 350 | 395 | 54 | 70 | 8 | 940 | 190 | 350
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.79 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23827733 |  | END: | 23827739 |  |  | Alum | 4874 | 5461 | 5461 | 6145 | 6145 | 0 | [44 empty] | 0.47 | 10.7 | 23.7757 | 11.1746 | 6.08 | 18.8 | 10 | 1.1175
[73 empty] | FINISHED 2 | 17.2 |  | TOTAL MGD: |  | 13.784 |  |  | FINISHED SOUTH 2 |  | START: | 45097247 |  | END: | 45111031 |  |  | Caustic | 4210 | 7301 | 7301
[73 empty] | TOTAL RAW | 33.817 |  | TOTAL MGD: |  | 4.871 |  |  | FINISHED CONWAY |  | START: | 10741391 |  | END: | 10746262 |  |  | Hypochlorite | 12 |  | 11
[76 empty] | TOTAL MGD: |  | 12.329 |  |  | FINISHED PERRY |  | START: | 34920947 |  | END: | 34933276 |  |  | Phosphate | 3447
[76 empty] | TOTAL MGD: |  | 11.189 |  |  | RAW PLANT 1 |  | START: | 32000232 |  | END: | 32011421 |  |  | Fluoride | 1300 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.182 |  |  | RAW PLANT 2 |  | START: | 31963459 |  | END: | 31974641 |  |  | Cal~Flo | 11 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.446 |  |  | RAW PLANT 3 |  | START: | 8599131 |  | END: | 8610577 |  |  | Zinc | 2450
[76 empty] | TOTAL MGD: |  | 0.565 |  |  | DECANT |  | START: | 1953468 |  | END: | 1954033 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.0098 |  |  | BLOW DOWN |  | START: | 9259.6215 |  | END: | 9260.6312 |  |  | NH3 | 6.39 |  | BI-SUL | 1010
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 571
23827739
45111031
10746262
34933276
32011421
31974641
8610577
1954033
9260.6312
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 24
DATE: | 2019-04-24 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-24 | [23 empty] | DATE: | 2019-04-24
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-24 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43579.0016 | 2,3,4,6 | 52 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 15.2496 | 1,2 | 15.7306 | 30.9802 | 1.8888 | 43579.0016 | 81.9175 | 8239.3112 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8282 | 1.9872 | 1.7487 | 0.22104 | 0.23404 | 0.16903 | 0.20803 | 0.16903 | 0.16903 | 2.1876 | 6 | 0.069716 | 0.069716 | 0.069716 | 1.1084 | 0.49885 | 0.1032 | 3.7978 | 0.71277 | 5.1453 | 1.0673 | 0.54139 | 0.1032 | 4.0086 | 0.77387 | 9.1182 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.327 | 5 | 0.49 | 20.1 | 11.6 | 0.43918 |  | 6.04 | 0.371 | 6 | 0.52 | 20.2 | 11.6 | 0.43918 | 6.09 | 0.386 | 6 | 0.71 | 19.6 | 11.9 | 0.56074 | [13 empty] | 7.18 | 0.056 | 2 | 4.2 | 19.7 |  |  |  | 7.23 | 0.06 | 2 | 4.1 | 19.9 |  |  |  | 3.9 | 2.9 | 3.9 | [18 empty] | 11760 | [6 empty] | 0 | 0 | 0 | 460 | 500 | 440 | 680 | 720 | 520 | 640 | 520 | 520 | 1150 |  | 1480 | 1480 | 1480 | 108 | 129 | 16 | 1720 | 350 | 395 | 52 | 70 | 8 | 940 | 190 | 350 |  | 1:00 | 0.49 | 11.6 | 21.931 | 10.7462 | 6.01 | 20.1 | 7 | 1.5352 | 20 | 6.5 | 0.31918 | 1:00 | 0.52 | 11.6 | 21.931 | 11.4041 | 6.04 | 20.2 | 7 | 1.6292 | 20 | 6.5 | 0.31918 | 1:00 | 0.71 | 11.9 | 22.6891 | 16.1092 | 6.09 | 19.6 | 10 | 1.6109 | 15 | 6.5 | 0.44074
2:00 | [72 empty] | 43579.3149 | 2,3,4,6 | 51 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 14.6405 | 1,2 | 18.7214 | 33.3619 | 1.8888 | 43579.3149 | 80.5801 | 8177.8238 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8282 | 1.9077 | 1.5897 | 0.21128 | 0.23079 | 0.18203 | 0.19503 | 0.16903 | 0.16903 | 1.5408 | 7 | 0.071129 | 0.070658 | 0.069716 | 1.1084 | 0.49885 | 0.096754 | 3.7402 | 0.65168 | 5.1453 | 1.1084 | 0.49499 | 0.1032 | 4.1086 | 0.73314 | 9.1182 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.79 | 18 | 17 | 6.52 | 127 | 163 | 19.7 | 0.488 |  | 5.99 | 11 | 0.076 | 6.05 | 11 |  | 5.98 | 11 | [8 empty] | 0.056 | [14 empty] | 0.063 | 2 | 0.39 |  | 0.052 | 0.066 | 2 | 0.29 |  | 0.037 | 2 | 0.23 | [38 empty] | 11568 | [6 empty] | 0 | 0 | 0 | 460 | 480 | 400 | 650 | 710 | 560 | 600 | 520 | 520 | 810 |  | 1510 | 1500 | 1480 | 108 | 129 | 15 | 1650 | 320 | 395 | 54 | 64 | 8 | 940 | 180 | 350 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43579.8389 | 2,3,4,6 | 53 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 13.9997 | 1,2 | 17.113 | 31.1126 | 2.5286 | 43579.8389 | 82.8927 | 8977.16 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7885 | 1.8878 | 1.709 | 0.22754 | 0.23729 | 0.20153 | 0.21128 | 0.16903 | 0.16903 | 2.2827 | 9 | 0.070658 | 0.070658 | 0.070658 | 1.1494 | 0.49885 | 0.096754 | 3.6452 | 0.66186 | 5.1453 | 1.1084 | 0.50272 | 0.1032 | 4.0379 | 0.7535 | 9.1182 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.19 | 0.058 | 1 | 4.1 | 19.8 |  |  |  | 7.24 | 0.059 | 1 | 3.9 | 20 |  |  |  | 3.9 | 3.3 | 4 | [18 empty] | 11900 | [6 empty] | 0 | 0 | 0 | 450 | 475 | 430 | 700 | 730 | 620 | 650 | 520 | 520 | 1200 |  | 1500 | 1500 | 1500 | 112 | 129 | 15 | 1650 | 325 | 395 | 54 | 65 | 8 | 930 | 185 | 350 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.53 | 18 | 18 | 6.48 | 128 | 165 | 19.5 | 0.506 |  | 5.95 | 10 | 0.069 | 5.99 | 11 |  | 5.97 | 11 | [8 empty] | 0.061 | [14 empty] | 0.057 | 1 | 0.4 |  | 0.061 | 0.03 | 1 | 0.36 |  | 0.036 | 1 | 0.28 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.04 | [9 empty] | 6.06 | 0.33 | 5 | 0.53 | 19.3 | 11.6 | 0.57597 |  | 6.11 | 0.378 | 6 | 0.59 | 19.3 | 11.6 | 0.57597 | 6.04 | 0.438 | 6 | 0.69 | 19.2 | 11.8 | 0.55704 |  |  |  | 0.018 | [9 empty] | 7.21 | 0.058 | 2 | 4.3 | 19.1 | 20 | 44 | 0.022 | 7.21 | 0.059 | 2 | 4.6 | 19.1 | 21 | 45 | 0.019 | 4.5 | 3.5 | 4 | [55 empty] | 9:00 | 0.53 | 11.6 | 21.931 | 11.6234 | 6.06 | 19.3 | 10 | 1.1623 | 15 | 6.5 | 0.45597 | 9:00 | 0.59 | 11.6 | 21.931 | 12.9393 | 6.11 | 19.3 | 10 | 1.2939 | 15 | 6.5 | 0.45597 | 9:00 | 0.69 | 11.8 | 22.8814 | 15.7881 | 6.04 | 19.2 | 10 | 1.5788 | 15 | 6.5 | 0.43704
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 19 | 17 | 6.34 | 120 | 165 | 19.6 | 0.505 |  | 6 | 10 | 0.062 | 5.98 | 10 |  | 6.02 | 10 | [8 empty] | 0.054 | [14 empty] | 0.051 | 1 | 0.36 |  | 0.052 | 0.059 | 2 | 0.32 |  | 0.085 | 2 | 0.3 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.09 | 0.321 | 5 | 0.47 | 20 | 11.7 | 0.44193 |  | 6.07 | 0.469 | 6 | 0.49 | 20.3 | 11.7 | 0.44193 | 6.11 | 0.411 | 6 | 0.61 | 19.6 | 11.7 | 0.55333 | [13 empty] | 7.2 | 0.06 | 2 | 4.3 | 19.4 |  |  |  | 7.22 | 0.066 | 2 | 4.2 | 20.2 |  |  |  | 4.1 | 3.5 | 3.7 | [55 empty] | 13:00 | 0.47 | 11.7 | 21.7436 | 10.2195 | 6.09 | 20 | 7 | 1.4599 | 20 | 6.5 | 0.32193 | 13:00 | 0.49 | 11.7 | 21.7436 | 10.6544 | 6.07 | 20.3 | 7 | 1.5221 | 20 | 6.5 | 0.32193 | 13:00 | 0.61 | 11.7 | 23.0769 | 14.0769 | 6.11 | 19.6 | 10 | 1.4077 | 15 | 6.5 | 0.43333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 19 | 18 | 6.2 | 129 | 165 | 20.1 | 0.503 |  | 6 | 10 | 0.062 | 5.98 | 10 |  | 6.01 | 10 | [8 empty] | 0.05 | [14 empty] | 0.045 | 2 | 0.31 |  | 0.052 | 0.062 | 2 | 0.26 |  | 0.053 | 2 | 0.25 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.3 | 0.066 | 2 | 4.3 | 19.2 |  |  |  | 7.18 | 0.06 | 2 | 4.1 | 19.9 |  |  |  | 4 | 3.7 | 4.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.51 | 19 | 18 | 6.16 | 132 | 158 | 20.4 | 0.518 |  | 6.03 | 10 | 0.071 | 6.02 | 10 |  | 6.01 | 10 | [8 empty] | 0.054 | [14 empty] | 0.041 | 2 | 0.32 |  | 0.053 | 0.052 | 2 | 0.31 |  | 0.054 | 2 | 0.36 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.046 | [9 empty] | 6.08 | 0.298 | 5 | 0.49 | 20.5 | 11.7 | 0.44193 |  | 6.07 | 0.44 | 6 | 0.49 | 20.6 | 11.7 | 0.44193 | 6.06 | 0.439 | 8 | 0.56 | 20.2 | 11.9 | 0.42852 |  |  |  | 0.013 | [9 empty] | 7.3 | 0.069 | 2 | 4.2 | 19.5 | 21 | 45 | 0.03 | 7.29 | 0.063 | 2 | 4.1 | 19.7 | 21 | 45 | 0.015 | 4.1 | 3.4 | 3.9 | [55 empty] | 21:00 | 0.49 | 11.7 | 21.7436 | 10.6544 | 6.08 | 20.5 | 7 | 1.5221 | 20 | 6.5 | 0.32193 | 21:00 | 0.49 | 11.7 | 21.7436 | 10.6544 | 6.07 | 20.6 | 7 | 1.5221 | 20 | 6.5 | 0.32193 | 21:00 | 0.56 | 11.9 | 22.6891 | 12.7059 | 6.06 | 20.2 | 7 | 1.8151 | 20 | 6.5 | 0.30852
22:00 | [72 empty] | DOSE |  | TOTAL | 35.1 | 35.1 | 35.1 | 105.3 | 33.6 | 33.6 | 33.6 | 100.8 | 0 | 43.8898 | 0 | 51.565 | 95.4547 | 6.3063 | TOTAL | 245.3904 | 25394.295 | 0 | 1712.7753 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4448 | 5.7827 | 5.0474 | 0.65986 | 0.70212 | 0.55259 | 0.61435 | 0.50708 | 0.50708 | 6.0111 | 22 | 0.2115 | 0.21103 | 0.21009 | 3.3662 | 1.4966 | 0.29671 | 11.1832 | 2.0263 | 15.4358 | 3.2841 | 1.5391 | 0.30961 | 12.1551 | 2.2605 | 27.3545 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 19 | 18 | 6.5 | 132 | 166 | 20.4 | 0.513 |  | 6.02 | 10 | 0.061 | 6.02 | 11 |  | 6 | 11 | [8 empty] | 0.051 | [14 empty] | 0.043 | 2 | 0.36 |  | 0.055 | 0.053 | 2 | 0.33 |  | 0.056 | 2 | 0.39 | [22 empty] | AVERAGE | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 14.6299 |  | 17.1883 | 31.8182 | 2.1021 | AVERAGE | 81.7968 | 8464.765 |  | 570.9251 | 0 | 0 | 0 |  |  |  | 1.8149 | 1.9276 | 1.6825 | 0.21995 | 0.23404 | 0.1842 | 0.20478 | 0.16903 | 0.16903 | 2.0037 | 7.3333 | 0.070501 | 0.070344 | 0.07003 | 1.1221 | 0.49885 | 0.098905 | 3.7277 | 0.67544 | 5.1453 | 1.0947 | 0.51303 | 0.1032 | 4.0517 | 0.7535 | 9.1182 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.4 | 112 | 106 | 38.2 | 768 | 982 | 119.7 | 3.033 | 0.086 | 35.99 | 61 | 0.401 | 36.04 | 63 | 0 | 35.99 | 63 | 0 | 24.24 | 1.276 | 20 | 1.98 | 79.9 | 46.6 | 1.899 | 0.326 | 24.29 | 1.658 | 24 | 2.09 | 80.4 | 46.6 | 1.899 | 24.3 | 1.674 | 26 | 2.57 | 78.6 | 47.3 | 2.0996 | 0.3 | 10 | 2.14 | 0.031 | 0.325 | 0.322 | 11 | 1.87 | 0 |  | 11 | 1.81 | 0 | 43.38 | 0.367 | 11 | 25.4 | 116.7 | 41 | 89 | 0.052 | 43.37 | 0.367 | 11 | 25 | 118.8 | 42 | 90 | 0.034 | 24.5 | 20.3 | 23.7 |  |  | MINIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 13.9997 |  | 15.7306 | 30.9802 | 1.8888 | MINIMUM | 80.5801 | 8177.8238 |  | 570.9251 | [6 empty] | 1.7885 | 1.8878 | 1.5897 | 0.21128 | 0.23079 | 0.16903 | 0.19503 | 0.16903 | 0.16903 | 1.5408 | 6 | 0.069716 | 0.069716 | 0.069716 | 1.1084 | 0.49885 | 0.096754 | 3.6452 | 0.65168 | 5.1453 | 1.0673 | 0.49499 | 0.1032 | 4.0086 | 0.73314 | 9.1182 |  | MIN | 0.53 | 11.6 | 21.931 | 11.6234 | 6.06 | 19.3 | 10 | 1.1623 |  |  |  | MIN | 0.59 | 11.6 | 21.931 | 12.9393 | 6.11 | 19.3 | 10 | 1.2939 |  |  |  | MIN | 0.61 | 11.7 | 23.0769 | 14.0769 | 6.11 | 19.6 | 10 | 1.4077 |  |  |  | 1.1623
AVERAGE | 6.5667 | 18.6667 | 17.6667 | 6.3667 | 128 | 163.6667 | 19.95 | 0.5055 | 0.043 | 5.9983 | 10.1667 | 0.066833 | 6.0067 | 10.5 |  | 5.9983 | 10.5 |  | 6.06 | 0.319 | 5 | 0.495 | 19.975 | 11.65 | 0.47476 | 0.054333 | 6.0725 | 0.4145 | 6 | 0.5225 | 20.1 | 11.65 | 0.47476 | 6.075 | 0.4185 | 6.5 | 0.6425 | 19.65 | 11.825 | 0.52491 | 0.05 | 1.6667 | 0.35667 | 0.0155 | 0.054167 | 0.053667 | 1.8333 | 0.31167 |  |  | 1.8333 | 0.30167 |  | 7.23 | 0.061167 | 1.8333 | 4.2333 | 19.45 | 20.5 | 44.5 | 0.026 | 7.2283 | 0.061167 | 1.8333 | 4.1667 | 19.8 | 21 | 45 | 0.017 | 4.0833 | 3.3833 | 3.95 |  |  | MAXIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 15.2496 |  | 18.7214 | 33.3619 | 2.5286 | MAXIMUM | 82.8927 | 8977.16 |  | 570.9251 | [6 empty] | 1.8282 | 1.9872 | 1.7487 | 0.22754 | 0.23729 | 0.20153 | 0.21128 | 0.16903 | 0.16903 | 2.2827 | 9 | 0.071129 | 0.070658 | 0.070658 | 1.1494 | 0.49885 | 0.1032 | 3.7978 | 0.71277 | 5.1453 | 1.1084 | 0.54139 | 0.1032 | 4.1086 | 0.77387 | 9.1182
MINIMUM | 6.5 | 18 | 17 | 6.16 | 120 | 158 | 19.5 | 0.488 | 0.04 | 5.95 | 10 | 0.061 | 5.98 | 10 |  | 5.97 | 10 |  | 6.01 | 0.298 | 5 | 0.47 | 19.3 | 11.6 | 0.43918 | 0.05 | 6.04 | 0.371 | 6 | 0.49 | 19.3 | 11.6 | 0.43918 | 6.04 | 0.386 | 6 | 0.56 | 19.2 | 11.7 | 0.42852 | 0.041 | 1 | 0.31 | 0.013 | 0.052 | 0.03 | 1 | 0.26 |  |  | 1 | 0.23 |  | 7.18 | 0.056 | 1 | 4.1 | 19.1 | 20 | 44 | 0.022 | 7.18 | 0.059 | 1 | 3.9 | 19.1 | 21 | 45 | 0.015 | 3.9 | 2.9 | 3.7 | [15 empty] | MIL/MIN |  | TOTAL | 35228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1370 | 1455 | 1270 | 2030 | 2160 | 1700 | 1890 | 1560 | 1560 | 3160 | 0 | 4490 | 4480 | 4460 | 328 | 387 | 46 | 5020 | 995 | 1185 | 160 | 199 | 24 | 2810 | 555 | 1050
MAXIMUM | 6.79 | 19 | 18 | 6.52 | 132 | 166 | 20.4 | 0.518 | 0.046 | 6.03 | 11 | 0.076 | 6.05 | 11 |  | 6.02 | 11 |  | 6.09 | 0.33 | 5 | 0.53 | 20.5 | 11.7 | 0.57597 | 0.061 | 6.11 | 0.469 | 6 | 0.59 | 20.6 | 11.7 | 0.57597 | 6.11 | 0.439 | 8 | 0.71 | 20.2 | 11.9 | 0.56074 | 0.063 | 2 | 0.4 | 0.018 | 0.061 | 0.066 | 2 | 0.36 |  |  | 2 | 0.39 |  | 7.3 | 0.069 | 2 | 4.3 | 19.8 | 21 | 45 | 0.03 | 7.29 | 0.066 | 2 | 4.6 | 20.2 | 21 | 45 | 0.019 | 4.5 | 3.7 | 4.2 | [17 empty] | AVERAGE | 11742.6667 | [9 empty] | 456.6667 | 485 | 423.3333 | 676.6667 | 720 | 566.6667 | 630 | 520 | 520 | 1053.3333 |  | 1496.6667 | 1493.3333 | 1486.6667 | 109.3333 | 129 | 15.3333 | 1673.3333 | 331.6667 | 395 | 53.3333 | 66.3333 | 8 | 936.6667 | 185 | 350
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0011 |  | TOTAL AVG COAG ALK: |  |  |  | 10.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.469 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.0692 |  |  |  |  | 0.066 |  |  |  |  | 0.47 | [6 empty] | 0.066 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 11568 | [9 empty] | 450 | 475 | 400 | 650 | 710 | 520 | 600 | 520 | 520 | 810 |  | 1480 | 1480 | 1480 | 108 | 129 | 15 | 1650 | 320 | 395 | 52 | 64 | 8 | 930 | 180 | 350
[90 empty] | MAXIMUM | 11900 | [9 empty] | 460 | 500 | 440 | 700 | 730 | 620 | 650 | 520 | 520 | 1200 |  | 1510 | 1500 | 1500 | 112 | 129 | 16 | 1720 | 350 | 395 | 54 | 70 | 8 | 940 | 190 | 350
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.722 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827739 |  | END: | 23827740 |  |  | Alum | 4822 | 6432 | 6432 | 7296 | 7296 | 0 | [44 empty] | 0.53 | 11.6 | 21.931 | 11.6234 | 6.06 | 19.3 | 10 | 1.1623
[73 empty] | FINISHED 2 | 17.118 |  | TOTAL MGD: |  | 11.721 |  |  | FINISHED SOUTH 2 |  | START: | 45111031 |  | END: | 45122752 |  |  | Caustic | 4061 | 7226 | 7226
[73 empty] | TOTAL RAW | 29.7 |  | TOTAL MGD: |  | 4.453 |  |  | FINISHED CONWAY |  | START: | 10746262 |  | END: | 10750715 |  |  | Hypochlorite | 10 |  | 20
[76 empty] | TOTAL MGD: |  | 12.665 |  |  | FINISHED PERRY |  | START: | 34933276 |  | END: | 34945941 |  |  | Phosphate | 3414
[76 empty] | TOTAL MGD: |  | 9.938 |  |  | RAW PLANT 1 |  | START: | 32011421 |  | END: | 32021359 |  |  | Fluoride | 1250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.951 |  |  | RAW PLANT 2 |  | START: | 31974641 |  | END: | 31984592 |  |  | Cal~Flo | 6.93 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.811 |  |  | RAW PLANT 3 |  | START: | 8610577 |  | END: | 8620388 |  |  | Zinc | 2422
[76 empty] | TOTAL MGD: |  | 0.917 |  |  | DECANT |  | START: | 1954033 |  | END: | 1954950 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 0.95799 |  |  | BLOW DOWN |  | START: | 9260.6312 |  | END: | 9261.5892 |  |  | NH3 | 5.54 |  | BI-SUL | 1010
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 550
23827740
45122752
10750715
34945941
32021359
31984592
8620388
1954950
9261.5892
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 25
DATE: | 2019-04-25 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-25 | [23 empty] | DATE: | 2019-04-25
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-25 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43580.0294 | 2,3,4,6 | 53 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 13.9997 | 1,2 | 17.113 | 31.1126 | 2.5286 | 43580.0294 | 82.8927 | 8977.16 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7885 | 1.8878 | 1.709 | 0.23079 | 0.24379 | 0.21128 | 0.21128 | 0.16903 | 0.16903 | 2.2827 | 9 | 0.070658 | 0.070658 | 0.070658 | 1.1494 | 0.49885 | 0.096754 | 3.6452 | 0.66186 | 5.1453 | 1.1084 | 0.50272 | 0.1032 | 4.0379 | 0.7535 | 9.1182 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.09 | 0.339 | 6 | 0.5 | 20.3 | 11.7 | 0.44193 |  | 6.1 | 0.406 | 6 | 0.5 | 20.1 | 11.7 | 0.44193 | 6.09 | 0.433 | 8 | 0.6 | 20 | 11.9 | 0.42852 | [13 empty] | 7.43 | 0.069 | 2 | 4 | 19.7 |  |  |  | 7.3 | 0.073 | 2 | 3.9 | 19.3 |  |  |  | 3.9 | 3.5 | 4.2 | [18 empty] | 11900 | [6 empty] | 0 | 0 | 0 | 450 | 475 | 430 | 710 | 750 | 650 | 650 | 520 | 520 | 1200 |  | 1500 | 1500 | 1500 | 112 | 129 | 15 | 1650 | 325 | 395 | 54 | 65 | 8 | 930 | 185 | 350 |  | 1:00 | 0.5 | 11.7 | 21.7436 | 10.8718 | 6.09 | 20.3 | 7 | 1.5531 | 20 | 6.5 | 0.32193 | 1:00 | 0.5 | 11.7 | 21.7436 | 10.8718 | 6.1 | 20.1 | 7 | 1.5531 | 20 | 6.5 | 0.32193 | 1:00 | 0.6 | 11.9 | 22.6891 | 13.6134 | 6.09 | 20 | 7 | 1.9448 | 20 | 6.5 | 0.30852
2:00 | [72 empty] | 43580.1417 | 2,3,4,6 | 53 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 11.4898 | 1,2 | 17.4485 | 28.9382 | 2.5286 | 43580.1417 | 82.8927 | 8977.16 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7885 | 1.8878 | 1.709 | 0.23079 | 0.24379 | 0.21128 | 0.21128 | 0.16903 | 0.16903 | 2.2827 | 9 | 0.070658 | 0.070658 | 0.070658 | 1.1494 | 0.49885 | 0.096754 | 3.6452 | 0.66186 | 5.1453 | 1.1084 | 0.50272 | 0.1032 | 4.0379 | 0.7535 | 9.1182 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.52 | 18 | 18 | 6.36 | 132 | 161 | 20.2 | 0.512 |  | 6.1 | 11 | 0.071 | 6.11 | 10 |  | 6.07 | 10 | [8 empty] | 0.053 | [14 empty] | 0.046 | 2 | 0.3 |  | 0.051 | 0.053 | 2 | 0.31 |  | 0.05 | 2 | 0.46 | [38 empty] | 11900 | [6 empty] | 0 | 0 | 0 | 450 | 475 | 430 | 710 | 750 | 650 | 650 | 520 | 520 | 1200 |  | 1500 | 1500 | 1500 | 112 | 129 | 15 | 1650 | 325 | 395 | 54 | 65 | 8 | 930 | 185 | 350 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43580.2982 | 2,3,4,6 | 53 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 13.0954 | 1,2 | 20.0477 | 33.143 | 2.5286 | 43580.2982 | 85.6791 | 8977.16 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8282 | 1.8679 | 1.5897 | 0.22754 | 0.26004 | 0.19503 | 0.20803 | 0.16903 | 0.16903 | 2.2827 | 9 | 0.070658 | 0.070658 | 0.070658 | 1.1084 | 0.49885 | 0.096754 | 3.6591 | 0.65168 | 5.1453 | 1.0673 | 0.49499 | 0.1032 | 4.3715 | 0.71277 | 9.1182 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.34 | 0.069 | 2 | 4.2 | 19.7 |  |  |  | 7.31 | 0.07 | 2 | 4.1 | 19.4 |  |  |  | 4 | 3.6 | 4.1 | [18 empty] | 12300 | [6 empty] | 0 | 0 | 0 | 460 | 470 | 400 | 700 | 800 | 600 | 640 | 520 | 520 | 1200 |  | 1500 | 1500 | 1500 | 108 | 129 | 15 | 1620 | 320 | 395 | 52 | 64 | 8 | 980 | 175 | 350 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43580.8112 | 2,3,4,6 | 54 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 14.2589 | 1,2 | 17.6342 | 31.8931 | 2.317 | 43580.8112 | 86.3756 | 8977.16 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8282 | 1.8679 | 1.7885 | 0.22754 | 0.26004 | 0.19991 | 0.21128 | 0.17228 | 0.17228 | 2.4729 | 3 | 0.070658 | 0.070658 | 0.070658 | 1.1289 | 0.49885 | 0.096754 | 3.5191 | 0.69241 | 5.1453 | 1.1084 | 0.49499 | 0.1032 | 4.1508 | 0.71277 | 9.1182 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.52 | 18 | 18 | 6.43 | 128 | 164 | 20.2 | 0.498 |  | 5.99 | 10 | 0.058 | 6.04 | 11 |  | 6.05 | 11 | [8 empty] | 0.054 | [14 empty] | 0.04 | 2 | 0.36 |  | 0.051 | 0.05 | 2 | 0.38 |  | 0.055 | 2 | 0.38 | [38 empty] | 12400 | [6 empty] | 0 | 0 | 0 | 460 | 470 | 450 | 700 | 800 | 615 | 650 | 530 | 530 | 1300 |  | 1500 | 1500 | 1500 | 110 | 129 | 15 | 1620 | 340 | 395 | 54 | 64 | 8 | 970 | 175 | 350 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.21 | 0.332 | 4 | 0.46 | 20.1 | 11.4 | 0.43368 |  | 6.17 | 0.464 | 6 | 0.51 | 20 | 11.7 | 0.44193 | 6.2 | 0.539 | 6 | 0.53 | 19.9 | 11.9 | 0.56074 |  |  |  | 0.014 | [9 empty] | 7.29 | 0.071 | 2 | 4.3 | 19.7 | 21 | 46 | 0.023 | 7.27 | 0.076 | 2 | 4.2 | 20.3 | 21 | 49 | 0.02 | 3.7 | 3.4 | 3.6 | [55 empty] | 9:00 | 0.46 | 11.4 | 22.3158 | 10.2653 | 6.21 | 20.1 | 7 | 1.4665 | 20 | 6.5 | 0.31368 | 9:00 | 0.51 | 11.7 | 21.7436 | 11.0892 | 6.17 | 20 | 7 | 1.5842 | 20 | 6.5 | 0.32193 | 9:00 | 0.53 | 11.9 | 22.6891 | 12.0252 | 6.2 | 19.9 | 10 | 1.2025 | 15 | 6.5 | 0.44074
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.55 | 19 | 18 | 6.71 | 125 | 162 | 19.9 | 0.505 |  | 6.08 | 11 | 0.066 | 6.07 | 11 |  | 6.07 | 11 | [8 empty] | 0.052 | [14 empty] | 0.041 | 2 | 0.27 |  | 0.054 | 0.029 | 2 | 0.23 |  | 0.055 | 2 | 0.24 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.15 | 0.4 | 4 | 0.5 | 20.7 | 11.8 | 0.44469 |  | 6.16 | 0.451 | 5 | 0.44 | 20.8 | 11.8 | 0.44469 | 6.21 | 0.432 | 6 | 0.57 | 20.2 | 12.2 | 0.4363 | [13 empty] | 7.3 | 0.056 | 2 | 4.3 | 19.7 |  |  |  | 7.22 | 0.064 | 2 | 4.1 | 20.8 |  |  |  | 4 | 3.1 | 3.7 | [55 empty] | 13:00 | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.15 | 20.7 | 7 | 1.54 | 20 | 6.5 | 0.32469 | 13:00 | 0.44 | 11.8 | 21.5593 | 9.4861 | 6.16 | 20.8 | 7 | 1.3552 | 20 | 6.5 | 0.32469 | 13:00 | 0.57 | 12.2 | 22.1311 | 12.6148 | 6.21 | 20.2 | 7 | 1.8021 | 20 | 6.5 | 0.3163
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.53 | 18 | 18 | 6.43 | 129 | 163 | 20.7 | 0.509 |  | 6.1 | 11 | 0.066 | 6.18 | 11 |  | 6.15 | 11 | [8 empty] | 0.058 | [14 empty] | 0.04 | 2 | 0.24 |  | 0.058 | 0.035 | 2 | 0.2 |  | 0.052 | 2 | 0.2 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.47 | 0.061 | 2 | 4.3 | 19.8 |  |  |  | 7.41 | 0.066 | 2 | 4.2 | 20.4 |  |  |  | 3.8 | 3.2 | 4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.57 | 19 | 18 | 6.49 | 126 | 162 | 20.7 | 0.506 |  | 6.13 | 11 | 0.075 | 6.18 | 11 |  | 6.17 | 11 | [8 empty] | 0.055 | [14 empty] | 0.04 | 2 | 0.3 |  | 0.059 | 0.051 | 2 | 0.23 |  | 0.05 | 2 | 0.36 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.044 | [9 empty] | 6.21 | 0.381 | 5 | 0.5 | 21 | 11.8 | 0.44469 |  | 6.22 | 0.322 | 6 | 0.49 | 20.9 | 11.8 | 0.44469 | 6.21 | 0.439 | 7 | 0.59 | 20.7 | 12.1 | 0.4337 |  |  |  | 0.014 | [9 empty] | 7.46 | 0.066 | 2 | 4.3 | 20.2 | 21 | 48 | 0.038 | 7.4 | 0.069 | 2 | 4.1 | 20.2 | 22 | 50 | 0.03 | 3.9 | 3.6 | 3.9 | [55 empty] | 21:00 | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.21 | 21 | 7 | 1.54 | 20 | 6.5 | 0.32469 | 21:00 | 0.49 | 11.8 | 21.5593 | 10.5641 | 6.22 | 20.9 | 7 | 1.5092 | 20 | 6.5 | 0.32469 | 21:00 | 0.59 | 12.1 | 22.314 | 13.1653 | 6.21 | 20.7 | 7 | 1.8808 | 20 | 6.5 | 0.3137
22:00 | [72 empty] | DOSE |  | TOTAL | 46.8 | 46.8 | 46.8 | 140.4 | 44.8 | 44.8 | 44.8 | 134.4 | 0 | 52.8437 | 0 | 72.2434 | 125.087 | 9.9029 | TOTAL | 337.8402 | 35908.64 | 0 | 2283.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2333 | 7.5115 | 6.7961 | 0.91665 | 1.0077 | 0.81751 | 0.84189 | 0.67936 | 0.67936 | 9.321 | 30 | 0.28263 | 0.28263 | 0.28263 | 4.5361 | 1.9954 | 0.38702 | 14.4687 | 2.6678 | 20.581 | 4.3924 | 1.9954 | 0.41282 | 16.5981 | 2.9325 | 36.4727 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.52 | 19 | 18 | 6.41 | 131 | 164 | 21 | 0.511 |  | 6.06 | 11 | 0.077 | 6.2 | 11 |  | 6.18 | 11 | [8 empty] | 0.054 | [14 empty] | 0.04 | 2 | 0.3 |  | 0.056 | 0.049 | 2 | 0.26 |  | 0.053 | 2 | 0.36 | [22 empty] | AVERAGE | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 13.2109 |  | 18.0608 | 31.2718 | 2.4757 | AVERAGE | 84.46 | 8977.16 |  | 570.9251 | 0 | 0 | 0 |  |  |  | 1.8083 | 1.8779 | 1.699 | 0.22916 | 0.25192 | 0.20438 | 0.21047 | 0.16984 | 0.16984 | 2.3303 | 7.5 | 0.070658 | 0.070658 | 0.070658 | 1.134 | 0.49885 | 0.096754 | 3.6172 | 0.66695 | 5.1453 | 1.0981 | 0.49885 | 0.1032 | 4.1495 | 0.73314 | 9.1182 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.21 | 111 | 108 | 38.83 | 771 | 976 | 122.7 | 3.041 | 0.085 | 36.46 | 65 | 0.413 | 36.78 | 65 | 0 | 36.69 | 65 | 0 | 24.66 | 1.452 | 19 | 1.96 | 82.1 | 46.7 | 1.765 | 0.326 | 24.65 | 1.643 | 23 | 1.94 | 81.8 | 47 | 1.7732 | 24.71 | 1.843 | 27 | 2.29 | 80.8 | 48.1 | 1.8593 | 0.247 | 12 | 1.77 | 0.028 | 0.329 | 0.267 | 12 | 1.61 | 0 | 0.315 | 12 | 2 | 0 | 44.29 | 0.392 | 12 | 25.4 | 118.8 | 42 | 94 | 0.061 | 43.91 | 0.418 | 12 | 24.6 | 120.4 | 43 | 99 | 0.05 | 23.3 | 20.4 | 23.5 |  |  | MINIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 11.4898 |  | 17.113 | 28.9382 | 2.317 | MINIMUM | 82.8927 | 8977.16 |  | 570.9251 | [6 empty] | 1.7885 | 1.8679 | 1.5897 | 0.22754 | 0.24379 | 0.19503 | 0.20803 | 0.16903 | 0.16903 | 2.2827 | 3 | 0.070658 | 0.070658 | 0.070658 | 1.1084 | 0.49885 | 0.096754 | 3.5191 | 0.65168 | 5.1453 | 1.0673 | 0.49499 | 0.1032 | 4.0379 | 0.71277 | 9.1182 |  | MIN | 0.46 | 11.4 | 22.3158 | 10.2653 | 6.21 | 20.1 | 7 | 1.4665 |  |  |  | MIN | 0.44 | 11.8 | 21.5593 | 9.4861 | 6.16 | 20.8 | 7 | 1.3552 |  |  |  | MIN | 0.53 | 11.9 | 22.6891 | 12.0252 | 6.2 | 19.9 | 10 | 1.2025 |  |  |  | 1.2025
AVERAGE | 6.535 | 18.5 | 18 | 6.4717 | 128.5 | 162.6667 | 20.45 | 0.50683 | 0.0425 | 6.0767 | 10.8333 | 0.068833 | 6.13 | 10.8333 |  | 6.115 | 10.8333 |  | 6.165 | 0.363 | 4.75 | 0.49 | 20.525 | 11.675 | 0.44125 | 0.054333 | 6.1625 | 0.41075 | 5.75 | 0.485 | 20.45 | 11.75 | 0.44331 | 6.1775 | 0.46075 | 6.75 | 0.5725 | 20.2 | 12.025 | 0.46481 | 0.041167 | 2 | 0.295 | 0.014 | 0.054833 | 0.0445 | 2 | 0.26833 |  | 0.0525 | 2 | 0.33333 |  | 7.3817 | 0.065333 | 2 | 4.2333 | 19.8 | 21 | 47 | 0.0305 | 7.3183 | 0.069667 | 2 | 4.1 | 20.0667 | 21.5 | 49.5 | 0.025 | 3.8833 | 3.4 | 3.9167 |  |  | MAXIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 14.2589 |  | 20.0477 | 33.143 | 2.5286 | MAXIMUM | 86.3756 | 8977.16 |  | 570.9251 | [6 empty] | 1.8282 | 1.8878 | 1.7885 | 0.23079 | 0.26004 | 0.21128 | 0.21128 | 0.17228 | 0.17228 | 2.4729 | 9 | 0.070658 | 0.070658 | 0.070658 | 1.1494 | 0.49885 | 0.096754 | 3.6591 | 0.69241 | 5.1453 | 1.1084 | 0.50272 | 0.1032 | 4.3715 | 0.7535 | 9.1182
MINIMUM | 6.52 | 18 | 18 | 6.36 | 125 | 161 | 19.9 | 0.498 | 0.041 | 5.99 | 10 | 0.058 | 6.04 | 10 |  | 6.05 | 10 |  | 6.09 | 0.332 | 4 | 0.46 | 20.1 | 11.4 | 0.43368 | 0.052 | 6.1 | 0.322 | 5 | 0.44 | 20 | 11.7 | 0.44193 | 6.09 | 0.432 | 6 | 0.53 | 19.9 | 11.9 | 0.42852 | 0.04 | 2 | 0.24 | 0.014 | 0.051 | 0.029 | 2 | 0.2 |  | 0.05 | 2 | 0.2 |  | 7.29 | 0.056 | 2 | 4 | 19.7 | 21 | 46 | 0.023 | 7.22 | 0.064 | 2 | 3.9 | 19.3 | 21 | 49 | 0.02 | 3.7 | 3.1 | 3.6 | [15 empty] | MIL/MIN |  | TOTAL | 48500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1820 | 1890 | 1710 | 2820 | 3100 | 2515 | 2590 | 2090 | 2090 | 4900 | 0 | 6000 | 6000 | 6000 | 442 | 516 | 60 | 6540 | 1310 | 1580 | 214 | 258 | 32 | 3810 | 720 | 1400
MAXIMUM | 6.57 | 19 | 18 | 6.71 | 132 | 164 | 21 | 0.512 | 0.044 | 6.13 | 11 | 0.077 | 6.2 | 11 |  | 6.18 | 11 |  | 6.21 | 0.4 | 6 | 0.5 | 21 | 11.8 | 0.44469 | 0.058 | 6.22 | 0.464 | 6 | 0.51 | 20.9 | 11.8 | 0.44469 | 6.21 | 0.539 | 8 | 0.6 | 20.7 | 12.2 | 0.56074 | 0.046 | 2 | 0.36 | 0.014 | 0.059 | 0.053 | 2 | 0.38 |  | 0.055 | 2 | 0.46 |  | 7.47 | 0.071 | 2 | 4.3 | 20.2 | 21 | 48 | 0.038 | 7.41 | 0.076 | 2 | 4.2 | 20.8 | 22 | 50 | 0.03 | 4 | 3.6 | 4.2 | [17 empty] | AVERAGE | 12125 | [9 empty] | 455 | 472.5 | 427.5 | 705 | 775 | 628.75 | 647.5 | 522.5 | 522.5 | 1225 |  | 1500 | 1500 | 1500 | 110.5 | 129 | 15 | 1635 | 327.5 | 395 | 53.5 | 64.5 | 8 | 952.5 | 180 | 350
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1072 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.539 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.44 | [5 empty] | 6.1683 |  |  |  |  | 0.055 |  |  |  |  | 0.44 | [6 empty] | 0.055 | [16 empty] | Pump Station MIN |  | 3.1 | [17 empty] | MINIMUM | 11900 | [9 empty] | 450 | 470 | 400 | 700 | 750 | 600 | 640 | 520 | 520 | 1200 |  | 1500 | 1500 | 1500 | 108 | 129 | 15 | 1620 | 320 | 395 | 52 | 64 | 8 | 930 | 175 | 350
[90 empty] | MAXIMUM | 12400 | [9 empty] | 460 | 475 | 450 | 710 | 800 | 650 | 650 | 530 | 530 | 1300 |  | 1500 | 1500 | 1500 | 112 | 129 | 15 | 1650 | 340 | 395 | 54 | 65 | 8 | 980 | 185 | 350
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.308 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827740 |  | END: | 23827740 |  |  | Alum | 4815 | 7333 | 7333 | 6340 | 6340 | 0 | [44 empty] | 0.53 | 11.9 | 22.6891 | 12.0252 | 6.2 | 19.9 | 10 | 1.2025
[73 empty] | FINISHED 2 | 16.736 |  | TOTAL MGD: |  | 13.308 |  |  | FINISHED SOUTH 2 |  | START: | 45122752 |  | END: | 45136060 |  |  | Caustic | 3912 | 9149 | 9149
[73 empty] | TOTAL RAW | 34.274 |  | TOTAL MGD: |  | 3.786 |  |  | FINISHED CONWAY |  | START: | 10750715 |  | END: | 10754501 |  |  | Hypochlorite | 11 |  | 15
[76 empty] | TOTAL MGD: |  | 12.95 |  |  | FINISHED PERRY |  | START: | 34945941 |  | END: | 34958891 |  |  | Phosphate | 3348
[76 empty] | TOTAL MGD: |  | 11.212 |  |  | RAW PLANT 1 |  | START: | 32021359 |  | END: | 32032571 |  |  | Fluoride | 1150 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.189 |  |  | RAW PLANT 2 |  | START: | 31984592 |  | END: | 31995781 |  |  | Cal~Flo | 11.25 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.873 |  |  | RAW PLANT 3 |  | START: | 8620388 |  | END: | 8632261 |  |  | Zinc | 2437
[76 empty] | TOTAL MGD: |  | 0.944 |  |  | DECANT |  | START: | 1954950 |  | END: | 1955894 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.9432 |  |  | BLOW DOWN |  | START: | 9261.5892 |  | END: | 9263.5324 |  |  | NH3 | 5.34 |  | BI-SUL | 1010
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 690
23827740
45136060
10754501
34958891
32032571
31995781
8632261
1955894
9263.5324
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2BCOperator:
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. BuildingBCOperator:
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1BCOperator:
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 26
DATE: | 2019-04-26 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-26 | [23 empty] | DATE: | 2019-04-26
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-26 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43581.0047 | 2,3,4,6 | 54 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | ,1,3 | 14.2589 | 1,2 | 17.6342 | 31.8931 | 2.317 | 43581.0047 | 86.3756 | 8977.16 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8282 | 1.8679 | 1.7885 | 0.22754 | 0.26004 | 0.19991 | 0.21128 | 0.17228 | 0.17228 | 2.4729 | 3 | 0.070658 | 0.070658 | 0.070658 | 1.1289 | 0.49885 | 0.096754 | 3.5191 | 0.69241 | 5.1453 | 1.1084 | 0.49499 | 0.1032 | 4.1508 | 0.71277 | 9.1182 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.21 | 0.409 | 6 | 0.5 | 20.9 | 11.7 | 0.44193 |  | 6.2 | 0.393 | 7 | 0.51 | 20.8 | 11.7 | 0.44193 | 6.2 | 0.4 | 8 | 0.63 | 20.7 | 12 | 0.43111 | [13 empty] | 7.33 | 0.069 | 2 | 4.2 | 19.9 |  |  |  | 7.29 | 0.072 | 2 | 4.2 | 19.9 |  |  |  | 3.9 | 3.6 | 3.9 | [18 empty] | 12400 | [6 empty] | 0 | 0 | 0 | 460 | 470 | 450 | 700 | 800 | 615 | 650 | 530 | 530 | 1300 |  | 1500 | 1500 | 1500 | 110 | 129 | 15 | 1620 | 340 | 395 | 54 | 64 | 8 | 970 | 175 | 350 |  | 1:00 | 0.5 | 11.7 | 21.7436 | 10.8718 | 6.21 | 20.9 | 7 | 1.5531 | 20 | 6.5 | 0.32193 | 1:00 | 0.51 | 11.7 | 21.7436 | 11.0892 | 6.2 | 20.8 | 7 | 1.5842 | 20 | 6.5 | 0.32193 | 1:00 | 0.63 | 12 | 22.5 | 14.175 | 6.2 | 20.7 | 7 | 2.025 | 20 | 6.5 | 0.31111
2:00 | [72 empty] | 43581.3098 | 2,3,4,6 | 54 | 12.3 | 12.3 | 12.3 | 36.9 | 11.8 | 11.8 | 11.8 | 35.4 | ,1,3 | 14.099 | 1,2 | 19.7698 | 33.8688 | 2.317 | 43581.3098 | 85.6077 | 9346.0844 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8107 | 1.8107 | 1.5994 | 0.22881 | 0.25354 | 0.22262 | 0.22881 | 0.17006 | 0.17006 | 2.4729 | 3 | 0.069748 | 0.069748 | 0.070195 | 1.091 | 0.49918 | 0.097957 | 3.538 | 0.61854 | 5.1309 | 1.091 | 0.51386 | 0.097957 | 3.9999 | 0.71519 | 9.0996 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.55 | 18 | 18 | 6.29 | 132 | 165 | 21 | 0.513 |  | 6.1 | 11 | 0.071 | 6.16 | 11 |  | 6.16 | 11 | [8 empty] | 0.052 | [14 empty] | 0.041 | 2 | 0.31 |  | 0.056 | 0.043 | 2 | 0.33 |  | 0.053 | 2 | 0.39 | [38 empty] | 12920 | [6 empty] | 0 | 0 | 0 | 480 | 480 | 424 | 740 | 820 | 720 | 740 | 550 | 550 | 1300 |  | 1560 | 1560 | 1570 | 112 | 136 | 16 | 1670 | 320 | 415 | 56 | 70 | 8 | 970 | 185 | 368 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43581.8189 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 12.9902 | 1,2 | 19.0253 | 32.0155 | 2.8339 | 43581.8189 | 85.4431 | 9715.0088 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8703 | 1.8329 | 1.6832 | 0.23003 | 0.25303 | 0.22236 | 0.23003 | 0.16869 | 0.16869 | 2.4729 | 1.5 | 0.069605 | 0.069605 | 0.070048 | 1.1591 | 0.49863 | 0.094098 | 3.5226 | 0.67084 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 4.0134 | 0.70918 | 9.0232 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.3 | 0.063 | 2 | 4.2 | 20.3 |  |  |  | 7.27 | 0.069 | 2 | 4.1 | 20.1 |  |  |  | 3.9 | 3.5 | 4 | [18 empty] | 13000 | [6 empty] | 0 | 0 | 0 | 500 | 490 | 450 | 750 | 825 | 725 | 750 | 550 | 550 | 1300 |  | 1570 | 1570 | 1580 | 120 | 137 | 15.5 | 1710 | 350 | 415 | 57 | 69 | 8 | 1000 | 185 | 368 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.51 | 17 | 18 | 6.76 | 126 | 161 | 21.1 | 0.489 |  | 6.19 | 11 | 0.066 | 6.19 | 11 |  | 6.17 | 11 | [8 empty] | 0.061 | [14 empty] | 0.038 | 2 | 0.27 |  | 0.062 | 0.034 | 2 | 0.35 |  | 0.033 | 2 | 0.25 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.21 | 0.399 | 5 | 0.52 | 20.9 | 12.5 | 0.46395 |  | 6.13 | 0.452 | 5 | 0.47 | 20.8 | 12.5 | 0.46395 | 6.21 | 0.345 | 5 | 0.59 | 20.7 | 12.5 | 0.44407 |  |  |  | 0.011 | [9 empty] | 7.57 | 0.058 | 2 | 4.6 | 20.5 | 20 | 42 | 0.022 | 7.32 | 0.058 | 2 | 4 | 20.9 | 20 | 46 | 0.014 | 3.9 | 3.3 | 3.3 | [55 empty] | 9:00 | 0.52 | 12.5 | 20.352 | 10.583 | 6.21 | 20.9 | 7 | 1.5119 | 20 | 6.5 | 0.34395 | 9:00 | 0.47 | 12.5 | 20.352 | 9.5654 | 6.13 | 20.8 | 7 | 1.3665 | 20 | 6.5 | 0.34395 | 9:00 | 0.59 | 12.5 | 21.6 | 12.744 | 6.21 | 20.7 | 7 | 1.8206 | 20 | 6.5 | 0.32407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.54 | 17 | 18 | 6.37 | 123 | 159 | 20.9 | 0.476 |  | 6.13 | 11 | 0.063 | 6.14 | 11 |  | 6.16 | 11 | [8 empty] | 0.056 | [14 empty] | 0.036 | 2 | 0.4 |  | 0.059 | 0.037 | 2 | 0.55 |  | 0.041 | 2 | 0.23 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.16 | 0.34 | 5 | 0.41 | 21.1 | 12.3 | 0.45844 |  | 6.16 | 0.404 | 6 | 0.42 | 21.1 | 12.5 | 0.46395 | 6.19 | 0.406 | 5 | 0.65 | 20.8 | 12.7 | 0.44926 | [13 empty] | 7.45 | 0.066 | 2 | 4.2 | 20.2 |  |  |  | 7.31 | 0.067 | 2 | 3.8 | 20.9 |  |  |  | 3.9 | 3.3 | 3.7 | [55 empty] | 13:00 | 0.41 | 12.3 | 20.6829 | 8.48 | 6.16 | 21.1 | 7 | 1.2114 | 20 | 6.5 | 0.33844 | 13:00 | 0.42 | 12.5 | 20.352 | 8.5478 | 6.16 | 21.1 | 7 | 1.2211 | 20 | 6.5 | 0.34395 | 13:00 | 0.65 | 12.7 | 21.2598 | 13.8189 | 6.19 | 20.8 | 7 | 1.9741 | 20 | 6.5 | 0.32926
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 18 | 18 | 6.38 | 126 | 164 | 20.8 | 0.498 |  | 6.07 | 10 | 0.063 | 6.13 | 11 |  | 6.07 | 11 | [8 empty] | 0.053 | [14 empty] | 0.03 | 2 | 0.22 |  | 0.052 | 0.021 | 2 | 0.27 |  | 0.036 | 2 | 0.18 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.25 | 0.07 | 2 | 4.2 | 20.4 |  |  |  | 7.27 | 0.071 | 2 | 4 | 20.6 |  |  |  | 3.7 | 3.3 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.57 | 18 | 18 | 5.63 | 130 | 161 | 21.4 | 0.505 |  | 6.11 | 10 | 0.06 | 6.13 | 11 |  | 6.09 | 11 | [8 empty] | 0.057 | [14 empty] | 0.031 | 2 | 0.27 |  | 0.045 | 0.021 | 2 | 0.3 |  | 0.03 | 2 | 0.18 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.15 | 0.316 | 5 | 0.51 | 22 | 12.3 | 0.45844 |  | 6.15 | 0.369 | 6 | 0.43 | 22.2 | 12.3 | 0.45844 | 6.16 | 0.432 | 6 | 0.62 | 21.8 | 12.3 | 0.43889 |  |  |  | 0.015 | [9 empty] | 7.6 | 0.07 | 2 | 4 | 20.8 | 21 | 43 | 0.022 | 7.37 | 0.073 | 2 | 4 | 20.6 | 21 | 46 | 0.021 | 3.8 | 3.3 | 3.4 | [55 empty] | 21:00 | 0.51 | 12.3 | 20.6829 | 10.5483 | 6.15 | 22 | 7 | 1.5069 | 20 | 6.5 | 0.33844 | 21:00 | 0.43 | 12.3 | 20.6829 | 8.8937 | 6.15 | 22.2 | 7 | 1.2705 | 20 | 6.5 | 0.33844 | 21:00 | 0.62 | 12.3 | 21.9512 | 13.6098 | 6.16 | 21.8 | 7 | 1.9443 | 20 | 6.5 | 0.31889
22:00 | [72 empty] | DOSE |  | TOTAL | 36.4 | 36.4 | 36.4 | 109.2 | 34.9 | 34.9 | 34.9 | 104.7 | 0 | 41.3482 | 0 | 56.4293 | 97.7774 | 7.4678 | TOTAL | 257.4265 | 28038.2532 | 0 | 1712.7753 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5091 | 5.5115 | 5.0711 | 0.68637 | 0.76661 | 0.64489 | 0.67012 | 0.51102 | 0.51102 | 7.4188 | 7.5 | 0.21001 | 0.21001 | 0.2109 | 3.379 | 1.4967 | 0.28881 | 10.5797 | 1.9818 | 15.364 | 3.3005 | 1.5111 | 0.2983 | 12.1641 | 2.1371 | 27.241 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 18 | 18 | 6.13 | 126 | 163 | 21.3 | 0.5 |  | 6 | 11 | 0.065 | 6.04 | 11 |  | 6.07 | 10 | [8 empty] | 0.056 | [14 empty] | 0.036 | 2 | 0.29 |  | 0.057 | 0.026 | 2 | 0.31 |  | 0.036 | 2 | 0.23 | [22 empty] | AVERAGE | 12.1333 | 12.1333 | 12.1333 | 36.4 | 11.6333 | 11.6333 | 11.6333 | 34.9 |  | 13.7827 |  | 18.8098 | 32.5925 | 2.4893 | AVERAGE | 85.8088 | 9346.0844 |  | 570.9251 | 0 | 0 | 0 |  |  |  | 1.8364 | 1.8372 | 1.6904 | 0.22879 | 0.25554 | 0.21496 | 0.22337 | 0.17034 | 0.17034 | 2.4729 | 2.5 | 0.070003 | 0.070003 | 0.0703 | 1.1263 | 0.49889 | 0.09627 | 3.5266 | 0.6606 | 5.1213 | 1.1002 | 0.50371 | 0.099432 | 4.0547 | 0.71238 | 9.0803 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.24 | 106 | 108 | 37.56 | 763 | 973 | 126.5 | 2.981 | 0.084 | 36.6 | 64 | 0.388 | 36.79 | 66 | 0 | 36.72 | 65 | 0 | 24.73 | 1.464 | 21 | 1.94 | 84.9 | 48.8 | 1.8228 | 0.335 | 24.64 | 1.618 | 24 | 1.83 | 84.9 | 49 | 1.8283 | 24.76 | 1.583 | 24 | 2.49 | 84 | 49.5 | 1.7633 | 0.212 | 12 | 1.76 | 0.026 | 0.331 | 0.182 | 12 | 2.11 | 0 | 0.229 | 12 | 1.46 | 0 | 44.5 | 0.396 | 12 | 25.4 | 122.1 | 41 | 85 | 0.044 | 43.83 | 0.41 | 12 | 24.1 | 123 | 41 | 92 | 0.035 | 23.1 | 20.3 | 21.7 |  |  | MINIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 12.9902 |  | 17.6342 | 31.8931 | 2.317 | MINIMUM | 85.4431 | 8977.16 |  | 570.9251 | [6 empty] | 1.8107 | 1.8107 | 1.5994 | 0.22754 | 0.25303 | 0.19991 | 0.21128 | 0.16869 | 0.16869 | 2.4729 | 1.5 | 0.069605 | 0.069605 | 0.070048 | 1.091 | 0.49863 | 0.094098 | 3.5191 | 0.61854 | 5.0878 | 1.091 | 0.49499 | 0.097134 | 3.9999 | 0.70918 | 9.0232 |  | MIN | 0.41 | 12.3 | 20.6829 | 8.48 | 6.16 | 21.1 | 7 | 1.2114 |  |  |  | MIN | 0.42 | 12.5 | 20.352 | 8.5478 | 6.16 | 21.1 | 7 | 1.2211 |  |  |  | MIN | 0.59 | 12.5 | 21.6 | 12.744 | 6.21 | 20.7 | 7 | 1.8206 |  |  |  | 1.2114
AVERAGE | 6.54 | 17.6667 | 18 | 6.26 | 127.1667 | 162.1667 | 21.0833 | 0.49683 | 0.042 | 6.1 | 10.6667 | 0.064667 | 6.1317 | 11 |  | 6.12 | 10.8333 |  | 6.1825 | 0.366 | 5.25 | 0.485 | 21.225 | 12.2 | 0.45569 | 0.055833 | 6.16 | 0.4045 | 6 | 0.4575 | 21.225 | 12.25 | 0.45707 | 6.19 | 0.39575 | 6 | 0.6225 | 21 | 12.375 | 0.44083 | 0.035333 | 2 | 0.29333 | 0.013 | 0.055167 | 0.030333 | 2 | 0.35167 |  | 0.038167 | 2 | 0.24333 |  | 7.4167 | 0.066 | 2 | 4.2333 | 20.35 | 20.5 | 42.5 | 0.022 | 7.305 | 0.068333 | 2 | 4.0167 | 20.5 | 20.5 | 46 | 0.0175 | 3.85 | 3.3833 | 3.6167 |  |  | MAXIMUM | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 |  | 14.2589 |  | 19.7698 | 33.8688 | 2.8339 | MAXIMUM | 86.3756 | 9715.0088 |  | 570.9251 | [6 empty] | 1.8703 | 1.8679 | 1.7885 | 0.23003 | 0.26004 | 0.22262 | 0.23003 | 0.17228 | 0.17228 | 2.4729 | 3 | 0.070658 | 0.070658 | 0.070658 | 1.1591 | 0.49918 | 0.097957 | 3.538 | 0.69241 | 5.1453 | 1.1084 | 0.51386 | 0.1032 | 4.1508 | 0.71519 | 9.1182
MINIMUM | 6.51 | 17 | 18 | 5.63 | 123 | 159 | 20.8 | 0.476 | 0.041 | 6 | 10 | 0.06 | 6.04 | 11 |  | 6.07 | 10 |  | 6.15 | 0.316 | 5 | 0.41 | 20.9 | 11.7 | 0.44193 | 0.052 | 6.13 | 0.369 | 5 | 0.42 | 20.8 | 11.7 | 0.44193 | 6.16 | 0.345 | 5 | 0.59 | 20.7 | 12 | 0.43111 | 0.03 | 2 | 0.22 | 0.011 | 0.045 | 0.021 | 2 | 0.27 |  | 0.03 | 2 | 0.18 |  | 7.25 | 0.058 | 2 | 4 | 19.9 | 20 | 42 | 0.022 | 7.27 | 0.058 | 2 | 3.8 | 19.9 | 20 | 46 | 0.014 | 3.7 | 3.3 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 38320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1440 | 1440 | 1324 | 2190 | 2445 | 2060 | 2140 | 1630 | 1630 | 3900 | 0 | 4630 | 4630 | 4650 | 342 | 402 | 46.5 | 5000 | 1010 | 1225 | 167 | 203 | 24 | 2940 | 545 | 1086
MAXIMUM | 6.57 | 18 | 18 | 6.76 | 132 | 165 | 21.4 | 0.513 | 0.043 | 6.19 | 11 | 0.071 | 6.19 | 11 |  | 6.17 | 11 |  | 6.21 | 0.409 | 6 | 0.52 | 22 | 12.5 | 0.46395 | 0.061 | 6.2 | 0.452 | 7 | 0.51 | 22.2 | 12.5 | 0.46395 | 6.21 | 0.432 | 8 | 0.65 | 21.8 | 12.7 | 0.44926 | 0.041 | 2 | 0.4 | 0.015 | 0.062 | 0.043 | 2 | 0.55 |  | 0.053 | 2 | 0.39 |  | 7.6 | 0.07 | 2 | 4.6 | 20.8 | 21 | 43 | 0.022 | 7.37 | 0.073 | 2 | 4.2 | 20.9 | 21 | 46 | 0.021 | 3.9 | 3.6 | 4 | [17 empty] | AVERAGE | 12773.3333 | [9 empty] | 480 | 480 | 441.3333 | 730 | 815 | 686.6667 | 713.3333 | 543.3333 | 543.3333 | 1300 |  | 1543.3333 | 1543.3333 | 1550 | 114 | 134 | 15.5 | 1666.6667 | 336.6667 | 408.3333 | 55.6667 | 67.6667 | 8 | 980 | 181.6667 | 362
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1172 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.452 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.41 | [5 empty] | 6.1775 |  |  |  |  | 0.053 |  |  |  |  | 0.41 | [6 empty] | 0.053 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 12400 | [9 empty] | 460 | 470 | 424 | 700 | 800 | 615 | 650 | 530 | 530 | 1300 |  | 1500 | 1500 | 1500 | 110 | 129 | 15 | 1620 | 320 | 395 | 54 | 64 | 8 | 970 | 175 | 350
[90 empty] | MAXIMUM | 13000 | [9 empty] | 500 | 490 | 450 | 750 | 825 | 725 | 750 | 550 | 550 | 1300 |  | 1570 | 1570 | 1580 | 120 | 137 | 16 | 1710 | 350 | 415 | 57 | 70 | 8 | 1000 | 185 | 368
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.582 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827740 |  | END: | 23827740 |  |  | Alum | 4837 | 6635 | 6635 | 7566 | 7566 | 0 | [44 empty] | 0.41 | 12.3 | 20.6829 | 8.48 | 6.16 | 21.1 | 7 | 1.2114
[73 empty] | FINISHED 2 | 20.31 |  | TOTAL MGD: |  | 14.582 |  |  | FINISHED SOUTH 2 |  | START: | 45136060 |  | END: | 45150642 |  |  | Caustic | 3773 | 9114 | 9114
[73 empty] | TOTAL RAW | 36.477 |  | TOTAL MGD: |  | 6.081 |  |  | FINISHED CONWAY |  | START: | 10754501 |  | END: | 10760582 |  |  | Hypochlorite | 10 |  | 24
[76 empty] | TOTAL MGD: |  | 14.229 |  |  | FINISHED PERRY |  | START: | 34958891 |  | END: | 34973120 |  |  | Phosphate | 3341
[76 empty] | TOTAL MGD: |  | 12.044 |  |  | RAW PLANT 1 |  | START: | 32032571 |  | END: | 32044615 |  |  | Fluoride | 1050 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 12.084 |  |  | RAW PLANT 2 |  | START: | 31995781 |  | END: | 32007865 |  |  | Cal~Flo | 6.78 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.349 |  |  | RAW PLANT 3 |  | START: | 8632261 |  | END: | 8644610 |  |  | Zinc | 2452
[76 empty] | TOTAL MGD: |  | 0.962 |  |  | DECANT |  | START: | 1955894 |  | END: | 1956856 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.9298 |  |  | BLOW DOWN |  | START: | 9263.5324 |  | END: | 9265.4622 |  |  | NH3 | 12.22 |  | BI-SUL | 1000
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 571
23827740
45150642
10760582
34973120
32044615
32007865
8644610
1956856
9265.4622
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 27
DATE: | 2019-04-27 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-04-27 | [23 empty] | DATE: | 2019-04-27
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-27 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43582.0122 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 12.9902 | 1,2 | 19.0253 | 32.0155 | 2.8339 | 43582.0122 | 85.4431 | 9715.0088 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8703 | 1.8329 | 1.6832 | 0.23003 | 0.25303 | 0.22236 | 0.23003 | 0.16869 | 0.16869 | 2.4729 | 1.5 | 0.069605 | 0.069605 | 0.070048 | 1.1591 | 0.49863 | 0.094098 | 3.5226 | 0.67084 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 4.0134 | 0.70918 | 9.0232 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.12 | 0.436 | 6 | 0.46 | 21 | 12.3 | 0.45844 |  | 6.14 | 0.429 | 7 | 0.49 | 20.7 | 12.3 | 0.45844 | 6.15 | 0.41 | 7 | 0.59 | 20.7 | 12.3 | 0.43889 | [13 empty] | 7.3 | 0.07 | 2 | 4.1 | 19.9 |  |  |  | 7.23 | 0.0712 | 2 | 3.8 | 19.9 |  |  |  | 3.8 | 3.3 | 3.4 | [18 empty] | 13000 | [6 empty] | 0 | 0 | 0 | 500 | 490 | 450 | 750 | 825 | 725 | 750 | 550 | 550 | 1300 |  | 1570 | 1570 | 1580 | 120 | 137 | 15.5 | 1710 | 350 | 415 | 57 | 69 | 8 | 1000 | 185 | 368 |  | 1:00 | 0.46 | 12.3 | 20.6829 | 9.5141 | 6.12 | 21 | 7 | 1.3592 | 20 | 6.5 | 0.33844 | 1:00 | 0.49 | 12.3 | 20.6829 | 10.1346 | 6.14 | 20.7 | 7 | 1.4478 | 20 | 6.5 | 0.33844 | 1:00 | 0.59 | 12.3 | 21.9512 | 12.9512 | 6.15 | 20.7 | 7 | 1.8502 | 20 | 6.5 | 0.31889
2:00 | [72 empty] | 43582.0657 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 12.9902 | 1,2 | 19.0253 | 32.0155 | 2.8339 | 43582.0657 | 85.4431 | 9715.0088 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8703 | 1.8329 | 1.6832 | 0.23003 | 0.25303 | 0.22236 | 0.23003 | 0.16869 | 0.16869 | 2.4729 | 1.5 | 0.069605 | 0.069605 | 0.070048 | 1.1591 | 0.49863 | 0.094098 | 3.5226 | 0.67084 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 4.0134 | 0.70918 | 9.0232 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.51 | 18 | 18 | 6.7 | 129 | 161 | 20.8 | 0.496 |  | 6.11 | 11 | 0.067 | 6.09 | 11 |  | 6.07 | 11 | [8 empty] | 0.053 | [14 empty] | 0.036 | 2 | 0.3 |  | 0.055 | 0.031 | 2 | 0.29 |  | 0.04 | 2 | 0.23 | [38 empty] | 13000 | [6 empty] | 0 | 0 | 0 | 500 | 490 | 450 | 750 | 825 | 725 | 750 | 550 | 550 | 1300 |  | 1570 | 1570 | 1580 | 120 | 137 | 15.5 | 1710 | 350 | 415 | 57 | 69 | 8 | 1000 | 185 | 368 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43582.3285 | 2,3,4,6 | 63 | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 | 1,3 | 13.9 | 1,2 | 19.5 | 33.4 | 2.8 | 7:53 | 86 | 9592 | 0 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 1.7 | 0.22 | 0.26 | 0.22 | 0.22 | 0.2 | 0.21 | 2.28 | 3 | 0.07 | 0.07 | 0.07 | 1.1 | 0.5 | 0.1 | 3.5 | 0.6 | 5.1 | 1.1 | 0.49 | 0.1 | 4 | 0.6 | 9.1 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.23 | 0.07 | 2 | 4.3 | 19.9 |  |  |  | 7.38 | 0.073 | 2 | 4.2 | 19.5 |  |  |  | 3.7 | 3.3 | 3.5 | [18 empty] | 12300 | [6 empty] | 0 | 0 | 0 | 460 | 460 | 420 | 680 | 800 | 680 | 690 | 600 | 640 | 1200 |  | 1490 | 1480 | 1490 | 106 | 129 | 16 | 1580 | 300 | 395 | 54 | 64 | 8 | 910 | 155 | 349 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43582.8126 | 2,3,4,6 | 55 | 11.8 | 11.8 | 11.9 | 35.5 | 11.3 | 11.3 | 11.4 | 34 | ,1,3 | 16.9358 | 1,2 | 14.976 | 31.9118 | 2.1845 | 43582.8126 | 85.4024 | 9100.1348 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8711 | 1.8711 | 1.7571 | 0.22561 | 0.25784 | 0.21755 | 0.21755 | 0.16938 | 0.16938 | 2.2827 | 4 | 0.070032 | 0.070032 | 0.069418 | 1.0986 | 0.49444 | 0.095898 | 3.7268 | 0.64591 | 5.0997 | 1.0889 | 0.4939 | 0.10139 | 4.0415 | 0.66025 | 8.9326 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.52 | 18 | 17 | 6.58 | 124 | 160 | 21 | 0.494 |  | 6.06 | 11 | 0.054 | 6.06 | 11 |  | 6.05 | 11 | [8 empty] | 0.053 | [14 empty] | 0.033 | 2 | 0.3 |  | 0.05 | 0.026 | 2 | 0.29 |  | 0.053 | 2 | 0.28 | [38 empty] | 12400 | [6 empty] | 0 | 0 | 0 | 475 | 475 | 450 | 700 | 800 | 675 | 675 | 530 | 530 | 1200 |  | 1500 | 1500 | 1500 | 108 | 129 | 15 | 1720 | 320 | 395 | 54 | 65 | 8 | 950 | 165 | 349 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43582.9436 | 2,3,4,6 | 55 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 16.3267 | 1,2 | 17.7221 | 34.0488 | 2.1845 | 43582.9436 | 86.1004 | 9592.034 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 1.7955 | 1.6832 | 0.23003 | 0.2607 | 0.21776 | 0.21776 | 0.17482 | 0.17482 | 2.2827 | 4 | 0.066501 | 0.066501 | 0.066501 | 1.1398 | 0.49863 | 0.091063 | 3.7051 | 0.66126 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 3.9967 | 0.67084 | 8.9986 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6.15 | 0.36 | 6 | 0.52 | 20.5 | 11.7 | 0.44193 |  | 6.11 | 0.444 | 6 | 0.49 | 20.5 | 11.7 | 0.44193 | 6.16 | 0.463 | 6 | 0.64 | 20.5 | 11.9 | 0.42852 |  |  |  | 0.024 | [9 empty] | 7.11 | 0.072 | 2 | 4.4 | 20 | 20 | 42 | 0.021 | 7.59 | 0.077 | 2 | 4.7 | 19.9 | 20 | 45 | 0.013 | 3.9 | 3.4 | 3.6 | [18 empty] | 13100 | [6 empty] | 0 | 0 | 0 | 480 | 480 | 450 | 750 | 850 | 710 | 710 | 570 | 570 | 1200 |  | 1500 | 1500 | 1500 | 118 | 137 | 15 | 1800 | 345 | 415 | 57 | 69 | 8 | 980 | 175 | 367 |  | 9:00 | 0.52 | 11.7 | 21.7436 | 11.3067 | 6.15 | 20.5 | 7 | 1.6152 | 20 | 6.5 | 0.32193 | 9:00 | 0.49 | 11.7 | 21.7436 | 10.6544 | 6.11 | 20.5 | 7 | 1.5221 | 20 | 6.5 | 0.32193 | 9:00 | 0.64 | 11.9 | 22.6891 | 14.521 | 6.16 | 20.5 | 7 | 2.0744 | 20 | 6.5 | 0.30852
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.53 | 18 | 18 | 6.24 | 128 | 160 | 21 | 0.491 |  | 6 | 11 | 0.057 | 6.01 | 10 |  | 6.01 | 11 | [8 empty] | 0.05 | [14 empty] | 0.077 | 2 | 0.35 |  | 0.051 | 0.033 | 2 | 0.18 |  | 0.05 | 2 | 0.24 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.11 | 0.318 | 5 | 0.49 | 20.9 | 11.6 | 0.43918 |  | 6.19 | 0.333 | 5 | 0.43 | 21 | 11.7 | 0.44193 | 6.16 | 0.363 | 6 | 0.63 | 20.6 | 11.9 | 0.42852 | [13 empty] | 7.3 | 0.067 | 2 | 4.4 | 20.4 |  |  |  | 7.21 | 0.061 | 2 | 4.1 | 20.9 |  |  |  | 3.9 | 3.1 | 3.5 | [55 empty] | 13:00 | 0.49 | 11.6 | 21.931 | 10.7462 | 6.11 | 20.9 | 7 | 1.5352 | 20 | 6.5 | 0.31918 | 13:00 | 0.43 | 11.7 | 21.7436 | 9.3497 | 6.19 | 21 | 7 | 1.3357 | 20 | 6.5 | 0.32193 | 13:00 | 0.63 | 11.9 | 22.6891 | 14.2941 | 6.16 | 20.6 | 7 | 2.042 | 20 | 6.5 | 0.30852
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.56 | 18 | 18 | 6.31 | 125 | 160 | 21.3 | 0.484 |  | 6.14 | 11 | 0.063 | 6.2 | 11 |  | 6.2 | 11 | [8 empty] | 0.05 | [14 empty] | 0.057 | 2 | 0.3 |  | 0.05 | 0.019 | 2 | 0.21 |  | 0.048 | 2 | 0.24 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.36 | 0.07 | 2 | 4 | 20.2 |  |  |  | 7.3 | 0.072 | 2 | 3.8 | 20.4 |  |  |  | 3.9 | 3.4 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.51 | 18 | 18 | 6.03 | 123 | 162 | 21.2 | 0.471 |  | 6.18 | 11 | 0.074 | 6.21 | 11 |  | 6.19 | 11 | [8 empty] | 0.052 | [14 empty] | 0.052 | 2 | 0.33 |  | 0.055 | 0.031 | 2 | 0.26 |  | 0.046 | 2 | 0.29 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.039 | [9 empty] | 6.2 | 0.264 | 5 | 0.51 | 21 | 11.7 | 0.44193 |  | 6.23 | 0.249 | 5 | 0.46 | 21.1 | 11.7 | 0.44193 | 6.24 | 0.38 | 6 | 0.66 | 21 | 11.7 | 0.42333 |  |  |  | 0.008 | [9 empty] | 7.38 | 0.069 | 2 | 4 | 20.6 | 21 | 43 | 0.023 | 7.32 | 0.073 | 2 | 3.8 | 20.3 | 20 | 46 | 0.012 | 3.8 | 3.4 | 2.9 | [55 empty] | 21:00 | 0.51 | 11.7 | 21.7436 | 11.0892 | 6.2 | 21 | 7 | 1.5842 | 20 | 6.5 | 0.32193 | 21:00 | 0.46 | 11.7 | 21.7436 | 10.0021 | 6.23 | 21.1 | 7 | 1.4289 | 20 | 6.5 | 0.32193 | 21:00 | 0.66 | 11.7 | 23.0769 | 15.2308 | 6.24 | 21 | 7 | 2.1758 | 20 | 6.5 | 0.30333
22:00 | [72 empty] | DOSE |  | TOTAL | 60.7 | 60.7 | 60.8 | 182.2 | 58.2 | 58.2 | 58.3 | 174.7 | 0 | 73.143 | 0 | 90.2486 | 163.3917 | 12.8368 | TOTAL | 428.389 | 47714.1864 | 0 | 2854.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2071 | 9.1323 | 8.5068 | 1.1357 | 1.2846 | 1.1 | 1.1154 | 0.88158 | 0.89158 | 11.7912 | 14 | 0.34574 | 0.34574 | 0.34602 | 5.6565 | 2.4903 | 0.47516 | 17.9769 | 3.2489 | 25.4631 | 5.4923 | 2.4907 | 0.4928 | 20.065 | 3.3495 | 45.0776 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.52 | 18 | 18 | 6.06 | 119 | 160 | 21 | 0.493 |  | 6.18 | 11 | 0.073 | 6.19 | 11 |  | 6.18 | 11 | [8 empty] | 0.053 | [14 empty] | 0.046 | 2 | 0.33 |  | 0.054 | 0.033 | 2 | 0.29 |  | 0.05 | 2 | 0.3 | [22 empty] | AVERAGE | 12.14 | 12.14 | 12.16 | 36.44 | 11.64 | 11.64 | 11.66 | 34.94 |  | 14.6286 |  | 18.0497 | 32.6783 | 2.5674 | AVERAGE | 85.6778 | 9542.8373 |  | 570.9401 | 0 | 0 | 0 |  |  |  | 1.8414 | 1.8265 | 1.7014 | 0.22714 | 0.25692 | 0.22001 | 0.22307 | 0.17632 | 0.17832 | 2.3582 | 2.8 | 0.069149 | 0.069149 | 0.069203 | 1.1313 | 0.49806 | 0.095032 | 3.5954 | 0.64977 | 5.0926 | 1.0985 | 0.49814 | 0.098559 | 4.013 | 0.66989 | 9.0155 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.15 | 108 | 107 | 37.92 | 748 | 963 | 126.3 | 2.929 | 0.076 | 36.67 | 66 | 0.388 | 36.76 | 65 | 0 | 36.7 | 66 | 0 | 24.58 | 1.378 | 22 | 1.98 | 83.4 | 47.3 | 1.7815 | 0.311 | 24.67 | 1.455 | 23 | 1.87 | 83.3 | 47.4 | 1.7842 | 24.71 | 1.616 | 25 | 2.52 | 82.8 | 47.8 | 1.7193 | 0.301 | 12 | 1.91 | 0.032 | 0.315 | 0.173 | 12 | 1.52 | 0 | 0.287 | 12 | 1.58 | 0 | 43.68 | 0.418 | 12 | 25.2 | 121 | 41 | 85 | 0.044 | 44.03 | 0.4272 | 12 | 24.4 | 120.9 | 40 | 91 | 0.025 | 23 | 19.9 | 19.7 |  |  | MINIMUM | 11.7 | 11.7 | 11.7 | 35.1 | 11.2 | 11.2 | 11.2 | 33.6 |  | 12.9902 |  | 14.976 | 31.9118 | 2.1845 | MINIMUM | 85.4024 | 9100.1348 |  | 570.9251 | [6 empty] | 1.7955 | 1.7955 | 1.6832 | 0.22 | 0.25303 | 0.21755 | 0.21755 | 0.16869 | 0.16869 | 2.28 | 1.5 | 0.066501 | 0.066501 | 0.066501 | 1.0986 | 0.49444 | 0.091063 | 3.5 | 0.6 | 5.0878 | 1.0889 | 0.49 | 0.097134 | 3.9967 | 0.6 | 8.9326 |  | MIN | 0.46 | 12.3 | 20.6829 | 9.5141 | 6.12 | 21 | 7 | 1.3592 |  |  |  | MIN | 0.43 | 11.7 | 21.7436 | 9.3497 | 6.19 | 21 | 7 | 1.3357 |  |  |  | MIN | 0.59 | 12.3 | 21.9512 | 12.9512 | 6.15 | 20.7 | 7 | 1.8502 |  |  |  | 1.3357
AVERAGE | 6.525 | 18 | 17.8333 | 6.32 | 124.6667 | 160.5 | 21.05 | 0.48817 | 0.038 | 6.1117 | 11 | 0.064667 | 6.1267 | 10.8333 |  | 6.1167 | 11 |  | 6.145 | 0.3445 | 5.5 | 0.495 | 20.85 | 11.825 | 0.44537 | 0.051833 | 6.1675 | 0.36375 | 5.75 | 0.4675 | 20.825 | 11.85 | 0.44606 | 6.1775 | 0.404 | 6.25 | 0.63 | 20.7 | 11.95 | 0.42981 | 0.050167 | 2 | 0.31833 | 0.016 | 0.0525 | 0.028833 | 2 | 0.25333 |  | 0.047833 | 2 | 0.26333 |  | 7.28 | 0.069667 | 2 | 4.2 | 20.1667 | 20.5 | 42.5 | 0.022 | 7.3383 | 0.0712 | 2 | 4.0667 | 20.15 | 20 | 45.5 | 0.0125 | 3.8333 | 3.3167 | 3.2833 |  |  | MAXIMUM | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 |  | 16.9358 |  | 19.5 | 34.0488 | 2.8339 | MAXIMUM | 86.1004 | 9715.0088 |  | 571 | [6 empty] | 1.8711 | 1.8711 | 1.7571 | 0.23003 | 0.2607 | 0.22236 | 0.23003 | 0.2 | 0.21 | 2.4729 | 4 | 0.070032 | 0.070032 | 0.070048 | 1.1591 | 0.5 | 0.1 | 3.7268 | 0.67084 | 5.1 | 1.1011 | 0.50227 | 0.10139 | 4.0415 | 0.70918 | 9.1
MINIMUM | 6.51 | 18 | 17 | 6.03 | 119 | 160 | 20.8 | 0.471 | 0.037 | 6 | 11 | 0.054 | 6.01 | 10 |  | 6.01 | 11 |  | 6.11 | 0.264 | 5 | 0.46 | 20.5 | 11.6 | 0.43918 | 0.05 | 6.11 | 0.249 | 5 | 0.43 | 20.5 | 11.7 | 0.44193 | 6.15 | 0.363 | 6 | 0.59 | 20.5 | 11.7 | 0.42333 | 0.033 | 2 | 0.3 | 0.008 | 0.05 | 0.019 | 2 | 0.18 |  | 0.04 | 2 | 0.23 |  | 7.11 | 0.067 | 2 | 4 | 19.9 | 20 | 42 | 0.021 | 7.21 | 0.061 | 2 | 3.8 | 19.5 | 20 | 45 | 0.012 | 3.7 | 3.1 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 63800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2415 | 2395 | 2220 | 3630 | 4100 | 3515 | 3575 | 2800 | 2840 | 6200 | 0 | 7630 | 7620 | 7650 | 572 | 669 | 77 | 8520 | 1665 | 2035 | 279 | 336 | 40 | 4840 | 865 | 1801
MAXIMUM | 6.56 | 18 | 18 | 6.7 | 129 | 162 | 21.3 | 0.496 | 0.039 | 6.18 | 11 | 0.074 | 6.21 | 11 |  | 6.2 | 11 |  | 6.2 | 0.436 | 6 | 0.52 | 21 | 12.3 | 0.45844 | 0.053 | 6.23 | 0.444 | 7 | 0.49 | 21.1 | 12.3 | 0.45844 | 6.24 | 0.463 | 7 | 0.66 | 21 | 12.3 | 0.43889 | 0.077 | 2 | 0.35 | 0.024 | 0.055 | 0.033 | 2 | 0.29 |  | 0.053 | 2 | 0.3 |  | 7.38 | 0.072 | 2 | 4.4 | 20.6 | 21 | 43 | 0.023 | 7.59 | 0.077 | 2 | 4.7 | 20.9 | 20 | 46 | 0.013 | 3.9 | 3.4 | 3.6 | [17 empty] | AVERAGE | 12760 | [9 empty] | 483 | 479 | 444 | 726 | 820 | 703 | 715 | 560 | 568 | 1240 |  | 1526 | 1524 | 1530 | 114.4 | 133.8 | 15.4 | 1704 | 333 | 407 | 55.8 | 67.2 | 8 | 968 | 173 | 360.2
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1183 |  | TOTAL AVG COAG ALK: |  |  |  | 10.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.463 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.43 | [5 empty] | 6.1633 |  |  |  |  | 0.077 |  |  |  |  | 0.43 | [6 empty] | 0.077 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 12300 | [9 empty] | 460 | 460 | 420 | 680 | 800 | 675 | 675 | 530 | 530 | 1200 |  | 1490 | 1480 | 1490 | 106 | 129 | 15 | 1580 | 300 | 395 | 54 | 64 | 8 | 910 | 155 | 349
[90 empty] | MAXIMUM | 13100 | [9 empty] | 500 | 490 | 450 | 750 | 850 | 725 | 750 | 600 | 640 | 1300 |  | 1570 | 1570 | 1580 | 120 | 137 | 16 | 1800 | 350 | 415 | 57 | 69 | 8 | 1000 | 185 | 368
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.21 |  | TOTAL MGD: |  | 0.002 |  |  | FINISHED SOUTH 1 |  | START: | 23827740 |  | END: | 23827742 |  |  | Alum | 4837 | 4693 | 4693 | 6371 | 6371 | 0 | [44 empty] | 0.43 | 11.7 | 21.7436 | 9.3497 | 6.19 | 21 | 7 | 1.3357
[73 empty] | FINISHED 2 | 14.618 |  | TOTAL MGD: |  | 14.208 |  |  | FINISHED SOUTH 2 |  | START: | 45150642 |  | END: | 45164850 |  |  | Caustic | 3602 | 9159 | 9159
[73 empty] | TOTAL RAW | 36.581 |  | TOTAL MGD: |  | 4.003 |  |  | FINISHED CONWAY |  | START: | 10760582 |  | END: | 10764585 |  |  | Hypochlorite | 8 |  | 21
[76 empty] | TOTAL MGD: |  | 10.615 |  |  | FINISHED PERRY |  | START: | 34973120 |  | END: | 34983735 |  |  | Phosphate | 3332
[76 empty] | TOTAL MGD: |  | 12.139 |  |  | RAW PLANT 1 |  | START: | 32044615 |  | END: | 32056754 |  |  | Fluoride | 950 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 12.1 |  |  | RAW PLANT 2 |  | START: | 32007865 |  | END: | 32019965 |  |  | Cal~Flo | 11.59 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.342 |  |  | RAW PLANT 3 |  | START: | 8644610 |  | END: | 8656952 |  |  | Zinc | 2514
[76 empty] | TOTAL MGD: |  | 1.18 |  |  | DECANT |  | START: | 1956856 |  | END: | 1958036 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.811 |  |  | BLOW DOWN |  | START: | 9265.4622 |  | END: | 9267.2732 |  |  | NH3 | 11.96 |  | BI-SUL | 995
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 550
23827742
45164850
10764585
34983735
32056754
32019965
8656952
1958036
9267.2732
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 28
DATE: | 2019-04-28 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-04-28 | [23 empty] | DATE: | 2019-04-28
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-28 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43583.0105 | 2,3,4,6 | 55 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 16.3267 | 1,2 | 17.7221 | 34.0488 | 2.1845 | 43583.0105 | 86.1004 | 9592.034 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 1.7955 | 1.6832 | 0.23003 | 0.2607 | 0.21776 | 0.21776 | 0.17482 | 0.17482 | 2.2827 | 4 | 0.066501 | 0.066501 | 0.066501 | 1.1398 | 0.49863 | 0.091063 | 3.7051 | 0.66126 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 3.9967 | 0.67084 | 8.9986 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.21 | 0.4 | 7 | 0.49 | 21 | 12.4 | 0.46119 |  | 6.2 | 0.398 | 8 | 0.46 | 21.1 | 12.4 | 0.46119 | 6.22 | 0.416 | 8 | 0.63 | 21.2 | 12.4 | 0.44148 | [13 empty] | 7.25 | 0.073 | 2 | 4.4 | 20.5 |  |  |  | 7.23 | 0.076 | 2 | 4.1 | 20.1 |  |  |  | 3.8 | 3.4 | 2.9 | [18 empty] | 13100 | [6 empty] | 0 | 0 | 0 | 480 | 480 | 450 | 750 | 850 | 710 | 710 | 570 | 570 | 1200 |  | 1500 | 1500 | 1500 | 118 | 137 | 15 | 1800 | 345 | 415 | 57 | 69 | 8 | 980 | 175 | 367 |  | 1:00 | 0.49 | 12.4 | 20.5161 | 10.0529 | 6.21 | 21 | 7 | 1.4361 | 20 | 6.5 | 0.34119 | 1:00 | 0.46 | 12.4 | 20.5161 | 9.4374 | 6.2 | 21.1 | 7 | 1.3482 | 20 | 6.5 | 0.34119 | 1:00 | 0.63 | 12.4 | 21.7742 | 13.7177 | 6.22 | 21.2 | 7 | 1.9597 | 20 | 6.5 | 0.32148
2:00 | [72 empty] | 43583.3228 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 15.7104 | 1,2 | 19.8288 | 35.5392 | 2.1845 | 43583.3228 | 85.6272 | 9469.0592 | 0 | 618.5022 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 1.7955 | 1.6832 | 0.23003 | 0.27603 | 0.22696 | 0.24536 | 0.17482 | 0.17482 | 2.4729 | 6 | 0.070048 | 0.070935 | 0.070048 | 1.1011 | 0.49863 | 0.097134 | 3.6659 | 0.59418 | 5.0878 | 1.1204 | 0.50955 | 0.097134 | 4.1501 | 0.69001 | 8.9986 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.56 | 18 | 18 | 6.69 | 127 | 160 | 21.2 | 0.496 |  | 6.08 | 11 | 0.067 | 6.2 | 11 |  | 6.22 | 11 | [8 empty] | 0.053 | [14 empty] | 0.046 | 2 | 0.3 |  | 0.053 | 0.036 | 2 | 0.23 |  | 0.051 | 2 | 0.2 | [38 empty] | 13028 | [6 empty] | 0 | 0 | 0 | 480 | 480 | 450 | 750 | 900 | 740 | 800 | 570 | 570 | 1300 |  | 1580 | 1600 | 1580 | 114 | 137 | 16 | 1730 | 310 | 415 | 58 | 70 | 8 | 1020 | 180 | 367 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43583.8514 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 14.7384 | 1,2 | 18.2362 | 32.9746 | 1.8533 | 43583.8514 | 85.4431 | 9407.5718 | 0 | 618.5022 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 1.8703 | 1.7955 | 0.23003 | 0.27603 | 0.23003 | 0.24536 | 0.16255 | 0.17175 | 2.4729 | 4.5 | 0.070048 | 0.070935 | 0.070935 | 1.5261 | 0.49863 | 0.097134 | 3.5876 | 0.59418 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 4.1401 | 0.69001 | 8.9986 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.46 | 0.07 | 2 | 4.3 | 20.6 |  |  |  | 7.4 | 0.073 | 2 | 4.1 | 20.1 |  |  |  | 3.7 | 2.9 | 4.1 | [18 empty] | 13000 | [6 empty] | 0 | 0 | 0 | 480 | 500 | 480 | 750 | 900 | 750 | 800 | 530 | 560 | 1300 |  | 1580 | 1600 | 1600 | 158 | 137 | 16 | 1710 | 310 | 415 | 57 | 69 | 8 | 1020 | 180 | 367 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.54 | 18 | 18 | 6.63 | 123 | 159 | 21.1 | 0.486 |  | 6.09 | 10 | 0.06 | 6.15 | 11 |  | 6.14 | 11 | [8 empty] | 0.056 | [14 empty] | 0.046 | 2 | 0.43 |  | 0.052 | 0.024 | 2 | 0.27 |  | 0.046 | 2 | 0.24 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.28 | 0.362 | 6 | 0.59 | 20.5 | 12.3 | 0.45844 |  | 6.22 | 0.406 | 6 | 0.48 | 20.6 | 12.4 | 0.46119 | 6.25 | 0.461 | 7 | 0.65 | 20.6 | 12.8 | 0.45185 |  |  |  | 0.007 | [9 empty] | 7.22 | 0.073 | 2 | 4.6 | 19.9 | 20 | 46 | 0.021 | 7.28 | 0.076 | 2 | 4.3 | 20.2 | 20 | 48 | 0.015 | 3.9 | 3.3 | 4.2 | [55 empty] | 9:00 | 0.59 | 12.3 | 20.6829 | 12.2029 | 6.28 | 20.5 | 7 | 1.7433 | 20 | 6.5 | 0.33844 | 9:00 | 0.48 | 12.4 | 20.5161 | 9.8477 | 6.22 | 20.6 | 7 | 1.4068 | 20 | 6.5 | 0.34119 | 9:00 | 0.65 | 12.8 | 21.0938 | 13.7109 | 6.25 | 20.6 | 7 | 1.9587 | 20 | 6.5 | 0.33185
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.61 | 20 | 18 | 6.78 | 124 | 160 | 20.3 | 0.491 |  | 6.14 | 10 | 0.063 | 6.16 | 10 |  | 6.14 | 11 | [8 empty] | 0.055 | [14 empty] | 0.043 | 1 | 0.43 |  | 0.051 | 0.021 | 2 | 0.3 |  | 0.041 | 2 | 0.25 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.18 | 0.342 | 5 | 0.59 | 20.5 | 12.2 | 0.45569 |  | 6.16 | 0.362 | 5 | 0.56 | 21.1 | 12.2 | 0.45569 | 6.21 | 0.347 | 5 | 0.66 | 20.7 | 12.5 | 0.44407 | [13 empty] | 7.28 | 0.061 | 1 | 4.1 | 20.6 |  |  |  | 7.26 | 0.064 | 2 | 4.2 | 21 |  |  |  | 4.2 | 3.5 | 3.7 | [55 empty] | 13:00 | 0.59 | 12.2 | 20.8525 | 12.303 | 6.18 | 20.5 | 7 | 1.7576 | 20 | 6.5 | 0.33569 | 13:00 | 0.56 | 12.2 | 20.8525 | 11.6774 | 6.16 | 21.1 | 7 | 1.6682 | 20 | 6.5 | 0.33569 | 13:00 | 0.66 | 12.5 | 21.6 | 14.256 | 6.21 | 20.7 | 7 | 2.0366 | 20 | 6.5 | 0.32407
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.57 | 19 | 18 | 6.62 | 122 | 161 | 21.3 | 0.477 |  | 6.12 | 10 | 0.058 | 6.12 | 10 |  | 6.1 | 10 | [8 empty] | 0.05 | [14 empty] | 0.038 | 1 | 0.36 |  | 0.05 | 0.038 | 1 | 0.26 |  | 0.037 | 2 | 0.23 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.33 | 0.068 | 1 | 4.3 | 20.3 |  |  |  | 7.26 | 0.068 | 2 | 4.1 | 20.7 |  |  |  | 3.5 | 3.4 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.58 | 19 | 18 | 5.8 | 124 | 162 | 20.4 | 0.497 |  | 6.17 | 11 | 0.068 | 6.19 | 11 |  | 6.17 | 11 | [8 empty] | 0.057 | [14 empty] | 0.037 | 1 | 0.33 |  | 0.053 | 0.022 | 1 | 0.29 |  | 0.036 | 1 | 0.23 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.23 | 0.276 | 5 | 0.6 | 21.3 | 12.2 | 0.45569 |  | 6.22 | 0.249 | 5 | 0.59 | 21.2 | 12.3 | 0.45844 | 6.23 | 0.339 | 5 | 0.66 | 20.9 | 12.5 | 0.44407 |  |  |  | 0.014 | [9 empty] | 7.27 | 0.069 | 1 | 4.3 | 20.7 | 20 | 4.3 | 0.027 | 7.29 | 0.069 | 2 | 4.2 | 20 | 20 | 46 | 0.02 | 3.9 | 3.4 | 3.2 | [55 empty] | 21:00 | 0.6 | 12.2 | 20.8525 | 12.5115 | 6.23 | 21.3 | 7 | 1.7874 | 20 | 6.5 | 0.33569 | 21:00 | 0.59 | 12.3 | 20.6829 | 12.2029 | 6.22 | 21.2 | 7 | 1.7433 | 20 | 6.5 | 0.33844 | 21:00 | 0.66 | 12.5 | 21.6 | 14.256 | 6.23 | 20.9 | 7 | 2.0366 | 20 | 6.5 | 0.32407
22:00 | [72 empty] | DOSE |  | TOTAL | 37.2 | 37.2 | 37.2 | 111.6 | 35.7 | 35.7 | 35.7 | 107.1 | 0 | 46.7755 | 0 | 55.787 | 102.5626 | 6.2222 | TOTAL | 257.1706 | 28468.665 | 0 | 1807.9295 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3864 | 5.4612 | 5.162 | 0.69008 | 0.81276 | 0.67475 | 0.70849 | 0.5122 | 0.5214 | 7.2285 | 14.5 | 0.2066 | 0.20837 | 0.20748 | 3.767 | 1.4959 | 0.28533 | 10.9585 | 1.8496 | 15.2634 | 3.3227 | 1.5141 | 0.2914 | 12.2869 | 2.0509 | 26.9959 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 18 | 18 | 6.83 | 123 | 160 | 21.4 | 0.497 |  | 6.19 | 11 | 0.071 | 6.23 | 11 |  | 6.2 | 11 | [8 empty] | 0.057 | [14 empty] | 0.039 | 1 | 0.36 |  | 0.057 | 0.026 | 1 | 0.31 |  | 0.036 | 1 | 0.21 | [22 empty] | AVERAGE | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 |  | 15.5918 |  | 18.5957 | 34.1875 | 2.0741 | AVERAGE | 85.7235 | 9489.555 |  | 602.6432 | 0 | 0 | 0 |  |  |  | 1.7955 | 1.8204 | 1.7207 | 0.23003 | 0.27092 | 0.22492 | 0.23616 | 0.17073 | 0.1738 | 2.4095 | 4.8333 | 0.068866 | 0.069457 | 0.069161 | 1.2557 | 0.49863 | 0.09511 | 3.6528 | 0.61654 | 5.0878 | 1.1076 | 0.50469 | 0.097134 | 4.0956 | 0.68362 | 8.9986 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.39 | 112 | 108 | 39.35 | 743 | 962 | 125.7 | 2.944 | 0.084 | 36.79 | 63 | 0.387 | 37.05 | 64 | 0 | 36.97 | 65 | 0 | 24.9 | 1.38 | 23 | 2.27 | 83.3 | 49.1 | 1.831 | 0.328 | 24.8 | 1.415 | 24 | 2.09 | 84 | 49.3 | 1.8365 | 24.91 | 1.563 | 25 | 2.6 | 83.4 | 50.2 | 1.7815 | 0.249 | 8 | 2.21 | 0.021 | 0.316 | 0.167 | 9 | 1.66 | 0 | 0.247 | 10 | 1.36 | 0 | 43.81 | 0.414 | 9 | 26 | 122.6 | 40 | 50.3 | 0.048 | 43.72 | 0.426 | 12 | 25 | 122.1 | 40 | 94 | 0.035 | 23 | 19.9 | 21.5 |  |  | MINIMUM | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 |  | 14.7384 |  | 17.7221 | 32.9746 | 1.8533 | MINIMUM | 85.4431 | 9407.5718 |  | 570.9251 | [6 empty] | 1.7955 | 1.7955 | 1.6832 | 0.23003 | 0.2607 | 0.21776 | 0.21776 | 0.16255 | 0.17175 | 2.2827 | 4 | 0.066501 | 0.066501 | 0.066501 | 1.1011 | 0.49863 | 0.091063 | 3.5876 | 0.59418 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 3.9967 | 0.67084 | 8.9986 |  | MIN | 0.49 | 12.4 | 20.5161 | 10.0529 | 6.21 | 21 | 7 | 1.4361 |  |  |  | MIN | 0.46 | 12.4 | 20.5161 | 9.4374 | 6.2 | 21.1 | 7 | 1.3482 |  |  |  | MIN | 0.65 | 12.8 | 21.0938 | 13.7109 | 6.25 | 20.6 | 7 | 1.9587 |  |  |  | 1.3482
AVERAGE | 6.565 | 18.6667 | 18 | 6.5583 | 123.8333 | 160.3333 | 20.95 | 0.49067 | 0.042 | 6.1317 | 10.5 | 0.0645 | 6.175 | 10.6667 |  | 6.1617 | 10.8333 |  | 6.225 | 0.345 | 5.75 | 0.5675 | 20.825 | 12.275 | 0.45776 | 0.054667 | 6.2 | 0.35375 | 6 | 0.5225 | 21 | 12.325 | 0.45913 | 6.2275 | 0.39075 | 6.25 | 0.65 | 20.85 | 12.55 | 0.44537 | 0.0415 | 1.3333 | 0.36833 | 0.0105 | 0.052667 | 0.027833 | 1.5 | 0.27667 |  | 0.041167 | 1.6667 | 0.22667 |  | 7.3017 | 0.069 | 1.5 | 4.3333 | 20.4333 | 20 | 25.15 | 0.024 | 7.2867 | 0.071 | 2 | 4.1667 | 20.35 | 20 | 47 | 0.0175 | 3.8333 | 3.3167 | 3.5833 |  |  | MAXIMUM | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 |  | 16.3267 |  | 19.8288 | 35.5392 | 2.1845 | MAXIMUM | 86.1004 | 9592.034 |  | 618.5022 | [6 empty] | 1.7955 | 1.8703 | 1.7955 | 0.23003 | 0.27603 | 0.23003 | 0.24536 | 0.17482 | 0.17482 | 2.4729 | 6 | 0.070048 | 0.070935 | 0.070935 | 1.5261 | 0.49863 | 0.097134 | 3.7051 | 0.66126 | 5.0878 | 1.1204 | 0.50955 | 0.097134 | 4.1501 | 0.69001 | 8.9986
MINIMUM | 6.53 | 18 | 18 | 5.8 | 122 | 159 | 20.3 | 0.477 | 0.041 | 6.08 | 10 | 0.058 | 6.12 | 10 |  | 6.1 | 10 |  | 6.18 | 0.276 | 5 | 0.49 | 20.5 | 12.2 | 0.45569 | 0.05 | 6.16 | 0.249 | 5 | 0.46 | 20.6 | 12.2 | 0.45569 | 6.21 | 0.339 | 5 | 0.63 | 20.6 | 12.4 | 0.44148 | 0.037 | 1 | 0.3 | 0.007 | 0.05 | 0.021 | 1 | 0.23 |  | 0.036 | 1 | 0.2 |  | 7.22 | 0.061 | 1 | 4.1 | 19.9 | 20 | 4.3 | 0.021 | 7.23 | 0.064 | 2 | 4.1 | 20 | 20 | 46 | 0.015 | 3.5 | 2.9 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 39128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1440 | 1460 | 1380 | 2250 | 2650 | 2200 | 2310 | 1670 | 1700 | 3800 | 0 | 4660 | 4700 | 4680 | 390 | 411 | 47 | 5240 | 965 | 1245 | 172 | 208 | 24 | 3020 | 535 | 1101
MAXIMUM | 6.61 | 20 | 18 | 6.83 | 127 | 162 | 21.4 | 0.497 | 0.043 | 6.19 | 11 | 0.071 | 6.23 | 11 |  | 6.22 | 11 |  | 6.28 | 0.4 | 7 | 0.6 | 21.3 | 12.4 | 0.46119 | 0.057 | 6.22 | 0.406 | 8 | 0.59 | 21.2 | 12.4 | 0.46119 | 6.25 | 0.461 | 8 | 0.66 | 21.2 | 12.8 | 0.45185 | 0.046 | 2 | 0.43 | 0.014 | 0.057 | 0.038 | 2 | 0.31 |  | 0.051 | 2 | 0.25 |  | 7.46 | 0.073 | 2 | 4.6 | 20.7 | 20 | 46 | 0.027 | 7.4 | 0.076 | 2 | 4.3 | 21 | 20 | 48 | 0.02 | 4.2 | 3.5 | 4.2 | [17 empty] | AVERAGE | 13042.6667 | [9 empty] | 480 | 486.6667 | 460 | 750 | 883.3333 | 733.3333 | 770 | 556.6667 | 566.6667 | 1266.6667 |  | 1553.3333 | 1566.6667 | 1560 | 130 | 137 | 15.6667 | 1746.6667 | 321.6667 | 415 | 57.3333 | 69.3333 | 8 | 1006.6667 | 178.3333 | 367
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1561 |  | TOTAL AVG COAG ALK: |  |  |  | 10.6667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.461 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.2175 |  |  |  |  | 0.051 |  |  |  |  | 0.46 | [6 empty] | 0.051 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 13000 | [9 empty] | 480 | 480 | 450 | 750 | 850 | 710 | 710 | 530 | 560 | 1200 |  | 1500 | 1500 | 1500 | 114 | 137 | 15 | 1710 | 310 | 415 | 57 | 69 | 8 | 980 | 175 | 367
[90 empty] | MAXIMUM | 13100 | [9 empty] | 480 | 500 | 480 | 750 | 900 | 750 | 800 | 570 | 570 | 1300 |  | 1580 | 1600 | 1600 | 158 | 137 | 16 | 1800 | 345 | 415 | 58 | 70 | 8 | 1020 | 180 | 367
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.923 |  | TOTAL MGD: |  | 0.003 |  |  | FINISHED SOUTH 1 |  | START: | 23827742 |  | END: | 23827745 |  |  | Alum | 4916 | 3475 | 3475 | 4911 | 4911 | 0 | [44 empty] | 0.46 | 12.4 | 20.5161 | 9.4374 | 6.2 | 21.1 | 7 | 1.3482
[73 empty] | FINISHED 2 | 19.887 |  | TOTAL MGD: |  | 14.92 |  |  | FINISHED SOUTH 2 |  | START: | 45164850 |  | END: | 45179770 |  |  | Caustic | 3431 | 9016 | 9016
[73 empty] | TOTAL RAW | 38.496 |  | TOTAL MGD: |  | 5.467 |  |  | FINISHED CONWAY |  | START: | 10764585 |  | END: | 10770052 |  |  | Hypochlorite | 6 |  | 29.5
[76 empty] | TOTAL MGD: |  | 14.42 |  |  | FINISHED PERRY |  | START: | 34983735 |  | END: | 34998155 |  |  | Phosphate | 3275
[76 empty] | TOTAL MGD: |  | 12.664 |  |  | RAW PLANT 1 |  | START: | 32056754 |  | END: | 32069418 |  |  | Fluoride | 900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 12.785 |  |  | RAW PLANT 2 |  | START: | 32019965 |  | END: | 32032750 |  |  | Cal~Flo | 6.03 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 13.047 |  |  | RAW PLANT 3 |  | START: | 8656952 |  | END: | 8669999 |  |  | Zinc | 2508
[76 empty] | TOTAL MGD: |  | 1.128 |  |  | DECANT |  | START: | 1958036 |  | END: | 1959164 |  |  | Polymer | 21
[76 empty] | TOTAL MGD: |  | 1.8295 |  |  | BLOW DOWN |  | START: | 9267.2732 |  | END: | 9269.1027 |  |  | NH3 | 11.72 |  | BI-SUL | 990
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 619
23827745
45179770
10770052
34998155
32069418
32032750
8669999
1959164
9269.1027
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 29
DATE: | 2019-04-29 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2019-04-29 | [23 empty] | DATE: | 2019-04-29
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-29 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43584.0041 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 14.7384 | 1,2 | 18.2362 | 32.9746 | 1.8533 | 43584.0041 | 85.4431 | 9407.5718 | 0 | 618.5022 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 1.8703 | 1.7955 | 0.23003 | 0.27603 | 0.23003 | 0.24536 | 0.16255 | 0.17175 | 2.4729 | 4.5 | 0.070048 | 0.070935 | 0.070935 | 1.5261 | 0.49863 | 0.097134 | 3.5876 | 0.59418 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 4.1401 | 0.69001 | 8.9986 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.269 | 6 | 0.59 | 21.1 | 12.3 | 0.45844 |  | 6.19 | 0.283 | 5 | 0.6 | 21 | 12.3 | 0.45844 | 6.2 | 0.339 | 5 | 0.66 | 20.9 | 12.3 | 0.43889 | [13 empty] | 7.3 | 0.067 | 1 | 4.2 | 20.8 |  |  |  | 7.28 | 0.073 | 1 | 4.1 | 20.3 |  |  |  | 3.9 | 3.4 | 3.2 | [18 empty] | 13000 | [6 empty] | 0 | 0 | 0 | 480 | 500 | 480 | 750 | 900 | 750 | 800 | 530 | 560 | 1300 |  | 1580 | 1600 | 1600 | 158 | 137 | 16 | 1710 | 310 | 415 | 57 | 69 | 8 | 1020 | 180 | 367 |  | 1:00 | 0.59 | 12.3 | 20.6829 | 12.2029 | 6.19 | 21.1 | 7 | 1.7433 | 20 | 6.5 | 0.33844 | 1:00 | 0.6 | 12.3 | 20.6829 | 12.4098 | 6.19 | 21 | 7 | 1.7728 | 20 | 6.5 | 0.33844 | 1:00 | 0.66 | 12.3 | 21.9512 | 14.4878 | 6.2 | 20.9 | 7 | 2.0697 | 20 | 6.5 | 0.31889
2:00 | [72 empty] | 43584.1013 | 2,3,4,6 | 63 | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 | ,1,3 | 14.7384 | 1,2 | 18.2362 | 32.9746 | 1.8533 | 43584.1013 | 85.4431 | 9407.5718 | 0 | 618.5022 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7955 | 1.8703 | 1.7955 | 0.23003 | 0.27603 | 0.23003 | 0.24536 | 0.16255 | 0.17175 | 2.4729 | 4.5 | 0.070048 | 0.070935 | 0.070935 | 1.5261 | 0.49863 | 0.097134 | 3.5876 | 0.59418 | 5.0878 | 1.1011 | 0.50227 | 0.097134 | 4.1401 | 0.69001 | 8.9986 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.58 | 18 | 18 | 6.52 | 126 | 161 | 21.5 | 0.494 |  | 6.06 | 10 | 0.067 | 6.05 | 10 |  | 6.04 | 10 | [8 empty] | 0.048 | [14 empty] | 0.039 | 1 | 0.33 |  | 0.05 | 0.031 | 1 | 0.31 |  | 0.039 | 1 | 0.29 | [38 empty] | 13000 | [6 empty] | 0 | 0 | 0 | 480 | 500 | 480 | 750 | 900 | 750 | 800 | 530 | 560 | 1300 |  | 1580 | 1600 | 1600 | 158 | 137 | 16 | 1710 | 310 | 415 | 57 | 69 | 8 | 1020 | 180 | 367 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43584.3045 | 2,3,4,6 | 70 | 13 | 13 | 13 | 39 | 12.5 | 12.5 | 12.5 | 37.5 | ,1,3 | 14.9414 | 1,2 | 22.1659 | 37.1074 | 1.8533 | 43584.3045 | 83.606 | 9837.9836 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7805 | 1.7805 | 1.6381 | 0.21941 | 0.25744 | 0.21063 | 0.23404 | 0.15798 | 0.16383 | 2.4729 | 6 | 0.06964 | 0.070062 | 0.070062 | 1.1034 | 0.49895 | 0.095361 | 3.587 | 0.57478 | 5.0887 | 1.1034 | 0.48509 | 0.10403 | 4.2884 | 0.67514 | 9.0102 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.33 | 0.069 | 1 | 4.2 | 20.9 |  |  |  | 7.28 | 0.071 | 1 | 4.3 | 20.3 |  |  |  | 3.5 | 3.2 | 4 | [18 empty] | 13336 | [6 empty] | 0 | 0 | 0 | 500 | 500 | 460 | 750 | 880 | 720 | 800 | 540 | 560 | 1300 |  | 1650 | 1660 | 1660 | 120 | 144 | 16.5 | 1700 | 315 | 436 | 60 | 70 | 9 | 1060 | 185 | 386 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43584.8707 | 2,3,4,6 | 95 | 13 | 13 | 13 | 39 | 12 | 12 | 13.5 | 37.5 | ,1,2,3 | 15.4526 | 1,2 | 20.8253 | 36.2779 | 2.0376 | 43584.8707 | 83.255 | 9100.1348 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8547 | 1.8547 | 1.6486 | 0.21941 | 0.25598 | 0.21063 | 0.23404 | 0.15359 | 0.15505 | 2.4729 | 3 | 0.070344 | 0.070344 | 0.062528 | 1.1494 | 0.5053 | 0.096324 | 3.9744 | 0.45617 | 6.0788 | 1.1069 | 0.44915 | 0.096324 | 3.9756 | 0.7265 | 9.5099 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.53 | 19 | 18 | 6.85 | 123 | 162 | 21.4 | 0.483 |  | 6.05 | 11 | 0.058 | 6.01 | 11 |  | 6.01 | 11 | [8 empty] | 0.05 | [14 empty] | 0.026 | 2 | 0.46 |  | 0.051 | 0.025 | 2 | 0.51 |  | 0.067 | 2 | 0.42 | [38 empty] | 13280 | [6 empty] | 0 | 0 | 0 | 500 | 500 | 500 | 750 | 875 | 720 | 800 | 525 | 530 | 1300 |  | 1600 | 1600 | 1600 | 120 | 140 | 16 | 1870 | 240 | 500 | 65 | 70 | 9 | 1070 | 215 | 440 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.04 | [9 empty] | 6.18 | 0.342 | 5 | 0.55 | 21 | 12.9 | 0.47495 |  | 6.12 | 0.363 | 6 | 0.42 | 21.2 | 12.9 | 0.47495 | 6.15 | 0.48 | 6 | 0.66 | 20.9 | 13.3 | 0.46481 |  |  |  | 0.002 | [9 empty] | 7.06 | 0.063 | 2 | 4 | 20.4 | 21 | 42 | 0.021 | 6.95 | 0.058 | 2 | 2.8 | 20.5 | 22 | 44 | 0.008 | 3.9 | 3.2 | 3.7 | [55 empty] | 9:00 | 0.55 | 12.9 | 19.7209 | 10.8465 | 6.18 | 21 | 7 | 1.5495 | 20 | 6.5 | 0.35495 | 9:00 | 0.42 | 12.9 | 19.7209 | 8.2828 | 6.12 | 21.2 | 7 | 1.1833 | 20 | 6.5 | 0.35495 | 9:00 | 0.66 | 13.3 | 20.3008 | 13.3985 | 6.15 | 20.9 | 7 | 1.9141 | 20 | 6.5 | 0.34481
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.57 | 19 | 17 | 7.07 | 123 | 162 | 21.2 | 0.486 |  | 6.12 | 11 | 0.057 | 6.06 | 11 |  | 6.1 | 11 | [8 empty] | 0.053 | [14 empty] | 0.029 | 2 | 0.34 |  | 0.052 | 0.032 | 2 | 0.5 |  | 0.038 | 2 | 0.36 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.09 | 0.366 | 4 | 0.54 | 21.2 | 12.9 | 0.47495 |  | 6.04 | 0.36 | 4 | 0.46 | 21.6 | 12.9 | 0.47495 | 6.12 | 0.348 | 5 | 0.61 | 21.1 | 12.3 | 0.43889 | [13 empty] | 7.17 | 0.054 | 2 | 3.4 | 20.9 |  |  |  | 7.08 | 0.061 | 1 | 3.4 | 21 |  |  |  | 3.9 | 3.2 | 3.5 | [55 empty] | 13:00 | 0.54 | 12.9 | 19.7209 | 10.6493 | 6.09 | 21.2 | 7 | 1.5213 | 20 | 6.5 | 0.35495 | 13:00 | 0.46 | 12.9 | 19.7209 | 9.0716 | 6.04 | 21.6 | 7 | 1.2959 | 20 | 6.5 | 0.35495 | 13:00 | 0.61 | 12.3 | 21.9512 | 13.3902 | 6.12 | 21.1 | 7 | 1.9129 | 20 | 6.5 | 0.31889
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.56 | 20 | 17 | 6.78 | 119 | 159 | 21.6 | 0.454 |  | 6.11 | 12 | 0.048 | 6.07 | 12 |  | 6.07 | 12 | [8 empty] | 0.042 | [14 empty] | 0.042 | 2 | 0.3 |  | 0.043 | 0.026 | 2 | 0.38 |  | 0.049 | 2 | 0.22 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.17 | 0.06 | 2 | 4.2 | 21 |  |  |  | 7.11 | 0.064 | 2 | 3.4 | 20.8 |  |  |  | 3.8 | 3.3 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.49 | 19 | 18 | 6.84 | 124 | 162 | 21.8 | 0.485 |  | 6 | 11 | 0.06 | 6 | 11 |  | 6 | 11 | [8 empty] | 0.051 | [14 empty] | 0.04 | 2 | 0.33 |  | 0.049 | 0.029 | 2 | 0.36 |  | 0.05 | 2 | 0.21 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.05 | [9 empty] | 6.09 | 0.369 | 6 | 0.53 | 21.8 | 12.9 | 0.47495 |  | 6.08 | 0.356 | 6 | 0.5 | 21.7 | 12.9 | 0.47495 | 6.07 | 0.37 | 8 | 0.63 | 21.6 | 13.3 | 0.46481 |  |  |  | 0.016 | [9 empty] | 7.22 | 0.066 | 2 | 4.4 | 21 | 22 | 43 | 0.023 | 7.06 | 0.066 | 2 | 3.6 | 20.7 | 22 | 46 | 0.011 | 3.7 | 1.6 | 3.6 | [55 empty] | 21:00 | 0.53 | 12.9 | 19.7209 | 10.4521 | 6.09 | 21.8 | 7 | 1.4932 | 20 | 6.5 | 0.35495 | 21:00 | 0.5 | 12.9 | 19.7209 | 9.8605 | 6.08 | 21.7 | 7 | 1.4086 | 20 | 6.5 | 0.35495 | 21:00 | 0.63 | 13.3 | 20.3008 | 12.7895 | 6.07 | 21.6 | 7 | 1.8271 | 20 | 6.5 | 0.34481
22:00 | [72 empty] | DOSE |  | TOTAL | 50.8 | 50.8 | 50.8 | 152.4 | 48.3 | 48.3 | 49.8 | 146.4 | 0 | 59.8709 | 0 | 79.4635 | 139.3344 | 7.5974 | TOTAL | 337.7473 | 37753.262 | 0 | 2505.7269 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2261 | 7.3757 | 6.8776 | 0.89888 | 1.0655 | 0.88132 | 0.9588 | 0.63667 | 0.66239 | 9.8917 | 18 | 0.28008 | 0.28228 | 0.27446 | 5.3051 | 2.0015 | 0.38595 | 14.7364 | 2.2193 | 21.343 | 4.4126 | 1.9388 | 0.39462 | 16.5441 | 2.7817 | 36.5174 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.59 | 19 | 18 | 7.23 | 126 | 161 | 21.8 | 0.496 |  | 6 | 11 | 0.068 | 6 | 11 |  | 6 | 11 | [8 empty] | 0.057 | [14 empty] | 0.036 | 2 | 0.36 |  | 0.057 | 0.031 | 2 | 0.39 |  | 0.043 | 2 | 0.23 | [22 empty] | AVERAGE | 12.7 | 12.7 | 12.7 | 38.1 | 12.075 | 12.075 | 12.45 | 36.6 |  | 14.9677 |  | 19.8659 | 34.8336 | 1.8994 | AVERAGE | 84.4368 | 9438.3155 |  | 626.4317 | 0 | 0 | 0 |  |  |  | 1.8065 | 1.8439 | 1.7194 | 0.22472 | 0.26637 | 0.22033 | 0.2397 | 0.15917 | 0.1656 | 2.4729 | 4.5 | 0.07002 | 0.070569 | 0.068615 | 1.3263 | 0.50037 | 0.096488 | 3.6841 | 0.55483 | 5.3358 | 1.1031 | 0.48469 | 0.098656 | 4.136 | 0.69541 | 9.1294 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.32 | 114 | 106 | 41.29 | 741 | 967 | 129.3 | 2.898 | 0.09 | 36.34 | 66 | 0.358 | 36.19 | 66 | 0 | 36.22 | 66 | 0 | 24.55 | 1.346 | 21 | 2.21 | 85.1 | 51 | 1.8833 | 0.301 | 24.43 | 1.362 | 21 | 1.98 | 85.5 | 51 | 1.8833 | 24.54 | 1.537 | 24 | 2.56 | 84.5 | 51.2 | 1.8074 |  | 11 | 2.12 | 0.018 | 0.302 | 0.174 | 11 | 2.45 | 0 | 0.286 | 11 | 1.73 | 0 | 43.25 | 0.379 | 10 | 24.4 | 125 | 43 | 85 | 0.044 | 42.76 | 0.393 | 9 | 21.6 | 123.6 | 44 | 90 | 0.019 | 22.7 | 17.9 | 21.4 |  |  | MINIMUM | 12.4 | 12.4 | 12.4 | 37.2 | 11.9 | 11.9 | 11.9 | 35.7 |  | 14.7384 |  | 18.2362 | 32.9746 | 1.8533 | MINIMUM | 83.255 | 9100.1348 |  | 618.5022 | [6 empty] | 1.7805 | 1.7805 | 1.6381 | 0.21941 | 0.25598 | 0.21063 | 0.23404 | 0.15359 | 0.15505 | 2.4729 | 3 | 0.06964 | 0.070062 | 0.062528 | 1.1034 | 0.49863 | 0.095361 | 3.587 | 0.45617 | 5.0878 | 1.1011 | 0.44915 | 0.096324 | 3.9756 | 0.67514 | 8.9986 |  | MIN | 0.53 | 12.9 | 19.7209 | 10.4521 | 6.09 | 21.8 | 7 | 1.4932 |  |  |  | MIN | 0.42 | 12.9 | 19.7209 | 8.2828 | 6.12 | 21.2 | 7 | 1.1833 |  |  |  | MIN | 0.63 | 13.3 | 20.3008 | 12.7895 | 6.07 | 21.6 | 7 | 1.8271 |  |  |  | 1.1833
AVERAGE | 6.5533 | 19 | 17.6667 | 6.8817 | 123.5 | 161.1667 | 21.55 | 0.483 | 0.045 | 6.0567 | 11 | 0.059667 | 6.0317 | 11 |  | 6.0367 | 11 |  | 6.1375 | 0.3365 | 5.25 | 0.5525 | 21.275 | 12.75 | 0.47083 | 0.050167 | 6.1075 | 0.3405 | 5.25 | 0.495 | 21.375 | 12.75 | 0.47083 | 6.135 | 0.38425 | 6 | 0.64 | 21.125 | 12.8 | 0.45185 |  | 1.8333 | 0.35333 | 0.009 | 0.050333 | 0.029 | 1.8333 | 0.40833 |  | 0.047667 | 1.8333 | 0.28833 |  | 7.2083 | 0.063167 | 1.6667 | 4.0667 | 20.8333 | 21.5 | 42.5 | 0.022 | 7.1267 | 0.0655 | 1.5 | 3.6 | 20.6 | 22 | 45 | 0.0095 | 3.7833 | 2.9833 | 3.5667 |  |  | MAXIMUM | 13 | 13 | 13 | 39 | 12.5 | 12.5 | 13.5 | 37.5 |  | 15.4526 |  | 22.1659 | 37.1074 | 2.0376 | MAXIMUM | 85.4431 | 9837.9836 |  | 634.3612 | [6 empty] | 1.8547 | 1.8703 | 1.7955 | 0.23003 | 0.27603 | 0.23003 | 0.24536 | 0.16255 | 0.17175 | 2.4729 | 6 | 0.070344 | 0.070935 | 0.070935 | 1.5261 | 0.5053 | 0.097134 | 3.9744 | 0.59418 | 6.0788 | 1.1069 | 0.50227 | 0.10403 | 4.2884 | 0.7265 | 9.5099
MINIMUM | 6.49 | 18 | 17 | 6.52 | 119 | 159 | 21.2 | 0.454 | 0.04 | 6 | 10 | 0.048 | 6 | 10 |  | 6 | 10 |  | 6.09 | 0.269 | 4 | 0.53 | 21 | 12.3 | 0.45844 | 0.042 | 6.04 | 0.283 | 4 | 0.42 | 21 | 12.3 | 0.45844 | 6.07 | 0.339 | 5 | 0.61 | 20.9 | 12.3 | 0.43889 |  | 1 | 0.3 | 0.002 | 0.043 | 0.025 | 1 | 0.31 |  | 0.038 | 1 | 0.21 |  | 7.06 | 0.054 | 1 | 3.4 | 20.4 | 21 | 42 | 0.021 | 6.95 | 0.058 | 1 | 2.8 | 20.3 | 22 | 44 | 0.008 | 3.5 | 1.6 | 3.2 | [15 empty] | MIL/MIN |  | TOTAL | 52616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1960 | 2000 | 1920 | 3000 | 3555 | 2940 | 3200 | 2125 | 2210 | 5200 | 0 | 6410 | 6460 | 6460 | 556 | 558 | 64.5 | 6990 | 1175 | 1766 | 239 | 278 | 34 | 4170 | 760 | 1560
MAXIMUM | 6.59 | 20 | 18 | 7.23 | 126 | 162 | 21.8 | 0.496 | 0.05 | 6.12 | 12 | 0.068 | 6.07 | 12 |  | 6.1 | 12 |  | 6.19 | 0.369 | 6 | 0.59 | 21.8 | 12.9 | 0.47495 | 0.057 | 6.19 | 0.363 | 6 | 0.6 | 21.7 | 12.9 | 0.47495 | 6.2 | 0.48 | 8 | 0.66 | 21.6 | 13.3 | 0.46481 |  | 2 | 0.46 | 0.016 | 0.057 | 0.032 | 2 | 0.51 |  | 0.067 | 2 | 0.42 |  | 7.33 | 0.069 | 2 | 4.4 | 21 | 22 | 43 | 0.023 | 7.28 | 0.073 | 2 | 4.3 | 21 | 22 | 46 | 0.011 | 3.9 | 3.4 | 4 | [17 empty] | AVERAGE | 13154 | [9 empty] | 490 | 500 | 480 | 750 | 888.75 | 735 | 800 | 531.25 | 552.5 | 1300 |  | 1602.5 | 1615 | 1615 | 139 | 139.5 | 16.125 | 1747.5 | 293.75 | 441.5 | 59.75 | 69.5 | 8.5 | 1042.5 | 190 | 390
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0417 |  | TOTAL AVG COAG ALK: |  |  |  | 11 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.48 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.42 | [5 empty] | 6.1267 |  |  |  |  | 0.067 |  |  |  |  | 0.42 | [23 empty] | Pump Station MIN |  | 1.6 | [17 empty] | MINIMUM | 13000 | [9 empty] | 480 | 500 | 460 | 750 | 875 | 720 | 800 | 525 | 530 | 1300 |  | 1580 | 1600 | 1600 | 120 | 137 | 16 | 1700 | 240 | 415 | 57 | 69 | 8 | 1020 | 180 | 367
[63 empty] | 0 | [26 empty] | MAXIMUM | 13336 | [9 empty] | 500 | 500 | 500 | 750 | 900 | 750 | 800 | 540 | 560 | 1300 |  | 1650 | 1660 | 1660 | 158 | 144 | 16.5 | 1870 | 315 | 500 | 65 | 70 | 9 | 1070 | 215 | 440
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.815 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827745 |  | END: | 23827745 |  |  | Alum | 4835 | 4375 | 4375 | 3747 | 3747 | 0 | [44 empty] | 0.42 | 12.9 | 19.7209 | 8.2828 | 6.12 | 21.2 | 7 | 1.1833
[73 empty] | FINISHED 2 | 20.61 |  | TOTAL MGD: |  | 14.815 |  |  | FINISHED SOUTH 2 |  | START: | 45179770 |  | END: | 45194585 |  |  | Caustic | 3287 | 8957 | 8957
[73 empty] | TOTAL RAW | 38.162 |  | TOTAL MGD: |  | 5.798 |  |  | FINISHED CONWAY |  | START: | 10770052 |  | END: | 10775850 |  |  | Hypochlorite | 9 |  | 12
[76 empty] | TOTAL MGD: |  | 14.812 |  |  | FINISHED PERRY |  | START: | 34998155 |  | END: | 35012967 |  |  | Phosphate | 3219
[76 empty] | TOTAL MGD: |  | 12.532 |  |  | RAW PLANT 1 |  | START: | 32069418 |  | END: | 32081950 |  |  | Fluoride | 900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 12.64 |  |  | RAW PLANT 2 |  | START: | 32032750 |  | END: | 32045390 |  |  | Cal~Flo | 9.88 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.99 |  |  | RAW PLANT 3 |  | START: | 8669999 |  | END: | 8682989 |  |  | Zinc | 2498
[76 empty] | TOTAL MGD: |  | 0.951 |  |  | DECANT |  | START: | 1959164 |  | END: | 1960115 |  |  | Polymer | 20
[76 empty] | TOTAL MGD: |  | 2.0227 |  |  | BLOW DOWN |  | START: | 9269.1027 |  | END: | 9271.1254 |  |  | NH3 | 11.53 |  | BI-SUL | 990
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 634
23827745
45194585
10775850
35012967
32081950
32045390
8682989
1960115
9271.1254
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 30
DATE: | 2019-04-30 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2019-04-30 | [23 empty] | DATE: | 2019-04-30
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-04-30 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43585.0063 | 2,3,4,6 | 95 | 13 | 13 | 13 | 39 | 12 | 12 | 13.5 | 37.5 | ,1,2,3 | 15.4526 | 1,2 | 20.8253 | 36.2779 | 2.0376 | 43585.0063 | 83.255 | 9100.1348 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8547 | 1.8547 | 1.6486 | 0.21941 | 0.25598 | 0.21063 | 0.23404 | 0.15359 | 0.15505 | 2.4729 | 3 | 0.070344 | 0.070344 | 0.062528 | 1.1494 | 0.5053 | 0.096324 | 3.9744 | 0.45617 | 6.0788 | 1.1069 | 0.44915 | 0.096324 | 3.9756 | 0.7265 | 9.5099 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.31 | 5 | 0.55 | 21.7 | 12.9 | 0.47495 |  | 6.1 | 0.259 | 6 | 0.5 | 21.5 | 12.3 | 0.45844 | 6.09 | 0.339 | 7 | 0.7 | 21.5 | 13.2 | 0.46222 | [13 empty] | 7.67 | 0.071 | 2 | 4.3 | 21.3 |  |  |  | 7.2 | 0.069 | 2 | 3.8 | 20.7 |  |  |  | 2.9 | 1.9 | 3.9 | [18 empty] | 13280 | [6 empty] | 0 | 0 | 0 | 500 | 500 | 500 | 750 | 875 | 720 | 800 | 525 | 530 | 1300 |  | 1600 | 1600 | 1600 | 120 | 140 | 16 | 1870 | 240 | 500 | 65 | 70 | 9 | 1070 | 215 | 440 |  | 1:00 | 0.55 | 12.9 | 19.7209 | 10.8465 | 6.1 | 21.7 | 7 | 1.5495 | 20 | 6.5 | 0.35495 | 1:00 | 0.5 | 12.3 | 20.6829 | 10.3415 | 6.1 | 21.5 | 7 | 1.4774 | 20 | 6.5 | 0.33844 | 1:00 | 0.7 | 13.2 | 20.4545 | 14.3182 | 6.09 | 21.5 | 7 | 2.0455 | 20 | 6.5 | 0.34222
2:00 | [72 empty] | 43585.0907 | 2,3,4,6 | 95 | 13 | 13 | 13 | 39 | 12 | 12 | 13.5 | 37.5 | ,1,2,3 | 13.8888 | 1,2 | 20.8987 | 34.7875 | 2.0376 | 43585.0907 | 83.255 | 9100.1348 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8547 | 1.8547 | 1.6486 | 0.21941 | 0.25598 | 0.21063 | 0.23404 | 0.15359 | 0.15505 | 2.4729 | 3 | 0.070344 | 0.070344 | 0.062528 | 1.1494 | 0.5053 | 0.096324 | 3.9744 | 0.45617 | 6.0788 | 1.1069 | 0.44915 | 0.096324 | 3.9756 | 0.7265 | 9.5099 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.56 | 18 | 18 | 7.38 | 124 | 162 | 21.2 | 0.482 |  | 6.09 | 10 | 0.06 | 6.06 | 10 |  | 6.03 | 10 | [8 empty] | 0.043 | [14 empty] | 0.039 | 2 | 0.39 |  | 0.047 | 0.036 | 2 | 0.31 |  | 0.049 | 2 | 0.29 | [38 empty] | 13280 | [6 empty] | 0 | 0 | 0 | 500 | 500 | 500 | 750 | 875 | 720 | 800 | 525 | 530 | 1300 |  | 1600 | 1600 | 1600 | 120 | 140 | 16 | 1870 | 240 | 500 | 65 | 70 | 9 | 1070 | 215 | 440 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43585.3332 | 2,3,4,6 | 95 | 13.7 | 13.7 | 13.7 | 41.1 | 13 | 13 | 14.5 | 40.5 | ,1,2,3 | 17.231 | 1,2 | 20.1125 | 37.3435 | 2.0376 | 43585.3332 | 80.5954 | 9653.5214 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9175 | 1.9175 | 1.5042 | 0.2193 | 0.25262 | 0.20542 | 0.22486 | 0.18877 | 0.18599 | 2.6631 | 3 | 0.068179 | 0.068991 | 0.060035 | 1.0964 | 0.49975 | 0.10003 | 3.8689 | 0.46495 | 6.1162 | 1.1098 | 0.48987 | 0.099646 | 4.008 | 0.82741 | 9.498 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.33 | 0.069 | 2 | 4.1 | 20.7 |  |  |  | 7.11 | 0.071 | 2 | 4 | 20.7 |  |  |  | 3.5 | 2.1 | 4.2 | [18 empty] | 13548 | [6 empty] | 0 | 0 | 0 | 560 | 560 | 490 | 790 | 910 | 740 | 810 | 680 | 670 | 1400 |  | 1680 | 1700 | 1650 | 124 | 150 | 18 | 1980 | 265 | 545 | 70 | 82 | 10 | 1185 | 263 | 472 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43585.8069 | 2,3,4,6 | 62 | 13.7 | 13.7 | 13.7 | 41.1 | 13 | 13 | 14.5 | 40.5 | ,1,2,3 | 17.5565 | 1,2 | 20.6726 | 38.2291 | 2.5877 | 43585.8069 | 80.9047 | 9592.034 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9175 | 1.9175 | 1.627 | 0.22208 | 0.25262 | 0.2082 | 0.22208 | 0.19432 | 0.18044 | 2.6631 | 2 | 0.068991 | 0.068991 | 0.060035 | 1.1052 | 0.49975 | 0.10003 | 3.8689 | 0.48249 | 6.3968 | 1.1098 | 0.48987 | 0.099646 | 3.9923 | 0.75819 | 10.0614 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.52 | 20 | 18 | 7.4 | 120 | 165 | 21.6 | 0.471 |  | 5.98 | 11 | 0.056 | 6 | 10 |  | 6 | 11 | [8 empty] | 0.049 | [14 empty] | 0.029 | 2 | 0.37 |  | 0.053 | 0.022 | 2 | 0.42 |  | 0.039 | 2 | 0.28 | [38 empty] | 13600 | [6 empty] | 0 | 0 | 0 | 560 | 560 | 530 | 800 | 910 | 750 | 800 | 700 | 650 | 1400 |  | 1700 | 1700 | 1650 | 125 | 150 | 18 | 1980 | 275 | 570 | 70 | 82 | 10 | 1180 | 241 | 500 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 6.15 | [9 empty] | 6.15 | 0.412 | 6 | 0.43 | 21.2 | 13.7 | 0.49697 |  | 6.1 | 0.427 | 6 | 0.53 | 21.6 | 13.9 | 0.50247 | 6.17 | 0.6 | 7 | 0.6 | 21.4 | 14.2 | 0.48815 |  |  |  | 0.01 | [9 empty] | 7.13 | 0.07 | 2 | 4.3 | 21.3 | 21 | 40 | 0.021 | 7.11 | 0.071 | 2 | 4.2 | 21.4 | 21 | 43 | 0.01 | 3.9 | 2.3 | 3.6 | [55 empty] | 9:00 | 0.43 | 13.7 | 18.5693 | 7.9848 | 6.15 | 21.2 | 7 | 1.1407 | 20 | 6.5 | 0.37697 | 9:00 | 0.53 | 13.9 | 18.3022 | 9.7001 | 6.1 | 21.6 | 7 | 1.3857 | 20 | 6.5 | 0.38247 | 9:00 | 0.6 | 14.2 | 19.0141 | 11.4085 | 6.17 | 21.4 | 7 | 1.6298 | 20 | 6.5 | 0.36815
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.58 | 20 | 18 | 7.96 | 119 | 164 | 21.8 | 0.466 |  | 6.04 | 11 | 0.052 | 6.03 | 10 |  | 6.05 | 11 | [8 empty] | 0.042 | [14 empty] | 0.03 | 2 | 0.33 |  | 0.049 | 0.028 | 2 | 0.42 |  | 0.042 | 2 | 0.41 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.12 | 0.432 | 6 | 0.4 | 22.2 | 13.7 | 0.49697 |  | 6.09 | 0.444 | 6 | 0.43 | 22.2 | 13.8 | 0.49972 | 6.16 | 0.491 | 6 | 0.65 | 21.7 | 14 | 0.48296 | [13 empty] | 7.21 | 0.071 | 2 | 4.2 | 21.5 |  |  |  | 7.19 | 0.073 | 2 | 4.3 | 21.7 |  |  |  | 3.8 | 2.3 | 3.8 | [55 empty] | 13:00 | 0.4 | 13.7 | 18.5693 | 7.4277 | 6.12 | 22.2 | 7 | 1.0611 | 20 | 6.5 | 0.37697 | 13:00 | 0.43 | 13.8 | 18.4348 | 7.927 | 6.09 | 22.2 | 7 | 1.1324 | 20 | 6.5 | 0.37972 | 13:00 | 0.65 | 14 | 19.2857 | 12.5357 | 6.16 | 21.7 | 7 | 1.7908 | 20 | 6.5 | 0.36296
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.61 | 20 | 18 | 7.67 | 120 | 164 | 22 | 0.477 |  | 6.06 | 11 | 0.056 | 6.08 | 11 |  | 6.05 | 11 | [8 empty] | 0.045 | [14 empty] | 0.035 | 2 | 0.22 |  | 0.046 | 0.024 | 2 | 0.35 |  | 0.044 | 2 | 0.21 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.35 | 0.065 | 2 | 4.2 | 21.4 |  |  |  | 7.2 | 0.064 | 2 | 3.7 | 21.5 |  |  |  | 3.8 | 1.9 | 4.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.61 | 20 | 18 | 7.56 | 122 | 169 | 22 | 0.476 |  | 6.03 | 11 | 0.061 | 6.04 | 11 |  | 6.04 | 11 | [8 empty] | 0.049 | [14 empty] | 0.037 | 2 | 0.23 |  | 0.052 | 0.021 | 2 | 0.36 |  | 0.037 | 2 | 0.21 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.044 | [9 empty] | 6.09 | 0.322 | 5 | 0.48 | 22.5 | 13.7 | 0.49697 |  | 6.09 | 0.308 | 6 | 0.48 | 22.7 | 13.7 | 0.49697 | 6.1 | 0.357 | 7 | 0.6 | 22.3 | 14 | 0.48296 |  |  |  | 0.012 | [9 empty] | 7.36 | 0.069 | 2 | 4.2 | 21.4 | 21 | 43 | 0.023 | 7.2 | 0.066 | 2 | 3.9 | 21.4 | 22 | 46 | 0.009 | 3.7 | 2.5 | 4.1 | [55 empty] | 21:00 | 0.48 | 13.7 | 18.5693 | 8.9133 | 6.09 | 22.5 | 7 | 1.2733 | 20 | 6.5 | 0.37697 | 21:00 | 0.48 | 13.7 | 18.5693 | 8.9133 | 6.09 | 22.7 | 7 | 1.2733 | 20 | 6.5 | 0.37697 | 21:00 | 0.6 | 14 | 19.2857 | 11.5714 | 6.1 | 22.3 | 7 | 1.6531 | 20 | 6.5 | 0.36296
22:00 | [72 empty] | DOSE |  | TOTAL | 53.4 | 53.4 | 53.4 | 160.2 | 50 | 50 | 56 | 156 | 0 | 64.129 | 0 | 82.5091 | 146.6381 | 8.7005 | TOTAL | 328.01 | 37445.825 | 0 | 2664.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5443 | 7.5443 | 6.4285 | 0.88021 | 1.0172 | 0.83489 | 0.91501 | 0.69026 | 0.67653 | 10.2721 | 11 | 0.27786 | 0.27867 | 0.24512 | 4.5004 | 2.0101 | 0.39271 | 15.6866 | 1.8598 | 24.6705 | 4.4333 | 1.878 | 0.39194 | 15.9516 | 3.0386 | 38.5793 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 19 | 18 | 7.59 | 120 | 160 | 22 | 0.474 |  | 6.09 | 11 | 0.065 | 6.09 | 11 |  | 6.06 | 11 | [8 empty] | 0.053 | [14 empty] | 0.036 | 2 | 0.21 |  | 0.053 | 0.029 | 2 | 0.33 |  | 0.039 | 2 | 0.2 | [22 empty] | AVERAGE | 13.35 | 13.35 | 13.35 | 40.05 | 12.5 | 12.5 | 14 | 39 |  | 16.0322 |  | 20.6273 | 36.6595 | 2.1751 | AVERAGE | 82.0025 | 9361.4562 |  | 666.0793 | 0 | 0 | 0 |  |  |  | 1.8861 | 1.8861 | 1.6071 | 0.22005 | 0.2543 | 0.20872 | 0.22875 | 0.17257 | 0.16913 | 2.568 | 2.75 | 0.069464 | 0.069667 | 0.061281 | 1.1251 | 0.50252 | 0.098177 | 3.9216 | 0.46495 | 6.1676 | 1.1083 | 0.46951 | 0.097985 | 3.9879 | 0.75965 | 9.6448 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.41 | 117 | 108 | 45.56 | 725 | 984 | 130.6 | 2.846 | 6.194 | 36.29 | 65 | 0.35 | 36.3 | 63 | 0 | 36.23 | 65 | 0 | 24.46 | 1.476 | 22 | 1.86 | 87.6 | 54 | 1.9658 | 0.281 | 24.38 | 1.438 | 24 | 1.94 | 88 | 53.7 | 1.9576 | 24.52 | 1.787 | 27 | 2.55 | 86.9 | 55.4 | 1.9163 | 0.206 | 12 | 1.75 | 0.022 | 0.3 | 0.16 | 12 | 2.19 | 0 | 0.25 | 12 | 1.6 | 0 | 44.05 | 0.415 | 12 | 25.3 | 127.6 | 42 | 83 | 0.044 | 43.01 | 0.414 | 12 | 23.9 | 127.4 | 43 | 89 | 0.019 | 21.6 | 13 | 23.7 |  |  | MINIMUM | 13 | 13 | 13 | 39 | 12 | 12 | 13.5 | 37.5 |  | 13.8888 |  | 20.1125 | 34.7875 | 2.0376 | MINIMUM | 80.5954 | 9100.1348 |  | 634.3612 | [6 empty] | 1.8547 | 1.8547 | 1.5042 | 0.2193 | 0.25262 | 0.20542 | 0.22208 | 0.15359 | 0.15505 | 2.4729 | 2 | 0.068179 | 0.068991 | 0.060035 | 1.0964 | 0.49975 | 0.096324 | 3.8689 | 0.45617 | 6.0788 | 1.1069 | 0.44915 | 0.096324 | 3.9756 | 0.7265 | 9.498 |  | MIN | 0.4 | 13.7 | 18.5693 | 7.4277 | 6.12 | 22.2 | 7 | 1.0611 |  |  |  | MIN | 0.43 | 13.8 | 18.4348 | 7.927 | 6.09 | 22.2 | 7 | 1.1324 |  |  |  | MIN | 0.6 | 14.2 | 19.0141 | 11.4085 | 6.17 | 21.4 | 7 | 1.6298 |  |  |  | 1.0611
AVERAGE | 6.5683 | 19.5 | 18 | 7.5933 | 120.8333 | 164 | 21.7667 | 0.47433 | 3.097 | 6.0483 | 10.8333 | 0.058333 | 6.05 | 10.5 |  | 6.0383 | 10.8333 |  | 6.115 | 0.369 | 5.5 | 0.465 | 21.9 | 13.5 | 0.49146 | 0.046833 | 6.095 | 0.3595 | 6 | 0.485 | 22 | 13.425 | 0.4894 | 6.13 | 0.44675 | 6.75 | 0.6375 | 21.725 | 13.85 | 0.47907 | 0.034333 | 2 | 0.29167 | 0.011 | 0.05 | 0.026667 | 2 | 0.365 |  | 0.041667 | 2 | 0.26667 |  | 7.3417 | 0.069167 | 2 | 4.2167 | 21.2667 | 21 | 41.5 | 0.022 | 7.1683 | 0.069 | 2 | 3.9833 | 21.2333 | 21.5 | 44.5 | 0.0095 | 3.6 | 2.1667 | 3.95 |  |  | MAXIMUM | 13.7 | 13.7 | 13.7 | 41.1 | 13 | 13 | 14.5 | 40.5 |  | 17.5565 |  | 20.8987 | 38.2291 | 2.5877 | MAXIMUM | 83.255 | 9653.5214 |  | 697.7974 | [6 empty] | 1.9175 | 1.9175 | 1.6486 | 0.22208 | 0.25598 | 0.21063 | 0.23404 | 0.19432 | 0.18599 | 2.6631 | 3 | 0.070344 | 0.070344 | 0.062528 | 1.1494 | 0.5053 | 0.10003 | 3.9744 | 0.48249 | 6.3968 | 1.1098 | 0.48987 | 0.099646 | 4.008 | 0.82741 | 10.0614
MINIMUM | 6.52 | 18 | 18 | 7.38 | 119 | 160 | 21.2 | 0.466 | 0.044 | 5.98 | 10 | 0.052 | 6 | 10 |  | 6 | 10 |  | 6.09 | 0.31 | 5 | 0.4 | 21.2 | 12.9 | 0.47495 | 0.042 | 6.09 | 0.259 | 6 | 0.43 | 21.5 | 12.3 | 0.45844 | 6.09 | 0.339 | 6 | 0.6 | 21.4 | 13.2 | 0.46222 | 0.029 | 2 | 0.21 | 0.01 | 0.046 | 0.021 | 2 | 0.31 |  | 0.037 | 2 | 0.2 |  | 7.13 | 0.065 | 2 | 4.1 | 20.7 | 21 | 40 | 0.021 | 7.11 | 0.064 | 2 | 3.7 | 20.7 | 21 | 43 | 0.009 | 2.9 | 1.9 | 3.6 | [15 empty] | MIL/MIN |  | TOTAL | 53708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2120 | 2120 | 2020 | 3090 | 3570 | 2930 | 3210 | 2430 | 2380 | 5400 | 0 | 6580 | 6600 | 6500 | 489 | 580 | 68 | 7700 | 1020 | 2115 | 270 | 304 | 38 | 4505 | 934 | 1852
MAXIMUM | 6.61 | 20 | 18 | 7.96 | 124 | 169 | 22 | 0.482 | 6.15 | 6.09 | 11 | 0.065 | 6.09 | 11 |  | 6.06 | 11 |  | 6.15 | 0.432 | 6 | 0.55 | 22.5 | 13.7 | 0.49697 | 0.053 | 6.1 | 0.444 | 6 | 0.53 | 22.7 | 13.9 | 0.50247 | 6.17 | 0.6 | 7 | 0.7 | 22.3 | 14.2 | 0.48815 | 0.039 | 2 | 0.39 | 0.012 | 0.053 | 0.036 | 2 | 0.42 |  | 0.049 | 2 | 0.41 |  | 7.67 | 0.071 | 2 | 4.3 | 21.5 | 21 | 43 | 0.023 | 7.2 | 0.073 | 2 | 4.3 | 21.7 | 22 | 46 | 0.01 | 3.9 | 2.5 | 4.2 | [17 empty] | AVERAGE | 13427 | [9 empty] | 530 | 530 | 505 | 772.5 | 892.5 | 732.5 | 802.5 | 607.5 | 595 | 1350 |  | 1645 | 1650 | 1625 | 122.25 | 145 | 17 | 1925 | 255 | 528.75 | 67.5 | 76 | 9.5 | 1126.25 | 233.5 | 463
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0456 |  | TOTAL AVG COAG ALK: |  |  |  | 10.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.6 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.4 | [5 empty] | 6.1133 |  |  |  |  | 0.049 |  |  |  |  | 0.4 | [6 empty] | 0.049 | [16 empty] | Pump Station MIN |  | 1.9 | [17 empty] | MINIMUM | 13280 | [9 empty] | 500 | 500 | 490 | 750 | 875 | 720 | 800 | 525 | 530 | 1300 |  | 1600 | 1600 | 1600 | 120 | 140 | 16 | 1870 | 240 | 500 | 65 | 70 | 9 | 1070 | 215 | 440
[90 empty] | MAXIMUM | 13600 | [9 empty] | 560 | 560 | 530 | 800 | 910 | 750 | 810 | 700 | 670 | 1400 |  | 1700 | 1700 | 1650 | 125 | 150 | 18 | 1980 | 275 | 570 | 70 | 82 | 10 | 1185 | 263 | 500
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 14.837 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827745 |  | END: | 23827746 |  |  | Alum | 4825 | 5131 | 5131 | 2830 | 2830 | 0 | [44 empty] | 0.4 | 13.7 | 18.5693 | 7.4277 | 6.12 | 22.2 | 7 | 1.0611
[73 empty] | FINISHED 2 | 19.059 |  | TOTAL MGD: |  | 14.836 |  |  | FINISHED SOUTH 2 |  | START: | 45194585 |  | END: | 45209421 |  |  | Caustic | 3106 | 8914 | 8914
[73 empty] | TOTAL RAW | 39.048 |  | TOTAL MGD: |  | 5.306 |  |  | FINISHED CONWAY |  | START: | 10775850 |  | END: | 10781156 |  |  | Hypochlorite | 14 |  | 15
[76 empty] | TOTAL MGD: |  | 13.753 |  |  | FINISHED PERRY |  | START: | 35012967 |  | END: | 35026720 |  |  | Phosphate | 2132
[76 empty] | TOTAL MGD: |  | 12.97 |  |  | RAW PLANT 1 |  | START: | 32081950 |  | END: | 32094920 |  |  | Fluoride | 750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 12.855 |  |  | RAW PLANT 2 |  | START: | 32045390 |  | END: | 32058245 |  |  | Cal~Flo | 5.58 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 13.223 |  |  | RAW PLANT 3 |  | START: | 8682989 |  | END: | 8696212 |  |  | Zinc | 2494
[76 empty] | TOTAL MGD: |  | 1.077 |  |  | DECANT |  | START: | 1960115 |  | END: | 1961192 |  |  | Polymer | 19
[76 empty] | TOTAL MGD: |  | 1.8745 |  |  | BLOW DOWN |  | START: | 9271.1254 |  | END: | 9272.9999 |  |  | NH3 | 11.41 |  | BI-SUL | 990
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827746
45209421
10781156
35026720
32094920
32058245
8696212
1961192
9272.9999
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 31
DATE: | 2019-05-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 | [10 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 | [28 empty] | 6:00 - 18:00 |  | 0 |  | 0 | [37 empty] | 6:00 - 18:00 |  | 0 |  | 0
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 0 |  | 0 | [37 empty] | 18:00 - 6:00 |  | 0 |  | 0
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2019-05-01 | [23 empty] | DATE: | 2019-05-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-05-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [127 empty] | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [127 empty] | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 1:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
2:00 | [127 empty] | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | [127 empty] | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [127 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | [127 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [127 empty] | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 9:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | [127 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [127 empty] | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 13:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | [127 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [127 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | [127 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [127 empty] | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 21:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
22:00 | [72 empty] | DOSE |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | [74 empty] | AVERAGE | [14 empty] | AVERAGE |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | [30 empty] | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MINIMUM | [14 empty] | MINIMUM | [37 empty] | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | MIN | [7 empty] | 0 |  |  |  | 0
AVERAGE | [74 empty] | MAXIMUM | [14 empty] | MAXIMUM
MINIMUM | [87 empty] | MIL/MIN |  | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAXIMUM | [89 empty] | AVERAGE
# 0F DAYS IN THE MONTH |  | 30 |  |  |  | TOTAL AVG COAG PH: | [7 empty] | TOTAL AVG COAG ALK: | [5 empty] | TOTAL MAX SETTLED NTU: | [6 empty] | TOTAL MIN SETTLED DISEN.: |  |  | 0 | [10 empty] | 0 | [28 empty] | Pump Station MIN |  | 0 | [17 empty] | MINIMUM
MAXIMUM
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 19.388 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827746 |  | END: | 23827746 |  |  | Alum | 4820 | 6151 | 6151 | 6516 | 6516 | 0 | [51 empty] | 0
[73 empty] | FINISHED 2 | 26.213 |  | TOTAL MGD: |  | 19.388 |  |  | FINISHED SOUTH 2 |  | START: | 45209421 |  | END: | 45228809 |  |  | Caustic | 6622 | 8887 | 8887
[73 empty] | TOTAL RAW | 48.979 |  | TOTAL MGD: |  | 8.089 |  |  | FINISHED CONWAY |  | START: | 10781156 |  | END: | 10789245 |  |  | Hypochlorite | 18 |  | 27
[76 empty] | TOTAL MGD: |  | 18.124 |  |  | FINISHED PERRY |  | START: | 35026720 |  | END: | 35044844 |  |  | Phosphate | 3006
[76 empty] | TOTAL MGD: |  | 16.281 |  |  | RAW PLANT 1 |  | START: | 32094920 |  | END: | 32111201 |  |  | Fluoride | 750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 16.39 |  |  | RAW PLANT 2 |  | START: | 32058245 |  | END: | 32074635 |  |  | Cal~Flo | 9.67 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 16.308 |  |  | RAW PLANT 3 |  | START: | 8696212 |  | END: | 8712520 |  |  | Zinc | 2276
[76 empty] | TOTAL MGD: |  | 1.344 |  |  | DECANT |  | START: | 1961192 |  | END: | 1962536 |  |  | Polymer | 19
[76 empty] | TOTAL MGD: |  | 2.6069 |  |  | BLOW DOWN |  | START: | 9272.9999 |  | END: | 9275.6068 |  |  | NH3 | 11 |  | BI-SUL | 975
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827746
45228809
10789245
35044844
32111201
32074635
8712520
1962536
9275.6068
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN MONTH
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## BULK TANK LEVEL
cal-flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday
| 2019-04-01 | 2019-04-02 | 2019-04-03 | 2019-04-04 | 2019-04-05 | 2019-04-06 | 2019-04-07 | 2019-04-08 | 2019-04-09 | 2019-04-10 | 2019-04-11 | 2019-04-12 | 2019-04-13 | 2019-04-14 | 2019-04-15 | 2019-04-16 | 2019-04-17 | 2019-04-18 | 2019-04-19 | 2019-04-20 | 2019-04-21 | 2019-04-22 | 2019-04-23 | 2019-04-24 | 2019-04-25 | 2019-04-26 | 2019-04-27 | 2019-04-28 | 2019-04-29 | 2019-04-30 | 2019-05-01
Alum1 | 4858 | 4876 | 4907 | 4984 | 4864 | 4852 | 4847 | 4871 | 4899 | 4888 | 4892 | 4873 | 4853 | 4883 | 4887 | 4898 | 4885 | 4882 | 4905 | 4916 | 4924 | 4889 | 4874 | 4822 | 4815 | 4837 | 4837 | 4916 | 4835 | 4825 | 4820
Alum2 | 6194 | 5774 | 10200 | 9238 | 11000 | 10383 | 9482 | 8648 | 8020 | 9750 | 8933 | 7930 | 7932 | 6480 | 5557 | 4841 | 6369 | 8287 | 7017 | 6220 | 5279 | 6631 | 5461 | 6432 | 7333 | 6635 | 4693 | 3475 | 4375 | 5131 | 6151
Alum Tower | 874500% | 793800% | 752500% | 922000% | 870000% | 821100% | 787400% | 755800% | 907700% | 855000% | 780400% | 968800% | 889500% | 790500% | 707200% | 574200% | 679400% | 550200% | 704400% | 637600% | 556400% | 471500% | 614500% | 729600% | 634000% | 756600% | 637100% | 491100% | 374700% | 283000% | 651600%
Caustic | 7062 | 6932 | 6835 | 6705 | 6585 | 6468 | 6329 | 6240 | 6126 | 5973 | 5853 | 5698 | 5567 | 5445 | 5279 | 5133 | 4988 | 4865 | 4697 | 4618 | 4501 | 4387 | 4210 | 4061 | 3912 | 3773 | 3602 | 3431 | 3287 | 3106 | 6622
Caustic | 6140 | 8063 | 8040 | 8030 | 7960 | 7963 | 7875 | 7880 | 7830 | 7768 | 7731 | 7695 | 7658 | 7615 | 7578 | 7533 | 7518 | 7461 | 7461 | 7422 | 7365 | 7365 | 7301 | 7226 | 9149 | 9114 | 9159 | 9016 | 8957 | 8914 | 8887
Hypochlorite | 14 | 17 | 16 | 21 | 19 | 17 | 16 | 21 | 18 | 16 | 19 | 18 | 19 | 19 | 16 | 19 | 12 | 9 | 11 | 10 | 7.5 | 6 | 12 | 10 | 11 | 10 | 8 | 6 | 9 | 14 | 18
Hypochlorite | 33 | 28 | 27 | 31 | 41 | 40 | 39 | 32 | 30 | 39 | 31 | 42 | 40 | 35 | 31 | 22.5 | 20.5 | 20.5 | 24 | 24 | 23 | 23 | 11 | 20 | 15 | 24 | 21 | 29.5 | 12 | 15 | 27
Phosphate | 1550 | 1502 | 1443 | 1360 | 1358 | 1346 | 1258 | 1238 | 1216 | 1044 | 998 | 4025 | 3978 | 3932 | 3878 | 3827 | 3814 | 3719 | 3742 | 3760 | 3647 | 3549 | 3447 | 3414 | 3348 | 3341 | 3332 | 3275 | 3219 | 2132 | 3006
Fluoride | 2900 | 2900 | 2650 | 2650 | 2700 | 2750 | 2650 | 2400 | 2400 | 2250 | 2150 | 2100 | 2100 | 1900 | 1750 | 1700 | 1750 | 1750 | 1550 | 1550 | 1550 | 1550 | 1300 | 1250 | 1150 | 1050 | 950 | 900 | 900 | 750 | 750
Cal~Flo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zinc | 2683 | 2679 | 2485 | 2471 | 2478 | 2450 | 2466 | 2448 | 2483 | 2471 | 2467 | 2454 | 2458 | 2470 | 2475 | 2488 | 2470 | 2466 | 2502 | 2522 | 2509 | 2465 | 2450 | 2422 | 2437 | 2452 | 2514 | 2508 | 2498 | 2494 | 2276
Polymer | 26 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 19
NH3 | 11.08 | 10.9 | 11 | 10 | 10 | 10 | 10 | 10 | 9 | 9.2 | 9 | 8.82 | 8.65 | 8.45 | 8.21 | 7.95 | 7.69 | 7.45 | 7.27 | 7.08 | 6.86 | 6.61 | 6.39 | 5.54 | 5.34 | 12.22 | 11.96 | 11.72 | 11.53 | 11.41 | 11
Lime | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cabon | 500 | 480 | 507 | 492 | 492 | 492 | 492 | 523 | 476 | 700 | 490 | 550 | 520 | 520 | 500 | 500 | 555 | 587 | 460 | 428 | 492 | 523 | 571 | 550 | 690 | 571 | 550 | 619 | 634 | 650 | 650
filter aid | 2019-04-01: 3.7726

## AWOP 2018
2019-08-12 | Raw | Settled | Filter
Average | 6.5143 | 0.52953 | 0.062
Max | 10.3 | 0.776 | 0.08
Count |  | 0 | 0 | Average Raw
AWOP Count |  | 0 | 0 | Per day
2019-04-01 | 10.1 | 0.612 | 0.062
2019-04-02 | 10.3 | 0.776 | 0.045
2019-04-03 | 10.1 | 0.493 | 0.043
2019-04-04 | 7.7 | 0.481 | 0.046
2019-04-05 | 7.18 | 0.464 | 0.068
2019-04-06 | 7.75 | 0.427 | 0.044
2019-04-07 | 7 | 0.496 | 0.057
2019-04-08 | 6.2 | 0.449 | 0.05
2019-04-09 | 6.15 | 0.418 | 0.07
2019-04-10 | 5.31 | 0.653 | 0.059
2019-04-11 | 4.56 | 0.681 | 0.07
2019-04-12 | 3.92 | 0.702 | 0.078
2019-04-13 | 4.68 | 0.481 | 0.066
2019-04-14 | 4.8 | 0.588 | 0.08
2019-04-15 | 4.77 | 0.71 | 0.079
2019-04-16 | 4.63 | 0.639 | 0.07
2019-04-17 | 4.66 | 0.543 | 0.078
2019-04-18 | 6.15 | 0.487 | 0.065
2019-04-19 | 5.9 | 0.45 | 0.074
2019-04-20 | 5.63 | 0.491 | 0.063
2019-04-21 | 6.24 | 0.471 | 0.063
2019-04-22 | 6.41 | 0.418 | 0.056
2019-04-23 | 6.58 | 0.492 | 0.056
2019-04-24 | 6.52 | 0.469 | 0.066
2019-04-25 | 6.71 | 0.539 | 0.055
2019-04-26 | 6.76 | 0.452 | 0.053
2019-04-27 | 6.7 | 0.463 | 0.077
2019-04-28 | 6.83 | 0.461 | 0.051
2019-04-29 | 7.23 | 0.48 | 0.067
2019-04-30 | 7.96 | 0.6 | 0.049
2019-05-01

## REMOVAL
PLT1
2019-08-12 08:48 |  | DAILY AVG | RAW | RAW | RAW | RAW | RAW | RAW | RAW | RAW | avg last 12 | RAW | TREATED | TREATED | TREATED | Percent | Calculated Raw | Alum Dose: | Alum Dose | Treated pH | Settled UV | FILTER UV
Date | Time | ALUM DOSE | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | raw uv | MN | PH | ALKALINITY | Treated UV | Removal | TOC, mg/L | TOC Ratio | Divided By 100 | Divided By 10
2019-04-01 | 0:00 | 55.0817
| 1:00 | 55.0817 | [8 empty] | #DIV/0!
| 2:00 | 55.0817 | [8 empty] | #DIV/0!
| 3:00 | 55.0817 | 6.67 | 19 | 20 | 9.91 | 90 | 138 | 16.9 | 0.351 | 0.351 |  | 6.22 | 10 | 0.048 | 86.32% | 9.2368 | 5.9633 | 0.55082 | 0.622 | 0.04 | 0.039
| 4:00 | 55.0817 | [8 empty] | 0.351
| 5:00 | 55.0817 | [8 empty] | 0.351
| 6:00 | 55.0817 | [8 empty] | 0.351
| 7:00 | 55.0817 | 6.63 | 19 | 18 | 10.1 | 85 | 141 | 16.8 | 0.338 | 0.3445 |  | 6.13 | 10 | 0.048 | 85.8% | 8.8947 | 6.1926 | 0.55082 | 0.613 | 0.046 | 0.04
| 8:00 | 55.0817 | [8 empty] | 0.3445
| 9:00 | 55.0817 | [8 empty] | 0.3445 | 0.039
| 10:00 | 55.0817 | [8 empty] | 0.3445
| 11:00 | 55.0817 | 6.61 | 20 | 18 | 10 | 86 | 140 | 16.4 | 0.334 | 0.341 |  | 6.15 | 12 | 0.045 | 86.53% | 8.7895 | 6.2668 | 0.55082 | 0.615 | 0.042 | 0.042
| 12:00 | 55.0817 | [8 empty] | 0.341
| 13:00 | 55.0817 | [8 empty] | 0.341
| 14:00 | 55.0817 | [8 empty] | 0.341
| 15:00 | 55.0817 | 6.6 | 20 | 18 | 10.1 | 80 | 139 | 16.5 | 0.326 | 0.33725 |  | 6.14 | 11 | 0.044 | 86.5% | 8.5789 | 6.4206 | 0.55082 | 0.614 | 0.041 | 0.041
| 16:00 | 55.0817 | [8 empty] | 0.33267
| 17:00 | 55.0817 | [8 empty] | 0.33267
| 18:00 | 55.0817 | [8 empty] | 0.33267
| 19:00 | 55.0817 | 6.52 | 19 | 19 | 10.1 | 87 | 139 | 16.5 | 0.346 | 0.336 |  | 6.1 | 10 | 0.046 | 86.71% | 9.1053 | 6.0494 | 0.55082 | 0.61 | 0.038 | 0.036
| 20:00 | 55.0817 | [8 empty] | 0.336
| 21:00 | 55.0817 | [8 empty] | 0.33533 | 0.037
| 22:00 | 55.0817 | [8 empty] | 0.33533
| 23:00 | 55.0817 | 6.79 | 19 | 19 | 10.1 | 84 | 139 | 16.4 | 0.33 | 0.334 |  | 6.18 | 10 | 0.051 | 84.55% | 8.6842 | 6.3427 | 0.55082 | 0.618 | 0.037 | 0.038
2019-04-02 | 0:00 | 55.2527 | [8 empty] | 0.334
| 1:00 | 55.2527 | [8 empty] | 0.334
| 2:00 | 55.2527 | [8 empty] | 0.334
| 3:00 | 55.2527 | 6.68 | 19 | 19 | 10.3 | 78 | 138 | 16.5 | 0.338 | 0.335 |  | 6.14 | 10 | 0.05 | 85.21% | 8.8947 | 6.2118 | 0.55253 | 0.614 | 0.041 | 0.039
| 4:00 | 55.2527 | [8 empty] | 0.335
| 5:00 | 55.2527 | [8 empty] | 0.338
| 6:00 | 55.2527 | [8 empty] | 0.338
| 7:00 | 55.2527 | 6.49 | 19 | 17 | 10.1 | 81 | 140 | 16.2 | 0.331 | 0.33625 |  | 6.08 | 10 | 0.047 | 85.8% | 8.7105 | 6.3432 | 0.55253 | 0.608 | 0.042 | 0.044
| 8:00 | 55.2527 | [8 empty] | 0.33625
| 9:00 | 55.2527 | [8 empty] | 0.333 | 0.041
| 10:00 | 55.2527 | [8 empty] | 0.333
| 11:00 | 55.2527 | 6.6 | 18 | 18 | 9.86 | 78 | 137 | 16 | 0.323 | 0.3305 |  | 6.08 | 10 | 0.047 | 85.45% | 8.5 | 6.5003 | 0.55253 | 0.608 | 0.038 | 0.038
| 12:00 | 55.2527 | [8 empty] | 0.3305
| 13:00 | 55.2527 | [8 empty] | 0.33067
| 14:00 | 55.2527 | [8 empty] | 0.33067
| 15:00 | 55.2527 | 6.64 | 20 | 19 | 9.34 | 82 | 134 | 15.5 | 0.337 | 0.33225 |  | 6.14 | 10 | 0.05 | 85.16% | 8.8684 | 6.2303 | 0.55253 | 0.614 | 0.046 | 0.04
| 16:00 | 55.2527 | [8 empty] | 0.33225
| 17:00 | 55.2527 | [8 empty] | 0.33033
| 18:00 | 55.2527 | [8 empty] | 0.33033
| 19:00 | 55.2527 | 6.69 | 20 | 20 | 9.25 | 83 | 134 | 15.7 | 0.332 | 0.33075 |  | 6.17 | 10 | 0.048 | 85.54% | 8.7368 | 6.3241 | 0.55253 | 0.617 | 0.039 | 0.039
| 20:00 | 55.2527 | [8 empty] | 0.33075
| 21:00 | 55.2527 | [8 empty] | 0.33067 | 0.04
| 22:00 | 55.2527 | [8 empty] | 0.33067
| 23:00 | 55.2527 | 6.72 | 20 | 20 | 9.24 | 84 | 135 | 15.2 | 0.348 | 0.335 |  | 6.08 | 10 | 0.049 | 85.92% | 9.1579 | 6.0333 | 0.55253 | 0.608 | 0.04 | 0.04
2019-04-03 | 24:00 | 55.2139 | [8 empty] | 0.335
| 25:00 | 55.2139 | [8 empty] | 0.339
| 26:00 | 55.2139 | [8 empty] | 0.339
| 27:00 | 55.2139 | 6.62 | 19 | 20 | 9.59 | 88 | 137 | 15.4 | 0.35 | 0.34175 |  | 6.12 | 10 | 0.047 | 86.57% | 9.2105 | 5.9947 | 0.55214 | 0.612 | 0.039 | 0.038
| 28:00 | 55.2139 | [8 empty] | 0.34175
| 29:00 | 55.2139 | [8 empty] | 0.34333
| 30:00 | 55.2139 | [8 empty] | 0.34333
| 31:00 | 55.2139 | 6.61 | 17 | 24 | 9.26 | 89 | 143 | 15.9 | 0.329 | 0.33975 |  | 6.15 | 9 | 0.048 | 85.41% | 8.6579 | 6.3773 | 0.55214 | 0.615 | 0.04 | 0.038
| 32:00 | 55.2139 | [8 empty] | 0.33975
| 33:00 | 55.2139 | [8 empty] | 0.34233 | 0.047
| 34:00 | 55.2139 | [8 empty] | 0.34233
| 35:00 | 55.2139 | 6.6 | 20 | 15 | 10.1 | 83 | 146 | 15.5 | 0.333 | 0.34 |  | 6.32 | 11 | 0.069 | 79.28% | 8.7632 | 6.3007 | 0.55214 | 0.632 | 0.044 | 0.04
| 36:00 | 55.2139 | [8 empty] | 0.34
| 37:00 | 55.2139 | [8 empty] | 0.33733
| 38:00 | 55.2139 | [8 empty] | 0.33733
| 39:00 | 55.2139 | 6.6 | 21 | 18 | 8.71 | 80 | 133 | 15.8 | 0.333 | 0.33625 |  | 6.21 | 10 | 0.069 | 79.28% | 8.7632 | 6.3007 | 0.55214 | 0.621 | 0.039 | 0.039
| 40:00 | 55.2139 | [8 empty] | 0.33625
| 41:00 | 55.2139 | [8 empty] | 0.33167
| 42:00 | 55.2139 | [8 empty] | 0.33167
| 43:00 | 55.2139 | 6.55 | 20 | 18 | 8.05 | 81 | 129 | 15.9 | 0.333 | 0.332 |  | 6.09 | 12 | 0.049 | 85.29% | 8.7632 | 6.3007 | 0.55214 | 0.609 | 0.037 | 0.037
| 44:00 | 55.2139 | [8 empty] | 0.332
| 45:00 | 55.2139 | [8 empty] | 0.333 | 0.044
| 46:00 | 55.2139 | [8 empty] | 0.333
| 47:00 | 55.2139 | 6.51 | 19 | 18 | 7.52 | 83 | 125 | 15.6 | 0.34 | 0.33475 |  | 6.01 | 10 | 0.052 | 84.71% | 8.9474 | 6.171 | 0.55214 | 0.601 | 0.037 | 0.038
2019-04-04 | 48:00 | 51.755 | [8 empty] | 0.33475
| 49:00 | 51.755 | [8 empty] | 0.33533
| 50:00 | 51.755 | [8 empty] | 0.33533
| 51:00 | 51.755 | 6.58 | 20 | 18 | 7.7 | 80 | 126 | 16.6 | 0.303 | 0.32725 |  | 6.06 | 11 | 0.043 | 85.81% | 7.9737 | 6.4907 | 0.51755 | 0.606 | 0.029 | 0.032
| 52:00 | 51.755 | [8 empty] | 0.32725
| 53:00 | 51.755 | [8 empty] | 0.32533
| 54:00 | 51.755 | [8 empty] | 0.32533
| 55:00 | 51.755 | 6.59 | 15 | 16 | 7.49 | 81 | 124 | 15.9 | 0.318 | 0.3235 |  | 6.04 | 11 | 0.059 | 81.45% | 8.3684 | 6.1846 | 0.51755 | 0.604 | 0.036 | 0.033
| 56:00 | 51.755 | [8 empty] | 0.3235
| 57:00 | 51.755 | [8 empty] | 0.32033 | 0.032
| 58:00 | 51.755 | [8 empty] | 0.32033
| 59:00 | 51.755 | 6.6 | 17 | 16 | 7.12 | 77 | 117 | 16.4 | 0.333 | 0.3235 |  | 6.04 | 10 | 0.057 | 82.88% | 8.7632 | 5.906 | 0.51755 | 0.604 | 0.042 | 0.037
| 60:00 | 51.755 | [8 empty] | 0.3235
| 61:00 | 51.755 | [8 empty] | 0.318
| 62:00 | 51.755 | [8 empty] | 0.318
| 63:00 | 51.755 | 6.58 | 20 | 17 | 7.18 | 81 | 113 | 16.3 | 0.325 | 0.31975 |  | 6.07 | 11 | 0.058 | 82.15% | 8.5526 | 6.0514 | 0.51755 | 0.607 | 0.041 | 0.038
| 64:00 | 51.755 | [8 empty] | 0.31975
| 65:00 | 51.755 | [8 empty] | 0.32533
| 66:00 | 51.755 | [8 empty] | 0.32533
| 67:00 | 51.755 | 6.58 | 20 | 17 | 6.87 | 78 | 115 | 16.2 | 0.331 | 0.32675 |  | 6.1 | 10 | 0.058 | 82.48% | 8.7105 | 5.9417 | 0.51755 | 0.61 | 0.038 | 0.039
| 68:00 | 51.755 | [8 empty] | 0.32675
| 69:00 | 51.755 | [8 empty] | 0.32967 | 0.04
| 70:00 | 51.755 | [8 empty] | 0.32967
| 71:00 | 51.755 | 6.53 | 20 | 18 | 7.23 | 80 | 118 | 16.2 | 0.334 | 0.33075 |  | 6.01 | 10 | 0.06 | 82.04% | 8.7895 | 5.8883 | 0.51755 | 0.601 | 0.039 | 0.039
2019-04-05 | 72:00 | 49.9532 | [8 empty] | 0.33075
| 73:00 | 49.9532 | [8 empty] | 0.33
| 74:00 | 49.9532 | [8 empty] | 0.33
| 75:00 | 49.9532 | 6.58 | 22 | 18 | 7.18 | 78 | 116 | 17 | 0.312 | 0.3255 |  | 6.06 | 11 | 0.049 | 84.29% | 8.2105 | 6.084 | 0.49953 | 0.606 | 0.035 | 0.035
| 76:00 | 49.9532 | [8 empty] | 0.3255
| 77:00 | 49.9532 | [8 empty] | 0.32567
| 78:00 | 49.9532 | [8 empty] | 0.32567
| 79:00 | 49.9532 | 6.61 | 20 | 19 | 7.05 | 78 | 115 | 17.1 | 0.318 | 0.32375 |  | 6.05 | 10 | 0.061 | 80.82% | 8.3684 | 5.9692 | 0.49953 | 0.605 | 0.041 | 0.04
| 80:00 | 49.9532 | [8 empty] | 0.32375
| 81:00 | 49.9532 | [8 empty] | 0.32133 | 0.032
| 82:00 | 49.9532 | [8 empty] | 0.32133
| 83:00 | 49.9532 | 6.6 | 21 | 20 | 7.09 | 76 | 114 | 16.9 | 0.31 | 0.3185 |  | 5.98 | 11 | 0.055 | 82.26% | 8.1579 | 6.1233 | 0.49953 | 0.598 | 0.038 | 0.037
| 84:00 | 49.9532 | [8 empty] | 0.3185
| 85:00 | 49.9532 | [8 empty] | 0.31333
| 86:00 | 49.9532 | [8 empty] | 0.31333
| 87:00 | 49.9532 | 6.62 | 18 | 16 | 6.82 | 77 | 115 | 16.6 | 0.312 | 0.313 |  | 6.14 | 11 | 0.061 | 80.45% | 8.2105 | 6.084 | 0.49953 | 0.614 | 0.041 | 0.038
| 88:00 | 49.9532 | [8 empty] | 0.313
| 89:00 | 49.9532 | [8 empty] | 0.31333
| 90:00 | 49.9532 | [8 empty] | 0.31333
| 91:00 | 49.9532 | 6.67 | 21 | 19 | 6.81 | 75 | 109 | 16.7 | 0.304 | 0.311 |  | 6.08 | 12 | 0.053 | 82.57% | 8 | 6.2441 | 0.49953 | 0.608 | 0.038 | 0.038
| 92:00 | 49.9532 | [8 empty] | 0.311
| 93:00 | 49.9532 | [8 empty] | 0.30867 | 0.037
| 94:00 | 49.9532 | [8 empty] | 0.30867
| 95:00 | 49.9532 | 6.62 | 20 | 19 | 6.94 | 77 | 115 | 16.7 | 0.309 | 0.30875 |  | 6.1 | 11 | 0.06 | 80.58% | 8.1316 | 6.1431 | 0.49953 | 0.61 | 0.038 | 0.04
2019-04-06 | 96:00 | 49.9532 | [8 empty] | 0.30875
| 97:00 | 49.9532 | [8 empty] | 0.30833
| 98:00 | 49.9532 | [8 empty] | 0.30833
| 99:00 | 49.9532 | 6.68 | 22 | 20 | 7.35 | 75 | 116 | 17.4 | 0.294 | 0.30475 |  | 6.06 | 12 | 0.05 | 82.99% | 7.7368 | 6.4565 | 0.49953 | 0.606 | 0.038 | 0.039
| 100:00 | 49.9532 | [8 empty] | 0.30475
| 101:00 | 49.9532 | [8 empty] | 0.30233
| 102:00 | 49.9532 | [8 empty] | 0.30233
| 103:00 | 49.9532 | 6.65 | 23 | 18 | 7.75 | 73 | 112 | 17.4 | 0.296 | 0.30075 |  | 6.04 | 11 | 0.054 | 81.76% | 7.7895 | 6.4129 | 0.49953 | 0.604 | 0.041 | 0.04
| 104:00 | 49.9532 | [8 empty] | 0.30075
| 105:00 | 49.9532 | [8 empty] | 0.29967 | 0.029
| 106:00 | 49.9532 | [8 empty] | 0.29967
| 107:00 | 49.9532 | 6.76 | 20 | 18 | 7.24 | 74 | 109 | 17.4 | 0.298 | 0.29925 |  | 6.14 | 10 | 0.075 | 74.83% | 7.8421 | 6.3699 | 0.49953 | 0.614 | 0.041 | 0.037
| 108:00 | 49.9532 | [8 empty] | 0.29925
| 109:00 | 49.9532 | [8 empty] | 0.296
| 110:00 | 49.9532 | [8 empty] | 0.296
| 111:00 | 49.9532 | 6.7 | 21 | 19 | 7.02 | 73 | 112 | 17.5 | 0.303 | 0.29775 |  | 6.12 | 11 | 0.045 | 85.15% | 7.9737 | 6.2648 | 0.49953 | 0.612 | 0.037 | 0.033
| 112:00 | 49.9532 | [8 empty] | 0.29775
| 113:00 | 49.9532 | [8 empty] | 0.299
| 114:00 | 49.9532 | [8 empty] | 0.299
| 115:00 | 49.9532 | 6.7 | 20 | 19 | 6.7 | 73 | 111 | 17.1 | 0.302 | 0.29975 |  | 6.14 | 11 | 0.059 | 80.46% | 7.9474 | 6.2855 | 0.49953 | 0.614 | 0.038 | 0.041
| 116:00 | 49.9532 | [8 empty] | 0.29975
| 117:00 | 49.9532 | [8 empty] | 0.301 | 0.036
| 118:00 | 49.9532 | [8 empty] | 0.301
| 119:00 | 49.9532 | 6.7 | 20 | 18 | 6.94 | 78 | 112 | 17 | 0.317 | 0.305 |  | 6.14 | 11 | 0.051 | 83.91% | 8.3421 | 5.9881 | 0.49953 | 0.614 | 0.04 | 0.04
2019-04-07 | 120:00 | 49.8977 | [8 empty] | 0.305
| 121:00 | 49.8977 | [8 empty] | 0.30733
| 122:00 | 49.8977 | [8 empty] | 0.30733
| 123:00 | 49.8977 | 6.68 | 22 | 20 | 7 | 76 | 112 | 18 | 0.29 | 0.303 |  | 6.14 | 12 | 0.048 | 83.45% | 7.6316 | 6.5383 | 0.49898 | 0.614 | 0.034 | 0.035
| 124:00 | 49.8977 | [8 empty] | 0.303
| 125:00 | 49.8977 | [8 empty] | 0.303
| 126:00 | 49.8977 | [8 empty] | 0.303
| 127:00 | 49.8977 | 6.67 | 18 | 18 | 6.96 | 78 | 111 | 17.9 | 0.312 | 0.30525 |  | 6.07 | 12 | 0.055 | 82.37% | 8.2105 | 6.0773 | 0.49898 | 0.607 | 0.038 | 0.048
| 128:00 | 49.8977 | [8 empty] | 0.30525
| 129:00 | 49.8977 | [8 empty] | 0.30633 | 0.032
| 130:00 | 49.8977 | [8 empty] | 0.30633
| 131:00 | 49.8977 | 6.64 | 19 | 18 | 6.63 | 79 | 110 | 18.1 | 0.311 | 0.3075 |  | 6.08 | 11 | 0.054 | 82.64% | 8.1842 | 6.0968 | 0.49898 | 0.608 | 0.036 | 0.035
| 132:00 | 49.8977 | [8 empty] | 0.3075
| 133:00 | 49.8977 | [8 empty] | 0.30433
| 134:00 | 49.8977 | [8 empty] | 0.30433
| 135:00 | 49.8977 | 6.64 | 18 | 17 | 6.28 | 76 | 109 | 17.7 | 0.304 | 0.30425 |  | 6.06 | 10 | 0.051 | 83.22% | 8 | 6.2372 | 0.49898 | 0.606 | 0.038 | 0.033
| 136:00 | 49.8977 | [8 empty] | 0.30425
| 137:00 | 49.8977 | [8 empty] | 0.309
| 138:00 | 49.8977 | [8 empty] | 0.309
| 139:00 | 49.8977 | 6.63 | 20 | 18 | 6.06 | 76 | 107 | 17.6 | 0.308 | 0.30875 |  | 6.14 | 12 | 0.053 | 82.79% | 8.1053 | 6.1562 | 0.49898 | 0.614 | 0.033 | 0.036
| 140:00 | 49.8977 | [8 empty] | 0.30875
| 141:00 | 49.8977 | [8 empty] | 0.30767 | 0.039
| 142:00 | 49.8977 | [8 empty] | 0.30767
| 143:00 | 49.8977 | 6.6 | 19 | 18 | 6.09 | 77 | 106 | 17.8 | 0.327 | 0.3125 |  | 6.03 | 11 | 0.05 | 84.71% | 8.6053 | 5.7985 | 0.49898 | 0.603 | 0.039 | 0.037
2019-04-08 | 144:00 | 49.9575 | [8 empty] | 0.3125
| 145:00 | 49.9575 | [8 empty] | 0.313
| 146:00 | 49.9575 | [8 empty] | 0.313
| 147:00 | 49.9575 | 6.6 | 21 | 20 | 5.9 | 75 | 107 | 18.5 | 0.292 | 0.30775 |  | 6.07 | 12 | 0.046 | 84.25% | 7.6842 | 6.5013 | 0.49957 | 0.607 | 0.032 | 0.035
| 148:00 | 49.9575 | [8 empty] | 0.30775
| 149:00 | 49.9575 | [8 empty] | 0.309
| 150:00 | 49.9575 | [8 empty] | 0.309
| 151:00 | 49.9575 | 6.69 | 22 | 18 | 5.64 | 76 | 105 | 18.6 | 0.318 | 0.31125 |  | 6.01 | 11 | 0.064 | 79.87% | 8.3684 | 5.9698 | 0.49957 | 0.601 | 0.038 | 0.037
| 152:00 | 49.9575 | [8 empty] | 0.31125
| 153:00 | 49.9575 | [8 empty] | 0.31233 | 0.028
| 154:00 | 49.9575 | [8 empty] | 0.31233
| 155:00 | 49.9575 | 6.6 | 20 | 19 | 6.09 | 80 | 111 | 18.4 | 0.329 | 0.3165 |  | 5.98 | 11 | 0.056 | 82.98% | 8.6579 | 5.7702 | 0.49957 | 0.598 | 0.04 | 0.038
| 156:00 | 49.9575 | [8 empty] | 0.3165
| 157:00 | 49.9575 | [8 empty] | 0.313
| 158:00 | 49.9575 | [8 empty] | 0.313
| 159:00 | 49.9575 | 6.64 | 18 | 17 | 6.09 | 76 | 108 | 18.1 | 0.326 | 0.31625 |  | 6.07 | 10 | 0.055 | 83.13% | 8.5789 | 5.8233 | 0.49957 | 0.607 | 0.039 | 0.036
| 160:00 | 49.9575 | [8 empty] | 0.31625
| 161:00 | 49.9575 | [8 empty] | 0.32433
| 162:00 | 49.9575 | [8 empty] | 0.32433
| 163:00 | 49.9575 | 6.58 | 20 | 18 | 5.8 | 77 | 107 | 18.1 | 0.331 | 0.326 |  | 6.08 | 10 | 0.07 | 78.85% | 8.7105 | 5.7353 | 0.49957 | 0.608 | 0.041 | 0.04
| 164:00 | 49.9575 | [8 empty] | 0.326
| 165:00 | 49.9575 | [8 empty] | 0.32867 | 0.037
| 166:00 | 49.9575 | [8 empty] | 0.32867
| 167:00 | 49.9575 | 6.74 | 21 | 18 | 6.2 | 82 | 115 | 18.6 | 0.344 | 0.3325 |  | 6.07 | 10 | 0.071 | 79.36% | 9.0526 | 5.5186 | 0.49957 | 0.607 | 0.041 | 0.041
2019-04-09 | 168:00 | 51.5151 | [8 empty] | 0.3325
| 169:00 | 51.5151 | [8 empty] | 0.33367
| 170:00 | 51.5151 | [8 empty] | 0.33367
| 171:00 | 51.5151 | 6.69 | 22 | 20 | 6.15 | 80 | 115 | 19.2 | 0.315 | 0.329 |  | 6.01 | 11 | 0.047 | 85.08% | 8.2895 | 6.2145 | 0.51515 | 0.601 | 0.034 | 0.035
| 172:00 | 51.5151 | [8 empty] | 0.329
| 173:00 | 51.5151 | [8 empty] | 0.33
| 174:00 | 51.5151 | [8 empty] | 0.33
| 175:00 | 51.5151 | 6.6 | 20 | 18 | 5.51 | 81 | 111 | 19.5 | 0.32 | 0.3275 |  | 5.93 | 10 | 0.054 | 83.12% | 8.4211 | 6.1174 | 0.51515 | 0.593 | 0.032 | 0.029
| 176:00 | 51.5151 | [8 empty] | 0.3275
| 177:00 | 51.5151 | [8 empty] | 0.32633 | 0.029
| 178:00 | 51.5151 | [8 empty] | 0.32633
| 179:00 | 51.5151 | 6.58 | 20 | 18 | 5.74 | 78 | 112 | 19.8 | 0.327 | 0.3265 |  | 5.98 | 10 | 0.064 | 80.43% | 8.6053 | 5.9865 | 0.51515 | 0.598 | 0.046 | 0.044
| 180:00 | 51.5151 | [8 empty] | 0.3265
| 181:00 | 51.5151 | [8 empty] | 0.32067
| 182:00 | 51.5151 | [8 empty] | 0.32067
| 183:00 | 51.5151 | 6.6 | 20 | 17 | 5.63 | 78 | 110 | 19.4 | 0.335 | 0.32425 |  | 6 | 9 | 0.062 | 81.49% | 8.8158 | 5.8435 | 0.51515 | 0.6 | 0.047 | 0.043
| 184:00 | 51.5151 | [8 empty] | 0.32425
| 185:00 | 51.5151 | [8 empty] | 0.32733
| 186:00 | 51.5151 | [8 empty] | 0.32733
| 187:00 | 51.5151 | 6.54 | 22 | 18 | 5.26 | 76 | 106 | 19.3 | 0.336 | 0.3295 |  | 6.06 | 10 | 0.066 | 80.36% | 8.8421 | 5.8261 | 0.51515 | 0.606 | 0.044 | 0.043
| 188:00 | 51.5151 | [8 empty] | 0.3295
| 189:00 | 51.5151 | [8 empty] | 0.33267 | 0.036
| 190:00 | 51.5151 | [8 empty] | 0.33267
| 191:00 | 51.5151 | 6.57 | 21 | 17 | 5.29 | 82 | 110 | 19.4 | 0.343 | 0.33525 |  | 6.02 | 10 | 0.059 | 82.8% | 9.0263 | 5.7072 | 0.51515 | 0.602 | 0.041 | 0.044
2019-04-10 | 192:00 | 55.262 | [8 empty] | 0.33525
| 193:00 | 55.262 | [8 empty] | 0.338
| 194:00 | 55.262 | [8 empty] | 0.338
| 195:00 | 55.262 | 6.67 | 22 | 20 | 4.98 | 75 | 105 | 20 | 0.318 | 0.333 |  | 6.05 | 11 | 0.055 | 82.7% | 8.3684 | 6.6036 | 0.55262 | 0.605 | 0.035 | 0.038
| 196:00 | 55.262 | [8 empty] | 0.333
| 197:00 | 55.262 | [8 empty] | 0.33233
| 198:00 | 55.262 | [8 empty] | 0.33233
| 199:00 | 55.262 | 6.57 | 19 | 20 | 5.31 | 81 | 108 | 19.2 | 0.342 | 0.33475 |  | 5.96 | 10 | 0.05 | 85.38% | 9 | 6.1402 | 0.55262 | 0.596 | 0.042 | 0.044
| 200:00 | 55.262 | [8 empty] | 0.33475
| 201:00 | 55.262 | [8 empty] | 0.33433 | 0.024
| 202:00 | 55.262 | [8 empty] | 0.33433
| 203:00 | 55.262 | 6.56 | 19 | 19 | 4.77 | 77 | 107 | 19.4 | 0.354 | 0.33925 |  | 6.02 | 10 | 0.053 | 85.03% | 9.3158 | 5.9321 | 0.55262 | 0.602 | 0.043 | 0.042
| 204:00 | 55.262 | [8 empty] | 0.33925
| 205:00 | 55.262 | [8 empty] | 0.338
| 206:00 | 55.262 | [8 empty] | 0.338
| 207:00 | 55.262 | 6.54 | 19 | 19 | 4.43 | 80 | 105 | 19.6 | 0.353 | 0.34175 |  | 6.12 | 10 | 0.056 | 84.14% | 9.2895 | 5.9489 | 0.55262 | 0.612 | 0.045 | 0.042
| 208:00 | 55.262 | [8 empty] | 0.34175
| 209:00 | 55.262 | [8 empty] | 0.34967
| 210:00 | 55.262 | [8 empty] | 0.34967
| 211:00 | 55.262 | 6.55 | 18 | 18 | 4.63 | 81 | 105 | 19.8 | 0.348 | 0.34925 |  | 5.99 | 8 | 0.056 | 83.91% | 9.1579 | 6.0344 | 0.55262 | 0.599 | 0.046 | 0.05
| 212:00 | 55.262 | [8 empty] | 0.34925
| 213:00 | 55.262 | [8 empty] | 0.35167 | 0.024
| 214:00 | 55.262 | [8 empty] | 0.35167
| 215:00 | 55.262 | 6.57 | 20 | 19 | 4.7 | 82 | 107 | 19.7 | 0.349 | 0.351 |  | 6.02 | 10 | 0.058 | 83.38% | 9.1842 | 6.0171 | 0.55262 | 0.602 | 0.052 | 0.048
2019-04-11 | 216:00 | 58.0187 | [8 empty] | 0.351
| 217:00 | 58.0187 | [8 empty] | 0.35
| 218:00 | 58.0187 | [8 empty] | 0.35
| 219:00 | 58.0187 | 6.59 | 19 | 18 | 4.36 | 82 | 110 | 19.7 | 0.348 | 0.3495 |  | 5.99 | 10 | 0.056 | 83.91% | 9.1579 | 6.3354 | 0.58019 | 0.599 | 0.05 | 0.051
| 220:00 | 58.0187 | [8 empty] | 0.3495
| 221:00 | 58.0187 | [8 empty] | 0.34833
| 222:00 | 58.0187 | [8 empty] | 0.34833
| 223:00 | 58.0187 | 6.56 | 19 | 18 | 4.56 | 80 | 102 | 19.7 | 0.37 | 0.35375 |  | 6.02 | 10 | 0.058 | 84.32% | 9.7368 | 5.9587 | 0.58019 | 0.602 | 0.049 | 0.057
| 224:00 | 58.0187 | [8 empty] | 0.35375
| 225:00 | 58.0187 | [8 empty] | 0.35567 | 0.019
| 226:00 | 58.0187 | [8 empty] | 0.35567
| 227:00 | 58.0187 | 6.53 | 18 | 18 | 4.15 | 85 | 106 | 19.8 | 0.368 | 0.35875 |  | 6.06 | 10 | 0.06 | 83.7% | 9.6842 | 5.9911 | 0.58019 | 0.606 | 0.049 | 0.051
| 228:00 | 58.0187 | [8 empty] | 0.35875
| 229:00 | 58.0187 | [8 empty] | 0.362
| 230:00 | 58.0187 | [8 empty] | 0.362
| 231:00 | 58.0187 | 6.51 | 18 | 18 | 3.89 | 92 | 108 | 20.1 | 0.381 | 0.36675 |  | 6.07 | 10 | 0.062 | 83.73% | 10.0263 | 5.7866 | 0.58019 | 0.607 | 0.048 | 0.052
| 232:00 | 58.0187 | [8 empty] | 0.36675
| 233:00 | 58.0187 | [8 empty] | 0.373
| 234:00 | 58.0187 | [8 empty] | 0.373
| 235:00 | 58.0187 | 6.54 | 20 | 18 | 3.85 | 88 | 109 | 20.4 | 0.38 | 0.37475 |  | 6.02 | 10 | 0.061 | 83.95% | 10 | 5.8019 | 0.58019 | 0.602 | 0.052 | 0.056
| 236:00 | 58.0187 | [8 empty] | 0.37475
| 237:00 | 58.0187 | [8 empty] | 0.37633 | 0.024
| 238:00 | 58.0187 | [8 empty] | 0.37633
| 239:00 | 58.0187 | 6.53 | 20 | 18 | 3.99 | 99 | 119 | 20.4 | 0.384 | 0.37825 |  | 6.11 | 11 | 0.066 | 82.81% | 10.1053 | 5.7414 | 0.58019 | 0.611 | 0.056 | 0.049
2019-04-12 | 240:00 | 63.37 | [8 empty] | 0.37825
| 241:00 | 63.37 | [8 empty] | 0.38167
| 242:00 | 63.37 | [8 empty] | 0.38167
| 243:00 | 63.37 | 6.54 | 20 | 18 | 3.81 | 89 | 111 | 20.5 | 0.379 | 0.381 |  | 6 | 10 | 0.064 | 83.11% | 9.9737 | 6.3537 | 0.6337 | 0.6 | 0.058 | 0.054
| 244:00 | 63.37 | [8 empty] | 0.381
| 245:00 | 63.37 | [8 empty] | 0.381
| 246:00 | 63.37 | [8 empty] | 0.381
| 247:00 | 63.37 | 6.54 | 19 | 18 | 3.92 | 91 | 112 | 20.5 | 0.389 | 0.383 |  | 6.01 | 10 | 0.059 | 84.83% | 10.2368 | 6.1904 | 0.6337 | 0.601 | 0.049 | 0.056
| 248:00 | 63.37 | [8 empty] | 0.383
| 249:00 | 63.37 | [8 empty] | 0.384 | 0.025
| 250:00 | 63.37 | [8 empty] | 0.384
| 251:00 | 63.37 | 6.52 | 18 | 18 | 3.61 | 92 | 111 | 21 | 0.4 | 0.388 |  | 6.09 | 10 | 0.069 | 82.75% | 10.5263 | 6.0201 | 0.6337 | 0.609 | 0.05 | 0.051
| 252:00 | 63.37 | [8 empty] | 0.388
| 253:00 | 63.37 | [8 empty] | 0.38933
| 254:00 | 63.37 | [8 empty] | 0.38933
| 255:00 | 63.37 | 6.52 | 19 | 18 | 3.62 | 93 | 112 | 21.2 | 0.397 | 0.39125 |  | 6.06 | 10 | 0.067 | 83.12% | 10.4474 | 6.0656 | 0.6337 | 0.606 | 0.05 | 0.051
| 256:00 | 63.37 | [8 empty] | 0.39125
| 257:00 | 63.37 | [8 empty] | 0.39533
| 258:00 | 63.37 | [8 empty] | 0.39533
| 259:00 | 63.37 | 6.46 | 19 | 18 | 3.74 | 94 | 113 | 21.1 | 0.399 | 0.39625 |  | 6.04 | 10 | 0.067 | 83.21% | 10.5 | 6.0352 | 0.6337 | 0.604 | 0.055 | 0.055
| 260:00 | 63.37 | [8 empty] | 0.39625
| 261:00 | 63.37 | [8 empty] | 0.39867 | 0.024
| 262:00 | 63.37 | [8 empty] | 0.39867
| 263:00 | 63.37 | 6.5 | 20 | 17 | 3.76 | 88 | 114 | 20.5 | 0.369 | 0.39125 |  | 6 | 10 | 0.057 | 84.55% | 9.7105 | 6.5259 | 0.6337 | 0.6 | 0.053 | 0.051
2019-04-13 | 264:00 | 65.3137 | [8 empty] | 0.39125
| 265:00 | 65.3137 | [8 empty] | 0.38833
| 266:00 | 65.3137 | [8 empty] | 0.38833
| 267:00 | 65.3137 | 6.55 | 19 | 18 | 3.71 | 89 | 115 | 20.4 | 0.38 | 0.38625 |  | 6.01 | 10 | 0.06 | 84.21% | 10 | 6.5314 | 0.65314 | 0.601 | 0.055 | 0.054
| 268:00 | 65.3137 | [8 empty] | 0.38625
| 269:00 | 65.3137 | [8 empty] | 0.38267
| 270:00 | 65.3137 | [8 empty] | 0.38267
| 271:00 | 65.3137 | 6.53 | 18 | 18 | 4.45 | 97 | 122 | 20.3 | 0.407 | 0.38875 |  | 6.06 | 10 | 0.068 | 83.29% | 10.7105 | 6.0981 | 0.65314 | 0.606 | 0.053 | 0.053
| 272:00 | 65.3137 | [8 empty] | 0.38875
| 273:00 | 65.3137 | [8 empty] | 0.38533 | 0.025
| 274:00 | 65.3137 | [8 empty] | 0.38533
| 275:00 | 65.3137 | 6.5 | 18 | 18 | 4.61 | 97 | 121 | 20.5 | 0.4 | 0.389 |  | 6.02 | 10 | 0.059 | 85.25% | 10.5263 | 6.2048 | 0.65314 | 0.602 | 0.042 | 0.043
| 276:00 | 65.3137 | [8 empty] | 0.389
| 277:00 | 65.3137 | [8 empty] | 0.39567
| 278:00 | 65.3137 | [8 empty] | 0.39567
| 279:00 | 65.3137 | 6.49 | 19 | 18 | 4.56 | 97 | 121 | 20.3 | 0.412 | 0.39975 |  | 6.1 | 10 | 0.074 | 82.04% | 10.8421 | 6.0241 | 0.65314 | 0.61 | 0.053 | 0.052
| 280:00 | 65.3137 | [8 empty] | 0.39975
| 281:00 | 65.3137 | [8 empty] | 0.40633
| 282:00 | 65.3137 | [8 empty] | 0.40633
| 283:00 | 65.3137 | 6.46 | 19 | 18 | 4.4 | 93 | 118 | 20.8 | 0.39 | 0.40225 |  | 6.06 | 10 | 0.07 | 82.05% | 10.2632 | 6.3639 | 0.65314 | 0.606 | 0.048 | 0.058
| 284:00 | 65.3137 | [8 empty] | 0.40225
| 285:00 | 65.3137 | [8 empty] | 0.40067 | 0.026
| 286:00 | 65.3137 | [8 empty] | 0.40067
| 287:00 | 65.3137 | 6.48 | 19 | 18 | 4.68 | 97 | 125 | 20.8 | 0.4 | 0.4005 |  | 6 | 10 | 0.066 | 83.5% | 10.5263 | 6.2048 | 0.65314 | 0.6 | 0.054 | 0.055
2019-04-14 | 288:00 | 68.6648 | [8 empty] | 0.4005
| 289:00 | 68.6648 | [8 empty] | 0.40067
| 290:00 | 68.6648 | [8 empty] | 0.40067
| 291:00 | 68.6648 | 6.45 | 18 | 18 | 4.75 | 99 | 127 | 20.8 | 0.409 | 0.40275 |  | 6.06 | 10 | 0.06 | 85.33% | 10.7632 | 6.3796 | 0.68665 | 0.606 | 0.058 | 0.065
| 292:00 | 68.6648 | [8 empty] | 0.40275
| 293:00 | 68.6648 | [8 empty] | 0.39967
| 294:00 | 68.6648 | [8 empty] | 0.39967
| 295:00 | 68.6648 | 6.44 | 18 | 18 | 4.8 | 94 | 125 | 20.6 | 0.431 | 0.4075 |  | 6.04 | 10 | 0.07 | 83.76% | 11.3421 | 6.054 | 0.68665 | 0.604 | 0.06 | 0.066
| 296:00 | 68.6648 | [8 empty] | 0.4075
| 297:00 | 68.6648 | [8 empty] | 0.41333 | 0.025
| 298:00 | 68.6648 | [8 empty] | 0.41333
| 299:00 | 68.6648 | 6.5 | 18 | 18 | 4.64 | 103 | 124 | 20.7 | 0.431 | 0.41775 |  | 6.05 | 10 | 0.069 | 83.99% | 11.3421 | 6.054 | 0.68665 | 0.605 | 0.056 | 0.07
| 300:00 | 68.6648 | [8 empty] | 0.41775
| 301:00 | 68.6648 | [8 empty] | 0.42367
| 302:00 | 68.6648 | [8 empty] | 0.42367
| 303:00 | 68.6648 | 6.45 | 18 | 18 | 4.58 | 103 | 126 | 20.9 | 0.425 | 0.424 |  | 6.1 | 11 | 0.067 | 84.24% | 11.1842 | 6.1394 | 0.68665 | 0.61 | 0.054 | 0.053
| 304:00 | 68.6648 | [8 empty] | 0.424
| 305:00 | 68.6648 | [8 empty] | 0.429
| 306:00 | 68.6648 | [8 empty] | 0.429
| 307:00 | 68.6648 | 6.54 | 19 | 18 | 4.75 | 100 | 128 | 22 | 0.378 | 0.41625 |  | 6.04 | 12 | 0.044 | 88.36% | 9.9474 | 6.9028 | 0.68665 | 0.604 | 0.026 | 0.029
| 308:00 | 68.6648 | [8 empty] | 0.41625
| 309:00 | 68.6648 | [8 empty] | 0.41133 | 0.021
| 310:00 | 68.6648 | [8 empty] | 0.41133
| 311:00 | 68.6648 | 6.45 | 18 | 18 | 4.66 | 101 | 130 | 21.1 | 0.417 | 0.41275 |  | 6 | 10 | 0.051 | 87.77% | 10.9737 | 6.2572 | 0.68665 | 0.6 | 0.032 | 0.03
2019-04-15 | 312:00 | 72.3067 | [8 empty] | 0.41275
| 313:00 | 72.3067 | [8 empty] | 0.40667
| 314:00 | 72.3067 | [8 empty] | 0.40667
| 315:00 | 72.3067 | 6.45 | 19 | 18 | 4.77 | 104 | 131 | 21 | 0.43 | 0.4125 |  | 6.02 | 10 | 0.047 | 89.07% | 11.3158 | 6.3899 | 0.72307 | 0.602 | 0.04 | 0.046
| 316:00 | 72.3067 | [8 empty] | 0.4125
| 317:00 | 72.3067 | [8 empty] | 0.40833
| 318:00 | 72.3067 | [8 empty] | 0.40833
| 319:00 | 72.3067 | 6.45 | 19 | 18 | 4.7 | 107 | 132 | 21 | 0.435 | 0.415 |  | 6.02 | 10 | 0.064 | 85.29% | 11.4474 | 6.3164 | 0.72307 | 0.602 | 0.059 | 0.057
| 320:00 | 72.3067 | [8 empty] | 0.415
| 321:00 | 72.3067 | [8 empty] | 0.42733 | 0.027
| 322:00 | 72.3067 | [8 empty] | 0.42733
| 323:00 | 72.3067 | 6.47 | 19 | 19 | 4.46 | 107 | 130 | 20.8 | 0.45 | 0.433 |  | 6.13 | 10 | 0.074 | 83.56% | 11.8421 | 6.1059 | 0.72307 | 0.613 | 0.057 | 0.061
| 324:00 | 72.3067 | [8 empty] | 0.433
| 325:00 | 72.3067 | [8 empty] | 0.43833
| 326:00 | 72.3067 | [8 empty] | 0.43833
| 327:00 | 72.3067 | 6.35 | 18 | 18 | 4.47 | 111 | 138 | 20.8 | 0.446 | 0.44025 |  | 6.02 | 9 | 0.066 | 85.2% | 11.7368 | 6.1607 | 0.72307 | 0.602 | 0.055 | 0.052
| 328:00 | 72.3067 | [8 empty] | 0.44025
| 329:00 | 72.3067 | [8 empty] | 0.44367
| 330:00 | 72.3067 | [8 empty] | 0.44367
| 331:00 | 72.3067 | 6.45 | 19 | 18 | 4.76 | 110 | 135 | 21.1 | 0.444 | 0.44375 |  | 6.01 | 10 | 0.067 | 84.91% | 11.6842 | 6.1884 | 0.72307 | 0.601 | 0.057 | 0.051
| 332:00 | 72.3067 | [8 empty] | 0.44375
| 333:00 | 72.3067 | [8 empty] | 0.44667 | 0.031
| 334:00 | 72.3067 | [8 empty] | 0.44667
| 335:00 | 72.3067 | 6.49 | 20 | 17 | 4.66 | 108 | 134 | 19.9 | 0.442 | 0.4455 |  | 6.03 | 10 | 0.067 | 84.84% | 11.6316 | 6.2164 | 0.72307 | 0.603 | 0.057 | 0.056
2019-04-16 | 336:00 | 74.1304 | [8 empty] | 0.4455
| 337:00 | 74.1304 | [8 empty] | 0.444
| 338:00 | 74.1304 | [8 empty] | 0.444
| 339:00 | 74.1304 | 6.45 | 19 | 17 | 4.63 | 104 | 134 | 20.8 | 0.424 | 0.439 |  | 6.07 | 10 | 0.065 | 84.67% | 11.1579 | 6.6438 | 0.7413 | 0.607 | 0.054 | 0.053
| 340:00 | 74.1304 | [8 empty] | 0.439
| 341:00 | 74.1304 | [8 empty] | 0.43667
| 342:00 | 74.1304 | [8 empty] | 0.43667
| 343:00 | 74.1304 | 6.44 | 19 | 18 | 4.55 | 113 | 133 | 20.7 | 0.455 | 0.44125 |  | 6.03 | 10 | 0.072 | 84.18% | 11.9737 | 6.1911 | 0.7413 | 0.603 | 0.056 | 0.054
| 344:00 | 74.1304 | [8 empty] | 0.44125
| 345:00 | 74.1304 | [8 empty] | 0.44033 | 0.029
| 346:00 | 74.1304 | [8 empty] | 0.44033
| 347:00 | 74.1304 | 6.36 | 19 | 19 | 4.56 | 111 | 132 | 20.5 | 0.45 | 0.44275 |  | 6.14 | 10 | 0.068 | 84.89% | 11.8421 | 6.2599 | 0.7413 | 0.614 | 0.055 | 0.055
| 348:00 | 74.1304 | [8 empty] | 0.44275
| 349:00 | 74.1304 | [8 empty] | 0.443
| 350:00 | 74.1304 | [8 empty] | 0.443
| 351:00 | 74.1304 | 6.48 | 19 | 18 | 4.43 | 109 | 131 | 20.4 | 0.449 | 0.4445 |  | 6.19 | 11 | 0.07 | 84.41% | 11.8158 | 6.2738 | 0.7413 | 0.619 | 0.055 | 0.056
| 352:00 | 74.1304 | [8 empty] | 0.4445
| 353:00 | 74.1304 | [8 empty] | 0.45133
| 354:00 | 74.1304 | [8 empty] | 0.45133
| 355:00 | 74.1304 | 6.43 | 19 | 19 | 4.16 | 108 | 131 | 20.7 | 0.44 | 0.4485 |  | 6.14 | 11 | 0.067 | 84.77% | 11.5789 | 6.4022 | 0.7413 | 0.614 | 0.057 | 0.054
| 356:00 | 74.1304 | [8 empty] | 0.4485
| 357:00 | 74.1304 | [8 empty] | 0.44633 | 0.027
| 358:00 | 74.1304 | [8 empty] | 0.44633
| 359:00 | 74.1304 | 6.46 | 19 | 19 | 4.27 | 106 | 133 | 20.2 | 0.442 | 0.44525 |  | 6.11 | 12 | 0.067 | 84.84% | 11.6316 | 6.3732 | 0.7413 | 0.611 | 0.055 | 0.057
2019-04-17 | 360:00 | 75.5548 | [8 empty] | 0.44525
| 361:00 | 75.5548 | [8 empty] | 0.44367
| 362:00 | 75.5548 | [8 empty] | 0.44367
| 363:00 | 75.5548 | 6.42 | 18 | 18 | 4.22 | 105 | 133 | 20.2 | 0.434 | 0.44125 |  | 6.07 | 11 | 0.069 | 84.1% | 11.4211 | 6.6154 | 0.75555 | 0.607 | 0.056 | 0.055
| 364:00 | 75.5548 | [8 empty] | 0.44125
| 365:00 | 75.5548 | [8 empty] | 0.43867
| 366:00 | 75.5548 | [8 empty] | 0.43867
| 367:00 | 75.5548 | 6.4 | 20 | 18 | 4.4 | 107 | 137 | 20.2 | 0.44 | 0.439 |  | 6.03 | 14 | 0.072 | 83.64% | 11.5789 | 6.5252 | 0.75555 | 0.603 | 0.052 | 0.057
| 368:00 | 75.5548 | [8 empty] | 0.439
| 369:00 | 75.5548 | [8 empty] | 0.43867 | 0.05
| 370:00 | 75.5548 | [8 empty] | 0.43867
| 371:00 | 75.5548 | 6.47 | 20 | 18 | 4.26 | 109 | 133 | 20 | 0.444 | 0.44 |  | 6.07 | 10 | 0.07 | 84.23% | 11.6842 | 6.4664 | 0.75555 | 0.607 | 0.052 | 0.056
| 372:00 | 75.5548 | [8 empty] | 0.44
| 373:00 | 75.5548 | [8 empty] | 0.43933
| 374:00 | 75.5548 | [8 empty] | 0.43933
| 375:00 | 75.5548 | 6.46 | 21 | 18 | 4.52 | 105 | 135 | 21.5 | 0.427 | 0.43625 |  | 6.03 | 11 | 0.068 | 84.07% | 11.2368 | 6.7238 | 0.75555 | 0.603 | 0.052 | 0.055
| 376:00 | 75.5548 | [8 empty] | 0.43625
| 377:00 | 75.5548 | [8 empty] | 0.437
| 378:00 | 75.5548 | [8 empty] | 0.437
| 379:00 | 75.5548 | 6.52 | 20 | 15 | 4.49 | 108 | 134 | 21.3 | 0.433 | 0.436 |  | 5.92 | 11 | 0.087 | 79.91% | 11.3947 | 6.6307 | 0.75555 | 0.592 | 0.054 | 0.074
| 380:00 | 75.5548 | [8 empty] | 0.436
| 381:00 | 75.5548 | [8 empty] | 0.43467 | 0.033
| 382:00 | 75.5548 | [8 empty] | 0.43467
| 383:00 | 75.5548 | 6.5 | 18 | 16 | 4.66 | 106 | 136 | 21.4 | 0.415 | 0.42975 |  | 5.99 | 11 | 0.075 | 81.93% | 10.9211 | 6.9183 | 0.75555 | 0.599 | 0.055 | 0.048
2019-04-18 | 384:00 | 74.6442 | [8 empty] | 0.42975
| 385:00 | 74.6442 | [8 empty] | 0.425
| 386:00 | 74.6442 | [8 empty] | 0.425
| 387:00 | 74.6442 | 6.54 | 18 | 17 | 4.69 | 102 | 137 | 19.8 | 0.42 | 0.42375 |  | 6.05 | 11 | 0.096 | 77.14% | 11.0526 | 6.7535 | 0.74644 | 0.605 | 0.054 | 0.051
| 388:00 | 74.6442 | [8 empty] | 0.42375
| 389:00 | 74.6442 | [8 empty] | 0.42267
| 390:00 | 74.6442 | [8 empty] | 0.42267
| 391:00 | 74.6442 | 6.45 | 20 | 18 | 4.68 | 108 | 139 | 20.4 | 0.445 | 0.42825 |  | 6 | 12 | 0.089 | 80% | 11.7105 | 6.3741 | 0.74644 | 0.6 | 0.054 | 0.053
| 392:00 | 74.6442 | [8 empty] | 0.42825
| 393:00 | 74.6442 | [8 empty] | 0.42667 | 0.081
| 394:00 | 74.6442 | [8 empty] | 0.42667
| 395:00 | 74.6442 | 6.5 | 20 | 18 | 4.7 | 111 | 137 | 20.3 | 0.447 | 0.43175 |  | 6.04 | 12 | 0.091 | 79.64% | 11.7632 | 6.3456 | 0.74644 | 0.604 | 0.056 | 0.055
| 396:00 | 74.6442 | [8 empty] | 0.43175
| 397:00 | 74.6442 | [8 empty] | 0.43733
| 398:00 | 74.6442 | [8 empty] | 0.43733
| 399:00 | 74.6442 | 6.58 | 19 | 18 | 4.49 | 111 | 141 | 20.3 | 0.446 | 0.4395 |  | 6.07 | 11 | 0.082 | 81.61% | 11.7368 | 6.3598 | 0.74644 | 0.607 | 0.053 | 0.051
| 400:00 | 74.6442 | [8 empty] | 0.4395
| 401:00 | 74.6442 | [8 empty] | 0.446
| 402:00 | 74.6442 | [8 empty] | 0.446
| 403:00 | 74.6442 | 6.49 | 20 | 17 | 6.15 | 112 | 150 | 21.4 | 0.448 | 0.4465 |  | 6.03 | 10 | 0.08 | 82.14% | 11.7895 | 6.3314 | 0.74644 | 0.603 | 0.05 | 0.049
| 404:00 | 74.6442 | [8 empty] | 0.4465
| 405:00 | 74.6442 | [8 empty] | 0.447 | 0.034
| 406:00 | 74.6442 | [8 empty] | 0.447
| 407:00 | 74.6442 | 6.51 | 21 | 17 | 5.59 | 106 | 140 | 21.4 | 0.403 | 0.436 |  | 6.04 | 11 | 0.068 | 83.13% | 10.6053 | 7.0384 | 0.74644 | 0.604 | 0.052 | 0.052
2019-04-19 | 408:00 | 75.3955 | [8 empty] | 0.436
| 409:00 | 75.3955 | [8 empty] | 0.43233
| 410:00 | 75.3955 | [8 empty] | 0.43233
| 411:00 | 75.3955 | 6.55 | 18 | 15 | 5.44 | 109 | 141 | 20.7 | 0.44 | 0.43425 |  | 6.12 | 12 | 0.072 | 83.64% | 11.5789 | 6.5114 | 0.75395 | 0.612 | 0.053 | 0.052
| 412:00 | 75.3955 | [8 empty] | 0.43425
| 413:00 | 75.3955 | [8 empty] | 0.43033
| 414:00 | 75.3955 | [8 empty] | 0.43033
| 415:00 | 75.3955 | 6.51 | 20 | 17 | 5.9 | 112 | 146 | 20.7 | 0.444 | 0.43375 |  | 6.02 | 12 | 0.07 | 84.23% | 11.6842 | 6.4528 | 0.75395 | 0.602 | 0.049 | 0.048
| 416:00 | 75.3955 | [8 empty] | 0.43375
| 417:00 | 75.3955 | [8 empty] | 0.429 | 0.057
| 418:00 | 75.3955 | [8 empty] | 0.429
| 419:00 | 75.3955 | 6.51 | 20 | 18 | 5.79 | 112 | 145 | 20.7 | 0.452 | 0.43475 |  | 6.01 | 14 | 0.071 | 84.29% | 11.8947 | 6.3386 | 0.75395 | 0.601 | 0.049 | 0.049
| 420:00 | 75.3955 | [8 empty] | 0.43475
| 421:00 | 75.3955 | [8 empty] | 0.44533
| 422:00 | 75.3955 | [8 empty] | 0.44533
| 423:00 | 75.3955 | 6.64 | 20 | 17 | 5.46 | 107 | 137 | 20.7 | 0.46 | 0.449 |  | 6.2 | 12 | 0.064 | 86.09% | 12.1053 | 6.2283 | 0.75395 | 0.62 | 0.045 | 0.046
| 424:00 | 75.3955 | [8 empty] | 0.449
| 425:00 | 75.3955 | [8 empty] | 0.452
| 426:00 | 75.3955 | [8 empty] | 0.452
| 427:00 | 75.3955 | 6.55 | 19 | 19 | 5.34 | 110 | 141 | 21.7 | 0.444 | 0.45 |  | 6.09 | 12 | 0.066 | 85.14% | 11.6842 | 6.4528 | 0.75395 | 0.609 | 0.046 | 0.045
| 428:00 | 75.3955 | [8 empty] | 0.45
| 429:00 | 75.3955 | [8 empty] | 0.452 | 0.028
| 430:00 | 75.3955 | [8 empty] | 0.452
| 431:00 | 75.3955 | 6.52 | 18 | 19 | 5.26 | 111 | 144 | 21.6 | 0.417 | 0.44325 |  | 6.16 | 11 | 0.081 | 80.58% | 10.9737 | 6.8706 | 0.75395 | 0.616 | 0.054 | 0.05
2019-04-20 | 432:00 | 74.7879 | [8 empty] | 0.44325
| 433:00 | 74.7879 | [8 empty] | 0.44033
| 434:00 | 74.7879 | [8 empty] | 0.44033
| 435:00 | 74.7879 | 6.48 | 17 | 17 | 5.12 | 110 | 143 | 20.4 | 0.451 | 0.443 |  | 6.07 | 11 | 0.086 | 80.93% | 11.8684 | 6.3014 | 0.74788 | 0.607 | 0.052 | 0.051
| 436:00 | 74.7879 | [8 empty] | 0.443
| 437:00 | 74.7879 | [8 empty] | 0.43733
| 438:00 | 74.7879 | [8 empty] | 0.43733
| 439:00 | 74.7879 | 6.48 | 20 | 17 | 4.74 | 120 | 144 | 20.6 | 0.469 | 0.44525 |  | 6.03 | 10 | 0.081 | 82.73% | 12.3421 | 6.0596 | 0.74788 | 0.603 | 0.05 | 0.05
| 440:00 | 74.7879 | [8 empty] | 0.44525
| 441:00 | 74.7879 | [8 empty] | 0.44567 | 0.057
| 442:00 | 74.7879 | [8 empty] | 0.44567
| 443:00 | 74.7879 | 6.49 | 20 | 18 | 5.19 | 114 | 144 | 20.4 | 0.468 | 0.45125 |  | 6.04 | 10 | 0.084 | 82.05% | 12.3158 | 6.0725 | 0.74788 | 0.604 | 0.051 | 0.05
| 444:00 | 74.7879 | [8 empty] | 0.45125
| 445:00 | 74.7879 | [8 empty] | 0.46267
| 446:00 | 74.7879 | [8 empty] | 0.46267
| 447:00 | 74.7879 | 6.51 | 20 | 18 | 5.47 | 110 | 143 | 21.4 | 0.427 | 0.45375 |  | 6.05 | 11 | 0.072 | 83.14% | 11.2368 | 6.6556 | 0.74788 | 0.605 | 0.049 | 0.055
| 448:00 | 74.7879 | [8 empty] | 0.45375
| 449:00 | 74.7879 | [8 empty] | 0.45467
| 450:00 | 74.7879 | [8 empty] | 0.45467
| 451:00 | 74.7879 | 6.56 | 19 | 17 | 5.36 | 119 | 148 | 21.1 | 0.456 | 0.455 |  | 6.04 | 10 | 0.071 | 84.43% | 12 | 6.2323 | 0.74788 | 0.604 | 0.048 | 0.048
| 452:00 | 74.7879 | [8 empty] | 0.455
| 453:00 | 74.7879 | [8 empty] | 0.45033 | 0.033
| 454:00 | 74.7879 | [8 empty] | 0.45033
| 455:00 | 74.7879 | 6.5 | 18 | 18 | 5.63 | 115 | 150 | 21.1 | 0.434 | 0.44625 |  | 6.05 | 12 | 0.079 | 81.8% | 11.4211 | 6.5482 | 0.74788 | 0.605 | 0.057 | 0.049
2019-04-21 | 456:00 | 74.7596 | [8 empty] | 0.44625
| 457:00 | 74.7596 | [8 empty] | 0.439
| 458:00 | 74.7596 | [8 empty] | 0.439
| 459:00 | 74.7596 | 6.51 | 18 | 19 | 5.54 | 119 | 150 | 20 | 0.468 | 0.44625 |  | 6.11 | 12 | 0.087 | 81.41% | 12.3158 | 6.0702 | 0.7476 | 0.611 | 0.056 | 0.053
| 460:00 | 74.7596 | [8 empty] | 0.44625
| 461:00 | 74.7596 | [8 empty] | 0.45267
| 462:00 | 74.7596 | [8 empty] | 0.45267
| 463:00 | 74.7596 | 6.5 | 20 | 18 | 5.74 | 120 | 150 | 19.8 | 0.48 | 0.4595 |  | 5.99 | 12 | 0.088 | 81.67% | 12.6316 | 5.9185 | 0.7476 | 0.599 | 0.054 | 0.052
| 464:00 | 74.7596 | [8 empty] | 0.4595
| 465:00 | 74.7596 | [8 empty] | 0.46067 | 0.054
| 466:00 | 74.7596 | [8 empty] | 0.46067
| 467:00 | 74.7596 | 6.5 | 17 | 17 | 6.11 | 124 | 155 | 19.7 | 0.485 | 0.46675 |  | 6 | 10 | 0.084 | 82.68% | 12.7632 | 5.8575 | 0.7476 | 0.6 | 0.054 | 0.055
| 468:00 | 74.7596 | [8 empty] | 0.46675
| 469:00 | 74.7596 | [8 empty] | 0.47767
| 470:00 | 74.7596 | [8 empty] | 0.47767
| 471:00 | 74.7596 | 6.54 | 20 | 18 | 6.24 | 115 | 154 | 20.5 | 0.44 | 0.46825 |  | 6.03 | 12 | 0.074 | 83.18% | 11.5789 | 6.4565 | 0.7476 | 0.603 | 0.048 | 0.05
| 472:00 | 74.7596 | [8 empty] | 0.46825
| 473:00 | 74.7596 | [8 empty] | 0.46833
| 474:00 | 74.7596 | [8 empty] | 0.46833
| 475:00 | 74.7596 | 6.58 | 18 | 16 | 5.98 | 116 | 152 | 20.4 | 0.45 | 0.46375 |  | 5.99 | 11 | 0.077 | 82.89% | 11.8421 | 6.313 | 0.7476 | 0.599 | 0.055 | 0.053
| 476:00 | 74.7596 | [8 empty] | 0.46375
| 477:00 | 74.7596 | [8 empty] | 0.45833 | 0.033
| 478:00 | 74.7596 | [8 empty] | 0.45833
| 479:00 | 74.7596 | 6.52 | 19 | 17 | 6.1 | 118 | 153 | 20.4 | 0.457 | 0.458 |  | 6.01 | 12 | 0.072 | 84.25% | 12.0263 | 6.2163 | 0.7476 | 0.601 | 0.05 | 0.049
2019-04-22 | 480:00 | 77.922 | [8 empty] | 0.458
| 481:00 | 77.922 | [8 empty] | 0.449
| 482:00 | 77.922 | [8 empty] | 0.449
| 483:00 | 77.922 | 6.49 | 19 | 16 | 5.87 | 124 | 155 | 19.5 | 0.473 | 0.455 |  | 6.1 | 10 | 0.066 | 86.05% | 12.4474 | 6.2601 | 0.77922 | 0.61 | 0.057 | 0.051
| 484:00 | 77.922 | [8 empty] | 0.455
| 485:00 | 77.922 | [8 empty] | 0.46
| 486:00 | 77.922 | [8 empty] | 0.46
| 487:00 | 77.922 | 6.51 | 20 | 16 | 5.86 | 124 | 157 | 19.4 | 0.488 | 0.467 |  | 5.94 | 10 | 0.077 | 84.22% | 12.8421 | 6.0677 | 0.77922 | 0.594 | 0.055 | 0.052
| 488:00 | 77.922 | [8 empty] | 0.467
| 489:00 | 77.922 | [8 empty] | 0.47267 | 0.091
| 490:00 | 77.922 | [8 empty] | 0.47267
| 491:00 | 77.922 | 6.5 | 20 | 17 | 5.9 | 130 | 147 | 19.3 | 0.499 | 0.47925 |  | 6 | 10 | 0.073 | 85.37% | 13.1316 | 5.9339 | 0.77922 | 0.6 | 0.055 | 0.053
| 492:00 | 77.922 | [8 empty] | 0.47925
| 493:00 | 77.922 | [8 empty] | 0.48667
| 494:00 | 77.922 | [8 empty] | 0.48667
| 495:00 | 77.922 | 6.59 | 20 | 18 | 6.21 | 118 | 159 | 20 | 0.455 | 0.47875 |  | 6.05 | 11 | 0.075 | 83.52% | 11.9737 | 6.5078 | 0.77922 | 0.605 | 0.058 | 0.062
| 496:00 | 77.922 | [8 empty] | 0.47875
| 497:00 | 77.922 | [8 empty] | 0.48067
| 498:00 | 77.922 | [8 empty] | 0.48067
| 499:00 | 77.922 | 6.53 | 21 | 19 | 6.08 | 125 | 158 | 20.3 | 0.484 | 0.4815 |  | 5.93 | 10 | 0.07 | 85.54% | 12.7368 | 6.1178 | 0.77922 | 0.593 | 0.052 | 0.048
| 500:00 | 77.922 | [8 empty] | 0.4815
| 501:00 | 77.922 | [8 empty] | 0.47933 | 0.038
| 502:00 | 77.922 | [8 empty] | 0.47933
| 503:00 | 77.922 | 6.51 | 21 | 19 | 6.41 | 127 | 159 | 20.2 | 0.456 | 0.4735 |  | 6 | 12 | 0.076 | 83.33% | 12 | 6.4935 | 0.77922 | 0.6 | 0.054 | 0.049
2019-04-23 | 504:00 | 81.2014 | [8 empty] | 0.4735
| 505:00 | 81.2014 | [8 empty] | 0.465
| 506:00 | 81.2014 | [8 empty] | 0.465
| 507:00 | 81.2014 | 6.55 | 19 | 18 | 6.28 | 126 | 162 | 19.4 | 0.483 | 0.4695 |  | 6.01 | 8 | 0.075 | 84.47% | 12.7105 | 6.3885 | 0.81201 | 0.601 | 0.053 | 0.05
| 508:00 | 81.2014 | [8 empty] | 0.4695
| 509:00 | 81.2014 | [8 empty] | 0.47433
| 510:00 | 81.2014 | [8 empty] | 0.47433
| 511:00 | 81.2014 | 6.53 | 22 | 19 | 6.11 | 130 | 164 | 19.1 | 0.503 | 0.4815 |  | 6 | 13 | 0.077 | 84.69% | 13.2368 | 6.1345 | 0.81201 | 0.6 | 0.052 | 0.05
| 512:00 | 81.2014 | [8 empty] | 0.4815
| 513:00 | 81.2014 | [8 empty] | 0.48067 | 0.074
| 514:00 | 81.2014 | [8 empty] | 0.48067
| 515:00 | 81.2014 | 6.49 | 16 | 17 | 6.42 | 129 | 163 | 19.3 | 0.505 | 0.48675 |  | 6.02 | 10 | 0.075 | 85.15% | 13.2895 | 6.1102 | 0.81201 | 0.602 | 0.055 | 0.055
| 516:00 | 81.2014 | [8 empty] | 0.48675
| 517:00 | 81.2014 | [8 empty] | 0.497
| 518:00 | 81.2014 | [8 empty] | 0.497
| 519:00 | 81.2014 | 6.55 | 20 | 18 | 6.58 | 125 | 164 | 20 | 0.463 | 0.4885 |  | 6.03 | 11 | 0.072 | 84.45% | 12.1842 | 6.6645 | 0.81201 | 0.603 | 0.05 | 0.055
| 520:00 | 81.2014 | [8 empty] | 0.4885
| 521:00 | 81.2014 | [8 empty] | 0.49033
| 522:00 | 81.2014 | [8 empty] | 0.49033
| 523:00 | 81.2014 | 6.53 | 21 | 17 | 5.6 | 129 | 162 | 20.1 | 0.477 | 0.487 |  | 6.08 | 12 | 0.068 | 85.74% | 12.5526 | 6.4689 | 0.81201 | 0.608 | 0.046 | 0.063
| 524:00 | 81.2014 | [8 empty] | 0.487
| 525:00 | 81.2014 | [8 empty] | 0.48167 | 0.041
| 526:00 | 81.2014 | [8 empty] | 0.48167
| 527:00 | 81.2014 | 6.5 | 19 | 18 | 6.48 | 132 | 160 | 20.4 | 0.471 | 0.479 |  | 6 | 12 | 0.057 | 87.9% | 12.3947 | 6.5513 | 0.81201 | 0.6 | 0.042 | 0.05
2019-04-24 | 528:00 | 81.7968 | [8 empty] | 0.479
| 529:00 | 81.7968 | [8 empty] | 0.47033
| 530:00 | 81.7968 | [8 empty] | 0.47033
| 531:00 | 81.7968 | 6.79 | 18 | 17 | 6.52 | 127 | 163 | 19.7 | 0.488 | 0.47475 |  | 5.99 | 11 | 0.076 | 84.43% | 12.8421 | 6.3694 | 0.81797 | 0.599 | 0.056 | 0.052
| 532:00 | 81.7968 | [8 empty] | 0.47475
| 533:00 | 81.7968 | [8 empty] | 0.47867
| 534:00 | 81.7968 | [8 empty] | 0.47867
| 535:00 | 81.7968 | 6.53 | 18 | 18 | 6.48 | 128 | 165 | 19.5 | 0.506 | 0.4855 |  | 5.95 | 10 | 0.069 | 86.36% | 13.3158 | 6.1428 | 0.81797 | 0.595 | 0.061 | 0.061
| 536:00 | 81.7968 | [8 empty] | 0.4855
| 537:00 | 81.7968 | [8 empty] | 0.48833 | 0.04
| 538:00 | 81.7968 | [8 empty] | 0.48833
| 539:00 | 81.7968 | 6.5 | 19 | 17 | 6.34 | 120 | 165 | 19.6 | 0.505 | 0.4925 |  | 6 | 10 | 0.062 | 87.72% | 13.2895 | 6.155 | 0.81797 | 0.6 | 0.054 | 0.052
| 540:00 | 81.7968 | [8 empty] | 0.4925
| 541:00 | 81.7968 | [8 empty] | 0.49967
| 542:00 | 81.7968 | [8 empty] | 0.49967
| 543:00 | 81.7968 | 6.54 | 19 | 18 | 6.2 | 129 | 165 | 20.1 | 0.503 | 0.5005 |  | 6 | 10 | 0.062 | 87.67% | 13.2368 | 6.1795 | 0.81797 | 0.6 | 0.05 | 0.052
| 544:00 | 81.7968 | [8 empty] | 0.5005
| 545:00 | 81.7968 | [8 empty] | 0.50467
| 546:00 | 81.7968 | [8 empty] | 0.50467
| 547:00 | 81.7968 | 6.51 | 19 | 18 | 6.16 | 132 | 158 | 20.4 | 0.518 | 0.508 |  | 6.03 | 10 | 0.071 | 86.29% | 13.6316 | 6.0005 | 0.81797 | 0.603 | 0.054 | 0.053
| 548:00 | 81.7968 | [8 empty] | 0.508
| 549:00 | 81.7968 | [8 empty] | 0.50867 | 0.046
| 550:00 | 81.7968 | [8 empty] | 0.50867
| 551:00 | 81.7968 | 6.53 | 19 | 18 | 6.5 | 132 | 166 | 20.4 | 0.513 | 0.50975 |  | 6.02 | 10 | 0.061 | 88.11% | 13.5 | 6.059 | 0.81797 | 0.602 | 0.051 | 0.055
2019-04-25 | 552:00 | 84.46 | [8 empty] | 0.50975
| 553:00 | 84.46 | [8 empty] | 0.51133
| 554:00 | 84.46 | [8 empty] | 0.51133
| 555:00 | 84.46 | 6.52 | 18 | 18 | 6.36 | 132 | 161 | 20.2 | 0.512 | 0.5115 |  | 6.1 | 11 | 0.071 | 86.13% | 13.4737 | 6.2685 | 0.8446 | 0.61 | 0.053 | 0.051
| 556:00 | 84.46 | [8 empty] | 0.5115
| 557:00 | 84.46 | [8 empty] | 0.51433
| 558:00 | 84.46 | [8 empty] | 0.51433
| 559:00 | 84.46 | 6.52 | 18 | 18 | 6.43 | 128 | 164 | 20.2 | 0.498 | 0.51025 |  | 5.99 | 10 | 0.058 | 88.35% | 13.1053 | 6.4447 | 0.8446 | 0.599 | 0.054 | 0.051
| 560:00 | 84.46 | [8 empty] | 0.51025
| 561:00 | 84.46 | [8 empty] | 0.50767 | 0.041
| 562:00 | 84.46 | [8 empty] | 0.50767
| 563:00 | 84.46 | 6.55 | 19 | 18 | 6.71 | 125 | 162 | 19.9 | 0.505 | 0.507 |  | 6.08 | 11 | 0.066 | 86.93% | 13.2895 | 6.3554 | 0.8446 | 0.608 | 0.052 | 0.054
| 564:00 | 84.46 | [8 empty] | 0.507
| 565:00 | 84.46 | [8 empty] | 0.505
| 566:00 | 84.46 | [8 empty] | 0.505
| 567:00 | 84.46 | 6.53 | 18 | 18 | 6.43 | 129 | 163 | 20.7 | 0.509 | 0.506 |  | 6.1 | 11 | 0.066 | 87.03% | 13.3947 | 6.3055 | 0.8446 | 0.61 | 0.058 | 0.058
| 568:00 | 84.46 | [8 empty] | 0.506
| 569:00 | 84.46 | [8 empty] | 0.504
| 570:00 | 84.46 | [8 empty] | 0.504
| 571:00 | 84.46 | 6.57 | 19 | 18 | 6.49 | 126 | 162 | 20.7 | 0.506 | 0.5045 |  | 6.13 | 11 | 0.075 | 85.18% | 13.3158 | 6.3428 | 0.8446 | 0.613 | 0.055 | 0.059
| 572:00 | 84.46 | [8 empty] | 0.5045
| 573:00 | 84.46 | [8 empty] | 0.50667 | 0.044
| 574:00 | 84.46 | [8 empty] | 0.50667
| 575:00 | 84.46 | 6.52 | 19 | 18 | 6.41 | 131 | 164 | 21 | 0.511 | 0.50775 |  | 6.06 | 11 | 0.077 | 84.93% | 13.4474 | 6.2808 | 0.8446 | 0.606 | 0.054 | 0.056
2019-04-26 | 576:00 | 85.8088 | [8 empty] | 0.50775
| 577:00 | 85.8088 | [8 empty] | 0.50867
| 578:00 | 85.8088 | [8 empty] | 0.50867
| 579:00 | 85.8088 | 6.55 | 18 | 18 | 6.29 | 132 | 165 | 21 | 0.513 | 0.50975 |  | 6.1 | 11 | 0.071 | 86.16% | 13.5 | 6.3562 | 0.85809 | 0.61 | 0.052 | 0.056
| 580:00 | 85.8088 | [8 empty] | 0.50975
| 581:00 | 85.8088 | [8 empty] | 0.51
| 582:00 | 85.8088 | [8 empty] | 0.51
| 583:00 | 85.8088 | 6.51 | 17 | 18 | 6.76 | 126 | 161 | 21.1 | 0.489 | 0.50475 |  | 6.19 | 11 | 0.066 | 86.5% | 12.8684 | 6.6682 | 0.85809 | 0.619 | 0.061 | 0.062
| 584:00 | 85.8088 | [8 empty] | 0.50475
| 585:00 | 85.8088 | [8 empty] | 0.50433 | 0.041
| 586:00 | 85.8088 | [8 empty] | 0.50433
| 587:00 | 85.8088 | 6.54 | 17 | 18 | 6.37 | 123 | 159 | 20.9 | 0.476 | 0.49725 |  | 6.13 | 11 | 0.063 | 86.76% | 12.5263 | 6.8503 | 0.85809 | 0.613 | 0.056 | 0.059
| 588:00 | 85.8088 | [8 empty] | 0.49725
| 589:00 | 85.8088 | [8 empty] | 0.49267
| 590:00 | 85.8088 | [8 empty] | 0.49267
| 591:00 | 85.8088 | 6.54 | 18 | 18 | 6.38 | 126 | 164 | 20.8 | 0.498 | 0.494 |  | 6.07 | 10 | 0.063 | 87.35% | 13.1053 | 6.5477 | 0.85809 | 0.607 | 0.053 | 0.052
| 592:00 | 85.8088 | [8 empty] | 0.494
| 593:00 | 85.8088 | [8 empty] | 0.48767
| 594:00 | 85.8088 | [8 empty] | 0.48767
| 595:00 | 85.8088 | 6.57 | 18 | 18 | 5.63 | 130 | 161 | 21.4 | 0.505 | 0.492 |  | 6.11 | 10 | 0.06 | 88.12% | 13.2895 | 6.4569 | 0.85809 | 0.611 | 0.057 | 0.045
| 596:00 | 85.8088 | [8 empty] | 0.492
| 597:00 | 85.8088 | [8 empty] | 0.493 | 0.043
| 598:00 | 85.8088 | [8 empty] | 0.493
| 599:00 | 85.8088 | 6.53 | 18 | 18 | 6.13 | 126 | 163 | 21.3 | 0.5 | 0.49475 |  | 6 | 11 | 0.065 | 87% | 13.1579 | 6.5215 | 0.85809 | 0.6 | 0.056 | 0.057
2019-04-27 | 600:00 | 85.6778 | [8 empty] | 0.49475
| 601:00 | 85.6778 | [8 empty] | 0.501
| 602:00 | 85.6778 | [8 empty] | 0.501
| 603:00 | 85.6778 | 6.51 | 18 | 18 | 6.7 | 129 | 161 | 20.8 | 0.496 | 0.49975 |  | 6.11 | 11 | 0.067 | 86.49% | 13.0526 | 6.564 | 0.85678 | 0.611 | 0.053 | 0.055
| 604:00 | 85.6778 | [8 empty] | 0.49975
| 605:00 | 85.6778 | [8 empty] | 0.50033
| 606:00 | 85.6778 | [8 empty] | 0.50033
| 607:00 | 85.6778 | 6.52 | 18 | 17 | 6.58 | 124 | 160 | 21 | 0.494 | 0.49875 |  | 6.06 | 11 | 0.054 | 89.07% | 13 | 6.5906 | 0.85678 | 0.606 | 0.053 | 0.05
| 608:00 | 85.6778 | [8 empty] | 0.49875
| 609:00 | 85.6778 | [8 empty] | 0.49667 | 0.037
| 610:00 | 85.6778 | [8 empty] | 0.49667
| 611:00 | 85.6778 | 6.53 | 18 | 18 | 6.24 | 128 | 160 | 21 | 0.491 | 0.49525 |  | 6 | 11 | 0.057 | 88.39% | 12.9211 | 6.6309 | 0.85678 | 0.6 | 0.05 | 0.051
| 612:00 | 85.6778 | [8 empty] | 0.49525
| 613:00 | 85.6778 | [8 empty] | 0.49367
| 614:00 | 85.6778 | [8 empty] | 0.49367
| 615:00 | 85.6778 | 6.56 | 18 | 18 | 6.31 | 125 | 160 | 21.3 | 0.484 | 0.49125 |  | 6.14 | 11 | 0.063 | 86.98% | 12.7368 | 6.7268 | 0.85678 | 0.614 | 0.05 | 0.05
| 616:00 | 85.6778 | [8 empty] | 0.49125
| 617:00 | 85.6778 | [8 empty] | 0.48967
| 618:00 | 85.6778 | [8 empty] | 0.48967
| 619:00 | 85.6778 | 6.51 | 18 | 18 | 6.03 | 123 | 162 | 21.2 | 0.471 | 0.485 |  | 6.18 | 11 | 0.074 | 84.29% | 12.3947 | 6.9124 | 0.85678 | 0.618 | 0.052 | 0.055
| 620:00 | 85.6778 | [8 empty] | 0.485
| 621:00 | 85.6778 | [8 empty] | 0.482 | 0.039
| 622:00 | 85.6778 | [8 empty] | 0.482
| 623:00 | 85.6778 | 6.52 | 18 | 18 | 6.06 | 119 | 160 | 21 | 0.493 | 0.48475 |  | 6.18 | 11 | 0.073 | 85.19% | 12.9737 | 6.604 | 0.85678 | 0.618 | 0.053 | 0.054
2019-04-28 | 624:00 | 85.7235 | [8 empty] | 0.48475
| 625:00 | 85.7235 | [8 empty] | 0.48267
| 626:00 | 85.7235 | [8 empty] | 0.48267
| 627:00 | 85.7235 | 6.56 | 18 | 18 | 6.69 | 127 | 160 | 21.2 | 0.496 | 0.486 |  | 6.08 | 11 | 0.067 | 86.49% | 13.0526 | 6.5675 | 0.85724 | 0.608 | 0.053 | 0.053
| 628:00 | 85.7235 | [8 empty] | 0.486
| 629:00 | 85.7235 | [8 empty] | 0.48667
| 630:00 | 85.7235 | [8 empty] | 0.48667
| 631:00 | 85.7235 | 6.54 | 18 | 18 | 6.63 | 123 | 159 | 21.1 | 0.486 | 0.4865 |  | 6.09 | 10 | 0.06 | 87.65% | 12.7895 | 6.7027 | 0.85724 | 0.609 | 0.056 | 0.052
| 632:00 | 85.7235 | [8 empty] | 0.4865
| 633:00 | 85.7235 | [8 empty] | 0.49167 | 0.041
| 634:00 | 85.7235 | [8 empty] | 0.49167
| 635:00 | 85.7235 | 6.61 | 20 | 18 | 6.78 | 124 | 160 | 20.3 | 0.491 | 0.4915 |  | 6.14 | 10 | 0.063 | 87.17% | 12.9211 | 6.6344 | 0.85724 | 0.614 | 0.055 | 0.051
| 636:00 | 85.7235 | [8 empty] | 0.4915
| 637:00 | 85.7235 | [8 empty] | 0.491
| 638:00 | 85.7235 | [8 empty] | 0.491
| 639:00 | 85.7235 | 6.57 | 19 | 18 | 6.62 | 122 | 161 | 21.3 | 0.477 | 0.4875 |  | 6.12 | 10 | 0.058 | 87.84% | 12.5526 | 6.8291 | 0.85724 | 0.612 | 0.05 | 0.05
| 640:00 | 85.7235 | [8 empty] | 0.4875
| 641:00 | 85.7235 | [8 empty] | 0.48467
| 642:00 | 85.7235 | [8 empty] | 0.48467
| 643:00 | 85.7235 | 6.58 | 19 | 18 | 5.8 | 124 | 162 | 20.4 | 0.497 | 0.48775 |  | 6.17 | 11 | 0.068 | 86.32% | 13.0789 | 6.5543 | 0.85724 | 0.617 | 0.057 | 0.053
| 644:00 | 85.7235 | [8 empty] | 0.48775
| 645:00 | 85.7235 | [8 empty] | 0.48833 | 0.043
| 646:00 | 85.7235 | [8 empty] | 0.48833
| 647:00 | 85.7235 | 6.53 | 18 | 18 | 6.83 | 123 | 160 | 21.4 | 0.497 | 0.4905 |  | 6.19 | 11 | 0.071 | 85.71% | 13.0789 | 6.5543 | 0.85724 | 0.619 | 0.057 | 0.057
2019-04-29 | 648:00 | 84.4368 | [8 empty] | 0.4905
| 649:00 | 84.4368 | [8 empty] | 0.49033
| 650:00 | 84.4368 | [8 empty] | 0.49033
| 651:00 | 84.4368 | 6.58 | 18 | 18 | 6.52 | 126 | 161 | 21.5 | 0.494 | 0.49125 |  | 6.06 | 10 | 0.067 | 86.44% | 13 | 6.4951 | 0.84437 | 0.606 | 0.048 | 0.05
| 652:00 | 84.4368 | [8 empty] | 0.49125
| 653:00 | 84.4368 | [8 empty] | 0.496
| 654:00 | 84.4368 | [8 empty] | 0.496
| 655:00 | 84.4368 | 6.53 | 19 | 18 | 6.85 | 123 | 162 | 21.4 | 0.483 | 0.49275 |  | 6.05 | 11 | 0.058 | 87.99% | 12.7105 | 6.6431 | 0.84437 | 0.605 | 0.05 | 0.051
| 656:00 | 84.4368 | [8 empty] | 0.49275
| 657:00 | 84.4368 | [8 empty] | 0.49133 | 0.04
| 658:00 | 84.4368 | [8 empty] | 0.49133
| 659:00 | 84.4368 | 6.57 | 19 | 17 | 7.07 | 123 | 162 | 21.2 | 0.486 | 0.49 |  | 6.12 | 11 | 0.057 | 88.27% | 12.7895 | 6.6021 | 0.84437 | 0.612 | 0.053 | 0.052
| 660:00 | 84.4368 | [8 empty] | 0.49
| 661:00 | 84.4368 | [8 empty] | 0.48767
| 662:00 | 84.4368 | [8 empty] | 0.48767
| 663:00 | 84.4368 | 6.56 | 20 | 17 | 6.78 | 119 | 159 | 21.6 | 0.454 | 0.47925 |  | 6.11 | 12 | 0.048 | 89.43% | 11.9474 | 7.0674 | 0.84437 | 0.611 | 0.042 | 0.043
| 664:00 | 84.4368 | [8 empty] | 0.47925
| 665:00 | 84.4368 | [8 empty] | 0.47433
| 666:00 | 84.4368 | [8 empty] | 0.47433
| 667:00 | 84.4368 | 6.49 | 19 | 18 | 6.84 | 124 | 162 | 21.8 | 0.485 | 0.477 |  | 6 | 11 | 0.06 | 87.63% | 12.7632 | 6.6157 | 0.84437 | 0.6 | 0.051 | 0.049
| 668:00 | 84.4368 | [8 empty] | 0.477
| 669:00 | 84.4368 | [8 empty] | 0.475 | 0.05
| 670:00 | 84.4368 | [8 empty] | 0.475
| 671:00 | 84.4368 | 6.59 | 19 | 18 | 7.23 | 126 | 161 | 21.8 | 0.496 | 0.48025 |  | 6 | 11 | 0.068 | 86.29% | 13.0526 | 6.4689 | 0.84437 | 0.6 | 0.057 | 0.057
2019-04-30 | 672:00 | 82.0025 | [8 empty] | 0.48025
| 673:00 | 82.0025 | [8 empty] | 0.47833
| 674:00 | 82.0025 | [8 empty] | 0.47833
| 675:00 | 82.0025 | 6.56 | 18 | 18 | 7.38 | 124 | 162 | 21.2 | 0.482 | 0.47925 |  | 6.09 | 10 | 0.06 | 87.55% | 12.6842 | 6.4649 | 0.82003 | 0.609 | 0.043 | 0.047
| 676:00 | 82.0025 | [8 empty] | 0.47925
| 677:00 | 82.0025 | [8 empty] | 0.48767
| 678:00 | 82.0025 | [8 empty] | 0.48767
| 679:00 | 82.0025 | 6.52 | 20 | 18 | 7.4 | 120 | 165 | 21.6 | 0.471 | 0.4835 |  | 5.98 | 11 | 0.056 | 88.11% | 12.3947 | 6.6159 | 0.82003 | 0.598 | 0.049 | 0.053
| 680:00 | 82.0025 | [8 empty] | 0.4835
| 681:00 | 82.0025 | [8 empty] | 0.483 | 6.15
| 682:00 | 82.0025 | [8 empty] | 0.483
| 683:00 | 82.0025 | 6.58 | 20 | 18 | 7.96 | 119 | 164 | 21.8 | 0.466 | 0.47875 |  | 6.04 | 11 | 0.052 | 88.84% | 12.2632 | 6.6869 | 0.82003 | 0.604 | 0.042 | 0.049
| 684:00 | 82.0025 | [8 empty] | 0.47875
| 685:00 | 82.0025 | [8 empty] | 0.473
| 686:00 | 82.0025 | [8 empty] | 0.473
| 687:00 | 82.0025 | 6.61 | 20 | 18 | 7.67 | 120 | 164 | 22 | 0.477 | 0.474 |  | 6.06 | 11 | 0.056 | 88.26% | 12.5526 | 6.5327 | 0.82003 | 0.606 | 0.045 | 0.046
| 688:00 | 82.0025 | [8 empty] | 0.474
| 689:00 | 82.0025 | [8 empty] | 0.47133
| 690:00 | 82.0025 | [8 empty] | 0.47133
| 691:00 | 82.0025 | 6.61 | 20 | 18 | 7.56 | 122 | 169 | 22 | 0.476 | 0.4725 |  | 6.03 | 11 | 0.061 | 87.18% | 12.5263 | 6.5464 | 0.82003 | 0.603 | 0.049 | 0.052
| 692:00 | 82.0025 | [8 empty] | 0.4725
| 693:00 | 82.0025 | [8 empty] | 0.473 | 0.044
| 694:00 | 82.0025 | [8 empty] | 0.473
| 695:00 | 82.0025 | 6.53 | 19 | 18 | 7.59 | 120 | 160 | 22 | 0.474 | 0.47325 |  | 6.09 | 11 | 0.065 | 86.29% | 12.4737 | 6.574 | 0.82003 | 0.609 | 0.053 | 0.053
2019-05-01 | 696:00 | 0 | [8 empty] | 0.47325
. | 697:00 | 0 | [8 empty] | 0.47567
| 698:00 | 0 | [8 empty] | 0.47567
| 699:00 | 0 | [8 empty] | 0.47567
| 700:00 | 0 | [8 empty] | 0.47567
| 701:00 | 0 | [8 empty] | 0.475
| 702:00 | 0 | [8 empty] | 0.475
| 703:00 | 0 | [8 empty] | 0.475
| 704:00 | 0 | [8 empty] | 0.475
| 705:00 | 0 | [8 empty] | 0.474
| 706:00 | 0 | [8 empty] | 0.474
| 707:00 | 0 | [8 empty] | 0.474
| 708:00 | 0 | [8 empty] | 0.474
| 709:00 | 0 | [8 empty] | #DIV/0!
| 710:00 | 0 | [8 empty] | #DIV/0!
| 711:00 | 0 | [8 empty] | #DIV/0!
| 712:00 | 0 | [8 empty] | #DIV/0!
| 713:00 | 0 | [8 empty] | #DIV/0!
| 714:00 | 0 | [8 empty] | #DIV/0!
| 715:00 | 0 | [8 empty] | #DIV/0!
| 716:00 | 0 | [8 empty] | #DIV/0!
| 717:00 | 0 | [8 empty] | #DIV/0!
| 718:00 | 0 | [8 empty] | #DIV/0!
| 719:00 | 0 | [8 empty] | #DIV/0!
TOTAL |  | 49195.6325 | 1179.38 | 3460 | 3240 | 1103.29 | 18435 | 24557 | 3522.7 | 74.027 |  | 8.409 | 1091.41 | 1918 | 11.438 | 151.8277 | 1948.0789 | 1133.1741 | 122.9891 | 109.141 | 8.637 | 8.666
AVERAGE |  | 66.138 | 6.5521 | 19.2222 | 18 | 6.1294 | 102.4167 | 136.4278 | 19.5706 | 0.41126 |  | 0.14015 | 6.0634 | 10.6556 | 0.063544 | 0.84349 | 10.8227 | 6.2954 | 0.68327 | 0.60634 | 0.047983 | 0.048144
MINIMUM |  | 0 | 6.35 | 15 | 15 | 3.61 | 73 | 102 | 15.2 | 0.29 |  | 0.019 | 5.92 | 8 | 0.043 | 0.74832 | 7.6316 | 5.5186 | 0.49898 | 0.592 | 0.026 | 0.029
MAXIMUM |  | 85.8088 | 6.79 | 23 | 24 | 10.3 | 132 | 169 | 22 | 0.518 |  | 6.15 | 6.32 | 14 | 0.096 | 0.89427 | 13.6316 | 7.0674 | 0.85809 | 0.632 | 0.061 | 0.074
08:47 |  | 08:47 | [13 empty] | HIGHLIGHT BETWEEN LIME |  | 5
08/12/19 |  | 08/13/19 | [12 empty] | TOTAL # IN THIS RANGE |  | 0 | 5.5
| 08:47 |  | TRUE | [11 empty] | TOTAL SAMPLES |  | 180
FALSE
WHAT
2019-08-12 08:48
1901-12-21
Formulas:
Date = MATCH([Date, row above],A4:A747,1)

## BW 1
|  | Surface Water System Monthly Operation Report | [10 empty] | DATE | TIME
|  | Operation of Filters | [9 empty] | LAST WASH | 1900-01-18 | 3:00 | 1900-01-18 03:00
|  | Bureau of Water | [9 empty] | THIS WASH | 1900-01-22 | 23:30 | 1900-01-22 23:30
TOTAL HOURS
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 1 |  |  |  |  | 2019-04-01 | [8 empty] | 116.5
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED
2019-04-01 | 22:00 | 20 | 30 | 22 | 117200 | 54166.6667 | 10.4 | 5212.32 | CBW |  | 171366.6667
2019-04-02
2019-04-03
2019-04-04
2019-04-05
2019-04-06
2019-04-07 | 6:00 | 20 | 30 | 128 | 117200 | 51041.6667 | 9.8 | 28576.6357 | DB |  | 168241.6667
2019-04-08
2019-04-09
2019-04-10
2019-04-11 | 14:00 | 20 | 30 | 104 | 117200 | 51041.6667 | 9.8 | 23218.5165 | CBW |  | 168241.6667
2019-04-12
2019-04-13
2019-04-14
2019-04-15
2019-04-16 | 5:00 | 20 | 30 | 99 | 117200 | 56770.8333 | 10.9 | 24583.1055 | R.H. |  | 173970.8333
2019-04-17
2019-04-18
2019-04-19 | 10:00 | 20 | 30 | 77 | 117200 | 58854.1667 | 11.3 | 19821.8516 | DH |  | 176054.1667
2019-04-20
2019-04-21
2019-04-22
2019-04-23 | 23:30 | 20 | 30 | 116.5 | 117200 | 60416.6667 | 11.6 | 30786.4042 | GHE | HEAD | 177616.6667
2019-04-24
2019-04-25
2019-04-26
2019-04-27 | 9:00 | 20 | 30 | 82.5 | 117200 | 60937.5 | 11.7 | 21989.4751 | SN | HEAD | 178137.5
2019-04-28
2019-04-29
2019-04-30
2019-05-01
Total |  | 140 | 210 | 629 | 820400
Average |  | 20 | 30 | 89.8571 | 117200
Maximum |  | 20 | 30 | 128 | 117200
Minimum |  | 20 | 30 | 22 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Formulas:
Day = [Day, row above]+1
Note on F8: BCOperator: 5860 = water wash / min

## BW 2
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 2 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-12 | 23:30 | 1900-01-12 23:30
2 | [11 empty] | THIS WASH | 1900-01-17 | 2:00 | 1900-01-17 02:00
3 | [12 empty] | TOTAL HOURS
4 | 7:00 | 20 | 30 | 79 | 117200 | 51041.6667 | 9.8 | 14736.5616 | DB | HEAD 9 PSI | 168241.6667
5 | [13 empty] | 98.5
6
7
8
9 | 4:00 | 20 | 30 | 117 | 117200 | 56250 | 10.8 | 24052.0786 | MN | 8PSI | 173450
10
11
12
13 | 23:30 | 20 | 30 | 115.5 | 117200 | 50520.8333 | 9.7 | 21325.3769 | R.H. |  | 167720.8333
14
15
16
17
18 | 2:00 | 20 | 30 | 98.5 | 117200 | 61458.3333 | 11.8 | 22123.877 | GE | HEAD 9 PSI | 178658.3333
19
20
21
22 | 14:30 | 20 | 30 | 108.5 | 117200 | 55729.1667 | 10.7 | 22098.1803 | DH |  | 172929.1667
23
24
25
26 | 16:30 | 20 | 30 | 98 | 117200 | 65104.1667 | 12.5 | 23317.3443 | SN | HEAD | 182304.1667
27
28
29
30 | 7:00 | 20 | 30 | 88 | 117200 | 71875 | 13.8 | 23115.5779 | SN | HEAD | 189075
31
Total |  | 140 | 210 | 704.5 | 820400
Average |  | 20 | 30 | 100.6429 | 117200
Maximum |  | 20 | 30 | 117 | 117200
Minimum |  | 20 | 30 | 79 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash /min

## BW 3
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 3 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-22 | 19:00 | 1900-01-22 19:00
2 | 15:30 | 20 | 30 | 39.5 | 117200 | 45312.5 | 8.7 | 7828.7315 | WL | 9 PSI HEAD | 162512.5 | THIS WASH | 1900-01-26 | 1:30 | 1900-01-26 01:30
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 78.5
6
7 | 11:30 | 20 | 30 | 116 | 117200 | 51041.6667 | 9.8 | 25897.5761 | GE | HEAD | 168241.6667
8
9
10
11
12 | 8:30 | 20 | 30 | 117 | 117200 | 53645.8333 | 10.3 | 27453.5265 | CBW |  | 170845.8333
13
14
15
16 | 9:00 | 20 | 30 | 96.5 | 117200 | 57291.6667 | 11 | 24182.1578 | JMM |  | 174491.6667
17
18
19 | 9:00 | 20 | 30 | 72 | 117200 | 58854.1667 | 11.3 | 18534.7184 | DH |  | 176054.1667
20
21
22
23 | 19:00 | 20 | 30 | 106 | 117200 | 60416.6667 | 11.6 | 28011.6639 | GHE |  | 177616.6667
24
25
26
27 | 1:30 | 20 | 30 | 78.5 | 117200 | 64583.3333 | 12.4 | 22175.1412 | JMM |  | 181783.3333
28
29
30 | 10:00 | 20 | 30 | 70.5 | 117200 | 71875 | 13.8 | 22163.7507 | SN | HEAD | 189075
31
Total |  | 160 | 240 | 696 | 937600
Average |  | 20 | 30 | 87 | 117200
Maximum |  | 20 | 30 | 117 | 117200
Minimum |  | 20 | 30 | 39.5 | 117200
|  | 8 | 8 | 8 | 8
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 4
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 4 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-23 | 3:00 | 1900-01-23 03:00
2 | [11 empty] | THIS WASH | 1900-01-26 | 3:00 | 1900-01-26 03:00
3 | 7:00 | 20 | 30 | 55 | 117200 | 51041.6667 | 9.8 | 12279.0231 | GHE | HEAD | 168241.6667 |  | TOTAL HOURS
4
5 | [13 empty] | 72
6
7
8 | 19:00 | 20 | 30 | 132 | 117200 | 55729.1667 | 10.7 | 32176.0525 | DH | AUTO | 172929.1667
9
10
11
12 | 18:00 | 20 | 30 | 95 | 117200 | 54166.6667 | 10.4 | 22507.7456 | RH | HEAD | 171366.6667
13
14
15
16 | 10:30 | 20 | 30 | 88.5 | 117200 | 57291.6667 | 11 | 22177.4194 | CBW |  | 174491.6667
17
18
19 | 14:30 | 20 | 30 | 76 | 117200 | 52083.3333 | 10 | 17313.6504 | DH |  | 169283.3333
20
21
22
23
24 | 3:00 | 20 | 30 | 108.5 | 117200 | 60416.6667 | 11.6 | 28672.3164 | GHE | HEAD | 177616.6667
25
26
27 | 3:00 | 20 | 30 | 72 | 117200 | 64583.3333 | 12.4 | 20338.9831 | JMM |  | 181783.3333
28
29
30 | 11:00 | 20 | 30 | 80 | 117200 | 71875 | 13.8 | 25150.3554 | SN | HEAD | 189075
31
Total |  | 160 | 240 | 707 | 937600
Average |  | 20 | 30 | 88.375 | 117200
Maximum |  | 20 | 30 | 132 | 117200
Minimum |  | 20 | 30 | 55 | 117200
|  | 8 | 8 | 8 | 8
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 5
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 5 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-24 | 15:00 | 1900-01-24 15:00
2 | 18:30 | 20 | 30 | 42.5 | 117200 | 44270.8333 | 8.5 | 8229.6792 | CBW |  | 161470.8333 | THIS WASH | 1900-01-28 | 1:00 | 1900-01-28 01:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 82
6
7
8 | 11:00 | 20 | 30 | 136.5 | 117200 | 51041.6667 | 9.8 | 30474.3029 | GE | TIME | 168241.6667
9
10
11
12
13 | 13:30 | 20 | 30 | 122.5 | 117200 | 54687.5 | 10.5 | 29302.2143 | CBW |  | 171887.5
14
15
16
17 | 11:30 | 20 | 30 | 94 | 117200 | 54166.6667 | 10.4 | 22270.8219 | MN |  | 171366.6667
18
19
20
21 | 13:30 | 20 | 30 | 98 | 117200 | 52083.3333 | 10 | 22325.4966 | DH |  | 169283.3333
22
23
24
25 | 15:00 | 20 | 30 | 97.5 | 117200 | 61458.3333 | 11.8 | 26209.6774 | SN | HEAD 6PSI | 178658.3333
26
27
28
29 | 1:00 | 20 | 30 | 82 | 117200 | 64583.3333 | 12.4 | 23163.8418 | JMM |  | 181783.3333
30
31
Total |  | 140 | 210 | 673 | 820400
Average |  | 20 | 30 | 96.1429 | 117200
Maximum |  | 20 | 30 | 136.5 | 117200
Minimum |  | 20 | 30 | 42.5 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 6
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 6 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-08 | 13:30 | 1900-01-08 13:30
2 | [11 empty] | THIS WASH | 1900-01-13 | 2:30 | 1900-01-13 02:30
3 | [12 empty] | TOTAL HOURS
4 | 10:30 | 20 | 30 | 82.5 | 117200 | 51041.6667 | 9.8 | 18418.5347 | GHE | 10 PSI | 168241.6667
5 | [13 empty] | 109
6
7
8
9 | 13:30 | 20 | 30 | 123 | 117200 | 55729.1667 | 10.7 | 29982.2307 | DB | TIME | 172929.1667
10
11
12
13
14 | 2:30 | 20 | 30 | 109 | 117200 | 51041.6667 | 9.8 | 24334.7913 | R.H. |  | 168241.6667
15
16
17 | 23:30 | 20 | 30 | 93 | 117200 | 61458.3333 | 11.8 | 25000 | GE | 10PSI HEAD | 178658.3333
18
19
20
21
22 | 10:30 | 20 | 30 | 109 | 117200 | 55729.1667 | 10.7 | 26569.6191 | DH |  | 172929.1667
23
24
25
26 | 9:30 | 20 | 30 | 95 | 117200 | 64062.5 | 12.3 | 26619.7376 | SN | HEAD 9PSI | 181262.5
27
28
29 | 3:00 | 20 | 30 | 65.5 | 117200 | 67708.3333 | 13 | 19398.1228 | JMM |  | 184908.3333
30
31
Total |  | 140 | 210 | 677 | 820400
Average |  | 20 | 30 | 96.7143 | 117200
Maximum |  | 20 | 30 | 123 | 117200
Minimum |  | 20 | 30 | 65.5 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 7
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 7 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-23 | 15:30 | 1900-01-23 15:30
2 | [11 empty] | THIS WASH | 1900-01-26 | 21:00 | 1900-01-26 21:00
3 | 4:00 | 20 | 30 | 52 | 117200 | 47916.6667 | 9.2 | 10898.4873 | CBW |  | 165116.6667 |  | TOTAL HOURS
4
5 | [13 empty] | 77.5
6
7
8 | 9:30 | 20 | 30 | 125.5 | 117200 | 51041.6667 | 9.8 | 28018.4983 | DB | TIME | 168241.6667
9
10
11
12
13 | 8:30 | 20 | 30 | 119 | 117200 | 53645.8333 | 10.3 | 27922.8176 | JMM |  | 170845.8333
14
15
16 | 15:00 | 20 | 30 | 78.5 | 117200 | 57291.6667 | 11 | 19671.4963 | CBW |  | 174491.6667
17
18
19
20
21 | 7:00 | 20 | 30 | 112 | 117200 | 46875 | 9 | 22963.368 | DH |  | 164075
22
23
24 | 15:30 | 20 | 30 | 80.5 | 117200 | 60937.5 | 11.7 | 21456.3969 | SN | HEAD 8.5 PSI | 178137.5
25
26
27 | 21:00 | 20 | 30 | 77.5 | 117200 | 64583.3333 | 12.4 | 21892.6554 | JMM |  | 181783.3333
28
29
30 | 23:00 | 20 | 30 | 74 | 117200 | 71354.1667 | 13.7 | 23095.4985 |  |  | 188554.1667
31
Total |  | 160 | 240 | 719 | 937600
Average |  | 20 | 30 | 89.875 | 117200
Maximum |  | 20 | 30 | 125.5 | 117200
Minimum |  | 20 | 30 | 52 | 117200
|  | 8 | 8 | 8 | 8
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 8
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 8 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-20 | 9:00 | 1900-01-20 09:00
2 | 11:00 | 20 | 30 | 35 | 117200 | 48958.3333 | 9.4 | 7494.9882 | SN | HEAD | 166158.3333 | THIS WASH | 1900-01-24 | 5:00 | 1900-01-24 05:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 92
6
7
8 | 5:30 | 20 | 30 | 138.5 | 117200 | 51041.6667 | 9.8 | 30920.8128 | DB | TIME | 168241.6667
9
10
11
12 | 15:00 | 20 | 30 | 105.5 | 117200 | 56250 | 10.8 | 25956.807 | CBW |  | 173450
13
14
15
16 | 12:00 | 20 | 30 | 93 | 117200 | 57291.6667 | 11 | 23305.0847 | CBW |  | 174491.6667
17
18
19
20
21 | 9:00 | 20 | 30 | 117 | 117200 | 46875 | 9 | 23988.5183 | DH |  | 164075
22
23
24
25 | 5:00 | 20 | 30 | 92 | 117200 | 60937.5 | 11.7 | 24521.5965 | CBW |  | 178137.5
26
27
28 | 9:00 | 20 | 30 | 76 | 117200 | 64583.3333 | 12.4 | 21468.9266 | SN | HEAD 9PSI | 181783.3333
29
30
31
Total |  | 140 | 210 | 657 | 820400
Average |  | 20 | 30 | 93.8571 | 117200
Maximum |  | 20 | 30 | 138.5 | 117200
Minimum |  | 20 | 30 | 35 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 9
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 9 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-24 | 5:00 | 1900-01-24 05:00
2 | 11:00 | 20 | 30 | 35 | 125000 | 48958.3333 | 9.4 | 6503.0044 | WL | HEAD | 173958.3333 | THIS WASH | 1900-01-27 | 2:00 | 1900-01-27 02:00
3 | [12 empty] | TOTAL HOURS
4
5 | [13 empty] | 69
6
7 | 8:00 | 20 | 30 | 117 | 125000 | 51041.6667 | 9.8 | 22663.6622 | GE | 2.5 PSI | 176041.6667
8
9
10
11
12 | 0:30 | 20 | 30 | 112.5 | 125000 | 54166.6667 | 10.4 | 23126.186 | SN | HEAD 3PSI | 179166.6667
13
14
15 | 4:00 | 20 | 30 | 51.5 | 125000 | 54687.5 | 10.5 | 10688.4488 | R.H. |  | 179687.5
16
17 | 19:30 | 20 | 30 | 63.5 | 125000 | 61458.3333 | 11.8 | 14810.642 | GE | HEAD 2.5 PSI | 186458.3333
18
19
20
21 | 20:30 | 20 | 30 | 97 | 125000 | 52083.3333 | 10 | 19172.9918 | GHE | HEAD 4 PSI | 177083.3333
22
23
24
25 | 5:00 | 20 | 30 | 80 | 125000 | 60937.5 | 11.7 | 18500.9488 | JMM |  | 185937.5
26
27
28 | 2:00 | 20 | 30 | 69 | 125000 | 64583.3333 | 12.4 | 16911.7647 | CBW |  | 189583.3333
29
30 | 1400 | 35 | 30 | 60 | 218750 | 72916.6667 | 14 | 16603.4156 | SN | WL ADDED 5 BAGS OF MEDIA | 291666.6667
31
Total |  | 195 | 270 | 685.5 | 1218750
Average |  | 21.6667 | 30 | 76.1667 | 135416.6667
Maximum |  | 35 | 30 | 117 | 218750
Minimum |  | 20 | 30 | 35 | 125000
|  | 9 | 9 | 9 | 9
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 10
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 10 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-11 | 2:00 | 1900-01-11 02:00
2 | [11 empty] | THIS WASH | 1900-01-14 | 7:00 | 1900-01-14 07:00
3 | [12 empty] | TOTAL HOURS
4 | 2:00 | 20 | 30 | 98 | 125000 | 51041.6667 | 9.8 | 18983.2385 | DH |  | 176041.6667
5 | [13 empty] | 77
6
7
8 | 21:00 | 20 | 30 | 92 | 125000 | 56250 | 10.8 | 19639.4687 | DH |  | 181250
9
10
11
12 | 2:00 | 20 | 30 | 88 | 125000 | 53645.8333 | 10.3 | 17915.876 | R.H. | Head | 178645.8333
13
14
15 | 7:00 | 20 | 20 | 77 | 125000 | 36458.3333 | 10.5 | 15980.7875 | CBW |  | 161458.3333
16
17
18 | 6:00 | 20 | 30 | 71 | 125000 | 61458.3333 | 11.8 | 16559.9304 | DH |  | 186458.3333
19
20
21
22 | 8:00 | 20 | 30 | 98 | 125000 | 55729.1667 | 10.7 | 20726.5971 | MN |  | 180729.1667
23 | 13:00 | 25 | 30 | 29 | 156250 | 60937.5 | 11.7 | 6706.5939 | DH/WL | ADDED ANTHRICITE | 217187.5
24
25
26 | 14:00 | 20 | 30 | 71 | 125000 | 65625 | 12.6 | 17682.6376 | RH | HEAD | 190625
27
28
29 | 13:30 | 20 | 30 | 71.5 | 125000 | 68750 | 13.2 | 18655.1233 | R.H. | HEAD | 193750
30
31
Total |  | 185 | 260 | 695.5 | 1156250
Average |  | 20.5556 | 28.8889 | 77.2778 | 128472.2222
Maximum |  | 25 | 30 | 98 | 156250
Minimum |  | 20 | 20 | 29 | 125000
|  | 9 | 9 | 9 | 9
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 11
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 11 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 1:00 | 20 | 30 | 1 | 125000 | 54687.5 | 10.5 | 207.5427 | CBW |  | 179687.5 | LAST WASH | 1900-01-23 | 22:30 | 1900-01-23 22:30
2 | [11 empty] | THIS WASH | 1900-01-26 | 6:30 | 1900-01-26 06:30
3 | [12 empty] | TOTAL HOURS
4 | 23:00 | 20 | 30 | 94 | 125000 | 51041.6667 | 9.8 | 18208.4124 | DH |  | 176041.6667
5 | [13 empty] | 56
6
7
8 | 23:00 | 20 | 30 | 96 | 125000 | 56250 | 10.8 | 20493.3586 | DH |  | 181250
9
10
11
12 | 14:00 | 20 | 30 | 87 | 125000 | 56250 | 10.8 | 18572.1063 | CBW |  | 181250
13
14
15 | 9:30 | 20 | 20 | 67.5 | 125000 | 38194.4444 | 11 | 14676.2334 | CBW |  | 163194.4444
16
17
18 | 8:30 | 20 | 30 | 71 | 125000 | 61458.3333 | 11.8 | 16559.9304 | DH |  | 186458.3333
19
20
21
22 | 3:30 | 20 | 30 | 91 | 125000 | 52083.3333 | 10 | 17987.0335 | GE | HEAD | 177083.3333
23
24 | 22:30 | 20 | 30 | 67 | 125000 | 60937.5 | 11.7 | 15494.5446 | JMM |  | 185937.5
25
26
27 | 6:30 | 20 | 30 | 56 | 125000 | 61458.3333 | 11.8 | 13061.3536 | R.H. | H.L. | 186458.3333
28
29 | 22:30 | 20 | 30 | 63 | 125000 | 67708.3333 | 13 | 16188.3302 | JMM |  | 192708.3333
30
31
Total |  | 200 | 290 | 693.5 | 1250000
Average |  | 20 | 29 | 69.35 | 125000
Maximum |  | 20 | 30 | 96 | 125000
Minimum |  | 20 | 20 | 1 | 125000
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 12
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 12 |  |  |  |  | 2019-04-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | 8:30 | 20 | 30 | 8.5 | 125000 | 56250 | 10.8 | 1814.5161 | DH | HEAD | 181250 | LAST WASH | 1900-01-25 | 20:00 | 1900-01-25 20:00
2 | [11 empty] | THIS WASH | 1900-01-28 | 3:00 | 1900-01-28 03:00
3 | [12 empty] | TOTAL HOURS
4
5 | 7:00 | 20 | 30 | 94.5 | 125000 | 51041.6667 | 9.8 | 18305.2657 | GHE | HEAD 4PSI | 176041.6667 |  |  | 55
6
7
8
9 | 15:30 | 20 | 30 | 104.5 | 125000 | 53125 | 10.2 | 21068.5484 | GE | HEAD 4 PSI | 178125
10
11
12
13 | 8:00 | 20 | 30 | 88.5 | 125000 | 53645.8333 | 10.3 | 18017.6708 | CBW |  | 178645.8333
14
15 | 7:45 | 20 | 20 | 47.75 | 125000 | 36458.3333 | 10.5 | 9910.1637 | CBW |  | 161458.3333
16
17 | 15:00 | 20 | 30 | 55 | 125000 | 58854.1667 | 11.3 | 12284.5509 | DH |  | 183854.1667
18
19
20
21 | 11:00 | 20 | 30 | 92 | 125000 | 52083.3333 | 10 | 18184.6932 | DH |  | 177083.3333
22
23
24 | 7:30 | 20 | 30 | 68.5 | 125000 | 61458.3333 | 11.8 | 15976.8343 | R.H. |  | 186458.3333
25
26 | 20:00 | 20 | 30 | 60.5 | 125000 | 64583.3333 | 12.4 | 14828.4314 | JMM |  | 189583.3333
27
28
29 | 3:00 | 20 | 30 | 55 | 125000 | 64583.3333 | 12.4 | 13480.3922 | CBW |  | 189583.3333
30
31
Total |  | 200 | 290 | 674.75 | 1250000
Average |  | 20 | 29 | 67.475 | 125000
Maximum |  | 20 | 30 | 104.5 | 125000
Minimum |  | 20 | 20 | 8.5 | 125000
|  | 10 | 10 | 10 | 10
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## FILTER PERFORMANCE (hidden)
Filter Performance Test
[18 empty] | Filter 1 |  | Filter 2 |  | Filter 3 |  | Filter 4 |  | Filter 5 |  | Filter 6 |  | Filter 7 |  | Filter 8 |  | Filter 9 |  | Filter 10 |  | Filter 11 |  | Filter 12
Date | OPER | Time | Filter # washed | Flow to Filter Cluster, MGD | Raw Uv 254 | Calculated Alum Dose, mg/L | Alum Dose, mg/L | Filter Washed headloss, ft | Filter washed Time in service, hrs | Filter # Affected with turbidity spike | Filter affected by turbidity spike Headloss, ft | Filter affected by turbidity spike time in service, hrs | Reason for filter washed (time or Headloss) | Settled water turbidity avg. for plant that filter was washed on. 24 hr avg., ntu | Filter affected max turbidity, ntu | Filtration rate, gpm'sq.ft | Solids Loading onto Filters, lbs/day/filter | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs |  | DATE | TIME
[42 empty] | LAST WASH | 2015-05-29 | 1:00
2015-05-28 | CBW | 1800 | 9 | 11.4 | 0.294 | 38.6842 | 40 | 4.25 | 92 | 10 | 3.91 | 82 | TIME | 0.5 | 0.19 | 5.492 | 35.6535 | [18 empty] | 1.59 | 82 | 2.3 | 5 | 5.29 | 73.5 | THIS WASH | 2015-05-31 | 0:00
2015-05-28 | JM | 2100 | 7 | 10.6 | 0.357 | 46.9737 | 40 | 3.91 | 65 | NONE |  |  | HEAD | 0.47 |  | 5.1066 | 31.1624 | [8 empty] | 5.87 | 106 | 3.61 | 11 |  |  | 3.33 | 25 | [9 empty] | TOTAL HOURS
2015-05-29 | CBW | 100 | 10 | 11.3 | 0.292 | 38.4211 | 40 | 1.9 | 89 | 12 | 6.35 | 101.5 | TURB | 0.5 | 0.11 | 5.4438 | 35.3407 | [16 empty] | 2.45 | 7 |  |  | 2.8 | 12 | 6.35 | 102.5 |  | 2015-05-29 | 48
2015-05-29 | GE | 600 | 3 | 10.4 | 0.276 | 36.3158 | 40 | 4.11 | 87 | NONE |  |  | HEAD | 0.45 |  | 5.0102 | 29.2734 | 5.21 | 86 | 4.23 | 22 |  |  | 4.22 | 89 | [17 empty] | 2015-05-31
2015-05-29 | MN | 700 | 5 | 10.5 | 0.276 | 36.3158 | 40 | 4.74 | 116 | NONE |  |  | TIME/HEAD | 0.29 |  | 5.0584 | 19.0465 | [10 empty] | 3.47 | 21 | 2.29 | 10 | 2.66 | 35
[16 empty] | 0 | 0
2015-05-29 | CBW | 2300 | 12 | 11.2 | 0.312 | 41.0526 | 44 | 5.28 | 123.5 | NONE |  |  | NTU/TIME | 0.591 |  | 5.3956 | 41.4031 | [16 empty] | 1.91 | 29 | 2.4 | 22 | 2.76 | 34 | 5.28 | 132.5
2015-05-30 | GE | 600 | 4 | 10.4 | 0.229 | 30.1316 | 40 | 3.66 | 120 | NONE |  |  | TIME/HEAD | 0.46 |  | 5.0102 | 29.9239 | 4.1 | 110.5 | 3.69 | 75 | 1.98 | 24
2015-05-30 | GE | 1030 | 1 | 10.4 | 0.235 | 30.9211 | 40 | 3.54 | 115 | NONE |  |  | TIME/HEAD | 0.52 |  | 5.0102 | 33.827 |  |  | 3.13 | 79.5 | 1.86 | 29 | 1.01 | 4.5
2015-05-31 | MN | 1000 | 2 | 11.2 | 0.226 | 29.7368 | 40 | 3.25 | 103 | NONE |  |  | TIME/HEAD | 0.41 |  | 5.3956 | 28.723 | 0.083 | 23.5 |  |  | 1.25 | 52.5 | 0.47 | 28
NEW MONTH | [15 empty] | 0 | 0
2015-06-02 | CBW | 4:30 | 8 | 34.1 | 0.241 | 31.7105 | 35 | 4.57 | 127.5/28.5 | NONE |  |  | HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 4.93 | 66/28.5 | 5.78 | 28.5 | 4.24 | 105/28.5
2015-06-02 | MN | 600 | 6 | 34.1 | 0.176 | 23.1579 | 35 | 3.71 | 115 / 30 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.33 | 94 / 30 |  |  | 2.43 | 104 / 30 | 1.03 | 129/30
2015-06-02 | GE | 1000 | 7 | 34.1 | 0.195 | 25.6579 | 32 | 2.42 | 104/34 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.86 | 99/34 | 0.09 | 4 |  |  | 0.45 | 5.5
2015-06-02 | GE | 1330 | 11 | 34.1 | 0.217 | 28.5526 | 32 | 5.37 | 120.5/37.5 | NONE |  |  | TIME/HEAD | 0.272 |  | 4.4803 | 58.0164 | [16 empty] | 5.45 | 115.5 | 1.9 | 67.5 |  |  | 3.83 | 86.5
2015-06-02 | CBW | 1930 | 3 | 34.1 | 0.181 | 23.8158 | 35 | 2.57 | 65.5/43.5 | NONE |  |  | TIME/HEAD | 0.281 |  | 4.4803 | 59.936 | 1.07 | 43.5 | 1.23 | 43.5 | 1.55 | 43.5 | 0.77 | 43.5
2015-06-03 | HE | 700 | 10 | 26.1 | 0.247 | 32.5 | 35 | 1.4 | 55 | NONE |  |  | TIME/HEAD | 0.25 |  | 3.4292 | 40.8139 | [16 empty] | 4.9 | 55 | 1.4 | 55 | 1.49 | 17 | 3.82 | 55
2015-06-10 | CBW | 1130 | 2 | 33.2 | 0.251 | 33.0263 | 35 | 0.19 | 116.5 | NONE |  |  | TIME/HEAD | 0.3 |  | 4.362 | 62.2998 | 0.01 | 29.5 | 0.91 | 116.5 | 0.48 | 26 | 0.27 | 92.5
2015-06-10 | CBW | 1330 | 5 | 33.2 | 0.251 | 33.0263 | 35 | 1.77 | 117.5 | NONE |  |  | TIME/HEAD | 0.21 |  | 4.362 | 43.6099 | [8 empty] | 1.77 | 117.5 | 0.49 | 69 | 0.06 | 45 | 0.05 | 48
2015-06-10 | GHE | 1900 | 12 | 33.2 | 0.239 | 31.4474 | 35 | 4.72 | 156 | NONE |  |  | TIME/HEAD | 0.2 |  | 4.362 | 41.5332 | [16 empty] | 0.05 | 32.5 | 0.06 | 35 | 0.05 | 36
2015-06-11 | GHE | 2:00 | 4 | 33.1 | 0.239 | 31.4474 | 35 | 3.81 | 107 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.3489 | 64.1826 | 3.54 | 44 | 3.48 | 14.5 | 3.51 | 40.5
2015-06-11 | CBW | 6:00 | 7 | 33.1 | 0.283 | 37.2368 | 35 | 3.75 | 67 | NONE |  |  | HEAD/CLEAR | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 3.99 | 16.5 | 5.53 | 85.5 | 3.75 | 61.5 | 0.05 | 64.5
2015-06-11 | CBW | 8:00 | 6 | 33.1 | 0.283 | 37.2368 | 35 | 3.41 | 87.5 | NONE |  |  | TIME/HEAD | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 2.92 | 18.5 |  |  | 1.56 | 62.5 | 2.1 | 66.5
2015-06-12 | CBW | 9:00 | 11 | 35.7 | 0.291 | 38.2895 | 35 | 3.91 | 98 | NONE |  |  | TIME/HEAD | 0.228 |  | 4.6905 | 50.9132
2015-06-12 | CBW | 14:00 | 8 | 35.7 | 0.232 | 30.5263 | 35 | 1.53 | 96.5 | NONE |  |  | TIME/HEAD | 0.278 |  | 4.6905 | 62.0784 | [8 empty] | 2.67 | 48.5 | 2.35 | 30 | 2.66 | 32 | 1.53 | 96.5 | 2.98 | 70.5 | 2.21 | 75 | 3.91 | 98 | 2.28 | 38
2015-06-13 | CBW | 600 | 1 | 38.6 | 0.224 | 29.4737 | 35 | 3.91 | 96 | NONE |  |  | TIME/HEAD | 0.3 |  | 5.0715 | 72.4329 |  |  | 3.82 | 75.5 | 3.62 | 69.5 | 2.49 | 52
2015-06-13 | CBW | 800 | 10 | 38.6 | 0.224 | 29.4737 | 35 | 3.02 | 98 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [16 empty] | 4.78 | 94.5 |  |  | 2.36 | 23 | 3.36 | 61
2015-06-13 | CBW | 900 | 3 | 38.6 | 0.224 | 29.4737 | 35 | 3.54 | 95.5 | NONE |  |  | TIME/HEAD | 0.35 |  | 5.0715 | 84.505 | 1.91 | 3 | 3.66 | 78.5 |  |  | 2.4 | 55
2015-06-13 | CBW | 1100 | 9 | 38.6 | 0.224 | 29.4737 | 35 | 4.78 | 96.5 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [18 empty] | 2.49 | 3 | 2.36 | 26 | 3.36 | 64
2015-06-14 | CBW | 600 | 7 | 42 | 0.26 | 34.2105 | 35 | 3.27 | 72 | NONE |  |  | HEAD/CLEAR WELL | 0.208 |  | 5.5182 | 54.6437 | [8 empty] | 5.21 | 88.5 | 4.31 | 70 |  |  | 2.97 | 40
2015-06-14 | CBW | 800 | 2 | 42 | 0.26 | 34.2105 | 35 | 3.59 | 92.5 | NONE |  |  | TIME | 0.257 |  | 5.5182 | 67.5165 | 3.37 | 26 |  |  | 2.96 | 23 | 3.74 | 78
2015-06-14 | CBW | 900 | 5 | 42 | 0.26 | 34.2105 | 35 | 5.09 | 91.5 | NONE |  |  | TIME | 0.208 |  | 5.5182 | 54.6437 | [10 empty] | 3.86 | 73 | 2.16 | 3 | 2.4 | 43
2015-06-14 | CBW | 1430 | 4 | 42 | 0.24 | 31.5789 | 35 | 4.68 | 84.5 | NONE |  |  | HEAD/CLEAR WELL | 0.257 |  | 5.5182 | 67.5165 | 4.04 | 32.5 | 3.96 | 6.5 | 3.54 | 29.5 | [10 empty] | 2.47 |  | 2.49 |  | 3.36 |  | 4.67
2015-06-14 | GE | 1800 | 8 | 42 | 0.218 | 28.6842 | 35 | 3.61 | 22 | NONE |  |  | HEAD | 0.31 |  | 5.5182 | 81.4401 | [8 empty] | 4.08 | 9 | 5.65 | 82 | 3.52 | 12
2015-06-15 | GE | 500 | 6 | 41.4 | 0.22 | 28.9474 | 35 | 3.88 | 23 | NONE |  |  | HEAD | 0.32 |  | 5.4394 | 82.8662 | [8 empty] | 4.52 | 20 |  |  | 3.88 | 23 | 3.15 | 11
2015-06-15 | CBW | 10:00 | 12 | 41.4 | 0.254 | 33.4211 | 35 | 5.15 | 111 | NONE |  |  | TIME | 0.202 |  | 5.4394 | 52.3093
2015-06-16 | CBW | 13:30 | 11 | 40.4 | 0.229 | 30.1316 | 35 | 5.36 | 100.5 | NONE |  |  | TIME | 0.216 |  | 5.308 | 54.5836
2015-06-17 | DMH | 1500 | 10 | 40.2 | 0.251 | 33.0263 | 40 | 1.49 | 103 | None |  |  | TIME | 0.225 |  | 5.2817 | 56.5765 | [16 empty] | 5.1 | 100 |  |  | 2.8 | 25.5 | 3.6 | 53
2015-06-18 | WL | 6:00 | 1 | 36.8 | 0.262 | 34.4737 | 40 | 2.2 | 120 | None |  |  | Time | 0.316 |  | 4.835 | 72.7381 |  |  | 1.54 | 93.4 | 2.23 | 84 | 0.79 | 81.5
2015-06-18 | WL | 9:00 | 3 | 36.8 | 0.262 | 34.4737 | 40 | 1.55 | 120 | NONE |  |  | Time | 0.316 |  | 4.835 | 72.7381 | 0.23 | 0.75 | 1.55 | 95.4 |  |  | 1.31 | 83.5
2015-06-18 | DMH | 1300 | 4 | 36.8 | 0.262 | 34.4737 | 40 | 1.31 | 94.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 5.79 | 1.56 | 100.45 | 0 | 3.78
2015-06-18 | DMH | 1530 | 2 | 36.8 | 0.262 | 34.4737 | 40 | 1.57 | 103.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 8.17 |  |  | 0 | 6.16 | 0.31 | 0.64
2015-06-19 | WL | 9:00 | 7 | 33.7 | 0.274 | 36.0526 | 40 | 3.5 | 123 | NONE |  |  | Time/HEAD | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 3.7 | 118.54 | 2.4 | 98.21 |  |  | 2.7 | 109.62
2015-06-19 | DMH | 11:00 | 5 | 33.7 | 0.274 | 36.0526 | 40 | 3.88 | 122 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [10 empty] | 2.33 | 100.25 | 0.33 | 0.072 | 2.73 | 111.65
2015-06-19 | DMH | 13:00 | 6 | 33.7 | 0.274 | 36.0526 | 40 | 2.32 | 104 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 0.36 | 1.03 |  |  | 0.33 | 3.01 | 2.72 | 113.94
2015-06-20 | WL | 8:30 | 8 | 31.4 | 0.289 | 38.0263 | 45 | 2.72 | 134.5 | NONE |  |  | TIME | 0.243 |  | 4.1255 | 47.7269 | [8 empty] | 0.36 | 20.71 | 0.02 | 18.65 | 0.33 | 22.68
2015-06-20 | WL | 12:00 | 12 | 31.4 | 0.31 | 40.7895 | 45 | 5.32 | 122 | NONE | 9,11 |  | TIME | 0.374 | 0.06 | 4.1255 | 73.4562 | [16 empty] | 2.23 |  | 2.25 |  | 4.41
2015-06-22 | DMH | 13:30 | 11 | 33.5 | 0.327 | 43.0263 | 50 | 6.42 | 144 | 9,10 | 9 |  | TIME/HEAD | 0.466 | .09,.5 | 4.4015 | 97.6468 | [16 empty] | 4.28 | 114.5 | 1.75 | 118.5 |  |  | 2.4 | 49.5
2015-06-23 | WL | 6:00 | 10 | 42.1 | 0.305 | 40.1316 | 50 | 1.25 | 135 | 9 |  |  | TIME | 0.419 | 0.13 | 5.5314 | 110.3376 | [16 empty] | 5.28 |  |  |  | 2.21 |  | 3.47
2015-06-23 | WL | 9:00 | 9 | 42.1 | 0.305 | 40.1316 | 50 | 5.28 | 134 | None | 11,12 |  | TIME | 0.419 |  | 5.5314 | 110.3376 | [18 empty] | 2.26 |  | 2.72 |  | 3.98
2015-06-24 | MN | 1200 | 3 | 42.1 | 0.294 | 38.6842 | 40 | 3.54 | 147 | NONE |  |  | TIME/HEAD | 0.335 |  | 5.5314 | 88.2174 | 2.75 | 150 | 2.2 | 139 |  |  | 2.34 | 142
2015-06-24 | MN | 1600 | 7 | 37.1 | 0.297 | 39.0789 | 40 | 3.87 | 127 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.8744 | 71.9388 | [8 empty] | 3.89 | 125 | 3.05 | 119 |  |  | 2.9 | 104.5
2015-06-25 | GHE | 2:00 | 4 | 37.1 | 0.372 | 48.9474 | 50 | 3.83 | 157 | None |  |  | Time | 0.4 |  | 4.8744 | 92.8242 | 4.76 | 164 | 4.26 | 154.5 | 0.46 | 161
2015-06-25 | MN | 830 | 8 | 37.1 | 0.306 | 40.2632 | 40 | 3.96 | 120 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 | [8 empty] | 5.83 | 141.5 | 4.63 | 138.5 | 0.44 | 18.5
2015-06-25 | MN | 1000 | 1 | 37.1 | 0.306 | 40.2632 | 40 | 4.78 | 172 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 |  |  | 4.21 | 162.5 | 0.46 | 22 | 0.26 | 3 |  |  | 4.61 | 142.5 | 0.97 | 23 | 0.47 | 4.5
2015-06-25 | MN | 1300 | 5 | 37.1 | 0.306 | 40.2632 | 40 | 5.73 | 148 |  |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906
2015-06-25 | CBW | 1900 | 12 | 37.1 | 0.304 | 40 | 40 | 6.62 | 127 | NONE |  |  | TIME | 0.46 |  | 4.8744 | 106.7478 | [16 empty] | 4.39 | 58 | 1.26 | 61 | 5.75 | 77.5
2015-06-25 | CBW | 2300 | 11 | 37.1 | 0.304 | 40 | 40 | 5.75 | 81.5 | NONE |  |  | TIME | 0.68 |  | 4.8744 | 157.8011 | [16 empty] | 4.39 | 62 | 1.25 | 65 |  |  | 0.76 | 6
2015-06-26 | CBW | 1300 | 2 | 37.1 | 0.304 | 40 | 40 | 4.17 | 178.5 | NONE |  |  | TIME | 0.58 |  | 4.8744 | 134.5951 | 0.27 | 15 |  |  | 0.97 | 37 | 0.05 | 18 | 0.44 | 18 |  |  | 0.97 | 41 | 0.47 | 24.5
2015-06-26 | MN | 900 | 6 | 37.1 | 0.304 | 40 | 40 | 4.55 | 164 | NONE |  |  | TIME/HEAD | 0.52 |  | 4.8744 | 120.6715
2015-06-27 | CBW | 4:30 | 10 | 37.1 | 0.311 | 40.9211 | 40 | 2.81 | 94.5 | 9 | 6.4 | 91.5 | Turb. | 0.48 |  | 4.8744 | 111.389 | [16 empty] | 6.4 | 91.5 |  |  | 2.32 | 29.5 | 2.97 | 33.5
2015-06-27 | CBW | 19:00 | 9 | 37.1 | 0.338 | 44.4737 | 40 | 5.89 | 106 | NONE |  |  | TIME | 0.54 |  | 4.8744 | 125.3127 | [18 empty] | 2.89 | 14.5 | 3.4 | 44 | 3.37 | 48
2015-06-28 | GHE | 19:00 | 7 | 38.3 | 0.226 | 29.7368 | 35 | 2.94 | 101 | NONE |  |  | TIME/AUTO | 0.38 |  | 5.0321 | 91.0353 | [8 empty] | 2.46 | 78 | 1.4 | 58 |  |  | 1.81 | 82.5
2015-06-29 | CBW | 600 | 3 | 38.3 | 0.226 | 29.7368 | 35 | 4 | 114 | NONE |  |  | HEAD | 0.62 |  | 5.0321 | 148.5312 | 2.29 | 102 | 1.01 | 76 |  |  | 2.03 | 100
2015-06-29 | MN | 1030 | 8 | 42 | 0.226 | 29.7368 | 35 | 3.01 | 98 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [8 empty] | 3.47 | 93 | 2.42 | 73.5 | 0.18 | 15.5
2015-06-29 | MN | 1400 | 4 | 42 | 0.232 | 30.5263 | 35 | 2.03 | 103 | NONE |  |  | TIME | 0.31 |  | 5.5182 | 81.4401 | 3.31 | 100 | 2.06 | 61 | 0.11 | 8
2015-06-29 | CBW | 2000 | 12 | 42 | 0.251 | 33.0263 | 35 | 5.39 | 97 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [16 empty] | 3.31 | 49 | 2.31 | 63.5 | 5.42 | 93
2015-06-29 | CBW | 2200 | 1 | 42 | 0.251 | 33.0263 | 35 | 4.37 | 118 | NONE |  |  | TIME | 0.51 |  | 5.5182 | 133.9821 |  |  | 3.06 | 92 | 0.11 | 16 | 0.11 | 8
2015-06-30 | MN | 700 | 5 | 42 | 0.244 | 32.1053 | 35 | 4.47 | 114 | NONE |  |  | TIME | 0.45 |  | 5.5182 | 118.2195 | [10 empty] | 3.95 | 94 | 1.98 | 36 | 0.85 | 21.5
2015-07-01 | CBW | 1:30 | 6 | 40 | 0.252 | 33.1579 | 35 | 4.97 | 111 | NONE |  |  | TIME | 0.4 |  | 5.2555 | 100.08 | [8 empty] | 0.11 | 18.5 |  |  | 2.74 | 54.5 | 1.87 | 27
2015-07-02 | wl | 1:30 | 8 | 13.3 | 0.226 | 29.7368 | 45 | 3.3 | 63 | none |  |  | head | 0.327 |  | 1.7474 | 27.2036 | [8 empty] | 1.8 | 41.5 | 0.6 | 22.5 | 0 | 15.5
2015-07-02 | wl | 4:00 | 3 | 13.6 | 0.239 | 31.4474 | 45 | 2.8 | 70 | none |  |  | head | 0.306 |  | 1.7869 | 26.0308 | 1.7 | 54 | 0.7 | 38 |  |  | 2 | 61
2015-07-07 | wl | 18:00 | 1 | 11.6 | 0.217 | 28.5526 | 45 | 1.2 | 103 | none |  |  | time | 0.262 |  | 1.5241 | 19.0102 |  |  | 0.2 | 54 | 0 | 30.5 | 1.7 | 128
2015-07-07 | DMH | 20:00 | 4 | 11.6 | 0.217 | 28.5526 | 45 | 1.51 | 131 |  |  |  | time | 0.275 |  | 1.5241 | 19.9535 | 0.35 | 0.79 | 0.25 | 56.12 | 0.03 | 0.06
2015-07-09 | JM | 900 | 12 | 13.7 | 0.253 | 33.2895 | 40 | 6.27 | 147 | NONE |  |  | TIME | 0.372 |  | 1.8 | 31.878 | [16 empty] | 4.09 | 93 | 2.18 | 74 | 5.95 | 123
2015-07-09 | MN | 1100 | 5 | 13.2 | 0.253 | 33.2895 | 40 | 2.86 | 98 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | [10 empty] | 2.27 | 93.5 | 1.61 | 69.5 | 0.54 | 49
2015-07-09 | MN | 1530 | 2 | 13.2 | 0.253 | 33.2895 | 40 | 1.78 | 96 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | 0.3 | 44.5 |  |  | 1.05 | 67 | 0 | 43.5
2015-07-10 | JM | 800 | 11 | 13.8 | 0.252 | 33.1579 | 40 | 6.96 | 146 | NONE |  |  | TIME/TURB | 0.39 |  | 1.8131 | 33.6644 | [16 empty] | 5.09 | 116 | 1.68 | 97 |  |  | 2.17 | 23
2015-07-10 | MN | 1030 | 3 | 13.2 | 0.252 | 33.1579 | 40 | 2.05 | 96 | NONE |  |  | TIME | 0.42 |  | 1.7343 | 34.6777 | 0.86 | 66 | 0.07 | 19 |  |  | 1.01 | 62
2015-07-10 | MN | 1330 | 6 | 13.2 | 0.252 | 33.1579 | 40 | 3.29 | 120 | NONE |  |  | TIME | 0.38 |  | 1.7343 | 31.3751 | [8 empty] | 0.7 | 26.5 |  |  | 3.12 | 102 | 2.07 | 76
2015-07-10 | CBW | 2230 | 9 | 14.4 | 0.272 | 35.7895 | 40 | 6.1 | 130.5 | NONE |  |  | TIME/TURB | 0.52 |  | 1.892 | 46.8374 | [18 empty] | 1.68 | 111.5 | 2.18 | 14.5 | 3.26 | 37.5
2015-07-11 | CBW | 3:30 | 10 | 14.7 | 0.272 | 35.7895 | 40 | 3.01 | 116 | NONE |  |  | TIME/TURB | 0.56 |  | 1.9314 | 51.4912 | [16 empty] | 1.67 | 5 |  |  | 2.68 | 19.5 | 3.26 | 42.5
2015-07-11 | MN | 630 | 7 | 14.5 | 0.281 | 36.9737 | 40 | 4.61 | 118 | NONE |  |  | TIME/HEAD | 0.42 |  | 1.9051 | 38.093 | [8 empty] | 2.21 | 19.5 | 0.15 | 17 |  |  | 3.59 | 92.5
2015-07-11 | MN | 1100 | 4 | 14.4 | 0.281 | 36.9737 | 45 | 2.53 | 86 | NONE |  |  | TIME | 0.28 |  | 1.892 | 25.2202 | 2.4 | 89 | 1.07 | 44 | 0.5 | 24.5
2015-07-11 | MN | 1400 | 8 | 14.5 | 0.281 | 36.9737 | 45 | 4.12 | 100 | NONE |  |  | HEAD | 0.35 |  | 1.9051 | 31.7441 | [8 empty] | 2.71 | 27 | 0.7 | 24.5 | 0.06 | 7.5
2015-07-12 | MN | 900 | 1 | 13.4 | 0.305 | 40.1316 | 45 | 3.4 | 111 | NONE |  |  | TIME | 0.34 |  | 1.7606 | 28.4978 |  |  | 2.08 | 66.5 | 1.5 | 22.5 | 0.46 | 22
2015-07-13 | CBW | 4:00 | 12 | 12.7 | 0.319 | 41.9737 | 45 | 5.75 | 91 | NONE |  |  | TIME | 0.355 |  | 1.6686 | 28.2007 | [16 empty] | 3.68 | 53.5 | 2 | 48.5 | 5.19 | 67.5
2015-07-14 | MN | 600 | 5 | 12 | 0.345 | 45.3947 | 50 | 5.82 | 115 | NONE |  |  | TIME/HEAD | 0.25 |  | 1.5766 | 18.765 | [10 empty] | 3.25 | 91.5 | 2.6 | 71.5 | 2.51 | 62
2015-07-14 | MN | 830 | 2 | 12 | 0.345 | 45.3947 | 50 | 3.55 | 113 | NONE |  |  | TIME | 0.29 |  | 1.5766 | 21.7674 | 0.41 | 23.5 |  |  | 3.3 | 97 | 1 | 69.5
2015-07-15 | DMH | 830 | 3 | 12.1 | 0.388 | 51.0526 | 50 | 4 | 118 | NONE |  |  | TIME/HEAD | 0.23 |  | 1.5898 | 17.4077 | 0.91 | 70.02 | 0.26 | 0.079 |  |  | 1.5 | 91.16
2015-07-15 | DMH | 1130 | 11 | 13.7 | 0.388 | 51.0526 | 50 | 7.25 | 123.5 | 9,10 | 6.03,1.29 | 109104 | TIME/HEAD | 0.369 | 0.215 | 1.8 | 31.6209 | [16 empty] | 6.03 | 109 | 1.29 | 104 |  |  | 3.02 | 55.5
2015-07-15 | DMH | 1300 | 7 | 13.4 | 0.388 | 51.0526 | 50 | 4.14 | 102.5 | NONE |  |  | HEAD | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.26 | 29.63 | 4.25 | 118.24 |  |  | 3.52 | 93.34
2015-07-15 | DMH | 1430 | 6 | 13.4 | 0.388 | 51.0526 | 50 | 4.26 | 121 | NONE |  |  | TIME | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.77 | 30.97 |  |  | 0.49 | 0.27 | 3.52 | 94.69
2015-07-15 | DMH | 1630 | 9 | 13.7 | 0.346 | 45.5263 | 50 | 6.03 | 114 | NONE |  |  | TIME | 0.417 |  | 1.8 | 35.7342 | [18 empty] | 1.29 | 109 | 1.98 | 5 | 3.04 | 60.5
2015-07-16 | DMH | 1000 | 4 | 13 | 0.381 | 50.1316 | 55 | 3.02 | 119 | NONE |  |  | TIME/HEAD | 0.239 |  | 1.708 | 19.4343 | 2.47 | 95.77 | 0.76 | 48.68 | 0.49 | 24.61
2015-07-16 | DMH | 1130 | 1 | 10.8 | 0.381 | 50.1316 | 55 | 1.96 | 107.5 | NONE |  |  | TIME | 0.419 |  | 1.419 | 28.3051 |  |  | 0.76 | 50.32 | 0.49 | 26.25 | 0.47 | 0.86
2015-07-18 | DMH | 1300 | 12 | 10.3 | 0.391 | 51.4474 | 60 | 4.98 | 129 | NONE |  |  | TIME | 0.359 |  | 1.3533 | 23.1291 | [16 empty] | 3.24 | 69 | 1.99 | 65.5 | 4.01 | 74
2015-07-19 | R.H. | 400 | 8 | 10.8 | 0.365 | 48.0263 | 60 | 2.31 | 82 | NONE |  |  | TIME/HEAD | 0.22 |  | 1.419 | 14.8619 | [14 empty] | 2.33 | 82
2015-07-19 | DMH | 900 | 2 | 11.1 | 0.378 | 49.7368 | 60 | 1.77 | 120.5 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 67.03 |  |  | 2.02 | 95.23 | 0.47 | 69.84
2015-07-19 | DMH | 1030 | 7 | 11.2 | 0.378 | 49.7368 | 60 | 3.06 | 93.5 | NONE |  |  | TIME/HEAD | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 12.43 | 2.41 | 91.16 |  |  | 1.62 | 92.45
2015-07-19 | DMH | 1430 | 3 | 11.1 | 0.378 | 49.7368 | 60 | 2.02 | 102 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 72.28 | 0 | 4 |  |  | 0.47 | 75.1
2015-07-19 | DMH | 1600 | 6 | 11.2 | 0.331 | 43.5526 | 60 | 2.39 | 97.5 | NONE |  |  | TIME | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 18.01 |  |  | 0.48 | 4.33 | 0.01 | 10.56
2015-07-20 | DMH | 1300 | 10 | 13 | 0.341 | 44.8684 | 55 | 3.24 | 113 | NONE |  |  | TIME | 0.398 |  | 1.708 | 32.3634 | [16 empty] | 2.12 | 43 |  |  | 6.05 | 98 | 2.76 | 48
2015-07-21 | DMH | 1130 | 4 | 11 | 0.358 | 47.1053 | 55 | 1.47 | 121.5 | NONE |  |  | TIME | 0.204 |  | 1.4453 | 14.0362 | 1.02 | 117.42 | 0 | 49.14 | 0.33 | 43.89
2015-07-21 | DMH | 1400 | 1 | 10.7 | 0.358 | 47.1053 | 55 | 1.02 | 122.5 |  |  |  | TIME | 0.204 |  | 1.4058 | 13.6534 |  |  | 0 | 51.75 | 0.33 | 46.5 | 0.46 | 1.31
2015-07-23 | GE | 900 | 2 | 10.9 | 0.267 | 35.1316 | 45 | 0.53 | 96 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | 0.11 | 19 |  |  | 0.85 | 92.5 | 0.46 | 21.5
2015-07-23 | MN | 1200 | 5 | 10.9 | 0.267 | 35.1316 | 40 | 3.07 | 111 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | [10 empty] | 1.52 | 92 | 1.48 | 97.5 | 2.03 | 102
2015-07-24 | GE | 900 | 12 | 10.1 | 0.214 | 28.1579 | 40 | 4.78 | 140 | NONE |  |  | TIME | 0.35 |  | 1.327 | 22.1114 | [16 empty] | 4.16 | 110.5 | 2.21 | 86 | 3.37 | 92
2015-07-24 | MN | 1230 | 4 | 9.6 | 0.214 | 28.1579 | 35 | 0.46 | 73 | NONE |  |  | TIME | 0.3 |  | 1.2613 | 18.0144 | 0.12 | 68.5 | 0.24 | 51.5 | 0.84 | 118
2015-07-25 | GHE | 730 | 7 | 9.1 | 0.188 | 24.7368 | 35 | 2.01 | 141 | NONE |  |  | TIME | 0.24 |  | 1.1956 | 13.6609 | [8 empty] | 0.44 | 19.5 | 2.03 | 111.5 |  |  | 2.52 | 123.5
2015-07-25 | GE | 930 | 9 | 9.4 | 0.181 | 23.8158 | 35 | 4.64 | 160 | NONE |  |  | TIME | 0.31 |  | 1.235 | 18.2271 | [18 empty] | 2.21 | 116.5 | 3.36 | 110.5 | 1.3 | 11.5
2015-07-26 | CBW | 5:00 | 8 | 9.1 | 0.181 | 23.8158 | 35 | 3.75 | 169 | NONE |  |  | HEAD | 0.27 |  | 1.1956 | 15.3685 | [8 empty] | 1.45 | 65 | 3.57 | 157 | 0.02 | 21.5
2015-07-26 | MN | 730 | 3 | 9.1 | 0.163 | 21.4474 | 32 | 2.37 | 157 | NONE |  |  | TIME | 0.28 |  | 1.1956 | 15.9377 | 1.29 | 113 | 0.24 | 69.5 |  |  | 0.46 | 43
2015-07-26 | MN | 900 | 6 | 9.1 | 0.163 | 21.4474 | 32 | 3.05 | 161 | NONE |  |  | TIME | 0.26 |  | 1.1956 | 14.7993 | [8 empty] | 1.45 | 69 |  |  | 0.02 | 25.5 | 0.46 | 4
2015-07-27 | GE | 800 | 10 | 10.9 | 0.169 | 22.2368 | 30 | 1.71 | 163 | NONE |  |  | TIME | 0.29 |  | 1.4321 | 19.7721 | [16 empty] | 4.68 | 23.5 |  |  | 4.93 | 157 | 2.67 | 71
2015-07-27 | MN | 1500 | 1 | 11 | 0.172 | 22.6316 | 30 | 2.82 | 145 | NONE |  |  | TIME | 0.28 |  | 1.4453 | 19.2654 |  |  | 1.79 | 102 | 0 | 31.5 | 0.96 | 74.5
2015-07-28 | GE | 800 | 11 | 9.9 | 0.19 | 25 | 30 | 5.48 | 161 | NONE |  |  | TIME | 0.29 |  | 1.3007 | 17.9581 | [16 empty] | 3.2 | 47 | 2.14 | 24 |  |  | 4.39 | 95
2015-07-28 | MN | 1400 | 5 | 9.9 | 0.19 | 25 | 30 | 4.47 | 122 | NONE |  |  | TIME | 0.25 |  | 1.3007 | 15.4811 | [10 empty] | 0.72 | 52 | 2.06 | 78.5 | 1.47 | 57
2015-08-02 | dh | 2000 | 8 | 10.4 | 0.186 | 24.4737 | 38 | 1.84 | 44 | none |  |  | head | 0.228 |  | 1.3664 | 14.8319 | [8 empty] | 0.26 | 11.21 | 0.01 | 36.7 | 3.06 | 106.11
2015-08-04 | wl | 1800 | 2 | 7.2 | 0.156 | 20.5263 | 38 | 2.07 | 140 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 59 |  |  | 0.04 | 106 | 0 | 31.5
2015-08-04 | dh | 2000 | 3 | 7.2 | 0.156 | 20.5263 | 38 | 1.48 | 92 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 60.89 | 0 | 0.76 |  |  | 0 | 33.23
2015-08-05 | CBW | 13:30 | 9 | 9.1 | 0.151 | 19.8684 | 30 | 4.84 | 109.5 | NONE |  |  | TIME | 0.19 |  | 1.1956 | 10.8149 | [16 empty] | 4.84 | 109.5 | 109.5 | 1.65 | 4.14 | 102 | 2.18 | 53.5
2015-08-06 | CBW | 7:00 | 10 | 9.6 | 0.163 | 21.4474 | 30 | 2.83 | 127 | NONE |  |  | TIME | 0.391 |  | 1.2613 | 23.4788 | [16 empty] | 1.29 | 17.5 | 2.83 | 127 | 5.68 | 119 | 3.24 | 71
2015-08-06 | CBW | 1400 | 6 | 9.2 | 0.171 | 22.5 | 30 | 1.52 | 134 | NONE |  |  | TIME | 0.39 |  | 1.2088 | 22.4429 | [8 empty] | 1.27 | 102.5 | 1.52 | 134 | 0 | 78.5 | 0.81 | 90
2015-08-06 | CBW | 1600 | 11 | 9.6 | 0.174 | 22.8947 | 30 | 5.69 | 128.5 | NONE |  |  | TIME | 0.31 |  | 1.2613 | 18.6149 | [16 empty] | 1.29 | 26.5 | 2.32 | 9 |  |  | 3.24 | 80
2015-08-07 | CBW | 8:00 | 1 | 8.6 | 0.178 | 23.4211 | 37 | 1.02 | 128 | NONE |  |  | TIME | 0.5 |  | 1.1299 | 26.8965 | 1.02 | 128 | 0.39 | 62 | 0 | 60 | 0.5 | 95.5
2015-08-07 | CBW | 13:00 | 5 | 8.6 | 0.178 | 23.4211 | 37 | 2.27 | 125.5 | NONE |  |  | TIME | 0.32 |  | 1.1299 | 17.2138 | [8 empty] | 2.27 | 125.5 | 0 | 23 | 1.01 | 101.5 | 1.81 | 113
2015-08-08 | CBW | 6:00 | 8 | 8.5 | 0.235 | 30.9211 | 35 | 2.8 | 130 | NONE |  |  | TIME | 0.47 |  | 1.1168 | 24.9887 | [8 empty] | 0 | 17 | 0.5 | 40 | 2.52 | 118.5 | 2.8 | 130
2015-08-08 | CBW | 8:00 | 7 | 8.5 | 0.165 | 21.7105 | 35 | 2.52 | 120 | NONE |  |  | TIME | 0.46 |  | 1.1168 | 24.4571 | [8 empty] | 0 | 19 | 0.5 | 42 | 2.52 | 120 | 0 | 2
2015-08-09 | CBW | 6:30 | 12 | 9.2 | 0.169 | 22.2368 | 35 | 6.05 | 142.5 | NONE |  |  | TIME | 0.58 |  | 1.2088 | 33.3767 | [16 empty] | 3.81 | 89 | 2.34 | 71.5 | 3.42 | 62.5 | 6.05 | 142.5
2015-08-09 | CBW | 9:00 | 4 | 8.9 | 0.169 | 22.2368 | 35 | 2.18 | 144.5 | NONE |  |  | TIME | 0.43 |  | 1.1693 | 23.9379 | 0.46 | 49 | 0.78 | 111 | 2 | 109 | 2.18 | 144.5
2015-08-10 | CBW | 6:00 | 2 | 9.3 | 0.181 | 23.8158 | 35 | 2.37 | 132 | NONE |  |  | TIME | 0.66 |  | 1.2219 | 38.3932 | 0.46 | 70 | 2.37 | 132 | 3.52 | 130 | 0 | 21
2015-08-10 | CBW | 10:00 | 3 | 10 | 0.181 | 23.8158 | 35 | 3.52 | 134 | NONE |  |  | TIME | 0.33 |  | 1.3139 | 20.6415 | 0.96 | 74 | 0.06 | 136 | 3.52 | 134 | 0 | 25
2015-08-11 | CBW | 6:30 | 9 | 9.8 | 0.177 | 23.2895 | 34 | 6.84 | 137 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [18 empty] | 1.32 | 119.5 | 6.97 | 110.5 | 3.74 | 48
2015-08-11 | CBW | 8:00 | 10 | 9.8 | 0.177 | 23.2895 | 34 | 0.8 | 121 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 1.5 |  |  | 6.97 | 112 | 3.76 | 49.5
2015-08-11 | CBW | 13:30 | 11 | 9.8 | 0.177 | 23.2895 | 34 | 6.47 | 117.5 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 7 | 2.58 | 5.5 |  |  | 3.74 | 55
2015-08-11 | CBW | 1500 | 6 | 9.4 | 0.177 | 23.2895 | 34 | 5.01 | 121 | NONE |  |  | TIME | 0.27 |  | 1.235 | 15.8752 | [8 empty] | 4.56 | 98 | 5.01 | 121 | 0 | 79 | 3.53 | 81
2015-08-11 | GHE | 18:00 | 1 | 7.4 | 0.138 | 18.1579 | 35 | 1.45 | 106 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 |  |  | 0.06 | 37 | 0 | 32 | 0.51 | 57
2015-08-11 | GHE | 20:00 | 5 | 7.4 | 0.138 | 18.1579 | 35 | 2.5 | 103 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 | [10 empty] | 0 | 5 | 0 | 84 | 3.03 | 86
2015-08-12 | MN | 600 | 8 | 7.5 | 0.152 | 20 | 35 | 2.54 | 96 | NONE |  |  | TIME | 0.42 |  | 0.9854 | 19.7032 | [8 empty] | 0.12 | 9 | 0 | 14 | 0.2 | 93
2015-08-12 | DMH | 11:30 | 7 | 7.8 | 0.133 | 17.5 | 35 | 0.02 | 99.5 | NONE |  |  | TIME | 0.282 |  | 1.0248 | 13.7585 | [8 empty] | 0.09 | 14.45 | 0.06 | 19.07 |  |  | 0 | 4.64
2015-08-13 | wl | 10:00 | 12 | 9.3 | 0.149 | 19.6053 | 40 | 4.94 | 99.5 | none |  |  | time | 0.39 |  | 1.2219 | 22.6869 | [16 empty] | 1.37 | 51.5 | 2.57 | 50 | 2.05 | 44.5
2015-08-13 | wl | 16:00 | 4 | 8.8 | 0.15 | 19.7368 | 40 | 1.1 | 103 | none |  |  | time | 0.267 |  | 1.1562 | 14.6967 | 0 | 44.6 | 0.2 | 80.6 | 0.2 | 76
2015-08-14 | dmh | 11:00 | 2 | 10.4 | 0.15 | 19.7368 | 40 | 0.51 | 101 | none |  |  | time | 0.289 |  | 1.3664 | 18.8 | 0 | 63.34 |  |  | 1 | 95.12 | 0 | 17.27
2015-08-14 | dmh | 15:30 | 3 | 10.6 | 0.15 | 19.7368 | 40 | 0.1 | 99.5 | none |  |  | time | 0.289 |  | 1.3927 | 19.1616 | 0 | 3.56 | 0.45 | 68.11 |  |  | 0.06 | 22.04
2015-08-15 | wl | 9:30 | 1 | 9.9 | 0.149 | 19.6053 | 40 | 0 | 84 | none |  |  | time | 0.399 |  | 1.3007 | 24.7079 |  |  | 0 | 22 | 0 | 17 | 0 | 40.5
2015-08-15 | CBW | 11:30 | 9 | 10.4 | 0.149 | 19.6053 | 40 | 3.2 | 101 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [18 empty] | 2 | 99.5 | 3.5 | 94.5 | 2.6 | 49.5
2015-08-15 | CBW | 1400 | 10 | 10.4 | 0.149 | 19.6053 | 40 | 2.9 | 102 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [16 empty] | 1.1 |  |  |  | 3.6 |  | 2.8
2015-08-15 | wl | 1600 | 6 | 9.2 | 0.149 | 19.6053 | 40 | 0.5 | 96 | none |  |  | time | 0.448 |  | 1.2088 | 25.7806 | [8 empty] | 0.5 | 91 |  |  | 0.4 | 75 | 0.2 | 80
2015-08-15 | he | 1800 | 11 |  |  | 0 | 45 | 3.62 | 99.5 | none |  |  | time | 0.487 |  | 0 | 0
2015-08-16 | wl | 8:30 | 5 | 9.4 | 0.147 | 19.3421 | 45 | 1 | 110.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [10 empty] | 0 | 15.5 | 0.8 | 92 | 0.7 | 97
2015-08-16 | wl | 10:30 | 8 | 9.4 | 0.147 | 19.3421 | 45 | 0.7 | 100.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 1 | 0 | 17.5 | 0.8 | 94
2015-08-16 | wl | 13:30 | 7 | 9.4 | 0.147 | 19.3421 | 45 | 0.8 | 98 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 4 | 0 | 20.5 |  |  | 0 | 2
2015-08-17 | wl | 11:00 | 12 | 10.3 | 0.149 | 19.6053 | 45 | 3.63 | 97 | none |  |  | time | 0.348 |  | 1.3533 | 22.4204 | [16 empty] | 1.7 | 47.5 | 2.82 | 45 | 1.89 | 41
2015-08-17 | wl | 1600 | 4 | 9.7 | 0.149 | 19.6053 | 45 | 0.1 | 96 | none |  |  | time | 0.367 |  | 1.2745 | 22.2672 | 0 | 52.5 | 0 | 76 | 0 | 71.5
2015-08-18 | wl | 7:30 | 2 | 9.6 | 0.149 | 19.6053 | 45 | 0.3 | 91.6 | none |  |  | time | 0.354 |  | 1.2613 | 21.257 | 0 | 68.3 |  |  | 0.2 | 86.8 | 0 | 14.1
2015-08-18 | dh | 10:00 | 3 | 9.6 | 0.149 | 19.6053 | 45 | 0.04 | 89 | none |  |  | time | 0.403 |  | 1.2613 | 24.1993 | 0 | 70.53 | 0 | 1.01 |  |  | 0 | 16.39
2015-08-19 | GE | 9:30 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0.45 | 10 | 0.05 | 11.5 | 0 | 17.5
2015-08-19 | GE | 13:30 | 9 | 8.9 |  | 0 | 40 | 2.21 | 98 | NONE |  |  | TIME | 0.32 |  | 1.1693 | 17.8142 | [18 empty] | 2.32 | 93.5 | 2.43 | 91.5 | 1.59 | 51.5
2015-08-19 | GE | 16:00 | 6 | 8.3 |  | 0 | 40 | 0.22 | 96 | NONE |  |  | TIME | 0.3 |  | 1.0905 | 15.575 | [8 empty] | 0.31 | 79.5 |  |  | 0.34 | 74.5 | 0.23 | 77.5
2015-08-19 | CBW | 19:00 | 10 | 8.8 |  | 0 | 39 | 2.91 | 101 | NONE |  |  | TIME | 0.231 |  | 1.1562 | 12.7152 | [16 empty] | 1.26 | 5.5 |  |  | 2.43 | 99 | 1.6 | 56
2015-08-19 | CBW | 23:00 | 11 | 8.8 |  | 0 | 39 | 2.43 | 100.5 | NONE |  |  | TIME | 0.227 |  | 1.1562 | 12.495 | [16 empty] | 1.26 | 9.5 | 2.91 | 4 |  |  | 2.1 | 60
2015-08-20 | MN | 830 | 5 | 8.3 |  | 0 | 38 | 0.81 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [10 empty] | 0.21 | 16 | 0.34 | 91 | 0.23 | 94
2015-08-20 | MN | 1030 | 8 | 8.3 |  | 0 | 38 | 0.21 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [8 empty] | 0 | 2 | 0.21 | 18 | 0.34 | 93
2015-08-20 | MN | 1330 | 7 | 8.3 |  | 0 | 38 | 0.34 | 96 | NONE |  |  | TIME | 0.2 |  | 1.0905 | 10.3833 | [8 empty] | 0 | 5 | 0.21 | 21 |  |  | 0.13 | 3 | 1.29 | 45.5 | 2.51 | 28 | 1.36 | 38
2015-08-21 | MN | 1100 | 12 | 8.8 |  | 0 | 35 | 2.1 | 96 | NONE |  |  | TIME | 0.22 |  | 1.1562 | 12.1097
2015-08-21 | MN | 1600 | 4 | 8.3 | 0.176 | 23.1579 | 35 | 0 | 96 | NONE |  |  | TIME | 0.22 |  | 1.0905 | 11.4216 | 0 | 54.5 | 0 | 80.5 | 0 | 78
2015-08-22 | CBW | 4:00 | 2 | 8.3 | 0.176 | 23.1579 | 35 | N/A | 92.5 | NONE |  |  | TIME | 0.34 |  | 1.0905 | 17.6516 | N/A | 66.5 |  |  | N/A | 90 | N/A | 12
2015-08-22 | MN | 1000 | 3 | 8.3 |  | 0 | 35 | 0 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | 0 | 72.5 | 0 | 6 |  |  | 0 | 18
2015-08-23 | MN | 930 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0 | 29.5 | 0.44 | 23.5 | 0 | 42.5
2015-08-23 | MN | 1600 | 6 | 8.3 |  | 0 | 45 | 0 | 96 | NONE |  |  | TIME | 0.28 |  | 1.0905 | 14.5366 | [8 empty] | 0 | 78 |  |  | 0 | 73 | 0 | 76 |  |  | 2.51 | 110.5 | 1.86 | 105.5 | 1.47 | 69.5
2015-08-24 | MN | 830 | 9 | 9.5 |  | 0 | 45 | 2.3 | 115 | NONE |  |  | TIME | 0.25 |  | 1.2482 | 14.8556
2015-08-24 | MN | 1030 | 5 | 9 |  | 0 | 45 | 1.02 | 98 | NONE |  |  | TIME | 0.23 |  | 1.1825 | 12.9478 | [10 empty] | 0 | 16 | 0 | 92 | 0.52 | 95
2015-08-24 | CBW | 21:00 | 10 | 10.3 | 0.14 | 18.4211 | 35 | 3.03 | 124 | NONE |  |  | TIME | 0.25 |  | 1.3533 | 16.1066 | [16 empty] | 1.19 | 12.5 |  |  | 2.87 | 118 | 2.5 | 82
2015-08-25 | CBW | 2:00 | 11 | 10.2 | 0.14 | 18.4211 | 35 | 2.36 | 123 | NONE |  |  | TIME | 0.2 |  | 1.3401 | 12.7602 | [16 empty] | 1.19 | 17.5 | 2.5 | 5 |  |  | 1.99 | 87
2015-09-02 | CBW | 13:00 | 3 | 7.3 | 0.263 | 34.6053 | 45 | N/A | 37 | NONE |  |  | TIME | 0.26 |  | 0.95912 | 11.872 | N/A | 28 | N/A | 29 |  |  | N/A | 37
2015-09-02 | CBW | 15:00 | 1 | 7.7 | 0.263 | 34.6053 | 45 | N/A | 39 | NONE |  |  | TIME | 0.21 |  | 1.0117 | 10.1143 |  |  | N/A | 31 | N/A | 2 | N/A | 39
2015-09-03 | CBW | 6:00 | 6 | 8.5 | 0.256 | 33.6842 | 45 | 1 | 54 | NONE |  |  | TIME | 0.3 |  | 1.1168 | 15.9503 | [8 empty] | 0.5 | 54 | 1.01 | 54 | 0 | 54 | 0.01 | 54
2015-09-03 | CBW | 9:00 | 9 | 9.2 | 0.256 | 33.6842 | 45 | 2.24 | 57 | NONE |  |  | TIME | 0.276 |  | 1.2088 | 15.8827 | [18 empty] | 2.58 | 57 | 1.92 | 57 | 1.67 | 48
2015-09-03 | CBW | 12:00 | 5 | 7.3 | 0.256 | 33.6842 | 45 | 1 | 60 | NONE |  |  | TIME | 0.22 |  | 0.95912 | 10.0455 | [10 empty] | 0.29 | 6 | 0 | 60 | 0.01 | 60
2015-09-04 | CBW | 7:00 | 10 | 7 | 0.256 | 33.6842 | 45 | 2.08 | 79 | NONE |  |  | TIME | 0.58 |  | 0.91971 | 25.3953 | [16 empty] | 0.67 | 22 |  |  | 1.91 | 79 | 0.67 | 79
2015-09-04 | CBW | 9:30 | 11 | 8.5 | 0.256 | 33.6842 | 45 | 1.92 | 81.5 | NONE |  |  | TIME | 0.4 |  | 1.1168 | 21.267 | [16 empty] | 0.67 | 24.5 | 2.71 | 2.5 |  |  | 1.68 | 81.5
2015-09-04 | CBW | 13:00 | 8 | 8.5 | 0.256 | 33.6842 | 45 | N/A | 85 | NONE |  |  | TIME | 0.32 |  | 1.1168 | 17.0136 | [8 empty] | 4.7 | 25 | 0.29 | 31 | 0 | 85
2015-09-05 | CBW | 7:00 | 12 | 9.1 | 0.256 | 33.6842 | 45 | 1.38 | 103 | NONE |  |  | TIME | 0.6 |  | 1.1956 | 34.1523 | [16 empty] | 1.22 | 46 | 2.62 | 24 | 1.16 | 21.5
2015-09-05 | CBW | 9:00 | 7 | 8.3 | 0.304 | 40 | 45 | 0.31 | 105 | NONE |  |  | TIME | 0.27 |  | 1.0905 | 14.0175 | [8 empty] | N/A | 45 | N/A | 51 |  |  | N/A | 20
2015-09-05 | CBW | 1500 | 4 | 7.1 | 0.304 | 40 | 45 | N/A | 111 | NONE |  |  | TIME | 0.25 |  | 0.93285 | 11.1026 | N/A | 72 | N/A | 103 | N/A | 74
2015-09-06 | CBW | 7:00 | 2 | 7.1 | 0.295 | 38.8158 | 40 | N/A | 119 | NONE |  |  | TIME | 0.56 |  | 0.93285 | 24.8699 | N/A | 88 |  |  | N/A | 90 | N/A | 16
2015-09-07 | CBW | 9:00 | 3 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 116 | NONE |  |  | TIME | 0.49 |  | 1.0117 | 23.6001 | N/A | 114 | N/A | 26 |  |  | N/A | 4
2015-09-07 | CBW | 14:00 | 1 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 119 | NONE |  |  | TIME | 0.38 |  | 1.0117 | 18.3021 |  |  | N/A | 31 | N/A | 5 | N/A | 47
2015-09-08 | CBW | 6:00 | 6 | 8.1 | 0.233 | 30.6579 | 45 | 2.51 | 120 | NONE |  |  | TIME | 0.4 |  | 1.0642 | 20.2662 | [8 empty] | 2.02 | 114 |  |  | 1.72 | 69 | 2.53 | 89
2015-09-08 | CBW | 8:00 | 9 | 8.9 | 0.233 | 30.6579 | 45 | 3.74 | 119 | NONE |  |  | TIME | 0.5 |  | 1.1693 | 27.8347 | [18 empty] | 2.11 | 97 | 3.24 | 94 | 2.43 | 73
2015-09-08 | CBW | 12:00 | 5 | 0.31 | 0.233 | 30.6579 | 45 | 2.56 | 120 | NONE |  |  | TIME | 0.32 |  | 0.04073 | 0.6205 | [10 empty] | 0 | 6 | 2.24 | 7.5 | 3.05 | 95
2015-09-09 | wl | 8:00 | 8 | 7.2 | 0.335 | 44.0789 | 45 | 3.8 | 115 | NONE |  |  | time | 0.367 |  | 0.94598 | 16.5282 | [8 empty] | 0 | 18 | 0 | 25.5 | 2.9 | 93.5
2015-09-10 | wl | 8:30 | 4 | 6.6 | 0.345 | 45.3947 | 50 | 1.3 | 113.5 | NONE |  |  | time | 0.317 |  | 0.86715 | 13.0867 | 0 | 66 | 0.4 | 96 | 0 | 71
2015-09-10 | dh | 10:30 | 12 | 7.5 | 0.345 | 45.3947 | 50 | 3.05 | 123.5 | NONE |  |  | time | 0.381 |  | 0.9854 | 17.8737 | [16 empty] | 1.04 |  | 0.06 |  | 1.06
2015-09-11 | wl | 14:30 | 2 | 7.2 | 0.309 | 40.6579 | 50 | 0.8 | 127.5 | NONE |  |  | time | 0.301 |  | 0.94598 | 13.5558 | 0 | 95.5 |  |  | 0.3 | 101 | 7.4 | 28.5
2015-09-12 | DH | 10:00 | 1 | 7.2 | 0.31 | 40.7895 | 50 | 0.035 | 116 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 |  |  | 0.059 | 18.02 | 0.04 | 120.31 | 0.06 | 47.81
2015-09-12 | DH | 14:00 | 3 | 7.2 | 0.31 | 40.7895 | 50 | 0.04 | 125 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 | 0.069 | 2.97 | 0.063 | 22.42 |  |  | 0.06 | 52.21
2015-09-13 | wl | 10:00 | 6 | 6.6 | 0.31 | 40.7895 | 50 | 0.9 | 124 | none |  |  | Time | 0.285 |  | 0.86715 | 11.7657 | [8 empty] | 0.8 | 115.5 |  |  | 0 | 96 | 0 | 98
2015-09-13 | DH | 12:00 | 5 | 6.5 | 0.31 | 40.7895 | 50 | 0.06 | 120 | NONE |  |  | TIME | 0.285 |  | 0.85401 | 11.5874 | [10 empty] | 0.08 | 0.71 | 0.06 | 97.48 | 0.04 | 99.49
2015-09-14 | DH | 9:00 | 10 | 8.5 | 0.306 | 40.2632 | 60 | 2 | 115 | NONE |  |  | TIME | 0.438 |  | 1.1168 | 23.2874 | [16 empty] | 1 | 18 |  |  | 2.3 | 114.5 | 2 | 90.5
2015-09-15 | wl | 8:00 | 7 | 7.3 | 0.31 | 40.7895 | 60 | 1.4 | 142 | none |  |  | time | 0.461 |  | 0.95912 | 21.05 | [8 empty] | 0.2 | 43 | 0.1 | 45 |  |  | 0 | 16
2015-09-15 | wl | 10:00 | 4 | 7.3 | 0.31 | 40.7895 | 60 | 0 | 121.5 | none |  |  | time | 0.422 |  | 0.95912 | 19.2692 | 0 | 70.5 | 0 | 90 | 0 | 66.5
2015-09-15 | DH | 13:00 | 12 | 7.8 | 0.312 | 41.0526 | 60 | 2.4 | 122.5 | NONE |  |  | TIME | 0.426 |  | 1.0248 | 20.7841 | [16 empty] | 1.4 | 46 | 2.5 | 28 | 1.2 | 26.5
2015-09-18 | CBW | 22:00 | 9 | 7.9 | 0.283 | 37.2368 | 45 | 4.58 | 127 | NONE |  |  | TIME | 0.423 |  | 1.038 | 20.9023 | [18 empty] | 1.71 | 109 | 3.78 | 107.5 | 3.01 | 81

## FILTER STUDY
Hour
| DATE | 2019-04-01 | 2019-04-02 | 2019-04-03 | 2019-04-04 | 2019-04-05 | 2019-04-06 | 2019-04-07 | 2019-04-08 | 2019-04-09 | 2019-04-10 | 2019-04-11 | 2019-04-12 | 2019-04-13 | 2019-04-14 | 2019-04-15 | 2019-04-16 | 2019-04-17 | 2019-04-18 | 2019-04-19 | 2019-04-20 | 2019-04-21 | 2019-04-22 | 2019-04-23 | 2019-04-24 | 2019-04-25 | 2019-04-26 | 2019-04-27 | 2019-04-28 | 2019-04-29 | 2019-04-30 | 2019-05-01
| DOSE | 7062.5 | 6188.3333 | 6390 | 6223.3333 | 6006.6667 | 6013.3333 | 6000 | 6320 | 6448 | 6357 | 7049.6 | 8107.5 | 8175 | 8400 | 9584 | 9820 | 10170 | 10623.3333 | 9232 | 7800 | 8600 | 10070 | 11160 | 11742.6667 | 12125 | 12773.3333 | 12760 | 13042.6667 | 13154 | 13427 |  |  | NUMBER OF WASHS
| Alum Dose:TOC Ratio | 795.1852 | 702.3096 | 721.9623 | 729.8971 | 734.3271 | 757.4807 | 738.6609 | 742.7629 | 744 | 702.2267 | 720.4432 | 792.3318 | 780.2009 | 768.8479 | 825.5202 | 841.7143 | 894.2383 | 928.371 | 792.2078 | 657.4492 | 705.3237 | 804.1891 | 876.8022 | 882.7326 | 909.076 | 976.9608 | 993.2673 | 1010.0978 | 1034.8903 | 1075.6697 | #VALUE!
| UV 254 | 0.3375 | 0.33483 | 0.33633 | 0.324 | 0.31083 | 0.30167 | 0.30867 | 0.32333 | 0.32933 | 0.344 | 0.37183 | 0.38883 | 0.39817 | 0.41517 | 0.44117 | 0.44333 | 0.43217 | 0.43483 | 0.44283 | 0.45083 | 0.46333 | 0.47583 | 0.48367 | 0.5055 | 0.50683 | 0.49683 | 0.48817 | 0.49067 | 0.483 | 0.47433
RAW | FLOWS | 31.023 | 26.83 | 29.927 | 29.878 | 29.629 | 29.173 | 29.225 | 31.116 | 30.636 | 29.183 | 29.659 | 31.356 | 29.827 | 30.345 | 32.17 | 32.464 | 32.662 | 34.596 | 29.5 | 25.901 | 28.486 | 30.993 | 33.817 | 29.7 | 34.274 | 36.477 | 36.581 | 38.496 | 38.162 | 39.048 | 0
FILTERS | [34 empty] | Days | GAL USED
| FILT 1 | 22 | [5 empty] | 128 |  |  |  | 104 |  |  |  |  | 99 |  |  | 77 |  |  |  | 116.5 |  |  |  | 82.5 | [5 empty] | 7 | 1 | 171366.6667 | [9 empty] | 179687.5 | 181250 | 532304.1667
| FILT 2 |  |  |  | 79 |  |  |  |  | 117 |  |  |  | 115.5 |  |  |  |  | 98.5 |  |  |  | 108.5 |  |  |  | 98 |  |  |  | 88 |  |  | 7 | 2 |  |  | 162512.5 |  | 161470.8333 |  |  | 166158.3333 | 173958.3333 |  |  |  | 664100
| FILT 3 |  | 39.5 |  |  |  |  | 116 |  |  |  |  | 117 |  |  |  | 96.5 |  |  | 72 |  |  |  | 106 |  |  |  | 78.5 |  |  | 70.5 |  |  | 8 | 3 |  |  |  | 168241.6667 |  |  | 165116.6667 | [5 empty] | 333358.3333
| FILT 4 |  |  | 55 |  |  |  |  | 132 |  |  |  | 95 |  |  |  | 88.5 |  |  | 76 |  |  |  |  | 108.5 |  |  | 72 |  |  | 80 |  |  | 8 | 4 |  | 168241.6667 |  |  |  | 168241.6667 |  |  |  | 176041.6667 | 176041.6667 |  | 688566.6667
| FILT 5 |  | 42.5 | [5 empty] | 136.5 |  |  |  |  | 122.5 |  |  |  | 94 |  |  |  | 98 |  |  |  | 97.5 |  |  |  | 82 |  |  |  | 7 | 5 | [11 empty] | 176041.6667 | 176041.6667
| FILT 6 |  |  |  | 82.5 |  |  |  |  | 123 |  |  |  |  | 109 |  |  | 93 |  |  |  |  | 109 |  |  |  | 95 |  |  | 65.5 |  |  |  | 7 | 6 | [12 empty] | 0
| FILT 7 |  |  | 52 |  |  |  |  | 125.5 |  |  |  |  | 119 |  |  | 78.5 |  |  |  |  | 112 |  |  | 80.5 |  |  | 77.5 |  |  | 74 |  |  | 8 | 7 | 168241.6667 |  | 168241.6667 | [5 empty] | 176041.6667 |  |  |  | 512525
| FILT 8 |  | 35 | [5 empty] | 138.5 |  |  |  | 105.5 |  |  |  | 93 |  |  |  |  | 117 |  |  |  | 92 |  |  | 76 |  |  |  |  | 7 | 8 |  |  |  | 172929.1667 | 168241.6667 |  | 168241.6667 | 168241.6667 |  | 181250 | 181250 |  | 1040154.1667
| FILT 9 |  | 35 |  |  |  |  | 117 |  |  |  |  | 112.5 |  |  | 51.5 |  | 63.5 |  |  |  | 97 |  |  |  | 80 |  |  | 69 |  | 60 |  |  | 9 | 9 |  | 173450 |  |  |  | 172929.1667 | [5 empty] | 178125 | 524504.1667
| FILT 10 |  |  |  | 98 |  |  |  | 92 |  |  |  | 88 |  |  | 77 |  |  | 71 |  |  |  | 98 | 29 |  |  | 71 |  |  | 71.5 |  |  |  | 9 | 10 | [12 empty] | 0
| FILT 11 | 1 |  |  | 94 |  |  |  | 96 |  |  |  | 87 |  |  | 67.5 |  |  | 71 |  |  |  | 91 |  | 67 |  |  | 56 |  | 63 |  |  |  | 10 | 11 | 168241.6667 | [11 empty] | 168241.6667
| FILT 12 | 8.5 |  |  |  | 94.5 |  |  |  | 104.5 |  |  |  | 88.5 |  | 47.75 |  | 55 |  |  |  | 92 |  |  | 68.5 |  | 60.5 |  |  | 55 |  |  |  | 10 | 12 |  |  | 170845.8333 | 171366.6667 |  |  |  | 173450 | 179166.6667 | 178645.8333 | 181250 |  | 1054725
NUMBER WASHED |  | 3 | 4 | 2 | 4 | 1 | 0 | 3 | 6 | 3 | 0 | 1 | 6 | 4 | 1 | 4 | 5 | 4 | 3 | 3 | 0 | 5 | 4 | 3 | 4 | 3 | 4 | 5 | 2 | 5 | 5 | 0 | 0 |  | 13 |  | 167720.8333 |  |  | 171887.5 |  | 170845.8333 |  |  |  |  | 178645.8333 | 689100
GAL USED |  | 532304.1667 | 664100 | 333358.3333 | 688566.6667 | 176041.6667 | 0 | 512525 | 1040154.1667 | 524504.1667 | 0 | 168241.6667 | 1054725 | 689100 | 168241.6667 | 665798.6111 | 871937.5 | 720337.5 | 551575 | 521391.6667 | 0 | 851600 | 703670.8333 | 572420.8333 | 728150 | 542733.3333 | 743775 | 909945.8333 | 371366.6667 | 942733.3333 | 1047445.8333 | 0 | 17296744.4444 |  | 14 | [5 empty] | 168241.6667 | [6 empty] | 168241.6667
| UV TIMES 100 | 33.75 | 33.4833 | 33.6333 | 32.4 | 31.0833 | 30.1667 | 30.8667 | 32.3333 | 32.9333 | 34.4 | 37.1833 | 38.8833 | 39.8167 | 41.5167 | 44.1167 | 44.3333 | 43.2167 | 43.4833 | 44.2833 | 45.0833 | 46.3333 | 47.5833 | 48.3667 | 50.55 | 50.6833 | 49.6833 | 48.8167 | 49.0667 | 48.3 | 47.4333 |  |  |  | 15 | [8 empty] | 179687.5 | 161458.3333 | 163194.4444 | 161458.3333 | 665798.6111
[35 empty] | 16 | 173970.8333 |  | 174491.6667 | 174491.6667 |  |  | 174491.6667 | 174491.6667 |  |  |  |  | 871937.5
[35 empty] | 17 |  |  |  |  | 171366.6667 | 178658.3333 |  |  | 186458.3333 |  |  | 183854.1667 | 720337.5
[35 empty] | 18 |  | 178658.3333 | [7 empty] | 186458.3333 | 186458.3333 |  | 551575
[35 empty] | 19 | 176054.1667 |  | 176054.1667 | 169283.3333 | [8 empty] | 521391.6667
[35 empty] | 20 | [12 empty] | 0
[35 empty] | 21 |  |  |  |  | 169283.3333 |  | 164075 | 164075 | 177083.3333 |  |  | 177083.3333 | 851600
[35 empty] | 22 |  | 172929.1667 |  |  |  | 172929.1667 |  |  |  | 180729.1667 | 177083.3333 |  | 703670.8333
[35 empty] | 23 | 177616.6667 |  | 177616.6667 | [6 empty] | 217187.5 |  |  | 572420.8333
[35 empty] | 24 |  |  |  | 177616.6667 |  |  | 178137.5 |  |  |  | 185937.5 | 186458.3333 | 728150
[35 empty] | 25 |  |  |  |  | 178658.3333 |  |  | 178137.5 | 185937.5 |  |  |  | 542733.3333
[35 empty] | 26 |  | 182304.1667 |  |  |  | 181262.5 |  |  |  | 190625 |  | 189583.3333 | 743775
[35 empty] | 27 | 178137.5 |  | 181783.3333 | 181783.3333 |  |  | 181783.3333 |  |  |  | 186458.3333 |  | 909945.8333
[35 empty] | 28 | [7 empty] | 181783.3333 | 189583.3333 |  |  |  | 371366.6667
[35 empty] | 29 |  |  |  |  | 181783.3333 | 184908.3333 |  |  |  | 193750 | 192708.3333 | 189583.3333 | 942733.3333
[35 empty] | 30 |  | 189075 | 189075 | 189075 |  |  | 188554.1667 |  | 291666.6667 |  |  |  | 1047445.8333
[35 empty] | 31 | [12 empty] | 0

## Total Flows
Water Production and Waste (MGD) | [7 empty] | 2019-04-01
Day | Raw Flow | Finished 1 Flow | Finished 2 Flow | Combined Finished | Finished South Meter 1 | Finished South Meter 2 | Finished Conway #66 | Finished Perry #67 | Blowdown | Backwash | Decant Flow | Decant Actual Flow | Plant 1 Raw Flow, MGD | Plant 2 Raw Flow, MGD | Plant 3 Raw Flow, MGD | Plant 1 Polymer Dose, mg/L | Plant 2 Polymer Dose, mg/L | Plant 3 Polymer Dose, mg/L | Plant 1 Settled Turb. | Plant 2 Settled Turb. | Plant 3 Settled Turb.
1 | 31.023 | 13.178 | 13.66 | 26.838 | 0.011 | 13.167 | 3.825 | 9.835 | 0.83503 | 0.5323 | 0.555 | 11.0146 | 10.45 | 10.45 | 10.45 | 533.75 | 453.75 | 396.75 | 0.4365 | 0.4985 | 0.324
2 | 26.83 | 11.163 | 17.165 | 28.328 | 0.015 | 11.148 | 4.982 | 12.183 | 0.7343 | 0.6641 | 0.745 | 0.96192 | 9.1167 | 9.1333 | 9.1333 | 475 | 396.9167 | 357.0833 | 0.54125 | 0.5545 | 0.39325
3 | 29.927 | 11.341 | 15.857 | 27.198 | 0.019 | 11.322 | 4.822 | 11.035 | 0.87993 | 0.33336 | 0.75 | 2.3112 | 9.4 | 9.4 | 9.425 | 475 | 421.25 | 367.5 | 0.4775 | 0.3735 | 0.39125
4 | 29.878 | 11.582 | 15.629 | 27.211 | 0.012 | 11.57 | 4.581 | 11.048 | 0.79311 | 0.68857 | 0.617 | 1.0354 | 9.8 | 9.8 | 9.8 | 465 | 408.3333 | 353.3333 | 0.42575 | 0.296 | 0.38225
5 | 29.629 | 11.575 | 15.323 | 26.898 | 0.011 | 11.564 | 4.236 | 11.087 | 0.7395 | 0.17604 | 0.645 | 1.1578 | 9.8 | 9.8 | 9.8 | 500 | 386.6667 | 353.3333 | 0.41025 | 0.2745 | 0.30975
6 | 29.173 | 11.017 | 15.764 | 26.781 | 0.009 | 11.008 | 4.794 | 10.97 | 0.98629 | 0 | 0.474 | 1.3104 | 9.8 | 9.8 | 9.8 | 490 | 410 | 356.6667 | 0.369 | 0.28675 | 0.29075
7 | 29.225 | 11.901 | 15.339 | 27.24 | 0.009 | 11.892 | 4.4 | 10.939 | 0.81549 | 0.51253 | 0.674 | 1.3104 | 9.8 | 9.8 | 9.8 | 486.6667 | 416.6667 | 343.3333 | 0.414 | 0.3125 | 0.2895
8 | 31.116 | 9.529 | 16.876 | 26.405 | 0.006 | 9.523 | 5.52 | 11.356 | 0.79504 | 1.0402 | 0.665 | 1.525 | 10.25 | 10.25 | 10.25 | 535 | 465 | 375 | 0.36625 | 0.27175 | 0.301
9 | 30.636 | 11.939 | 15.844 | 27.783 | 0.001 | 11.938 | 4.953 | 10.891 | 0.89143 | 0.5245 | 0.774 | 1.4544 | 10.22 | 10.22 | 10.22 | 526 | 458 | 364 | 0.37725 | 0.269 | 0.2575
10 | 29.183 | 11.757 | 16.067 | 27.824 | 0.003 | 11.754 | 4.619 | 11.448 | 0.81052 | 0 | 0.59 | 0.0014184 | 9.375 | 9.375 | 9.375 | 497.5 | 448.125 | 377.5 | 0.465 | 0.355 | 0.37875
11 | 29.659 | 11.592 | 15.681 | 27.273 | 0.004 | 11.588 | 4.434 | 11.247 | 1.1043 | 0.16824 | 0.77 | 1.722 | 9.88 | 9.88 | 9.92 | 515 | 465.5 | 424 | 0.6395 | 0.4975 | 0.457
12 | 31.356 | 11.823 | 16.398 | 28.221 | 0.001 | 11.822 | 4.727 | 11.671 | 0.57281 | 1.0547 | 0.711 | 1.6762 | 10.4 | 10.4 | 10.475 | 543.75 | 477.5 | 440 | 0.4495 | 0.42725 | 0.49225
13 | 29.827 | 12.721 | 14.7 | 27.421 | 0 | 12.721 | 4.123 | 10.577 | 0.85084 | 0.6891 | 0.741 | 1.7389 | 10.175 | 10.175 | 10.25 | 545 | 442 | 430 | 0.36125 | 0.35 | 0.398
14 | 30.345 | 12.69 | 15.62 | 28.31 | 0 | 12.69 | 4.865 | 10.755 | 0.94004 | 0.16824 | 0.623 | 1.1246 | 9.975 | 9.975 | 9.975 | 522.5 | 423.75 | 410 | 0.399 | 0.4545 | 0.56
15 | 32.17 | 13.849 | 15.926 | 29.775 | 0.001 | 13.848 | 4.673 | 11.253 | 0.85782 | 0.6658 | 0.701 | 1.7971 | 10.8 | 10.8 | 10.8 | 539 | 455 | 436 | 0.45225 | 0.49675 | 0.594
16 | 32.464 | 13.444 | 16.431 | 29.875 | 0.006 | 13.438 | 4.857 | 11.574 | 0.78677 | 0.87194 | 0.753 | 1.2908 | 10.8 | 10.8 | 10.8 | 560.8333 | 506.6667 | 453.3333 | 0.416 | 0.51725 | 0.44375
17 | 32.662 | 13.635 | 15.684 | 29.319 | 0.006 | 13.629 | 4.365 | 11.319 | 0.80548 | 0.72034 | 0.623 | 1.2634 | 10.975 | 10.975 | 10.975 | 601.25 | 551.25 | 457.5 | 0.35475 | 0.342 | 0.4565
18 | 34.596 | 13.945 | 17.706 | 31.651 | 0.003 | 13.942 | 5.391 | 12.315 | 1.1752 | 0.55158 | 0.907 | 2.1135 | 11.6 | 11.6 | 11.6 | 646.6667 | 560 | 466.6667 | 0.3585 | 0.326 | 0.42975
19 | 29.5 | 11.224 | 15.664 | 26.888 | 0.001 | 11.223 | 5.345 | 10.319 | 1.2488 | 0.52139 | 0.894 | 1.531 | 9.98 | 9.98 | 9.98 | 546 | 473.5 | 415.5 | 0.2925 | 0.2715 | 0.38075
20 | 25.901 | 10.444 | 13.312 | 23.756 | 0.006 | 10.438 | 4.256 | 9.056 | 1.1688 | 0 | 0.63 | 1.7555 | 8.5 | 8.5 | 8.5 | 468.3333 | 363.3333 | 350 | 0.3155 | 0.30675 | 0.39175
21 | 28.486 | 10.795 | 14.789 | 25.584 | 0.01 | 10.785 | 4.489 | 10.3 | 0.89261 | 0.8516 | 0.784 | 1.171 | 9.375 | 9.375 | 9.375 | 493.75 | 419.375 | 415 | 0.373 | 0.3555 | 0.4125
22 | 30.993 | 12.613 | 16.191 | 28.804 | 0.009 | 12.604 | 4.92 | 11.271 | 0.90338 | 0.70367 | 0.842 | 2.0557 | 10.525 | 10.525 | 10.525 | 555 | 480 | 475 | 0.35425 | 0.3075 | 0.368
23 | 33.817 | 13.79 | 17.2 | 30.99 | 0.006 | 13.784 | 4.871 | 12.329 | 1.0098 | 0.57242 | 0.565 | 1.5 | 11.2 | 11.2 | 11.2 | 641.25 | 535 | 475 | 0.38275 | 0.38475 | 0.40825
24 | 29.7 | 11.722 | 17.118 | 28.84 | 0.001 | 11.721 | 4.453 | 12.665 | 0.95799 | 0.72815 | 0.917 | 1.8888 | 11.7 | 11.7 | 11.7 | 698.3333 | 598.3333 | 520 | 0.319 | 0.4145 | 0.4185
25 | 34.274 | 13.308 | 16.736 | 30.044 | 0 | 13.308 | 3.786 | 12.95 | 1.9432 | 0.54273 | 0.944 | 2.5286 | 11.7 | 11.7 | 11.7 | 740 | 638.125 | 522.5 | 0.363 | 0.41075 | 0.46075
26 | 36.477 | 14.582 | 20.31 | 34.892 | 0 | 14.582 | 6.081 | 14.229 | 1.9298 | 0.74377 | 0.962 | 2.317 | 12.1333 | 12.1333 | 12.1333 | 772.5 | 700 | 543.3333 | 0.366 | 0.4045 | 0.39575
27 | 36.581 | 14.21 | 14.618 | 28.828 | 0.002 | 14.208 | 4.003 | 10.615 | 1.811 | 0.90995 | 1.18 | 2.8339 | 12.14 | 12.14 | 12.16 | 773 | 709 | 564 | 0.3445 | 0.36375 | 0.404
28 | 38.496 | 14.923 | 19.887 | 34.81 | 0.003 | 14.92 | 5.467 | 14.42 | 1.8295 | 0.37137 | 1.128 | 2.1845 | 12.4 | 12.4 | 12.4 | 816.6667 | 751.6667 | 561.6667 | 0.345 | 0.35375 | 0.39075
29 | 38.162 | 14.815 | 20.61 | 35.425 | 0 | 14.815 | 5.798 | 14.812 | 2.0227 | 0.94273 | 0.951 | 1.8533 | 12.7 | 12.7 | 12.7 | 819.375 | 767.5 | 541.875 | 0.3365 | 0.3405 | 0.38425
30 | 39.048 | 14.837 | 19.059 | 33.896 | 0.001 | 14.836 | 5.306 | 13.753 | 1.8745 | 1.0474 | 1.077 | 2.0376 | 13.35 | 13.35 | 13.35 | 832.5 | 767.5 | 601.25 | 0.369 | 0.3595 | 0.44675
31 | [11 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Total | 951.134 | 375.944 | 491.164 | 867.108 | 0.156 | 375.788 | 142.942 | 348.222 | 32.9659 | 17.2967 | 23.192 |  | 318.32 | 318.3367 | 318.5717 | #DIV/0! | #DIV/0! | #DIV/0! | 11.8745 | 11.1765 | 12.0113
Average | 31.7045 | 12.5315 | 16.3721 | 28.9036 | 0.0052 | 12.5263 | 4.7647 | 11.6074 | 1.0989 | 0.57656 | 0.77307 |  | 10.6107 | 10.6112 | 10.6191 | #DIV/0! | #DIV/0! | #DIV/0! | 0.39582 | 0.37255 | 0.40038
Maximum | 39.048 | 14.923 | 20.61 | 35.425 | 0.019 | 14.92 | 6.081 | 14.812 | 2.0227 | 1.0547 | 1.18 |  | 13.35 | 13.35 | 13.35 | #DIV/0! | #DIV/0! | #DIV/0! | 0.6395 | 0.5545 | 0.594
Minimum | 25.901 | 9.529 | 13.312 | 23.756 | 0 | 9.523 | 3.786 | 9.056 | 0.57281 | 0 | 0.474 |  | 8.5 | 8.5 | 8.5 | #DIV/0! | #DIV/0! | #DIV/0! | 0.2925 | 0.269 | 0.2575
Finished Water Pumped (from South + Conway+ Perry Meters) | [7 empty] | 867.108
Finished Water Pumped (Raw Flow - Blowdown + Backwash) | [7 empty] | 900.8714
Finished Water Pumped (Raw Flow -Decant + Sludge) | [7 empty] | 923.942
Total Decant Flow |  |  | 23.192 |  |  | MG
Total Sudge Pumped (est) |  |  | 4
Total Blowdown Flow |  |  | 32.9659
Total Backwash Flow |  |  | 17.2967
Total Waste Flow from Decant and Sludge | [7 empty] | 27.192
Total Waste Flow from Blowdown and Backwash | [7 empty] | 50.2626

## Flows
Surface Water System Monthly Operation Report
Water Production Log
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  | 2019-04-01
Plant Name: Bull Creek SWTP |  |  | Plant Id #: | A26001 |  | Capacity (MGD): 45
| Number and Grade of Operator in Charge |  | Hours in Operation | Water Pumped (MG) |  |  |  | Peak Hourly Flow Rate (MGD)
Day | 1st Shift | 2nd Shift |  | Raw | Finished1 | Finished2 | Combined
1 | 4 | 14 | 24 | 31.023 | 13.178 | 13.66 | 26.838 | 32.4
2 | 3 | 14 | 24 | 26.83 | 11.163 | 17.165 | 28.328 | 30.3
3 | 20 | 4 | 24 | 29.927 | 11.341 | 15.857 | 27.198 | 29.9
4 | 20 | 4 | 24 | 29.878 | 11.582 | 15.629 | 27.211 | 29.9
5 | 20 | 4 | 24 | 29.629 | 11.575 | 15.323 | 26.898 | 29.9
6 | 20 | 4 | 24 | 29.173 | 11.017 | 15.764 | 26.781 | 29.4
7 | 20 | 4 | 24 | 29.225 | 11.901 | 15.339 | 27.24 | 29.4
8 | 20 | 4 | 24 | 31.116 | 9.529 | 16.876 | 26.405 | 32.1
9 | 20 | 4 | 24 | 30.636 | 11.939 | 15.844 | 27.783 | 32.1
10 | 14 | 17 | 24 | 29.183 | 11.757 | 16.067 | 27.824 | 29.3
11 | 14 | 17 | 24 | 29.659 | 11.592 | 15.681 | 27.273 | 31
12 | 14 | 17 | 24 | 31.356 | 11.823 | 16.398 | 28.221 | 32.1
13 | 14 | 17 | 24 | 29.827 | 12.721 | 14.7 | 27.421 | 31
14 | 14 | 17 | 24 | 30.345 | 12.69 | 15.62 | 28.31 | 31.5
15 | 14 | 17 | 24 | 32.17 | 13.849 | 15.926 | 29.775 | 33
16 | 14 | 17 | 24 | 32.464 | 13.444 | 16.431 | 29.875 | 33
17 | 4 | 20 | 24 | 32.662 | 13.635 | 15.684 | 29.319 | 35.4
18 | 4 | 20 | 24 | 34.596 | 13.945 | 17.706 | 31.651 | 35.4
19 | 4 | 20 | 24 | 29.5 | 11.224 | 15.664 | 26.888 | 33.9
20 | 4 | 20 | 24 | 25.901 | 10.444 | 13.312 | 23.756 | 26
21 | 4 | 20 | 24 | 28.486 | 10.795 | 14.789 | 25.584 | 30
22 | 4 | 20 | 24 | 30.993 | 12.613 | 16.191 | 28.804 | 32.1
23 | 4 | 20 | 24 | 33.817 | 13.79 | 17.2 | 30.99 | 35.1
24 | 17 | 14 | 24 | 29.7 | 11.722 | 17.118 | 28.84 | 35.1
25 | 17 | 14 | 24 | 34.274 | 13.308 | 16.736 | 30.044 | 35.1
26 | 17 | 18 | 24 | 36.477 | 14.582 | 20.31 | 34.892 | 37.2
27 | 17 | 14 | 24 | 36.581 | 14.21 | 14.618 | 28.828 | 37.2
28 | 17 | 14 | 24 | 38.496 | 14.923 | 19.887 | 34.81 | 38.7
29 | 17 | 18 | 24 | 38.162 | 14.815 | 20.61 | 35.425 | 39
30 | 17 | 18 | 24 | 39.048 | 14.837 | 19.059 | 33.896 | 41.1
31
Total |  |  | 720 | 951.134 | 375.944 | 491.164 | 867.108 | 987.6
Average |  |  | 24 | 31.7045 | 12.5315 | 16.3721 | 28.9036 | 32.92
Maximum |  |  | 24 | 39.048 | 14.923 | 20.61 | 35.425 | 41.1
Minimum |  |  | 24 | 25.901 | 9.529 | 13.312 | 23.756 | 26
| #3-Lederman A #21- Nobles D | #4-Hughes B #5-Nicolosi B | #12-Eaddy A #20 Brookover A | #14-Wall A #16-Eaton A | #17-Holden B #18-Mercer A
Prepared by: ___________________________________________ |  |  |  |  | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## Raw & Coagulated
Surface Water System Monthly Operation Report
Chemical & Physical Analyses of
Raw, Coagulated, & Settled Water
Bureau of Water
System Name: Grand Strand Regional | [6 empty] | System Number: 2620004
Certified Lab ID#: 26102 | [6 empty] | 2019-04-01
| Raw Water | [6 empty] | Coagulated Water |  | Settled Water
Day | pH | Alkalinity (mg/L) | Temp (oC) | Hardness (mg/L) | Turbidity (NTU) | True Color (CU) | Apparent Color (CU) | pH | Alkalinity (mg/L) | Turbidity (NTU) | Disinfectant Residual (mg/L)
1 | 6.6367 | 19.3333 | 16.5833 | 18.6667 | 10.1 | 85.3333 | 139.3333 | 6.1428 | 10.6667 | 0.612 | 0.49
2 | 6.6367 | 19.3333 | 15.85 | 18.8333 | 10.3 | 81 | 136.3333 | 6.0889 | 10 | 0.776 | 0.54
3 | 6.5817 | 19.3333 | 15.6833 | 18.8333 | 10.1 | 84 | 135.5 | 6.1222 | 10.2778 | 0.493 | 0.41
4 | 6.5767 | 18.6667 | 16.2667 | 17 | 7.7 | 79.5 | 118.8333 | 6.0311 | 10.3889 | 0.481 | 0.55
5 | 6.6167 | 20.3333 | 16.8333 | 18.5 | 7.18 | 76.8333 | 114 | 6.0567 | 11.1667 | 0.464 | 0.54
6 | 6.6983 | 21 | 17.3 | 18.6667 | 7.75 | 74.3333 | 112 | 6.1139 | 11.3889 | 0.427 | 0.48
7 | 6.6433 | 19.3333 | 17.85 | 18.1667 | 7 | 77 | 109.1667 | 6.0839 | 11.5556 | 0.496 | 0.49
8 | 6.6417 | 20.3333 | 18.3833 | 18.3333 | 6.2 | 77.6667 | 108.8333 | 6.0217 | 10.8889 | 0.449 | 0.43
9 | 6.5967 | 20.8333 | 19.4333 | 18 | 6.15 | 79.1667 | 110.6667 | 5.9922 | 10.1667 | 0.418 | 0.48
10 | 6.5767 | 19.5 | 19.6167 | 19.1667 | 5.31 | 79.3333 | 106.1667 | 6.0078 | 10 | 0.653 | 0.49
11 | 6.5433 | 19 | 20.0167 | 18 | 4.56 | 87.6667 | 109 | 6.0433 | 10.2222 | 0.681 | 0.43
12 | 6.5133 | 19.1667 | 20.8 | 17.8333 | 3.92 | 91.1667 | 112.1667 | 6.01 | 9.9444 | 0.702 | 0.34
13 | 6.5017 | 18.6667 | 20.5167 | 18 | 4.68 | 95 | 120.3333 | 6.0572 | 10 | 0.481 | 0.32
14 | 6.4717 | 18.1667 | 21.0167 | 18 | 4.8 | 100 | 126.6667 | 6.0456 | 10.4444 | 0.588 | 0.31
15 | 6.4433 | 19 | 20.7667 | 18 | 4.77 | 107.8333 | 133.3333 | 6.0456 | 10 | 0.71 | 0.3
16 | 6.4367 | 19 | 20.55 | 18.3333 | 4.63 | 108.5 | 132.3333 | 6.1239 | 10.7222 | 0.639 | 0.36
17 | 6.4617 | 19.5 | 20.7667 | 17.1667 | 4.66 | 106.6667 | 134.6667 | 6.0228 | 11.4667 | 0.543 | 0.43
18 | 6.5117 | 19.6667 | 20.6 | 17.5 | 6.15 | 108.3333 | 140.6667 | 6.0389 | 11.3333 | 0.487 | 0.5
19 | 6.5467 | 19.1667 | 21.0167 | 17.5 | 5.9 | 110.1667 | 142.3333 | 6.0822 | 11.7222 | 0.45 | 0.68
20 | 6.5033 | 19 | 20.8333 | 17.5 | 5.63 | 114.6667 | 145.3333 | 6.0356 | 10.8333 | 0.491 | 0.52
21 | 6.525 | 18.6667 | 20.1333 | 17.5 | 6.24 | 118.6667 | 152.3333 | 6.0128 | 11.2778 | 0.471 | 0.42
22 | 6.5217 | 20.1667 | 19.7833 | 17.5 | 6.41 | 124.6667 | 155.8333 | 5.9967 | 10.6111 | 0.418 | 0.49
23 | 6.525 | 19.5 | 19.7167 | 17.8333 | 6.58 | 128.5 | 162.5 | 6.0239 | 11 | 0.492 | 0.47
24 | 6.5667 | 18.6667 | 19.95 | 17.6667 | 6.52 | 128 | 163.6667 | 6.0011 | 10.3889 | 0.469 | 0.47
25 | 6.535 | 18.5 | 20.45 | 18 | 6.71 | 128.5 | 162.6667 | 6.1072 | 10.8333 | 0.539 | 0.44
26 | 6.54 | 17.6667 | 21.0833 | 18 | 6.76 | 127.1667 | 162.1667 | 6.1172 | 10.8333 | 0.452 | 0.41
27 | 6.525 | 18 | 21.05 | 17.8333 | 6.7 | 124.6667 | 160.5 | 6.1183 | 10.9444 | 0.463 | 0.43
28 | 6.565 | 18.6667 | 20.95 | 18 | 6.83 | 123.8333 | 160.3333 | 6.1561 | 10.6667 | 0.461 | 0.46
29 | 6.5533 | 19 | 21.55 | 17.6667 | 7.23 | 123.5 | 161.1667 | 6.0417 | 11 | 0.48 | 0.42
30 | 6.5683 | 19.5 | 21.7667 | 18 | 7.96 | 120.8333 | 164 | 6.0456 | 10.7222 | 0.6 | 0.4
31
Avg. | 6.5521 | 19.2222 | 19.5706 | 18 | 6.5143 | 102.4167 | 136.4278 | 6.0596 | 10.7156 | 0.52953 | 0.45
Max. | 6.6983 | 21 | 21.7667 | 19.1667 | 10.3 | 128.5 | 164 | 6.1561 | 11.7222 | 0.776 | 0.68
Min. | 6.4367 | 17.6667 | 15.6833 | 17 | 3.92 | 74.3333 | 106.1667 | 5.9922 | 9.9444 | 0.418 | 0.3
Prepared by: ____________________________________________ | [7 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## Finished
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2019-04-01
Finished Water 1
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.3383 | 20 | 15.85 | 3.9 |  |  | 31.5 | 0.064 | 1 | 0.5524
2 | 7.4083 | 20 | 15.3167 | 4.2 |  |  | 35 | 0.063 | 1 | 0.58
3 | 7.2683 | 20.5 | 14.9 | 3.4 |  |  | 32 | 0.064 | 1 | 0.5967
4 | 7.17 | 21 | 15.1333 | 3.8 |  |  | 36.5 | 0.06 | 1 | 0.5574
5 | 7.14 | 22 | 15.6 | 3.8 |  |  | 33 | 0.06 | 1 | 0.5729
6 | 7.37 | 22 | 15.9333 | 3.6 |  |  | 31 | 0.058 | 1 | 0.5961
7 | 7.485 | 21.5 | 16.3167 | 3.6 |  |  | 37.5 | 0.055 | 1 | 0.5859
8 | 7.27 | 25 | 17.0833 | 3.8 | 0.42 | 0.012 | 31 | 0.06 | 1 | 0.5991
9 | 7.2683 | 21 | 18.1167 | 4 |  |  | 32 | 0.061 | 1 | 0.5899
10 | 7.335 | 20.5 | 18.6333 | 4.2 |  |  | 39 | 0.06 | 1 | 0.6601
11 | 7.3683 | 23.5 | 19.0667 | 4 |  |  | 36.5 | 0.062 | 1 | 0.6141
12 | 7.3533 | 24 | 19.4833 | 4.2 |  |  | 40.5 | 0.066 | 1.1667 | 0.6257
13 | 7.33 | 20.5 | 19.8 | 4.2 |  |  | 35.5 | 0.073 | 1 | 0.6134
14 | 7.465 | 20 | 20.1667 | 4.2 |  |  | 35 | 0.077 | 1 | 0.5932
15 | 7.3983 | 23.5 | 20.3 | 4.1 |  |  | 45.5 | 0.078 | 3.2 | 0.5742
16 | 7.5133 | 24.5 | 19.9167 | 4.2 |  |  | 48 | 0.08 | 1.1667 | 0.6304
17 | 7.2208 | 25 | 19.8667 | 3.9 |  |  | 44.5 | 0.067 | 1.1667 | 0.6254
18 | 7.2733 | 24.5 | 20.05 | 4 |  |  | 46 | 0.071 | 1.5 | 0.613
19 | 7.4833 | 26.5 | 20.2833 | 3.6 |  |  | 46.5 | 0.068 | 1.3333 | 0.624
20 | 7.4817 | 21.5 | 20.3167 | 3.8 |  |  | 38 | 0.059 | 1.6667 | 0.5836
21 | 7.3583 | 21.5 | 19.9667 | 3.9 |  |  | 38.5 | 0.059 | 1.3333 | 0.6185
22 | 7.35 | 23 | 19.0667 | 3.9 | 0.38 | 0.01 | 48.5 | 0.064 | 1.8333 | 0.5981
23 | 7.23 | 24 | 19.1167 | 3.8 |  |  | 45 | 0.06 | 2 | 0.6006
24 | 7.23 | 20.5 | 19.45 | 4.1 |  |  | 44.5 | 0.069 | 1.8333 | 0.5541
25 | 7.3817 | 21 | 19.8 | 4 |  |  | 47 | 0.071 | 2 | 0.6331
26 | 7.4167 | 20.5 | 20.35 | 4 |  |  | 42.5 | 0.07 | 2 | 0.5905
27 | 7.28 | 20.5 | 20.1667 | 4 |  |  | 42.5 | 0.072 | 2 | 0.5795
28 | 7.3017 | 20 | 20.4333 | 4.1 |  |  | 25.15 | 0.073 | 1.5 | 0.6453
29 | 7.2083 | 21.5 | 20.8333 | 3.4 |  |  | 42.5 | 0.069 | 1.6667 | 0.6402
30 | 7.3417 | 21 | 21.2667 | 4.1 |  |  | 41.5 | 0.071 | 2 | 0.6219
31
Avg. | 7.3346 | 22.0167 | 18.7528 | 3.9267 | 0.4 | 0.011 | 39.0717 | 0.066133 | 1.4122 | 0.60231
Max. | 7.5133 | 26.5 | 21.2667 | 4.2 | 0.42 | 0.012 | 48.5 | 0.08 | 3.2 | 0.6601
Min. | 7.14 | 20 | 14.9 | 3.4 | 0.38 | 0.01 | 25.15 | 0.055 | 1 | 0.5524
Notes: | Phosphate reported as P
Prepared by: ____________________________________________ | [6 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## Finished2
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2019-04-01
Finished Water 2
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.2767 | 20 | 16 | 3.8 |  |  | 30.5 | 0.064 | 1 | 0.4619
2 | 7.4067 | 20 | 15.2 | 3.8 |  |  | 33 | 0.068 | 1 | 0.4924
3 | 7.21 | 22 | 15.55 | 3.3 |  |  | 33 | 0.07 | 1 | 0.4586
4 | 7.1483 | 21 | 16.2667 | 3.6 |  |  | 31.5 | 0.059 | 1 | 0.4752
5 | 7.2233 | 21.5 | 16.4833 | 3.5 |  |  | 32.5 | 0.062 | 1.1667 | 0.5753
6 | 7.3533 | 22.5 | 16.7667 | 3.4 |  |  | 32 | 0.058 | 1 | 0.4791
7 | 7.4767 | 21.5 | 17.3667 | 3.7 |  |  | 30.5 | 0.052 | 1 | 0.6139
8 | 7.2367 | 22.5 | 18.0167 | 3.2 | 0.38 | 0.009 | 32 | 0.06 | 1 | 0.4453
9 | 7.3417 | 21.5 | 18.35 | 3.7 |  |  | 33.5 | 0.06 | 1 | 0.4725
10 | 7.2533 | 22.5 | 18.5333 | 3.6 |  |  | 37.5 | 0.062 | 1 | 0.529
11 | 7.3067 | 22 | 18.7 | 3.7 |  |  | 38.5 | 0.067 | 1 | 0.5226
12 | 7.27 | 26 | 19.1667 | 3.8 |  |  | 39 | 0.071 | 1.1667 | 0.5439
13 | 7.3183 | 20 | 19.4167 | 3.7 |  |  | 37 | 0.08 | 1 | 0.5229
14 | 7.3783 | 20.5 | 19.4833 | 3.6 |  |  | 37 | 0.081 | 1 | 0.5424
15 | 7.53 | 24.5 | 20 | 3.8 |  |  | 46.5 | 0.084 | 1.1667 | 0.6702
16 | 7.4917 | 25 | 19.4167 | 3.8 |  |  | 46.5 | 0.079 | 1 | 0.5082
17 | 7.2683 | 23.5 | 19.9667 | 3.9 |  |  | 42 | 0.065 | 1.1667 | 0.5061
18 | 7.3317 | 25 | 20.0167 | 3.9 |  |  | 47 | 0.071 | 1.5 | 0.6031
19 | 7.3517 | 25.5 | 20.1333 | 3.7 |  |  | 46.5 | 0.07 | 1.3333 | 0.5176
20 | 7.375 | 22 | 20.3167 | 3.5 |  |  | 38 | 0.059 | 1.3333 | 0.4535
21 | 7.2867 | 21 | 19.8 | 3.6 |  |  | 39 | 0.058 | 1.3333 | 0.6541
22 | 7.2933 | 22.5 | 19.3667 | 3.6 | 0.37 | 0.009 | 46.5 | 0.07 | 1.6667 | 0.5103
23 | 7.2933 | 23.5 | 19.7667 | 3.6 |  |  | 53 | 0.07 | 1.6667 | 0.4747
24 | 7.2283 | 21 | 19.8 | 3.9 |  |  | 45 | 0.066 | 1.8333 | 0.7983
25 | 7.3183 | 21.5 | 20.0667 | 3.9 |  |  | 49.5 | 0.076 | 2 | 0.5272
26 | 7.305 | 20.5 | 20.5 | 3.8 |  |  | 46 | 0.073 | 2 | 0.5082
27 | 7.3383 | 20 | 20.15 | 3.8 |  |  | 45.5 | 0.077 | 2 | 0.5437
28 | 7.2867 | 20 | 20.35 | 4.1 |  |  | 47 | 0.076 | 2 | 0.5183
29 | 7.1267 | 22 | 20.6 | 2.8 |  |  | 45 | 0.073 | 1.5 | 0.496
30 | 7.1683 | 21.5 | 21.2333 | 3.7 |  |  | 44.5 | 0.073 | 2 | 0.5312
31
Avg. | 7.3064 | 22.0833 | 18.8928 | 3.66 | 0.375 | 0.009 | 40.1667 | 0.068467 | 1.3278 | 0.53186
Max. | 7.53 | 26 | 21.2333 | 4.1 | 0.38 | 0.009 | 53 | 0.084 | 2 | 0.7983
Min. | 7.1267 | 20 | 15.2 | 2.8 | 0.37 | 0.009 | 30.5 | 0.052 | 1 | 0.4453
Notes: | Phosphate reported as P
Prepared by: ____________________________________________ | [6 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## Chems lbs
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2019-04-01
Pounds or Gallons of Chemicals Used
Day | Pre Disinf (gal) | Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | Post Disenfectant (gal) (gal) |  | Post-pH (gal) | Fluoride (gal) | Phosphate (gal) | Zinc (gal) | Filter Aid (gal) | Polymer (gal) | Pre-pH (gal) | PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 348.7792 | 2657.412 |  | 2006.9486 | 716.3262 | 105.3595 | 234.0576 | 60.0192 | 51.0041 | 7.2549 | 3.7726 | 4.4186 |  | 775.5066
2 | 305.4923 | 2305.3759 |  | 1782.6425 | 748.4652 | 108.1735 | 276.9209 | 63.313 | 53.3617 | 7.6721 | 3.2359 | 4.7407 |  | 581.4978
3 | 340.244 | 2569.6812 |  | 1676.3907 | 725.05 | 108.7517 | 268.7472 | 60.6087 | 51.3856 | 7.1629 | 3.3668 | 4.4478 |  | 483.7577
4 | 346.956 | 2404.7587 |  | 1298.6137 | 723.6114 | 109.7698 | 264.257 | 60.9526 | 51.1539 | 7.0222 | 3.5206 | 4.2316 |  | 502.2026
5 | 356.0112 | 2301.6933 |  | 1212.0395 | 717.4992 | 109.54 | 264.923 | 60.6217 | 50.5655 | 6.9414 | 3.5206 | 4.2284 |  | 491.63
6 | 331.7115 | 2268.7847 |  | 1267.1322 | 715.0898 | 107.9142 | 275.6997 | 60.9109 | 50.9112 | 6.9112 | 3.5206 | 4.2665 |  | 491.63
7 | 329.946 | 2267.7892 |  | 1251.3914 | 724.9003 | 110.6866 | 276.1911 | 61.2051 | 51.3043 | 7.0297 | 3.5174 | 4.3051 |  | 491.63
8 | 355.1215 | 2417.4185 |  | 1192.2788 | 704.6635 | 107.92 | 276.0546 | 59.8019 | 49.9218 | 7.1857 | 3.6767 | 4.4003 |  | 507.5815
9 | 380.9534 | 2454.336 |  | 1364.725 | 741.8216 | 112.7101 | 285.8795 | 62.0939 | 52.5383 | 7.5564 | 3.6569 | 4.5583 |  | 510.6608
10 | 368.8094 | 2507.9793 |  | 1457.9891 | 732.4218 | 110.6849 | 297.3807 | 61.3073 | 52.421 | 7.2198 | 3.3526 | 4.8794 |  | 475.7709
11 | 369.7423 | 2676.0379 |  | 1728.3369 | 714.7481 | 96.3452 | 289.9721 | 61.003 | 51.6447 | 7.2435 | 3.5251 | 4.8093 |  | 482.1145
12 | 363.8684 | 3090.095 |  | 1971.5318 | 751.2738 | 110.2251 | 300.1174 | 81.0241 | 53.1432 | 5.2224 | 3.699 | 4.9165 |  | 511.4537
13 | 363.4658 | 3029.5724 |  | 2160.4469 | 726.9818 | 109.6624 | 286.6239 | 79.0388 | 51.8525 | 5.095 | 3.6531 | 4.7337 |  | 523.348
14 | 414.8712 | 3240.3268 |  | 2313.8937 | 756.0082 | 117.596 | 300.0175 | 81.3211 | 53.8597 | 5.2366 | 3.5845 | 4.7865 |  | 523.348
15 | 462.6877 | 3617.4063 |  | 2620.8388 | 788.6207 | 123.2527 | 312.1249 | 85.4237 | 56.2224 | 5.5713 | 3.8935 | 4.8967 | 58.4127 | 529.6916
16 | 465.3859 | 3742.5372 |  | 2770.3761 | 784.6547 | 115.2571 | 300.845 | 86.1396 | 56.6028 | 5.4667 | 3.8897 | 5.2296 |  | 539.207
17 | 491.6081 | 3837.7113 |  | 2744.1254 | 776.2341 | 117.0513 | 283.4661 | 85.2145 | 55.266 | 5.4314 | 3.9488 | 5.3459 |  | 531.2775
18 | 509.82 | 4015.9633 |  | 2959.2654 | 835.6461 | 127.2716 | 296.0728 | 92.3658 | 58.9849 | 6.0398 | 4.1673 | 5.6715 |  | 576.2115
19 | 466.4538 | 3458.876 |  | 2685.6444 | 703.5165 | 98.9894 | 277.3071 | 77.6299 | 50.2365 | 5.1378 | 3.5546 | 4.8171 |  | 517.0044
20 | 417.6364 | 3012.4178 |  | 2298.1529 | 632.3591 | 95.0622 | 237.5707 | 71.5089 | 45.6938 | 4.5393 | 3.0032 | 4.103 |  | 438.7665
21 | 410.7432 | 3311.8158 |  | 2307.9909 | 682.9805 | 105.1737 | 254.2479 | 75.3414 | 48.4505 | 5.4176 | 3.3242 | 4.508 |  | 471.8062
22 | 436.2888 | 3755.7027 |  | 2644.4499 | 767.8493 | 118.149 | 288.8284 | 87.0743 | 54.7282 | 5.5703 | 3.7524 | 5.1344 |  | 515.4185
23 | 477.5633 | 4270.378 |  | 3087.5109 | 827.6113 | 126.582 | 306.3718 | 90.6132 | 58.7581 | 5.7722 | 4.0103 | 5.6775 |  | 547.1366
24 | 407.198 | 3777.9858 |  | 3250.4698 | 766.8648 | 113.8595 | 284.7907 | 83.9258 | 54.6296 | 5.3954 | 4.2367 | 5.5634 |  | 570.9251
25 | 466.4667 | 4501.7739 |  | 3447.2294 | 797.5709 | 116.218 | 290.9462 | 86.2044 | 57.3055 | 5.5608 | 4.2588 | 6.0635 |  | 570.9251
26 | 494.4857 | 4867.6417 |  | 3588.8964 | 904.156 | 132.3578 | 340.9898 | 100.6048 | 66.3837 | 6.3207 | 4.3881 | 7.2 |  | 570.9251
27 | 496.3879 | 4874.0665 |  | 3664.4495 | 749.692 | 105.1085 | 268.6786 | 82.5906 | 54.9275 | 5.1658 | 4.3345 | 6.0354 |  | 570.9401
28 | 519.1893 | 5131.9606 |  | 3643.9891 | 921.9239 | 125.0435 | 335.437 | 100.441 | 70.2957 | 6.1944 | 4.4291 | 7.4288 |  | 602.6432
29 | 517.9009 | 5011.0706 |  | 3624.3132 | 946.8914 | 122.367 | 351.6562 | 100.3562 | 73.5409 | 6.3989 | 4.5734 | 7.3826 |  | 626.4317
30 | 530.8526 | 4979.5885 |  | 3594.7992 | 916.3804 | 114.6837 | 362.3484 | 94.754 | 64.6901 | 6.1547 | 4.6562 | 6.9401 |  | 666.0793
31
Tot | 12546.6407 | 102358.1569 |  | 71616.8623 | 23001.8127 | 3381.7658 | 8688.5236 | 2313.4097 | 1651.7838 | 184.8911 | 114.0231 | 155.7203 | 58.4127 | 16197.5216
Avg | 418.2214 | 3411.9386 |  | 2387.2287 | 766.7271 | 112.7255 | 289.6175 | 77.1137 | 55.0595 | 6.163 | 3.8008 | 5.1907 | 58.4127 | 539.9174
Max | 530.8526 | 5131.9606 |  | 3664.4495 | 946.8914 | 132.3578 | 362.3484 | 100.6048 | 73.5409 | 7.6721 | 4.6562 | 7.4288 | 58.4127 | 775.5066
Min | 305.4923 | 2267.7892 |  | 1192.2788 | 632.3591 | 95.0622 | 234.0576 | 59.8019 | 45.6938 | 4.5393 | 3.0032 | 4.103 | 58.4127 | 438.7665
* Please specify the chemical compound(s) and units used. Include product name if applicable
Pre-ph=Liquid Lime |  |  |  | Pre & Post Disinfectant= Sodium Hypochlorite | [5 empty] | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC | [5 empty] | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Polytec 1114 PWG | [5 empty] | Coagulant= Aluminum Sulfate
PAC= WaterCarb CW |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## Chem Dose
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2019-04-01
Chemical dosage mg/l
Day | Pre Disinf (gal) | * Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | * Post Disenfectant (gal) (gal) |  | * Post-pH (gal) | * Fluoride (gal) | * Phosphate (gal) | * Zinc (gal) | Filter Aid | * Polymer (gal) | Pre-pH | * PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 1.4828 | 55.0817 |  | 19.3922 | 3.9044 | 0.71045 | 6.5907 | 0.50448 | 1.112 | 0.10171 | 0.070444 | 0.168 |  | 2.9973
2 | 1.5018 | 55.2527 |  | 19.9167 | 3.865 | 0.69106 | 6.967 | 0.50417 | 1.1022 | 0.10191 | 0.070563 | 0.17076 |  | 2.5987
3 | 1.4995 | 55.2139 |  | 16.7914 | 3.8996 | 0.72362 | 7.1254 | 0.50269 | 1.1055 | 0.099095 | 0.070487 | 0.16687 |  | 1.9382
4 | 1.5316 | 51.755 |  | 13.0287 | 3.89 | 0.73004 | 7.0514 | 0.5053 | 1.1 | 0.097101 | 0.070344 | 0.15868 |  | 2.0154
5 | 1.5848 | 49.9532 |  | 12.2624 | 3.9021 | 0.73699 | 7.1717 | 0.5084 | 1.1 | 0.097101 | 0.070344 | 0.1604 |  | 1.9896
6 | 1.4997 | 50.0086 |  | 13.0201 | 3.906 | 0.72922 | 7.4122 | 0.51306 | 1.1123 | 0.097101 | 0.070344 | 0.16256 |  | 2.0207
7 | 1.4891 | 49.8977 |  | 12.8355 | 3.8928 | 0.73536 | 7.4122 | 0.50685 | 1.102 | 0.097101 | 0.070344 | 0.16127 |  | 2.0171
8 | 1.5053 | 49.9575 |  | 11.486 | 3.9038 | 0.73965 | 7.3146 | 0.51089 | 1.1063 | 0.1024 | 0.070344 | 0.17004 |  | 1.9559
9 | 1.6401 | 51.5151 |  | 13.3533 | 3.9058 | 0.73416 | 7.4996 | 0.50416 | 1.1065 | 0.10234 | 0.071942 | 0.16741 |  | 1.9986
10 | 1.6669 | 55.262 |  | 14.9761 | 3.8507 | 0.71991 | 7.7567 | 0.49704 | 1.1024 | 0.097634 | 0.071942 | 0.17894 |  | 1.9548
11 | 1.6443 | 58.0187 |  | 17.4681 | 3.8337 | 0.6393 | 7.7248 | 0.50457 | 1.108 | 0.099934 | 0.07004 | 0.17993 |  | 1.9491
12 | 1.5306 | 63.37 |  | 18.8476 | 3.8942 | 0.70683 | 7.6959 | 0.49916 | 1.1019 | 0.099959 | 0.070104 | 0.17777 |  | 1.9558
13 | 1.6072 | 65.3137 |  | 21.7124 | 3.8782 | 0.72374 | 7.7722 | 0.50114 | 1.1065 | 0.10037 | 0.070344 | 0.17615 |  | 2.1039
14 | 1.8032 | 68.6648 |  | 22.8576 | 3.9064 | 0.75173 | 7.8046 | 0.49942 | 1.1132 | 0.099917 | 0.070344 | 0.17252 |  | 2.0679
15 | 1.897 | 72.3067 |  | 24.421 | 3.8745 | 0.74912 | 7.7975 | 0.4988 | 1.1049 | 0.10107 | 0.070344 | 0.16781 | 1.3699 | 1.9743
16 | 1.8908 | 74.1304 |  | 25.5806 | 3.8421 | 0.69818 | 7.3918 | 0.5013 | 1.1086 | 0.098844 | 0.070344 | 0.17862 |  | 1.9915
17 | 1.9852 | 75.5548 |  | 25.1846 | 3.8729 | 0.7225 | 7.1956 | 0.50532 | 1.103 | 0.10007 | 0.070877 | 0.18605 |  | 1.9504
18 | 1.9436 | 74.6442 |  | 25.6408 | 3.8621 | 0.7277 | 6.8671 | 0.50737 | 1.0905 | 0.10308 | 0.070355 | 0.18284 |  | 1.9971
19 | 2.0855 | 75.3955 |  | 27.2898 | 3.8275 | 0.66625 | 7.4655 | 0.50196 | 1.0932 | 0.10322 | 0.07104 | 0.18281 |  | 2.1014
20 | 2.1267 | 74.7879 |  | 26.5972 | 3.8939 | 0.72418 | 7.3401 | 0.52335 | 1.1255 | 0.10322 | 0.070783 | 0.17624 |  | 2.0312
21 | 1.9018 | 74.7596 |  | 24.2872 | 3.9051 | 0.74396 | 7.2207 | 0.512 | 1.1081 | 0.11439 | 0.070899 | 0.1798 |  | 1.9859
22 | 1.8567 | 77.922 |  | 25.5768 | 3.8996 | 0.74231 | 7.3538 | 0.52558 | 1.1118 | 0.10446 | 0.070246 | 0.18189 |  | 1.994
23 | 1.8626 | 81.2014 |  | 27.3683 | 3.9066 | 0.7392 | 7.2846 | 0.50836 | 1.1094 | 0.10061 | 0.070104 | 0.18694 |  | 1.94
24 | 1.8083 | 81.7968 |  | 32.8068 | 3.8897 | 0.71447 | 7.1317 | 0.50594 | 1.1084 | 0.10105 | 0.070815 | 0.19684 |  | 2.3049
25 | 1.7951 | 84.46 |  | 30.1494 | 3.8833 | 0.70004 | 7.1317 | 0.49885 | 1.1161 | 0.09998 | 0.070658 | 0.20593 |  | 1.9973
26 | 1.788 | 85.8088 |  | 29.4928 | 3.7906 | 0.68649 | 7.1008 | 0.5013 | 1.1132 | 0.097851 | 0.070658 | 0.21056 |  | 1.8767
27 | 1.7897 | 85.6778 |  | 30.028 | 3.8042 | 0.65983 | 7.0541 | 0.4981 | 1.1149 | 0.096795 | 0.070038 | 0.21363 |  | 1.8714
28 | 1.7788 | 85.7235 |  | 28.375 | 3.8742 | 0.65008 | 7.0432 | 0.50166 | 1.1816 | 0.096122 | 0.070639 | 0.21776 |  | 1.8771
29 | 1.79 | 84.4368 |  | 28.4688 | 3.9101 | 0.62512 | 7.2326 | 0.49253 | 1.2147 | 0.097572 | 0.070738 | 0.21265 |  | 1.9682
30 | 1.7931 | 82.0025 |  | 27.5962 | 3.9548 | 0.6123 | 7.9062 | 0.48602 | 1.1167 | 0.098081 | 0.067738 | 0.20892 |  | 2.0453
31
Tot | 52.0798 | 2049.8735 |  | 666.8113 | 116.4239 | 21.2338 | 219.8161 | 15.1298 | 33.3994 | 3.0101 | 2.1142 | 5.4606 | 1.3699 | 61.4696
Avg | 1.736 | 68.3291 |  | 22.227 | 3.8808 | 0.70779 | 7.3272 | 0.50433 | 1.1133 | 0.10034 | 0.070473 | 0.18202 | 1.3699 | 2.049
Max | 2.1267 | 85.8088 |  | 32.8068 | 3.9548 | 0.75173 | 7.9062 | 0.52558 | 1.2147 | 0.11439 | 0.071942 | 0.21776 | 1.3699 | 2.9973
Min | 1.4828 | 49.8977 |  | 11.486 | 3.7906 | 0.6123 | 6.5907 | 0.48602 | 1.0905 | 0.096122 | 0.067738 | 0.15868 | 1.3699 | 1.8714
* Please specify the chemical compound(s) and units used. Include product name if applicable | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 1 | 30
Pre-ph = Liquid Lime |  |  |  | Pre and Post Disinfectant= Sodium Hypochlorite |  |  |  |  | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC |  |  |  |  | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Polytec 1114 PWG |  |  |  |  | Coagulant= Aluminum Sulfate
PAC= WaterCarb CW |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Supervisor

## Turbidity
Surface Water System Monthly Operation Report
Compliance with Turbidity Requirements for Filtered Systems &
Bacteriological Analysis for Raw and Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  | 2019-04-01
Lab Cert ID #: 26102 |  |  |  | Total Population: | >10,000
| Combined Filtered Water Turbidity Compliance |  |  |  | Bacteriological Analysis
Day | Maximum Filtered Water Turbidity | (A) Number of Turbidity Measurements | (B) Number of Turbidity Measurements <= 95% Limit | Number of Turbidity Measurements > Max Allowed | Raw Water |  | Finished1 Finished2
[5 empty] | Total Coliform per 100 mls | E.coli per 100 mls | Total Coliform P/A | Total Coliform P/A
1 | 0.062 | 18 | 18 | 0 | 86 | <10 | A | A
2 | 0.045 | 18 | 18 | 0 | 187 | <10 | A | A
3 | 0.043 | 18 | 18 | 0 | 399 | 20 | A | A
4 | 0.046 | 18 | 18 | 0 | 85 | 10 | A | A
5 | 0.068 | 18 | 18 | 0 | 75 | <10 | A | A
6 | 0.044 | 18 | 18 | 0 | 185 | <10 | A | A
7 | 0.057 | 18 | 18 | 0 | 132 | <10 | A | A
8 | 0.05 | 18 | 18 | 0 | 63 | 10 | A | A
9 | 0.07 | 18 | 18 | 0 | 41 | <10 | A | A
10 | 0.059 | 18 | 18 | 0 | 20 | 10 | A | A
11 | 0.07 | 18 | 18 | 0 | 52 | <10 | A | A
12 | 0.078 | 18 | 18 | 0 | 41 | <10 | A | A
13 | 0.066 | 18 | 18 | 0 | 132 | <10 | A | A
14 | 0.08 | 18 | 18 | 0 | 75 | >10 | A | A
15 | 0.079 | 18 | 18 | 0 | 97 | <10 | A | A
16 | 0.07 | 18 | 18 | 0 | 160 | <10 | A | A
17 | 0.078 | 18 | 18 | 0 | 52 | <10 | A | A
18 | 0.065 | 18 | 18 | 0 | 294 | 10 | A | A
19 | 0.074 | 18 | 18 | 0 | 259 | <10 | A | A
20 | 0.063 | 18 | 18 | 0 | 189 | <10 | A | A
21 | 0.063 | 18 | 18 | 0 | 228 | <10 | A | A
22 | 0.056 | 18 | 18 | 0 | 327 | <10 | A | A
23 | 0.056 | 18 | 18 | 0 | 243 | <10 | A | A
24 | 0.066 | 18 | 18 | 0 | 295 | <10 | A | A
25 | 0.055 | 18 | 18 | 0 | 350 | 10 | A | A
26 | 0.053 | 18 | 18 | 0 | 369 | <10 | A | A
27 | 0.077 | 18 | 18 | 0 | 480 | <10 | A | A
28 | 0.051 | 18 | 18 | 0 | 408 | <10 | A | A
29 | 0.067 | 18 | 18 | 0 | 441 | <10 | A | A
30 | 0.049 | 18 | 18 | 0 | 350 | <10 | A | A
31 | 0 | 18 | 18 | 0 | 0 | 0 | A | A
| Total | 558 | 558 | 0
Max. Allow. Turbidity: |  | 1 NTU |  | Type of Plant: |  | Super Pulsator/Greenleaf Filters
95% Turbidity Limit: |  | 0.3 NTU |  | Max. Approved Filtration Rate: |  | 6 |  | (gpm/ft2)
The percentage of turbidity measurements |  |  |  | 100
meeting the specific limit is equal to: B/A x 100
Prepared by: ____________________________________________ |  |  |  |  | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## Indiv Filter
Surface Water System Monthly Operation Report
Turbidity Requirements for Individual Filters For Complaince With
Long Term 2 Enhanced Surface Water Treatment Rule
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  |  |  | 2019-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lab Cert ID #: 26102 |  |  | Population: >10,000
Turbidity Requirements |  |  |  | Individual Filters
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Was the turbidity recorded every 15 minutes for each
individual filter (while in operation) for the entire
month? | bar: Individual Filters 1 to Individual Filters 12
2 | Were 95% of the Turbidity Measurements less than
the 0.15 NTU Limit (excluding the 15 minute period
after a backwash cycle)? | bar: Individual Filters 1 to Individual Filters 12
3 | Were there any consecutive measurements greater
than 0.30 NTU? | bar: Individual Filters 1 to Individual Filters 12
Prepared by: |  |  |  | Individual Filters 5: Date:; Individual Filters 7: 2019-05-07
(signature) William Lederman Plant Superintendent

## Individual Filters
0 | Surface Water System Monthly Operation Report
Individual Filter Performance Worksheet
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  | 2019-04-01
Lab Cert ID #: 26102 |  | Total Population Served: >10,000
1. Was the turbidity recorded every 15 minutes for each individual filter |  |  |  |  | yes
(while in operation) for the entire month?
2a. Was there a failure of any of the continuous turbidity monitoring equipment during the month? |  |  |  |  | no
2b. If there was a failure, were grab samples taken from the filter effluent every 4 hours? |  |  |  |  | N.A.
2c. If there was failure of any continuous monitoring equipment, was it repaired within
5 working days? |  |  |  |  | N.A.
3a. Did any individual filter(s) have a measured effluent turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart? |  |  |  |  | yes
3b. If the answer to 3a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | yes
3c. If the answer to 3a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | yes
4a. Did any individual filter(s) have a measured effluent turbidity level of > 0.5 NTU in two consecutive
measurements taken 15 minutes apart, excluding the first four hours of operation after the filter
has been backwashed or otherwise taken out of service? |  |  |  |  | yes
4b. If the answer to 4a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | yes
4c. If the answer to 4a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | yes
5a. Did any individual filter(s) have a measured turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 3 months? |  |  |  |  | no
5b. If the answer to 5a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
5c. If the answer to 5a was "yes", have arrangements been made for a filter self-assessment to be
conducted within 14 days of the exceedance? |  |  |  |  | N.A.
6a. Did any individual filter(s) have a measured turbidity level of > 2.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 2 months? |  |  |  |  | no
6b. If the answer to 6a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
6c. If the answer to 6a was "yes", have arrangements been made to have a CPE conducted by the
Department or by a third party approved by the Department within 30 days of the exceedance? |  |  |  |  | N.A.
Prepared by: ___________________________________________ |  |  | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## MOR CT
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-04-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.49 | 10.5 | 24.2286 | 11.872 | 6.2 | 17 | 10 | 1.1872
2 | 0.54 | 8.2 | 31.0244 | 16.7532 | 6.16 | 14.9 | 15 | 1.1169
3 | 0.41 | 10.2 | 26.4706 | 10.8529 | 6.26 | 15.4 | 10 | 1.0853
4 | 0.55 | 9.9 | 25.697 | 14.1333 | 6.01 | 16.6 | 10 | 1.4133
5 | 0.54 | 9.9 | 25.697 | 13.8764 | 6.06 | 16.5 | 10 | 1.3876
6 | 0.48 | 9.5 | 26.7789 | 12.8539 | 6.13 | 16.2 | 10 | 1.2854
7 | 0.52 | 9.8 | 25.9592 | 13.4988 | 6.19 | 17.1 | 10 | 1.3499
8 | 0.44 | 9.6 | 26.5 | 11.66 | 6.1 | 17.2 | 10 | 1.166
9 | 0.48 | 10.6 | 25.4717 | 12.2264 | 6.05 | 19.2 | 10 | 1.2226
10 | 0.5 | 9.3 | 29.0323 | 14.5161 | 6.02 | 19.5 | 10 | 1.4516
11 | 0.51 | 9.7 | 26.2268 | 13.3757 | 6.12 | 19.8 | 10 | 1.3376
12 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.2 | 19.9 | 10 | 1.1115
13 | 0.32 | 9.8 | 27.551 | 8.8163 | 6.09 | 21.1 | 7 | 1.2595
14 | 0.31 | 10.5 | 25.7143 | 7.9714 | 6.214 | 21.5 | 7 | 1.1388
15 | 0.3 | 10.5 | 25.7143 | 7.7143 | 6.14 | 21.5 | 7 | 1.102
16 | 0.36 | 11 | 23.1273 | 8.3258 | 6.14 | 21 | 7 | 1.1894
17 | 0.43 | 10.4 | 24.4615 | 10.5185 | 6.23 | 19.9 | 10 | 1.0518
18 | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.12 | 19.8 | 10 | 1.078
19 | 0.68 | 11.3 | 22.5133 | 15.309 | 6.16 | 20.6 | 7 | 2.187
20 | 0.77 | 10.6 | 25.4717 | 19.6132 | 6.14 | 19.9 | 10 | 1.9613
21 | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.07 | 20.1 | 7 | 1.5576
22 | 0.49 | 10.7 | 23.7757 | 11.6501 | 6.08 | 18.6 | 10 | 1.165
23 | 0.47 | 10.7 | 23.7757 | 11.1746 | 6.08 | 18.8 | 10 | 1.1175
24 | 0.53 | 11.6 | 21.931 | 11.6234 | 6.06 | 19.3 | 10 | 1.1623
25 | 0.53 | 11.9 | 22.6891 | 12.0252 | 6.2 | 19.9 | 10 | 1.2025
26 | 0.41 | 12.3 | 20.6829 | 8.48 | 6.16 | 21.1 | 7 | 1.2114
27 | 0.43 | 11.7 | 21.7436 | 9.3497 | 6.19 | 21 | 7 | 1.3357
28 | 0.46 | 12.4 | 20.5161 | 9.4374 | 6.2 | 21.1 | 7 | 1.3482
29 | 0.42 | 12.9 | 19.7209 | 8.2828 | 6.12 | 21.2 | 7 | 1.1833
30 | 0.4 | 13.7 | 18.5693 | 7.4277 | 6.12 | 22.2 | 7 | 1.0611
31
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## CT AVG (hidden)
|  |  |  | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT
1 | #DIV/0! | 16.4 | 15 | 6.1925 | 6.5 | 10 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 17.05 | 15 | 6.2025 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 16.95 | 15 | 6.2075 | 6.5 | 10 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0!
2 | #DIV/0! | 15.4 | 15 | 6.1675 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 16.05 | 15 | 6.1575 | 6.5 | 10 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 16.175 | 15 | 6.155 | 6.5 | 10 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0!
3 | #DIV/0! | 15.025 | 15 | 6.1775 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 15.825 | 15 | 6.1625 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 15.375 | 15 | 6.1675 | 6.5 | 10 | 0 | #DIV/0! | 0.41 | #DIV/0! | #DIV/0!
4 | #DIV/0! | 15.35 | 15 | 6.0825 | 6.5 | 10 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 15.975 | 15 | 6.0575 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 15.975 | 15 | 6.06 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0!
5 | #DIV/0! | 15.7 | 15 | 6.0975 | 6.5 | 10 | 0 | #DIV/0! | 0.66 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 16.3 | 15 | 6.1175 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 16.6 | 15 | 6.0975 | 6.5 | 10 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
6 | #DIV/0! | 16.075 | 15 | 6.1425 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 16.975 | 15 | 6.17 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 17.1 | 15 | 6.165 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0!
7 | #DIV/0! | 16.5 | 15 | 6.1475 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 16.9 | 15 | 6.18 | 6.5 | 10 | 0 | #DIV/0! | 0.52 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 17.25 | 15 | 6.175 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0!
8 | #DIV/0! | 17.55 | 15 | 6.0475 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 17.825 | 15 | 6.085 | 6.5 | 10 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 17.8 | 15 | 6.0725 | 6.5 | 10 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0!
9 | #DIV/0! | 18.2 | 15 | 6.0425 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 19.05 | 15 | 6.06 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 19.2 | 15 | 6.045 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0!
10 | #DIV/0! | 19.175 | 15 | 6.0575 | 6.5 | 10 | 0 | #DIV/0! | 0.58 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 19.625 | 15 | 6.0575 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 19.775 | 15 | 6.0375 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0!
11 | #DIV/0! | 19.4 | 15 | 6.1225 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 19.625 | 15 | 6.1275 | 6.5 | 10 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 19.925 | 20 | 6.1025 | 6.5 | 7 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0!
12 | #DIV/0! | 20.15 | 20 | 6.115 | 6.5 | 7 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 20.375 | 20 | 6.11 | 6.5 | 7 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 20.6 | 20 | 6.0925 | 6.5 | 7 | 0 | #DIV/0! | 0.34 | #DIV/0! | #DIV/0!
13 | #DIV/0! | 20.475 | 20 | 6.0925 | 6.5 | 7 | 0 | #DIV/0! | 0.38 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 20.9 | 20 | 6.115 | 6.5 | 7 | 0 | #DIV/0! | 0.42 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 21.05 | 20 | 6.0775 | 6.5 | 7 | 0 | #DIV/0! | 0.32 | #DIV/0! | #DIV/0!
14 | #DIV/0! | 20.25 | 20 | 6.115 | 6.5 | 7 | 0 | #DIV/0! | 0.33 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 20.825 | 20 | 6.14 | 6.5 | 7 | 0 | #DIV/0! | 0.36 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 21.325 | 20 | 6.1485 | 6.5 | 7 | 0 | #DIV/0! | 0.31 | #DIV/0! | #DIV/0!
15 | #DIV/0! | 21.05 | 20 | 6.0925 | 6.5 | 7 | 0 | #DIV/0! | 0.37 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 21.15 | 20 | 6.1125 | 6.5 | 7 | 0 | #DIV/0! | 0.35 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 21.375 | 20 | 6.1275 | 6.5 | 7 | 0 | #DIV/0! | 0.3 | #DIV/0! | #DIV/0!
16 | #DIV/0! | 20.425 | 20 | 6.1925 | 6.5 | 7 | 0 | #DIV/0! | 0.37 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 20.675 | 20 | 6.1725 | 6.5 | 7 | 0 | #DIV/0! | 0.36 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 20.475 | 20 | 6.1825 | 6.5 | 7 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0!
17 | #DIV/0! | 20.225 | 20 | 6.1225 | 6.5 | 7 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 20.225 | 20 | 6.145 | 6.5 | 7 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 19.875 | 15 | 6.1625 | 6.5 | 10 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
18 | #DIV/0! | 20.45 | 20 | 6.0925 | 6.5 | 7 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 20.575 | 20 | 6.115 | 6.5 | 7 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 20.175 | 20 | 6.12 | 6.5 | 7 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
19 | #DIV/0! | 20.85 | 20 | 6.1425 | 6.5 | 7 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 20.75 | 20 | 6.1775 | 6.5 | 7 | 0 | #DIV/0! | 0.72 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 20.625 | 20 | 6.1975 | 6.5 | 7 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0!
20 | #DIV/0! | 20.775 | 20 | 6.115 | 6.5 | 7 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 20.7 | 20 | 6.1525 | 6.5 | 7 | 0 | #DIV/0! | 0.52 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 20.3 | 20 | 6.1575 | 6.5 | 7 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0!
21 | #DIV/0! | 20.025 | 20 | 6.1175 | 6.5 | 7 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 19.9 | 15 | 6.1225 | 6.5 | 10 | 0 | #DIV/0! | 0.42 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 19.6 | 15 | 6.1025 | 6.5 | 10 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
22 | #DIV/0! | 19.7 | 15 | 6.045 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 19.6 | 15 | 6.055 | 6.5 | 10 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 19.2 | 15 | 6.0725 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
23 | #DIV/0! | 19.825 | 15 | 6.0675 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 19.8 | 15 | 6.1075 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 19.225 | 15 | 6.1475 | 6.5 | 10 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
24 | #DIV/0! | 19.975 | 20 | 6.06 | 6.5 | 7 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 20.1 | 20 | 6.0725 | 6.5 | 7 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 19.65 | 15 | 6.075 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0!
25 | #DIV/0! | 20.525 | 20 | 6.165 | 6.5 | 7 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 20.45 | 20 | 6.1625 | 6.5 | 7 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 20.2 | 20 | 6.1775 | 6.5 | 7 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
26 | #DIV/0! | 21.225 | 20 | 6.1825 | 6.5 | 7 | 0 | #DIV/0! | 0.41 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 21.225 | 20 | 6.16 | 6.5 | 7 | 0 | #DIV/0! | 0.42 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 21 | 20 | 6.19 | 6.5 | 7 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
27 | #DIV/0! | 20.85 | 20 | 6.145 | 6.5 | 7 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 20.825 | 20 | 6.1675 | 6.5 | 7 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 20.7 | 20 | 6.1775 | 6.5 | 7 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0!
28 | #DIV/0! | 20.825 | 20 | 6.225 | 6.5 | 7 | 0 | #DIV/0! | 0.49 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 21 | 20 | 6.2 | 6.5 | 7 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 20.85 | 20 | 6.2275 | 6.5 | 7 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0!
29 | #DIV/0! | 21.275 | 20 | 6.1375 | 6.5 | 7 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 29 | #DIV/0! | 21.375 | 20 | 6.1075 | 6.5 | 7 | 0 | #DIV/0! | 0.42 | #DIV/0! | #DIV/0! | 29 | #DIV/0! | 21.125 | 20 | 6.135 | 6.5 | 7 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0!
30 | #DIV/0! | 21.9 | 20 | 6.115 | 6.5 | 7 | 0 | #DIV/0! | 0.4 | #DIV/0! | #DIV/0! | 30 | #DIV/0! | 22 | 20 | 6.095 | 6.5 | 7 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 30 | #DIV/0! | 21.725 | 20 | 6.13 | 6.5 | 7 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0!
31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE! | 31 | #VALUE! |  | 25 |  | 7 | 0 | 0 | #DIV/0! |  | #DIV/0! | #VALUE!
ONLY FILL GREEN
|  |  |  | TEST | [8 empty] | DALY CAL SHEET FLOW, DALY AVG TEMP & PH Min CT Calculater
| Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# |  |  |  | Settle temp |  | use temp | Settle PH |  | use ph |  | FLOW CAL SHEET | t10#
| Plt 1 | 18.8 | 15 | Plt 1 PH | 6.09 | 6.5 | plt 1 flow | 12 | 21.2 |  |  |  | Plt 1 | 20.15 | 20 | Plt 1 PH | 6.115 | 6.5 | plt 1 flow | 13.7 | 18.5693
| Plt 2 | 18.9 | 15 | Plt 2 PH | 6.13 | 6.5 | plt 2 flow | 12 | 21.2 |  |  |  | Plt 2 | 20.375 | 20 | Plt 2 PH | 6.11 | 6.5 | plt 2 flow | 13.7 | 18.5693
| Plt 3 | 19.5 | 15 | Plt 3 PH | 6.24 | 6.5 | plt 3 flow | 12 | 22.5 |  |  |  | Plt 3 | 20.6 | 20 | Plt 3 PH | 6.0925 | 6.5 | plt 3 flow | 13.7 | 19.708
2019-08-12 08:48
|  | min CT | TARGET CT |  | temp | ph | min ct table | [7 empty] | min CT | TARGET CT |  | temp | ph | min ct table
| ct plt 1 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 1 | 0.37697 | 0.47697 |  | 20 | 6.5 | 7
| ct plt 2 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 2 | 0.37697 | 0.47697 |  | 20 | 6.5 | 7
| ct plt 3 | 0.44444 | 0.54444 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 3 | 0.35519 | 0.45519 |  | 20 | 6.5 | 7
Bill's Cal | flow | temp | ph | t10# | cal ct table | MIN CT | target ct
plt1 | 12 | 18.8 | 6.09 | 21.2 | 7.1064 | 0.33521 | 0.43521
plt2 | 12 | 18.9 | 6.13 | 21.2 | 7.1599 | 0.33773 | 0.43773
plt3 | 12 | 19.5 | 6.24 | 22.5 | 7.1424 | 0.31744 | 0.41744

## CT Calc
Surface Water System Monthly Operation Report
Disinfection Information
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | 2019-04-01
| Min. Disinfect. Resid. | Sample Type for | CT calc/CT table Disinfectant Sequence | [5 empty] | SUM (CT calc/CT table)
Day | at Point-of-Entry to Distribution System (mg/L) | Point-of-Entry (POE) | 1st | 2nd | 3rd | 4th | 5th | 6th
1 | 3.4 | A | 1.1872 | 0 | 0 | 0 | 0 | 0 | 1.1872
2 | 1.7 | A | 1.1169 | 0 | 0 | 0 | 0 | 0 | 1.1169
3 | 1.8 | A | 1.0853 | 0 | 0 | 0 | 0 | 0 | 1.0853
4 | 2.3 | A | 1.4133 | 0 | 0 | 0 | 0 | 0 | 1.4133
5 | 1.6 | A | 1.3876 | 0 | 0 | 0 | 0 | 0 | 1.3876
6 | 1.7 | A | 1.2854 | 0 | 0 | 0 | 0 | 0 | 1.2854
7 | 1.9 | A | 1.3499 | 0 | 0 | 0 | 0 | 0 | 1.3499
8 | 1.7 | A | 1.166 | 0 | 0 | 0 | 0 | 0 | 1.166
9 | 1.7 | A | 1.2226 | 0 | 0 | 0 | 0 | 0 | 1.2226
10 | 1.9 | A | 1.4516 | 0 | 0 | 0 | 0 | 0 | 1.4516
11 | 3.1 | A | 1.3376 | 0 | 0 | 0 | 0 | 0 | 1.3376
12 | 2.7 | A | 1.1115 | 0 | 0 | 0 | 0 | 0 | 1.1115
13 | 1.6 | A | 1.2595 | 0 | 0 | 0 | 0 | 0 | 1.2595
14 | 1.6 | A | 1.1388 | 0 | 0 | 0 | 0 | 0 | 1.1388
15 | 2.2 | A | 1.102 | 0 | 0 | 0 | 0 | 0 | 1.102
16 | 2.7 | A | 1.1894 | 0 | 0 | 0 | 0 | 0 | 1.1894
17 | 1.9 | A | 1.0518 | 0 | 0 | 0 | 0 | 0 | 1.0518
18 | 3.3 | A | 1.078 | 0 | 0 | 0 | 0 | 0 | 1.078
19 | 1.8 | A | 2.187 | 0 | 0 | 0 | 0 | 0 | 2.187
20 | 2.7 | A | 1.9613 | 0 | 0 | 0 | 0 | 0 | 1.9613
21 | 2.6 | A | 1.5576 | 0 | 0 | 0 | 0 | 0 | 1.5576
22 | 2.5 | A | 1.165 | 0 | 0 | 0 | 0 | 0 | 1.165
23 | 3.4 | A | 1.1175 | 0 | 0 | 0 | 0 | 0 | 1.1175
24 | 2.9 | A | 1.1623 | 0 | 0 | 0 | 0 | 0 | 1.1623
25 | 3.1 | A | 1.2025 | 0 | 0 | 0 | 0 | 0 | 1.2025
26 | 3.3 | A | 1.2114 | 0 | 0 | 0 | 0 | 0 | 1.2114
27 | 2.8 | A | 1.3357 | 0 | 0 | 0 | 0 | 0 | 1.3357
28 | 2.9 | A | 1.3482 | 0 | 0 | 0 | 0 | 0 | 1.3482
29 | 1.6 | A | 1.1833 | 0 | 0 | 0 | 0 | 0 | 1.1833
30 | 1.9 | A | 1.0611 | 0 | 0 | 0 | 0 | 0 | 1.0611
31
A. Number of days SUM (CT calc/CT table) <1: |  |  | 0 |  | Days the Distribution Residual was <0.2 mg/L
[5 empty] | Day | Duration (hrs) |  | Date Reported
B. Compliance with disinfection residual criteria |  |  |  |  | None | None |  | None
at Point-of-Entry to distribution system: |  |  | Yes |  | None | None |  | None
Prepared by: _________________________________________________ | [6 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Superintendent

## CT (1)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-04-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.63 | 10.5 | 24.2286 | 15.264 | 6.19 | 17 | 10 | 1.5264
2 | 0.54 | 8.2 | 31.0244 | 16.7532 | 6.16 | 14.9 | 15 | 1.1169
3 | 0.69 | 9.8 | 25.9592 | 17.9118 | 6.12 | 14.7 | 15 | 1.1941
4 | 0.65 | 9.8 | 25.9592 | 16.8735 | 6.09 | 15.5 | 10 | 1.6873
5 | 0.66 | 9.8 | 25.9592 | 17.1331 | 6.19 | 15.8 | 10 | 1.7133
6 | 0.48 | 9.5 | 26.7789 | 12.8539 | 6.13 | 16.2 | 10 | 1.2854
7 | 0.54 | 9.8 | 25.9592 | 14.018 | 6.19 | 16.5 | 10 | 1.4018
8 | 0.6 | 10.7 | 23.7757 | 14.2654 | 6.06 | 17.7 | 10 | 1.4265
9 | 0.54 | 10.5 | 24.2286 | 13.0834 | 6.02 | 18.5 | 10 | 1.3083
10 | 0.58 | 9.3 | 27.3548 | 15.8658 | 6.04 | 19 | 10 | 1.5866
11 | 0.51 | 9.7 | 26.2268 | 13.3757 | 6.12 | 19.8 | 10 | 1.3376
12 | 0.59 | 10.3 | 24.699 | 14.5724 | 6.23 | 19.7 | 10 | 1.4572
13 | 0.38 | 9.8 | 25.9592 | 9.8645 | 6.13 | 20.7 | 7 | 1.4092
14 | 0.44 | 9.8 | 25.9592 | 11.422 | 6.13 | 19.8 | 10 | 1.1422
15 | 0.37 | 10.5 | 24.2286 | 8.9646 | 6.14 | 21 | 7 | 1.2807
16 | 0.51 | 10.9 | 23.3394 | 11.9031 | 6.16 | 19.9 | 10 | 1.1903
17 | 0.53 | 10.4 | 24.4615 | 12.9646 | 6.23 | 19.6 | 10 | 1.2965
18 | 0.5 | 11.8 | 21.5593 | 10.7797 | 6.12 | 19.8 | 10 | 1.078
19 | 0.68 | 11.3 | 22.5133 | 15.309 | 6.16 | 20.6 | 7 | 2.187
20 | 0.71 | 10.6 | 24 | 17.04 | 6.11 | 20 | 7 | 2.4343
21 | 0.66 | 9 | 28.2667 | 18.656 | 6.16 | 19.1 | 10 | 1.8656
22 | 0.55 | 10.7 | 23.7757 | 13.0766 | 6.06 | 18.6 | 10 | 1.3077
23 | 0.47 | 10.7 | 23.7757 | 11.1746 | 6.08 | 18.8 | 10 | 1.1175
24 | 0.53 | 11.6 | 21.931 | 11.6234 | 6.06 | 19.3 | 10 | 1.1623
25 | 0.46 | 11.4 | 22.3158 | 10.2653 | 6.21 | 20.1 | 7 | 1.4665
26 | 0.41 | 12.3 | 20.6829 | 8.48 | 6.16 | 21.1 | 7 | 1.2114
27 | 0.46 | 12.3 | 20.6829 | 9.5141 | 6.12 | 21 | 7 | 1.3592
28 | 0.49 | 12.4 | 20.5161 | 10.0529 | 6.21 | 21 | 7 | 1.4361
29 | 0.53 | 12.9 | 19.7209 | 10.4521 | 6.09 | 21.8 | 7 | 1.4932
30 | 0.4 | 13.7 | 18.5693 | 7.4277 | 6.12 | 22.2 | 7 | 1.0611
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) Randall Johnson Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (2)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-04-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.49 | 10.5 | 24.2286 | 11.872 | 6.2 | 17 | 10 | 1.1872
2 | 0.62 | 10.1 | 25.1881 | 15.6166 | 6.17 | 17 | 10 | 1.5617
3 | 0.48 | 10.2 | 24.9412 | 11.9718 | 6.24 | 16.1 | 10 | 1.1972
4 | 0.55 | 9.9 | 25.697 | 14.1333 | 6.01 | 16.6 | 10 | 1.4133
5 | 0.54 | 9.9 | 25.697 | 13.8764 | 6.06 | 16.5 | 10 | 1.3876
6 | 0.56 | 9.5 | 26.7789 | 14.9962 | 6.13 | 17.1 | 10 | 1.4996
7 | 0.52 | 9.8 | 25.9592 | 13.4988 | 6.19 | 17.1 | 10 | 1.3499
8 | 0.44 | 9.6 | 26.5 | 11.66 | 6.1 | 17.2 | 10 | 1.166
9 | 0.54 | 10.8 | 23.5556 | 12.72 | 6.06 | 19 | 10 | 1.272
10 | 0.55 | 9.3 | 27.3548 | 15.0452 | 6.06 | 19.5 | 10 | 1.5045
11 | 0.53 | 9.8 | 25.9592 | 13.7584 | 6.14 | 19.3 | 10 | 1.3758
12 | 0.45 | 10.3 | 24.699 | 11.1146 | 6.2 | 19.9 | 10 | 1.1115
13 | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.11 | 20.9 | 7 | 1.5576
14 | 0.36 | 10.5 | 24.2286 | 8.7223 | 6.17 | 21.2 | 7 | 1.246
15 | 0.35 | 10.5 | 24.2286 | 8.48 | 6.17 | 21.1 | 7 | 1.2114
16 | 0.36 | 11 | 23.1273 | 8.3258 | 6.14 | 21 | 7 | 1.1894
17 | 0.43 | 10.4 | 24.4615 | 10.5185 | 6.23 | 19.9 | 10 | 1.0518
18 | 0.59 | 11.8 | 21.5593 | 12.72 | 6.15 | 19.8 | 10 | 1.272
19 | 0.75 | 11.3 | 22.5133 | 16.885 | 6.2 | 20.6 | 7 | 2.4121
20 | 0.64 | 10.6 | 24 | 15.36 | 6.16 | 20 | 7 | 2.1943
21 | 0.42 | 9.8 | 25.9592 | 10.9029 | 6.07 | 20.1 | 7 | 1.5576
22 | 0.49 | 10.7 | 23.7757 | 11.6501 | 6.08 | 18.6 | 10 | 1.165
23 | 0.51 | 10.6 | 24 | 12.24 | 6.07 | 19.8 | 10 | 1.224
24 | 0.59 | 11.6 | 21.931 | 12.9393 | 6.11 | 19.3 | 10 | 1.2939
25 | 0.44 | 11.8 | 21.5593 | 9.4861 | 6.16 | 20.8 | 7 | 1.3552
26 | 0.42 | 12.5 | 20.352 | 8.5478 | 6.16 | 21.1 | 7 | 1.2211
27 | 0.43 | 11.7 | 21.7436 | 9.3497 | 6.19 | 21 | 7 | 1.3357
28 | 0.46 | 12.4 | 20.5161 | 9.4374 | 6.2 | 21.1 | 7 | 1.3482
29 | 0.42 | 12.9 | 19.7209 | 8.2828 | 6.12 | 21.2 | 7 | 1.1833
30 | 0.43 | 13.8 | 18.4348 | 7.927 | 6.09 | 22.2 | 7 | 1.1324
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (3)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-04-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.63 | 10.5 | 25.7143 | 16.2 | 6.21 | 17.5 | 10 | 1.62
2 | 0.68 | 10.1 | 26.7327 | 18.1782 | 6.18 | 16.8 | 10 | 1.8178
3 | 0.41 | 10.2 | 26.4706 | 10.8529 | 6.26 | 15.4 | 10 | 1.0853
4 | 0.55 | 9.8 | 27.551 | 15.1531 | 6.07 | 16 | 10 | 1.5153
5 | 0.59 | 10 | 27 | 15.93 | 6.05 | 16.7 | 10 | 1.593
6 | 0.49 | 9.6 | 28.125 | 13.7812 | 6.21 | 17.2 | 10 | 1.3781
7 | 0.49 | 9.6 | 28.125 | 13.7812 | 6.17 | 17 | 10 | 1.3781
8 | 0.43 | 9.9 | 27.2727 | 11.7273 | 6.07 | 17.2 | 10 | 1.1727
9 | 0.48 | 10.6 | 25.4717 | 12.2264 | 6.05 | 19.2 | 10 | 1.2226
10 | 0.5 | 9.3 | 29.0323 | 14.5161 | 6.02 | 19.5 | 10 | 1.4516
11 | 0.43 | 10.4 | 25.9615 | 11.1635 | 6.14 | 20.2 | 7 | 1.5948
12 | 0.34 | 10.4 | 25.9615 | 8.8269 | 6.06 | 21 | 7 | 1.261
13 | 0.32 | 9.8 | 27.551 | 8.8163 | 6.09 | 21.1 | 7 | 1.2595
14 | 0.31 | 10.5 | 25.7143 | 7.9714 | 6.214 | 21.5 | 7 | 1.1388
15 | 0.3 | 10.5 | 25.7143 | 7.7143 | 6.14 | 21.5 | 7 | 1.102
16 | 0.57 | 11.1 | 24.3243 | 13.8649 | 6.11 | 21.2 | 7 | 1.9807
17 | 0.73 | 10.6 | 25.4717 | 18.5943 | 6.26 | 19.8 | 10 | 1.8594
18 | 0.64 | 11.8 | 22.8814 | 14.6441 | 6.14 | 19.7 | 10 | 1.4644
19 | 0.68 | 10 | 27 | 18.36 | 6.19 | 20.6 | 7 | 2.6229
20 | 0.77 | 10.6 | 25.4717 | 19.6132 | 6.14 | 19.9 | 10 | 1.9613
21 | 0.59 | 10.1 | 26.7327 | 15.7723 | 6.04 | 19.4 | 10 | 1.5772
22 | 0.54 | 11.2 | 24.1071 | 13.0179 | 6.08 | 19.3 | 10 | 1.3018
23 | 0.59 | 11.9 | 22.6891 | 13.3866 | 6.18 | 19.7 | 10 | 1.3387
24 | 0.61 | 11.7 | 23.0769 | 14.0769 | 6.11 | 19.6 | 10 | 1.4077
25 | 0.53 | 11.9 | 22.6891 | 12.0252 | 6.2 | 19.9 | 10 | 1.2025
26 | 0.59 | 12.5 | 21.6 | 12.744 | 6.21 | 20.7 | 7 | 1.8206
27 | 0.59 | 12.3 | 21.9512 | 12.9512 | 6.15 | 20.7 | 7 | 1.8502
28 | 0.65 | 12.8 | 21.0938 | 13.7109 | 6.25 | 20.6 | 7 | 1.9587
29 | 0.63 | 13.3 | 20.3008 | 12.7895 | 6.07 | 21.6 | 7 | 1.8271
30 | 0.6 | 14.2 | 19.0141 | 11.4085 | 6.17 | 21.4 | 7 | 1.6298
31 | [7 empty] | 0
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-05-07
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## ct CAL
ONLY FILL GREEN
TEST
Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# | Flows from Plant Check Sheet
Plt 1 | 22.2 | 20 | Plt 1 PH | 6.12 | 6.5 | plt 1 flow | 13.7 | 18.5693 | Raw PLT 1 | 13.7
Plt 2 | 22.2 | 20 | Plt 2 PH | 6.09 | 6.5 | plt 2 flow | 13.7 | 18.5693 | Raw PLT 2 | 13.7
Plt 3 | 21.7 | 20 | Plt 3 PH | 6.19 | 6.5 | plt 3 flow | 13.7 | 19.708 | Raw PLT 3 | 13.7
| min CT | TARGET CT |  | temp | ph | min ct table
ct plt 1 | 0.37697 | 0.47697 |  | 20 | 6.5 | 7
ct plt 2 | 0.37697 | 0.47697 |  | 20 | 6.5 | 7
ct plt 3 | 0.35519 | 0.45519 |  | 20 | 6.5 | 7

## Turbidity Analysis
South Carolina Department of Health and Environmental Control
Bureau of Drinking Water Protection
Turbidity Analysis Input Form
System Number .............................................................…………… |  |  | 2620004
Name of Water System ................................................……………. |  |  | GSWSA
Analytical Method ..........................................................…………… |  |  | 001
Contaminant ID ..............................................................…………… |  |  | 0100
Compliance Period Begin (mo/day/yr) ........................………………. |  |  | 2019-04-01
Compliance Period End (mo/day/yr) ..........................……………….. |  |  | 2019-04-30
Number of Samples Required ....................................……………….. |  |  | 180
Number of Samples Taken .........................................………………. |  |  | 558
Highest Turbidity for Compliance Period ..................………………… |  |  | 0.08
Lowest Turbidity for Compliance Period ...................………………… |  |  | 0
Average Turbidity for Compliance Period ..................………………… |  |  | 0.06
Laboratory ID ..................................................................…………… |  |  | 26102
Laboratory Name ...........................................................……………. |  |  | GSWSA /BCSWTP
Comments:
Signature ________________________________ Date |  | 2019-05-07
William Lederman Plant Supervisor
This signature certifies that all samples were collected, analyzed and reported according to the State Primary Drinking
Water Regulations.
DHEC 1975 (Rev. 5/00)

## Distribution
Surface Water System Monthly Operation Report
Distribution System Disinfectant Residual Data
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: |  | 2016-08-01
Lab Cert ID #: 26102 |  |  | Lab # for lab conducting HPC analyses: 26102
Day | No. of Sites Disinfect. Residual was Measured | No. of Sites Disinfect. Residual NOT Measured, but HPC Measured | No. of Sites where Disinfect. Residual NOT Detected & HPC NOT Measured | No. of Sites where Disinfectant Residual was NOT Detected and HPC > 500/ml | No. of Sites Disinfect. Residual NOT Measured and HPC > 500/ml | Average Disinfectant Residual (mg/L)
1 |  | 0 | 0 | 0 | 0
2 |  | 0 | 0 | 0 | 0
3 |  | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 0 | 0
5 |  | 0 | 0 | 0 | 0
6 |  | 0 | 0 | 0 | 0
7 |  | 0 | 0 | 0 | 0
8 |  | 0 | 0 | 0 | 0
9 |  | 0 | 0 | 0 | 0
10 |  | 0 | 0 | 0 | 0
11 |  | 0 | 0 | 0 | 0
12 |  | 0 | 0 | 0 | 0
13 |  | 0 | 0 | 0 | 0
14 |  | 0 | 0 | 0 | 0
15 |  | 0 | 0 | 0 | 0
16 |  | 0 | 0 | 0 | 0
17 |  | 0 | 0 | 0 | 0
18 |  | 0 | 0 | 0 | 0
19 |  | 0 | 0 | 0 | 0
20 |  | 0 | 0 | 0 | 0
21 |  | 0 | 0 | 0 | 0
22 |  | 0 | 0 | 0 | 0
23 |  | 0 | 0 | 0 | 0
24 |  | 0 | 0 | 0 | 0
25 |  | 0 | 0 | 0 | 0
26 |  | 0 | 0 | 0 | 0
27 |  | 0 | 0 | 0 | 0
28 |  | 0 | 0 | 0 | 0
29 |  | 0 | 0 | 0 | 0
30 |  | 0 | 0 | 0 | 0
31 |  | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | Avg. Resid.
| a | b | c | d | e | #DIV/0!
Compliance with Distribution System Disinfectant Residual Criteria |  |  |  |  | #DIV/0!
V = ( c + d + e ) / ( a + b ) x 100 = ( + + ) / ( + ) x 100 =
For Previous Month: V =
Prepared by: __________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## Chloramine
Surface Water System Monthly Operation Report
For Systems Using Chlorine and/or Chloramines
To Maintain A Residual In The Distribution System
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | For (Month/yr): | 2016-08-01
Month/Year | *Average Residual |  | Quarterly Average (mg/L)
| Chlorine (mg/L) | Chloramines (mg/L)
2016-01-02 |  | 3.42 | 3.17
2016-02-03 |  | 2.79 |  | *Average residual values may be obtained from page 10 of 15 of this form
2016-03-03 |  | 3.3
2016-04-02 |  | 3.42 | 3.14
2016-05-03 |  | 3.46
2016-06-02 |  | 2.75
2016-07-02 |  | 3.42
2016-08-02 |  | 2.86
2016-09-02
2015-10-02 |  | 3.11 | 2.99
2015-11-02 |  | 2.78
2015-12-02 |  | 3.08
RAA at the end of the most recent quarter: |  |  | 3.1
Prepared by: _________________________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## TOC
Surface Water System Monthly Operation Report
Compliance With DBP Precursor Removal Requirements
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  |  | For (Month/yr): |  | 2016-08-01
Lab Cert ID #: 26102
Month | Source Water |  | Treated Water TOC (mg/L) | (A) Actual % TOC Removal | (B) Required % TOC Removal | Basis for Required % Removal | Removal Ratio (A) / (B) | Quarterly Average Ratio | RAA1 Ratio (Last 4 Quarters)
| Alkalinity (mg/L) | TOC (mg/L)
2016-01-01 | 14 | 21.88 | 4.05 | 81.4899 | 50 | Step 1 | 1.6298 | 1.51
2016-02-01 | 20 | 9.738 | 2.72 | 72.0682 | 50 | Step 1 | 1.4414
2016-03-01 | 14 | 10.23 | 2.81 | 72.5318 | 50 | Step 1 | 1.4506
2016-04-01 | 21 | 9.776 | 2.82 | 71.1538 | 50 | Step 1 | 1.4231 | 1.3387 | 1.37
2016-05-01 | 23 | 10.09 | 2.97 | 70.5649 | 50 | Step 1 | 1.4113
2016-06-01 | 23 | 8.579 | 3.51 | 59.0861 | 50 | Step 1 | 1.1817
2016-07-01 | 24 | 8.27 | 3.538 | 57.2189 | 50 | Step 1 | 1.1444
2016-08-01 | 22 | 11.4 | 3.69 | 67.6316 | 50 | Step 1 | 1.3526
2016-09-01
2015-10-01 | 21 | 12.04 | 3.49 | 71.0133 | 50 | Step 1 | 1.4203 | 1.5
2015-11-01 | 28 | 17.264 | 4.18 | 75.7878 | 50 | Step 1 | 1.5158
2015-12-01 | 18 | 18.612 | 4.11 | 77.9175 | 50 | Step 1 | 1.5583
1 RAA = Running Annual Average, Computed Quarterly
Alternate Criteria
**Should only be filled out if Alternate Criteria 3 or 4 are being used
Month | Source water |  |  |  | Finished water
| DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m) |  | DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m)
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
Alternate Criteria
Alt. 1 | Source Water TOC < 2.0 mg/L
Alt. 2 | Treated Water TOC < 2.0 mg/L
Alt. 3 | Source Water SUVA < 2.0 L/mg-m
Alt. 4 | Treated Water SUVA < 2.0 L/mg-m
Prepared by: ____________________________________________ | [5 empty] | Date:
(signature) Clint Elliott Lab Supervisor

## Bacteria(new)
Bacteriological Analysis Sample Summary
1. Please fill out page 2 of this form if you have a total coliform posative sample and repeat samples.
2. Submit this form to SCDHEC along with a copy of your labrotories chain of custody no later than ten (10) days after the end of the compliance period.
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
COMPLIANCE PERIOD |  |  | 2016-09-01
CYCLE |  |  | M
(Q)-QUARTERLY (M)-MONTHLY
CHLORINE RESIDUAL |  |  | #DIV/0!
Lab ID measuring chlorine residual |  |  | 26102
# OF INITIAL SAMPLES |  |  | 0
# OF INITIAL TC POSITIVE SAMPLES |  |  | 0
# OF E. COLI POSITIVE SAMPLES |  |  | 0
TOTAL COLIFORM ANALYSIS METHOD CODE |  |  | SM9223B-2004
E. COLI ANALYSIS METHOD |  |  | SM9223B-2004
Lab ID |  |  | 26102
SIGNATURE
Date
Bacteriological Analysis Individual Samples (Part 2)
PART 2 CAN BE USED FOR ALL TOTAL COLIFORM SAMPLES AND ASSOCIATED
REPEATS AND SOURCE WATER SAMPLES
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
LAB ID |  |  | #VALUE!
TYPE | REPEAT | LAB SAMPLE NUMBER | COLLECTION DATE (MM/DD/YYYY) | [7 empty] | SAMPLING LOCATION |  | SOURCE ID | TOTAL A/P | E.COLI A/P | TOTAL/FREE CHLORINE RESIDUAL
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
Explanation: | [11 empty] | Comments
Type (RT, RP or GW ) |  |  |  | RT = Routine; RP=Repeat; GW=Groundwater
Repeat (only if sample type =RP) |  |  |  | DN = Downstream; UP=Upstream;
Lab Sample # |  |  |  | # assigned by lab for that particular sample
Collection Date (mmddyyyy) |  |  |  | Date sample was collected
Sampling Location |  |  |  | Physical address where sample was collected
Source ID(only used for source samples) |  |  |  | 5 digit DHEC Source ID (ie. G_ _ _ _ _)
Total Coliform (A or P) |  |  |  | Indicate with an "A" if absent or a "P" if present
E. Coli = (A or P) |  |  |  | E = Ecoli Positive
Total/Free Chlorine Residual |  |  |  | Chlorine Residual Reading
Within 24 hours of learning of a total coliform-positive (TC+) sample result, REPEAT samples must be collected and analyzed for total coliforms:
One REPEAT sample must be collected from the same tap as the TC+ sample.
One REPEAT sample must be collected within five service connections upstream of the TC+ sample.
One REPEAT sample must be collected within five service connections downstream of the TC+ sample.
If the system is served by Ground water then a Triggered Source sample must be collected prior to treatment from each source in use at the time the total coliform-positive sample was collected. The number of samples taken PER WELL must equal the number of positive TCR samples. If you collected three TC+ samples, then three well samples must be taken at EACH WELL that was in service at the time.
The triggered source water sample must be analyzed for the presence of E.coli.
If any triggered source water sample is E.coli-positive, the Ground Water system (GWS) must either take corrective action, as directed by the state, or the GWS must take 5 additional source water sampleswithin 24 hours.
If the GW system Purchases some or all af there water they must notify the wholesale system (s) within 24 hours.
If any REPEAT sample is TC+:
The system must analyze that total coliform-positive culture for E.coli.
The system must collect another set of REPEAT samples, as before, unless the E.coli MCL has been violated or an assessment has been triggered.
For a system on quarterly monitoring, a TC+ result requires a minimum of three ROUTINE samples be collected the following month.
CALL SCDHEC on the same day you learned of the E. coli-positive (EC+) result, or by the end of the next business day if the result came in after business hours
Please submit a copy of your labrotories chain of custody along with this form.

## Bacteria
Bacteriological Analysis Sample Summary (Part 1)
PART 1 CAN BE USED IN ONE (1) OF TWO (2) WAYS
1. If the system has had no Total Coliform (TC) Positives samples for a compliance cycle or,
2. If the system wants to report those samples that were initial TC Absent and use Part 2 for
the TC Present and all repeats.
DESCRIPTION
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
0 | 4 | 0 | 1 | 2 | 0 | 1 | 6 | 2 |  |  |  |  | First day of month / quarter
1 | 2 | 0 | [10 empty] | # of Initial Total Coliform Negative
0 | 4 | 0 | 2 | 2 | 0 | 1 | 6 | [5 empty] | M=Month; Q=Quarter; Y=Year
| 2 | 6 | 1 | 0 | 2 |  |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
Note: This can be used for any system that does
not have a total coliform positive
DOES SYSTEM ADD DISINFECTION | [8 empty] | YES
AVERAGE DISINFECTION RESIDUAL | [8 empty] | 3 | . | 4 | 2
AND/OR
Bacteriological Analysis Individual Samples (Part 2)
NOTE: This form would only be used for the initial routine (RT) TC or TC/FC Positive and
and the Repeats that are required by regulation.
PART 2 CAN MUST BE USED FOR ALL TOTAL COLIFORM POSITIVES AND ALL ASSOCIATED
REPEATS
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
|  | 2 | 6 | 1 | 0 | 2 |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
[15 empty] | Total | Fecal (F) or | Free/Total
[13 empty] | TYPE | Lab Sample ID | Coliform | E Coli (E) + | Chlorine
SAMPLE ID # AND LOCATION | [8 empty] | COLLECTION DATE (MMDDYYYY) |  |  |  | (RT or RP) | Number | A/P | If Present | Residual*
.
.
.
.
.
.
Explanation:
Collection Date (mmddyyyy)………………..Date sample was collected
Lab Sample #…………………………………# assigned by lab for that particular sample
Type (RT or RP)………………………………RT = Routine; RP=Repeat
Sampling Point ID……………………………..If lab has something that identifies site other than physical location
Sampling Location……………………………Physical address where sample was collected from
Total Coliform (A or P)…………………….Indicate with an "A" if absent or a "P" if present
FC (F = FC+ or E = Ecoli+)…………………..F= Fecal Coliform Positive; E = Ecoli Positive
Total/Free Chlorine Residual…………………………Chlorine Residiual Reading

## TOC Sample ID
TOC SAMPLE ID LOG
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  | 2019-04-01
Lab Cert ID #: 26102
Treated | TOC | Raw | TOC | Alkalinity
D-02011608 |  | D-02011611 |  | 20
D-02011609
D-02011610

## Calculation for TOC
| TOC | [6 empty] | Sample Number | [5 empty] | Raw
| Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled |  | Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled | Alkalinity
Week 1
| 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 |  | D-07061506 | D-07061507 | D-07061511 | D-07061508 | D-07061509 | D-07061510 | 36
2.47
5.88
Week 2
#DIV/0!
#DIV/0!
Week 3
#DIV/0!
#DIV/0!
Week 4 | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786
2.931
7.579
Average | 2.7005 | 2.555 | 6.7295 | 4.2765 | 2.8045 | 2.619 | [5 empty] | Average Alkalinity Raw |  | 36
Max | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786 | 3.726
Min | 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 | 2.7407
Average Treated TOC |  |  | 3.2333
Average % TOC Removal |  |  | 51.9528
Max % TOC Removal |  |  | 59.2738
Min % TOC Removal |  |  | 44.6318
TOC Sample ID Number Submittal
Treated | TOC |  |  | Raw | TOC | Alkalinity

## Chem Cost
2019-04-01
Chemical Usage / Dosage / Cost
Chemical | Usage |  | Dosage (mg/l) |  |  | Cost ($) |  |  | Alternate Units |  |  | density as is |  | Purity
| Unit | Total | Average | Maximum | Minimum | $/Unit | Total $ | $/1000 gal water | Unit | Total | $/unit | g/ml | lb/gal | wt. % | lb/gal
Pre Chlorine | gals | 12546.6407 | 1.736 | 2.1267 | 1.4828 | 0.81 | 10162.779 | 0.01172 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Aluminum Sulfate | gals | 102358.1569 | 68.3291 | 85.8088 | 49.8977 | 1.69 | 172985.2852 | 0.1995 | lbs | 1133514.2298 | 0.15225 | 1.325 | 11.05 | 48.5 | 5.36
Pre Caustic | gals | 0 | 0 | 0 | 0 | 1.86 | 0 | 0 | lbs | 0 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Post Chlorine | gals | 23001.8127 | 3.8808 | 3.9548 | 3.7906 | 0.81 | 18631.4682 | 0.021487 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Ammonia | gals | 3381.7658 | 0.70779 | 0.75173 | 0.6123 | 0.68 | 2299.6008 | 0.002652 |  |  |  | 0.928 | 7.74 | 19.5 | 1.51
Post Caustic | gals | 8688.5236 | 7.3272 | 7.9062 | 6.5907 | 1.86 | 16160.654 | 0.018637 | lbs | 110865.5618 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Lime | gals | 71616.8623 | 22.227 | 32.8068 | 11.486 | 0.055 | 3938.9274 | 0.0045426
Fluoride | gals | 2313.4097 | 0.50433 | 0.52558 | 0.48602 | 3.2 | 7402.9111 | 0.0085375 | lbs | 23365.438
Activated Carbon | lbs | 16197.5216 | 2.049 | 2.9973 | 1.8714 | 0.89 | 14415.7942 | 0.016625
Polymer | gals | 155.7203 | 0.18202 | 0.21776 | 0.15868 | 11.95 | 1860.8582 | 0.0021461 | lbs | 1339.195 | 1.39
Filter Aid | gals | 58.4127 | 1.3699 | 1.3699 | 1.3699 | 5.59 | 326.5269 | 0.00037657 | lbs | 502.3491 | 0.65
Zinc Chloride Dosed as Zinc | gals | 184.8911 | 0.10034 | 0.11439 | 0.096122 | 6.89 | 1273.8996 | 0.0014691 | lbs | 2422.0732 | 0.526
Corrosion Inhibitor Dosed as Phosphorus | gals | 1651.7838 | 1.1133 | 1.2147 | 1.0905 | 11.72 | 19358.9057 | 0.022326 | lbs | 23950.8645 | 0.808
|  |  | Total Chemical Cost |  |  |  | 268817.6102
|  |  | Cost per 1000 gallons |  |  |  | 0.31002

## Extras
| TOC | [25 empty] | pH |  |  |  | Alkalinity |  |  |  | Hardness |  |  |  | Turbidity |  |  |  | Color |  |  |  | Temp |  |  |  | TRC |  |  | Fluoride |  |  | Flow (MG) |  |  |  | COLIFORM
| Finish1 | Finish2 | Raw |  | Conductivity |  |  | TDS |  |  | Chloride |  |  |  | Sodium |  |  | Sulfate |  |  | Iron |  |  | Manganese |  |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 |  | Finish1 | Finish2 |  | Raw | Finish1 | Finish2 |  | Raw | Finish1 | Finish2
Week 1 |  |  |  |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | 7.3383 | 7.2767 | 6.6367 |  | 20 | 20 | 19.3333 |  | 31.5 | 30.5 | 18.6667 |  | 0.064 | 0.064 | 10.1 |  | 1 | 1 | 85.3333 |  | 15.85 | 16 | 16.5833 |  | 3.9 | 3.8 |  | 0.5524 | 0.4619 |  | 31.023 | 13.178 | 13.66 |  | 86 | A | A
|  |  |  | Week 1 | [6 empty] | 11.1 | 11.3 | 7.27 |  |  |  |  | 21.8 | 21.9 | 7.46 | [6 empty] | 7.4083 | 7.4067 | 6.6367 |  | 20 | 20 | 19.3333 |  | 35 | 33 | 18.8333 |  | 0.063 | 0.068 | 10.3 |  | 1 | 1 | 81 |  | 15.3167 | 15.2 | 15.85 |  | 4.2 | 3.8 |  | 0.58 | 0.4924 |  | 11.163 | 11.163 | 17.165 |  | 187 | A | A
|  |  |  | Week 2 | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  |  |  |  | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.2683 | 7.21 | 6.5817 |  | 20.5 | 22 | 19.3333 |  | 32 | 33 | 18.8333 |  | 0.064 | 0.07 | 10.1 |  | 1 | 1 | 84 |  | 14.9 | 15.55 | 15.6833 |  | 3.4 | 3.3 |  | 0.5967 | 0.4586 |  | 11.341 | 11.341 | 15.857 |  | 399 | A | A
|  |  |  | Week 3 | [22 empty] | 7.17 | 7.1483 | 6.5767 |  | 21 | 21 | 18.6667 |  | 36.5 | 31.5 | 17 |  | 0.06 | 0.059 | 7.7 |  | 1 | 1 | 79.5 |  | 15.1333 | 16.2667 | 16.2667 |  | 3.8 | 3.6 |  | 0.5574 | 0.4752 |  | 11.582 | 11.582 | 15.629 |  | 85 | A | A
|  |  |  | Week 4 | [10 empty] | 13.3 | 13.5 | 9.1 | [9 empty] | 7.14 | 7.2233 | 6.6167 |  | 22 | 21.5 | 20.3333 |  | 33 | 32.5 | 18.5 |  | 0.06 | 0.062 | 7.18 |  | 1 | 1.1667 | 76.8333 |  | 15.6 | 16.4833 | 16.8333 |  | 3.8 | 3.5 |  | 0.5729 | 0.5753 |  | 11.575 | 11.575 | 15.323 |  | 75 | A | A
[27 empty] | 7.37 | 7.3533 | 6.6983 |  | 22 | 22.5 | 21 |  | 31 | 32 | 18.6667 |  | 0.058 | 0.058 | 7.75 |  | 1 | 1 | 74.3333 |  | 15.9333 | 16.7667 | 17.3 |  | 3.6 | 3.4 |  | 0.5961 | 0.4791 |  | 11.017 | 11.017 | 15.764 |  | 185 | A | A
#DIV/0! | [26 empty] | 7.485 | 7.4767 | 6.6433 |  | 21.5 | 21.5 | 19.3333 |  | 37.5 | 30.5 | 18.1667 |  | 0.055 | 0.052 | 7 |  | 1 | 1 | 77 |  | 16.3167 | 17.3667 | 17.85 |  | 3.6 | 3.7 |  | 0.5859 | 0.6139 |  | 11.901 | 11.901 | 15.339 |  | 132 | A | A
#DIV/0! |  |  |  | Average | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.8 | 11.95 | 8.535 |  | 13.3 | 13.5 | 9.1 | 23.65 | 23.8 | 8.705 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.27 | 7.2367 | 6.6417 |  | 25 | 22.5 | 20.3333 |  | 31 | 32 | 18.3333 |  | 0.06 | 0.06 | 6.2 |  | 1 | 1 | 77.6667 |  | 17.0833 | 18.0167 | 18.3833 |  | 3.8 | 3.2 |  | 0.5991 | 0.4453 |  | 9.529 | 9.529 | 16.876 |  | 63 | A | A
Week 2 | 2.74 | 2.51 | 7.02 | Max | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  | 13.3 | 13.5 | 9.1 | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.2683 | 7.3417 | 6.5967 |  | 21 | 21.5 | 20.8333 |  | 32 | 33.5 | 18 |  | 0.061 | 0.06 | 6.15 |  | 1 | 1 | 79.1667 |  | 18.1167 | 18.35 | 19.4333 |  | 4 | 3.7 |  | 0.5899 | 0.4725 |  | 11.939 | 11.939 | 15.844 |  | 41 | A | A
|  |  |  | Min | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.1 | 11.3 | 7.27 |  | 13.3 | 13.5 | 9.1 | 21.8 | 21.9 | 7.46 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.335 | 7.2533 | 6.5767 |  | 20.5 | 22.5 | 19.5 |  | 39 | 37.5 | 19.1667 |  | 0.06 | 0.062 | 5.31 |  | 1 | 1 | 79.3333 |  | 18.6333 | 18.5333 | 19.6167 |  | 4.2 | 3.6 |  | 0.6601 | 0.529 |  | 11.757 | 11.757 | 16.067 |  | 20 | A | A
[27 empty] | 7.3683 | 7.3067 | 6.5433 |  | 23.5 | 22 | 19 |  | 36.5 | 38.5 | 18 |  | 0.062 | 0.067 | 4.56 |  | 1 | 1 | 87.6667 |  | 19.0667 | 18.7 | 20.0167 |  | 4 | 3.7 |  | 0.6141 | 0.5226 |  | 11.592 | 11.592 | 15.681 |  | 52 | A | A
[15 empty] | Flow (MG) | [11 empty] | 7.3533 | 7.27 | 6.5133 |  | 24 | 26 | 19.1667 |  | 40.5 | 39 | 17.8333 |  | 0.066 | 0.071 | 3.92 |  | 1.1667 | 1.1667 | 91.1667 |  | 19.4833 | 19.1667 | 20.8 |  | 4.2 | 3.8 |  | 0.6257 | 0.5439 |  | 11.823 | 11.823 | 16.398 |  | 41 | A | A
[15 empty] | Raw | Comb Fin |  |  | Aluminum |  |  | Phosph Fin1 |  | Phosph Fin2 |  |  | 7.33 | 7.3183 | 6.5017 |  | 20.5 | 20 | 18.6667 |  | 35.5 | 37 | 18 |  | 0.073 | 0.08 | 4.68 |  | 1 | 1 | 95 |  | 19.8 | 19.4167 | 20.5167 |  | 4.2 | 3.7 |  | 0.6134 | 0.5229 |  | 12.721 | 12.721 | 14.7 |  | 132 | A | A
[14 empty] | 1 | 31.023 | 26.838 |  |  | 1 Filter | 2 Filter | 3 Filter | Total | Ortho | Total | Ortho |  | 7.465 | 7.3783 | 6.4717 |  | 20 | 20.5 | 18.1667 |  | 35 | 37 | 18 |  | 0.077 | 0.081 | 4.8 |  | 1 | 1 | 100 |  | 20.1667 | 19.4833 | 21.0167 |  | 4.2 | 3.6 |  | 0.5932 | 0.5424 |  | 12.69 | 12.69 | 15.62 |  | 75 | A | A
2.74 | [13 empty] | 2 | 26.83 | 28.328 |  | Week 1 |  |  |  | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.3983 | 7.53 | 6.4433 |  | 23.5 | 24.5 | 19 |  | 45.5 | 46.5 | 18 |  | 0.078 | 0.084 | 4.77 |  | 3.2 | 1.1667 | 107.8333 |  | 20.3 | 20 | 20.7667 |  | 4.1 | 3.8 |  | 0.5742 | 0.6702 |  | 13.849 | 13.849 | 15.926 |  | 97 | A | A
7.02 | [13 empty] | 3 | 29.927 | 27.198 |  | Week 2 | 0.036 | 0.036 | 0.029 | [5 empty] | 7.5133 | 7.4917 | 6.4367 |  | 24.5 | 25 | 19 |  | 48 | 46.5 | 18.3333 |  | 0.08 | 0.079 | 4.63 |  | 1.1667 | 1 | 108.5 |  | 19.9167 | 19.4167 | 20.55 |  | 4.2 | 3.8 |  | 0.6304 | 0.5082 |  | 13.444 | 13.444 | 16.431 |  | 160 | A | A
Week 3 | [13 empty] | 4 | 29.878 | 27.211 |  | Week 3 |  |  |  | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.2208 | 7.2683 | 6.4617 |  | 25 | 23.5 | 19.5 |  | 44.5 | 42 | 17.1667 |  | 0.067 | 0.065 | 4.66 |  | 1.1667 | 1.1667 | 106.6667 |  | 19.8667 | 19.9667 | 20.7667 |  | 3.9 | 3.9 |  | 0.6254 | 0.5061 |  | 13.635 | 13.635 | 15.684 |  | 52 | A | A
[14 empty] | 5 | 29.629 | 26.898 |  | Week 4 | [8 empty] | 7.2733 | 7.3317 | 6.5117 |  | 24.5 | 25 | 19.6667 |  | 46 | 47 | 17.5 |  | 0.071 | 0.071 | 6.15 |  | 1.5 | 1.5 | 108.3333 |  | 20.05 | 20.0167 | 20.6 |  | 4 | 3.9 |  | 0.613 | 0.6031 |  | 13.945 | 13.945 | 17.706 |  | 294 | A | A
[14 empty] | 6 | 29.173 | 26.781 | [10 empty] | 7.4833 | 7.3517 | 6.5467 |  | 26.5 | 25.5 | 19.1667 |  | 46.5 | 46.5 | 17.5 |  | 0.068 | 0.07 | 5.9 |  | 1.3333 | 1.3333 | 110.1667 |  | 20.2833 | 20.1333 | 21.0167 |  | 3.6 | 3.7 |  | 0.624 | 0.5176 |  | 11.224 | 11.224 | 15.664 |  | 259 | A | A
[14 empty] | 7 | 29.225 | 27.24 | [10 empty] | 7.4817 | 7.375 | 6.5033 |  | 21.5 | 22 | 19 |  | 38 | 38 | 17.5 |  | 0.059 | 0.059 | 5.63 |  | 1.6667 | 1.3333 | 114.6667 |  | 20.3167 | 20.3167 | 20.8333 |  | 3.8 | 3.5 |  | 0.5836 | 0.4535 |  | 10.444 | 10.444 | 13.312 |  | 189 | A | A
[14 empty] | 8 | 31.116 | 26.405 |  | Average | 0.036 | 0.036 | 0.029 | 0.681 | 0.048 | 0.6905 | 0.0445 |  | 7.3583 | 7.2867 | 6.525 |  | 21.5 | 21 | 18.6667 |  | 38.5 | 39 | 17.5 |  | 0.059 | 0.058 | 6.24 |  | 1.3333 | 1.3333 | 118.6667 |  | 19.9667 | 19.8 | 20.1333 |  | 3.9 | 3.6 |  | 0.6185 | 0.6541 |  | 10.795 | 10.795 | 14.789 |  | 228 | A | A
[14 empty] | 9 | 30.636 | 27.783 |  | Max | 0.036 | 0.036 | 0.029 | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.35 | 7.2933 | 6.5217 |  | 23 | 22.5 | 20.1667 |  | 48.5 | 46.5 | 17.5 |  | 0.064 | 0.07 | 6.41 |  | 1.8333 | 1.6667 | 124.6667 |  | 19.0667 | 19.3667 | 19.7833 |  | 3.9 | 3.6 |  | 0.5981 | 0.5103 |  | 12.613 | 12.613 | 16.191 |  | 327 | A | A
#DIV/0! | [13 empty] | 10 | 29.183 | 27.824 |  | Min | 0.036 | 0.036 | 0.029 | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.23 | 7.2933 | 6.525 |  | 24 | 23.5 | 19.5 |  | 45 | 53 | 17.8333 |  | 0.06 | 0.07 | 6.58 |  | 2 | 1.6667 | 128.5 |  | 19.1167 | 19.7667 | 19.7167 |  | 3.8 | 3.6 |  | 0.6006 | 0.4747 |  | 13.79 | 13.79 | 17.2 |  | 243 | A | A
#DIV/0! | [13 empty] | 11 | 29.659 | 27.273 | [10 empty] | 7.23 | 7.2283 | 6.5667 |  | 20.5 | 21 | 18.6667 |  | 44.5 | 45 | 17.6667 |  | 0.069 | 0.066 | 6.52 |  | 1.8333 | 1.8333 | 128 |  | 19.45 | 19.8 | 19.95 |  | 4.1 | 3.9 |  | 0.5541 | 0.7983 |  | 11.722 | 11.722 | 17.118 |  | 295 | A | A
Week 4 | [13 empty] | 12 | 31.356 | 28.221 |  | Average 1,2,3 |  | 0.033667 | [6 empty] | 7.3817 | 7.3183 | 6.535 |  | 21 | 21.5 | 18.5 |  | 47 | 49.5 | 18 |  | 0.071 | 0.076 | 6.71 |  | 2 | 2 | 128.5 |  | 19.8 | 20.0667 | 20.45 |  | 4 | 3.9 |  | 0.6331 | 0.5272 |  | 13.308 | 13.308 | 16.736 |  | 350 | A | A
[14 empty] | 13 | 29.827 | 27.421 | [10 empty] | 7.4167 | 7.305 | 6.54 |  | 20.5 | 20.5 | 17.6667 |  | 42.5 | 46 | 18 |  | 0.07 | 0.073 | 6.76 |  | 2 | 2 | 127.1667 |  | 20.35 | 20.5 | 21.0833 |  | 4 | 3.8 |  | 0.5905 | 0.5082 |  | 14.582 | 14.582 | 20.31 |  | 369 | A | A
[14 empty] | 14 | 30.345 | 28.31 | [8 empty] | Day |  | 7.28 | 7.3383 | 6.525 |  | 20.5 | 20 | 18 |  | 42.5 | 45.5 | 17.8333 |  | 0.072 | 0.077 | 6.7 |  | 2 | 2 | 124.6667 |  | 20.1667 | 20.15 | 21.05 |  | 4 | 3.8 |  | 0.5795 | 0.5437 |  | 14.21 | 14.21 | 14.618 |  | 480 | A | A
[14 empty] | 15 | 32.17 | 29.775 | [8 empty] | 28 |  | 7.3017 | 7.2867 | 6.565 |  | 20 | 20 | 18.6667 |  | 25.15 | 47 | 18 |  | 0.073 | 0.076 | 6.83 |  | 1.5 | 2 | 123.8333 |  | 20.4333 | 20.35 | 20.95 |  | 4.1 | 4.1 |  | 0.6453 | 0.5183 |  | 14.923 | 14.923 | 19.887 |  | 408 | A | A
[14 empty] | 16 | 32.464 | 29.875 | [8 empty] | 29 |  | 7.2083 | 7.1267 | 6.5533 |  | 21.5 | 22 | 19 |  | 42.5 | 45 | 17.6667 |  | 0.069 | 0.073 | 7.23 |  | 1.6667 | 1.5 | 123.5 |  | 20.8333 | 20.6 | 21.55 |  | 3.4 | 2.8 |  | 0.6402 | 0.496 |  | 14.815 | 14.815 | 20.61 |  | 441 | A | A
#DIV/0! | [13 empty] | 17 | 32.662 | 29.319 | [8 empty] | 30 |  | 7.3417 | 7.1683 | 6.5683 |  | 21 | 21.5 | 19.5 |  | 41.5 | 44.5 | 18 |  | 0.071 | 0.073 | 7.96 |  | 2 | 2 | 120.8333 |  | 21.2667 | 21.2333 | 21.7667 |  | 4.1 | 3.7 |  | 0.6219 | 0.5312 |  | 14.837 | 14.837 | 19.059 |  | 350 | A | A
#DIV/0! | [13 empty] | 18 | 34.596 | 31.651 | [8 empty] | 31 | [31 empty] | 0 | 0 | 0 |  | 0 | A | A
Average | 2.74 | 2.51 | 7.02 | [10 empty] | 19 | 29.5 | 26.888 | [8 empty] | Avg 1 |  | 7.3063 | 7.2915 | 6.629 | Avg 1 | 21.5 | 21.375 | 19.7083 | Avg 1 | 33.4375 | 31.875 | 18.375 | Avg 1 | 0.0605 | 0.061625 | 8.2912 | Avg 1 | 1 | 1.0208 | 79.4583 | Avg 1 | 15.7667 | 16.4562 | 16.8438 | Avg 1 | 3.7625 | 3.5375 | Avg 1 | 0.58006 | 0.50021 | Avg 1 | 13.6414 | 11.4107 | 15.7016 | Avg 1 | 151.5
Max | 2.74 | 2.51 | 7.02 | [10 empty] | 20 | 25.901 | 23.756 | [8 empty] | Avg 2 |  | 7.3598 | 7.3426 | 6.521 | Avg 2 | 21.8571 | 22.4286 | 19.1905 | Avg 2 | 37.7143 | 38.4286 | 18.1429 | Avg 2 | 0.068143 | 0.072143 | 4.8843 | Avg 2 | 1.3381 | 1.0476 | 91.4524 | Avg 2 | 19.3667 | 19.0929 | 20.3095 | Avg 2 | 4.1286 | 3.7 | Avg 2 | 0.61009 | 0.54336 | Avg 2 | 12.3387 | 12.3387 | 15.748 | Avg 2 | 65.4286
Min | 2.74 | 2.51 | 7.02 | [10 empty] | 21 | 28.486 | 25.584 | [8 empty] | Avg 3 |  | 7.3639 | 7.3365 | 6.504 | Avg 3 | 23.8125 | 23.5 | 19.3333 | Avg 3 | 44.375 | 44.8125 | 17.6042 | Avg 3 | 0.066 | 0.06775 | 5.775 | Avg 3 | 1.5 | 1.375 | 115.0208 | Avg 3 | 19.8229 | 19.8479 | 20.425 | Avg 3 | 3.8875 | 3.7 | Avg 3 | 0.6117 | 0.52845 | Avg 3 | 12.4863 | 12.4863 | 15.8721 | Avg 3 | 219
[14 empty] | 22 | 30.993 | 28.804 | [8 empty] | Avg 4 |  | 7.3086 | 7.2531 | 6.5505 | Avg 4 | 20.7143 | 20.9286 | 18.5714 | Avg 4 | 40.8071 | 46.0714 | 17.881 | Avg 4 | 0.070714 | 0.073429 | 6.9586 | Avg 4 | 1.8571 | 1.9048 | 125.2143 | Avg 4 | 20.3286 | 20.3857 | 20.9714 | Avg 4 | 3.9571 | 3.7143 | Avg 4 | 0.60923 | 0.56041 | Avg 4 | 12.2996 | 12.2996 | 16.0422 | Avg 4 | 336.625
Fin1 | [13 empty] | 23 | 33.817 | 30.99 | [12 empty] | pH | Alk | Hard |  | Turb | Color | Temp |  | Coliform | TRC | Fluoride
CCR Data | High |  | Low | Avg | [9 empty] | 24 | 29.7 | 28.84 | [8 empty] | Avg 1 |  | Raw |  | 6.629 | 19.7083 | 18.375 |  | 8.2912 | 79.4583 | 16.8438 |  | 151.5
Turbidity | 0.08 |  | 0 | 0.06 | [9 empty] | 25 | 34.274 | 30.044 | [8 empty] | Avg 2 |  |  |  | 6.521 | 19.1905 | 18.1429 |  | 4.8843 | 91.4524 | 20.3095 |  | 65.4286
Fluoride | 0.6601 |  | 0.5524 | 0.60231 | [9 empty] | 26 | 36.477 | 34.892 | [8 empty] | Avg 3 |  |  |  | 6.504 | 19.3333 | 17.6042 |  | 5.775 | 115.0208 | 20.425 |  | 219
Sulfate | 25.5 |  | 21.8 | 23.65 | [9 empty] | 27 | 36.581 | 28.828 | [8 empty] | Avg 4 |  |  |  | 6.5505 | 18.5714 | 17.881 |  | 6.9586 | 125.2143 | 20.9714 |  | 336.625
Iron | 0.003 |  | 0.003 | 0.003 | [9 empty] | 28 | 38.496 | 34.81 | [8 empty] | Avg 1 |  | Finished |  | 7.3063 | 21.5 | 33.4375 |  | 0.0605 | 1 | 15.7667 |  |  | 3.7625 | 0.58006
Manganes | 0.029 |  | 0.029 | 0.029 | [9 empty] | 29 | 38.162 | 35.425 | [8 empty] | Avg 2 |  |  |  | 7.3598 | 21.8571 | 37.7143 |  | 0.068143 | 1.3381 | 19.3667 |  |  | 4.1286 | 0.61009
pH | 7.5133 |  | 7.14 | 7.3346 | [9 empty] | 30 | 39.048 | 33.896 | [8 empty] | Avg 3 |  |  |  | 7.3639 | 23.8125 | 44.375 |  | 0.066 | 1.5 | 19.8229 |  |  | 3.8875 | 0.6117
Color | 3.2 |  | 1 | 1.4122 | [9 empty] | 31 | [10 empty] | Avg 4 |  |  |  | 7.3086 | 20.7143 | 40.8071 |  | 0.070714 | 1.8571 | 20.3286 |  |  | 3.9571 | 0.60923
Chloride | 12.5 |  | 11.1 | 11.8
TOC | 2.74 |  | 2.74 | 2.74
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.681
o-phosph |  |  |  | 0.048
Aluminum |  |  |  | 0.033667
Fin2
CCR Data | High |  | Low | Avg
Turbidity | 0.08 |  | 0 | 0.060118
Fluoride | 0.7983 |  | 0.4453 | 0.53186
Sulfate | 25.7 |  | 21.9 | 23.8
Iron | 0.006 |  | 0.006 | 0.006
Manganes | 0.033 |  | 0.033 | 0.033
pH | 7.53 |  | 7.1267 | 7.3064
Color | 2 |  | 1 | 1.3278
Chloride | 12.6 |  | 11.3 | 11.95
TOC | 2.51 |  | 2.51 | 2.51
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.6905
o-phosph |  |  |  | 0.0445
Aluminum |  |  |  | 0.033667
TOC Ratio |  |  |  | #REF!
TOC % Removal |  |  |  | #REF!

## LAB
DAILY LAB SHEET
2019-04-01
| RAW | [13 empty] | Filtered #1 |  |  |  | Filtered #2 |  |  |  | Filtered #3 |  |  |  | Treated #1 | Treated #2 | Treated #3 | Settled #1 | [11 empty] | Settled #2 | [11 empty] | Settled #3 | [12 empty] | Finished Plant #1 | [16 empty] | Finished Plant #2
| pH | Temp | Alk | DO | TOC | DOC | UV-254 | SUVA | Factor | Low | High | Total Coliform | E. coli | Temp. °C | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | pH | pH | pH | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Settled Water Average TOC | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T |  | Decant Flow | Back Wash Water | Backwash Waste Sludge flow | Alum sludge | Raw
1 | [11 empty] | 86 | <10 | [62 empty] | 0.5524 | [6 empty] | A | [9 empty] | 0.4619 | [6 empty] | A |  | 0.555 | 0 | 0 | 0
2 | [11 empty] | 187 | <10 | [62 empty] | 0.58 | [6 empty] | A | [9 empty] | 0.4924 | [6 empty] | A |  | 0.745 | 0 | 0 | 0
3 | [11 empty] | 399 | 20 | [62 empty] | 0.5967 | [6 empty] | A | [9 empty] | 0.4586 | [6 empty] | A |  | 0.75 | 0 | 0 | 0
4 | [11 empty] | 85 | 10 | [62 empty] | 0.5574 | [6 empty] | A | [9 empty] | 0.4752 | [6 empty] | A |  | 0.617 | 0 | 0 | 0
5 | [11 empty] | 75 | <10 | [62 empty] | 0.5729 | [6 empty] | A | [9 empty] | 0.5753 | [6 empty] | A |  | 0.645 | 0 | 0 | 0
6 | [11 empty] | 185 | <10 | [62 empty] | 0.5961 | [6 empty] | A | [9 empty] | 0.4791 | [6 empty] | A |  | 0.474 | 0 | 0 | 0
7 | [11 empty] | 132 | <10 | [62 empty] | 0.5859 | [6 empty] | A | [9 empty] | 0.6139 | [6 empty] | A |  | 0.674 | 0 | 0 | 0
8 | 6.77 | 17.8 | 28 |  | 7.518 | 7.396 | 0.351 | 4.746 | 21.0712 | 105.3561 | 210.7123 | 63 | 10 |  |  | 2 | 0.066 | 0.36 |  | 3 | 0.08 | 0.37 |  | 2 | 0.068 | 0.31 | 5.96 | 5.97 | 5.94 |  |  |  | 6.03 | 16.8 | 7 | 0.544 | 2.407 | 2.312 | 0.052 | 67.9835 | 2.2491 |  |  |  | 6.08 | 17.2 | 6 | 0.47 | 2.365 | 2.301 | 0.052 | 68.5422 | 2.2599 |  |  |  | 6.05 | 17.7 | 5 | 0.306 | 2.375 | 2.365 | 0.051 | 68.4092 | 2.1564 | 2.3823 | 7.31 | 17.1 | 2 | 0.061 | 26 | 35 | 4.2 |  |  | 0.5991 |  |  | 2.27 | 2.312 | 0.071 | 3.0709 | A | 7.25 | 17 | 2 | 0.059 | 23 | 37 | 4 |  |  | 0.4453 |  |  | 2.267 | 2.32 | 0.07 | 3.0172 | A |  | 0.665 | 0 | 0 | 0
9 | 6.74 | 18.8 | [9 empty] | 41 | <10 |  |  | 2 | 0.067 | 0.32 |  | 2 | 0.071 | 0.4 |  | 1 | 0.055 | 0.35 | 5.98 | 6.06 | 5.9 |  |  |  | 5.99 | 18.2 | 8 | 0.501 | [8 empty] | 6.02 | 18.5 | 6 | 0.375 | [8 empty] | 6.01 | 19 | 6 | 0.334 | [6 empty] | 7.28 | 18.3 | 2 | 0.059 | 21 | 40 | 4.4 |  |  | 0.5899 | [6 empty] | A | 7.26 | 17.7 | 3 | 0.062 | 23 | 41 | 4.2 |  |  | 0.4725 | [6 empty] | A |  | 0.774 | 0 | 0 | 0
10 | 6.69 | 19.2 | [9 empty] | 20 | 10 |  |  | 2 | 0.059 | 0.33 |  | 2 | 0.065 | 0.44 |  | 2 | 0.07 | 0.45 | 5.91 | 5.96 | 5.89 |  |  |  | 5.99 | 18.5 | 7 | 0.487 | [8 empty] | 6.03 | 18.8 | 6 | 0.354 | [8 empty] | 6.03 | 19.2 | 5 | 0.311 | [6 empty] | 7.26 | 18.7 | 2 | 0.058 | 21 | 45 | 4.4 |  |  | 0.6601 | [6 empty] | A | 7.18 | 18 | 2 | 0.062 | 25 | 40 | 3.9 |  |  | 0.529 | [6 empty] | A |  | 0.59 | 0 | 0 | 0
11 | 6.66 | 19.7 | 23 |  | 8.394 | 8.262 | 0.361 | 4.369 | 22.8864 | 114.4321 | 228.8643 | 52 | <10 |  |  | 2 | 0.062 | 0.32 |  | 2 | 0.063 | 0.3 |  | 3 | 0.082 | 0.35 | 6 | 6.05 | 5.94 |  |  |  | 6.07 | 18.9 | 9 | 0.642 | 2.831 | 2.724 | 0.045 | 66.2735 | 1.652 |  |  |  | 6.1 | 19.1 | 8 | 0.458 | 2.759 | 2.697 | 0.046 | 67.1313 | 1.7056 |  |  |  | 6.07 | 19.7 | 6 | 0.408 | 2.781 | 2.684 | 0.045 | 66.8692 | 1.6766 | 2.7903 | 7.31 | 19.1 | 2 | 0.062 | 25 | 38 | 4.2 |  |  | 0.6141 |  |  | 2.647 | 2.645 | 0.065 | 2.4575 | A | 7.23 | 18.4 | 2 | 0.062 | 23 | 41 | 3.8 |  |  | 0.5226 |  |  | 2.638 | 2.686 | 0.063 | 2.3455 | A |  | 0.77 | 0 | 0 | 0
12 | 6.61 | 20.5 | [9 empty] | 41 | <10 |  |  | 3 | 0.074 | 0.31 |  | 2 | 0.063 | 0.28 |  | 3 | 0.081 | 0.31 | 5.91 | 5.99 | 5.96 |  |  |  | 6.04 | 19.6 | 9 | 0.525 | [8 empty] | 6.09 | 19.8 | 10 | 0.444 | [8 empty] | 6.06 | 20.3 | 6 | 0.394 | [6 empty] | 7.16 | 19.6 | 2 | 0.061 | 27 | 42 | 4.2 |  |  | 0.6257 | [6 empty] | A | 7.17 | 18.8 | 2 | 0.066 | 29 | 41 | 3.8 |  |  | 0.5439 | [6 empty] | A |  | 0.711 | 0 | 0 | 0
13 | [11 empty] | 132 | <10 | [62 empty] | 0.6134 | [6 empty] | A | [9 empty] | 0.5229 | [6 empty] | A |  | 0.741 | 0 | 0 | 0
14 | [11 empty] | 75 | >10 | [62 empty] | 0.5932 | [6 empty] | A | [9 empty] | 0.5424 | [6 empty] | A |  | 0.623 | 0 | 0 | 0
15 | 6.61 | 20.4 | 24 |  | 9.949 | 9.755 | 0.444 | 4.552 | 21.9707 | 109.8536 | 219.7072 | 97 | <10 |  |  | 3 | 0.071 | 0.12 |  | 4 | 0.097 | 0.18 |  | 5 | 0.144 | 0.06 | 5.86 | 6.02 | 5.97 |  |  |  | 6.06 | 20.7 | 9 | 0.466 | 3.198 | 3.126 | 0.055 | 67.8561 | 1.7594 |  |  |  | 6.1 | 20.7 | 12 | 0.668 | 3.258 | 3.094 | 0.057 | 67.253 | 1.8423 |  |  |  | 6.11 | 21.3 | 14 | 0.885 | 3.403 | 3.137 | 0.056 | 65.7956 | 1.7851 | 3.2863 | 7.38 | 19.9 | 2 | 0.07 | 26 | 50 | 4 |  |  | 0.5742 |  |  | 3.06 | 3.083 | 0.075 | 2.4327 | A | 8.2 | 19.8 | 2 | 0.093 | 28 | 50 | 5.7 |  |  | 0.6702 |  |  | 3.078 | 3.114 | 0.078 | 2.5048 | A |  | 0.701 | 0 | 0 | 0
16 | 6.56 | 20.5 | [9 empty] | 160 | <10 |  |  | 2 | 0.107 | 0.38 |  | 2 | 0.065 | 0.24 |  | 2 | 0.073 | 0.34 | 6.09 | 6.13 | 6.02 |  |  |  | 6.15 | 20 | 7 | 0.474 | [8 empty] | 6.16 | 20.1 | 8 | 0.529 | [8 empty] | 6.14 | 20.7 | 8 | 0.495 | [6 empty] | 7.39 | 19.9 | 2 | 0.074 | 28 | 52 | 4.3 |  |  | 0.6304 | [6 empty] | A | 7.39 | 19.3 | 2 | 0.071 | 29 | 47 | 4.1 |  |  | 0.5082 | [6 empty] | A |  | 0.753 | 0 | 0 | 0
17 | 6.54 | 20.1 | [9 empty] | 52 | <10 |  |  | 3 | 0.074 | 0.37 |  | 4 | 0.062 | 0.3 |  | 3 | 0.063 | 0.25 | 6.02 | 6.07 | 5.99 |  |  |  | 6.11 | 19.6 | 7 | 0.342 | [8 empty] | 6.15 | 19.3 | 9 | 0.455 | [8 empty] | 6.15 | 19.5 | 10 | 0.548 | [6 empty] | 7.27 | 19.5 | 3 | 0.066 | 30 | 54 | 4.3 |  |  | 0.6254 | [6 empty] | A | 7.26 | 19.1 | 3 | 0.065 | 26 | 49 | 3.9 |  |  | 0.5061 | [6 empty] | A |  | 0.623 | 0 | 0 | 0
18 | 6.6 | 20.3 | 29 |  | 10.34 | 9.859 | 0.46 | 4.666 | 21.4326 | 107.163 | 214.3261 | 294 | 10 |  |  | 2 | 0.076 | 0.34 |  | 2 | 0.074 | 0.54 |  | 2 | 0.078 | 0.44 | 5.99 | 6.05 | 5.98 |  |  |  | 6.12 | 19.8 | 7 | 0.433 | 3.082 | 2.991 | 0.051 | 70.1934 | 1.7051 |  |  |  | 6.15 | 19.8 | 7 | 0.461 | 3.06 | 2.99 | 0.053 | 70.4062 | 1.7726 |  |  |  | 6.14 | 19.7 | 8 | 0.483 | 3.089 | 2.991 | 0.051 | 70.1257 | 1.7051 | 3.077 | 7.21 | 19.6 | 2 | 0.071 | 28 | 53 | 4.5 |  |  | 0.613 |  |  | 2.935 | 3.237 | 0.073 | 2.2552 | A | 7.55 | 19.1 | 3 | 0.071 | 28 | 53 | 5.2 |  |  | 0.6031 |  |  | 2.911 | 2.982 | 0.077 | 2.5822 | A |  | 0.907 | 0 | 0 | 0
19 | 6.65 | 20.7 | [9 empty] | 259 | <10 |  |  | 2 | 0.066 | 0.42 |  | 2 | 0.068 | 0.57 |  | 2 | 0.073 | 0.41 | 6.1 | 6.04 | 6.11 |  |  |  | 6.16 | 20.6 | 5 | 0.31 | [8 empty] | 6.2 | 20.6 | 6 | 0.352 | [8 empty] | 6.2 | 20.4 | 7 | 0.45 | [6 empty] | 7.37 | 19.9 | 2 | 0.068 | 30 | 55 | 4.4 |  |  | 0.624 | [6 empty] | A | 7.35 | 19.7 | 2 | 0.07 | 29 | 50 | 4.1 |  |  | 0.5176 | [6 empty] | A |  | 0.894 | 0 | 0 | 0
20 | [11 empty] | 189 | <10 | [62 empty] | 0.5836 | [6 empty] | A | [9 empty] | 0.4535 | [6 empty] | A |  | 0.63 | 0 | 0 | 0
21 | [11 empty] | 228 | <10 | [62 empty] | 0.6185 | [6 empty] | A | [9 empty] | 0.6541 | [6 empty] | A |  | 0.784 | 0 | 0 | 0
22 | 6.64 | 19.2 | 25 |  | 10.74 | 10.89 | 0.496 | 4.555 | 21.9556 | 109.7782 | 219.5565 | 327 | <10 |  |  | 4 | 0.072 | 0.34 |  | 4 | 0.075 | 0.51 |  | 4 | 0.074 | 0.3 | 5.84 | 5.89 | 5.85 |  |  |  | 6.06 | 18.6 | 7 | 0.412 | 3.09 | 3.004 | 0.052 | 71.2291 | 1.731 |  |  |  | 6.08 | 18.6 | 9 | 0.504 | 3.088 | 2.96 | 0.051 | 71.2477 | 1.723 |  |  |  | 6.06 | 18.4 | 9 | 0.546 | 3.112 | 2.994 | 0.052 | 71.0242 | 1.7368 | 3.0967 | 7.37 | 18.5 | 4 | 0.064 | 25 | 52 | 4.4 |  |  | 0.5981 |  |  | 2.955 | 2.983 | 0.074 | 2.4807 | A | 7.33 | 18.7 | 4 | 0.07 | 23 | 52 | 4.2 |  |  | 0.5103 |  |  | 2.931 | 2.986 | 0.074 | 2.4782 | A |  | 0.842 | 0 | 0 | 0
23 | 6.62 | 19.3 | [9 empty] | 243 | <10 |  |  | 2 | 0.062 | 0.34 |  | 3 | 0.065 | 0.48 |  | 2 | 0.064 | 0.3 | 6.06 | 6.16 | 6.02 |  |  |  | 6.08 | 18.8 | 7 | 0.415 | [8 empty] | 6.11 | 18.8 | 9 | 0.492 | [8 empty] | 6.13 | 18.6 | 7 | 0.433 | [6 empty] | 7.29 | 18.3 | 3 | 0.0612 | 26 | 50 | 4.3 |  |  | 0.6006 | [6 empty] | A | 7.23 | 18.9 | 4 | 0.066 | 24 | 57 | 4.1 |  |  | 0.4747 | [6 empty] | A |  | 0.565 | 0 | 0 | 0
24 | [11 empty] | 295 | <10 | [62 empty] | 0.5541 | [6 empty] | A | [9 empty] | 0.7983 | [6 empty] | A |  | 0.917 | 0 | 0 | 0
25 | 6.65 | 20.3 | 24 |  | 10.83 | 10.65 | 0.492 | 4.62 | 21.6463 | 108.2317 | 216.4634 | 350 | 10 |  |  | 2 | 0.071 | 0.41 |  | 3 | 0.069 | 0.36 |  | 2 | 0.079 | 0.33 | 6.08 | 6.14 | 6.09 |  |  |  | 6.13 | 20.1 | 5 | 0.286 | 3.011 | 3.012 | 0.056 | 72.1976 | 1.8592 |  |  |  | 6.14 | 19.9 | 9 | 0.478 | 3.086 | 2.992 | 0.053 | 71.5051 | 1.7714 |  |  |  | 6.13 | 19.9 | 9 | 0.476 | 3.1 | 3.003 | 0.053 | 71.3758 | 1.7649 | 3.0657 | 7.28 | 19.8 | 3 | 0.064 | 27 | 60 | 4.4 |  |  | 0.6331 |  |  | 2.977 | 3.03 | 0.073 | 2.4092 | A | 7.27 | 19.4 | 3 | 0.074 | 27 | 56 | 4.2 |  |  | 0.5272 |  |  | 2.931 | 2.982 | 0.071 | 2.381 | A |  | 0.944 | 0 | 0 | 0
26 | 6.62 | 20.9 | [9 empty] | 369 | <10 |  |  | 2 | 0.071 | 0.34 |  | 2 | 0.083 | 0.39 |  | 2 | 0.078 | 0.29 | 6.04 | 6.09 | 6.11 |  |  |  | 6.19 | 20.9 | 6 | 0.329 | [8 empty] | 6.22 | 20.8 | 7 | 0.484 | [8 empty] | 6.21 | 20.6 | 8 | 0.515 | [6 empty] | 7.32 | 20.2 | 3 | 0.065 | 28 | 55 | 4 |  |  | 0.5905 | [6 empty] | A | 7.29 | 20.5 | 2 | 0.069 | 29 | 58 | 3.9 |  |  | 0.5082 | [6 empty] | A |  | 0.962 | 0 | 0 | 0
27 | [11 empty] | 480 | <10 | [62 empty] | 0.5795 | [6 empty] | A | [9 empty] | 0.5437 | [6 empty] | A |  | 1.18 | 0 | 0 | 0
28 | [11 empty] | 408 | <10 | [62 empty] | 0.6453 | [6 empty] | A | [9 empty] | 0.5183 | [6 empty] | A |  | 1.128 | 0 | 0 | 0
29 | 6.67 | 21.2 | 26 |  | 10.71 | 10.26 | 0.477 | 4.649 | 21.5094 | 107.5472 | 215.0943 | 441 | <10 |  |  | 2 | 0.064 | 0.49 |  | 2 | 0.073 | 0.51 |  | 2 | 0.082 | 0.43 | 6.03 | 6.05 | 6.05 |  |  |  | 6.1 | 21 | 5 | 0.382 | 2.939 | 2.869 | 0.048 | 72.5584 | 1.6731 |  |  |  | 6.11 | 20.9 | 5 | 0.446 | 2.94 | 2.848 | 0.049 | 72.549 | 1.7205 |  |  |  | 6.1 | 20.9 | 6 | 0.481 | 2.966 | 2.872 | 0.047 | 72.3063 | 1.6365 | 2.9483 | 7.1 | 20.4 | 2 | 0.059 | 26 | 52 | 4.1 |  |  | 0.6402 |  |  | 2.824 | 2.86 | 0.066 | 2.3077 | A | 7.07 | 20.3 | 2 | 0.062 | 26 | 49 | 4.1 |  |  | 0.496 |  |  | 2.793 | 2.851 | 0.066 | 2.315 | A |  | 0.951 | 0 | 0 | 0
30 | 6.71 | 21.7 | [9 empty] | 350 | <10 |  |  | 3 | 0.062 | 0.42 |  | 3 | 0.062 | 0.48 |  | 3 | 0.064 | 0.35 | 6 | 6.03 | 6.04 |  |  |  | 6.1 | 21.5 | 6 | 0.388 | [8 empty] | 6.12 | 21.4 | 7 | 0.436 | [8 empty] | 6.13 | 21.4 | 11 | 0.698 | [6 empty] | 7.36 | 20.6 | 2 | 0.059 | 29 | 57 | 4.3 |  |  | 0.6219 | [6 empty] | A | 7.1 | 20.8 | 2 | 0.06 | 30 | 56 | 3.8 |  |  | 0.5312 | [6 empty] | A |  | 1.077 | 0 | 0 | 0
[103 empty] | 0 | 0 | 0
[5 empty] | 9.783 |  |  | 4.5939 | 21.7818 | 108.9089 | 217.8177 |  |  |  | #DIV/0! | 2.375 |  |  | #DIV/0! | 2.625 |  |  | #DIV/0! | 2.5 | [5 empty] | #DIV/0! | #DIV/0! | [5 empty] | 2.9369 |  |  | 69.7559 |  | #DIV/0! | #DIV/0! | [5 empty] | 2.9366 |  |  | 69.8049 |  | #DIV/0! | #DIV/0! | [5 empty] | 2.9751 |  |  | 69.4151 |  | 2.9495 | [12 empty] | 2.8097 | [16 empty] | 2.7927 |  |  |  |  | Sum | 23.192 | 0 | 0 | 0
[101 empty] | Max | 1.18 | 0 | 0 | 0
[101 empty] | Avg. | 0.77307 | 0 | 0 | 0
Note on DK37: Sum
Note on DK38: Max
Note on DK39: Avg.

## LAB pH
[5 empty] | pH |  |  |  | Meter: | VSTAS40B2
[9 empty] | Probe: | 8102BNUWP
Date | Time | Analyst | Slope | Std. | Lot Number | Sample ID | QC | Temp | PH | Comments
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
SETTLED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | Dup.
# 2
|  |  |  | 10 | 156700
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | D
# 2
SETTLED # 1
# 2
# 3
|  |  |  | 10 | 156700