## PLANT CHECK
BULL CREEK PLANT CHECK
SHEET KEY
DATE/TIME |  | 2019-08-12 08:45 |  |  |  |  | OPERATOR |  | CBW/JMM |  |  | FILL IN BEFORE GOING ON PLANT CK.
FILL IN AFTER GOING ON PLANT CK.
Raw Water Pumps |  |  | 2,3,5 |  |  | Raw UV | 0.367 | mg/l |  |  |  | FOR MIDNIGHT PLANT OK
Caison Level |  | 14.3 | SCADA Raw flow |  | 27 | Raw TOC | 9.6579 | mg/l |  |  |  | THIS IS WHAT YOU TRANSFER TO DAILY
Control Valve% Open Raw |  |  | 40 | Plant 1 | 68 | Plant 2 | 49 | Plant 3 | 47 |  |  | NO NEED TO TYPE IN THESE BLANKS FOR ROUNDS ONLY
MGD
Total Raw Flow |  |  | 27 |  | MGD | Fin North1 Flow |  |  | 0 | Master Meter Readings
Plant 1 Raw Flow |  |  | 5.3 |  | MGD | Fin 1 Pumps |  |  |  | South 1 |  | 0
Plant 2 Raw Flow |  |  | 10.3 |  | MGD | Fin Coastal1 Flow |  | 7534 | 10.849 | South 2 |  | 0
Plant 3 Raw Flow |  |  | 11.4 |  | MGD | Fin 1 Pumps |  | 1,3 |  | Conway |  | 0
Total Filter Flow |  |  | 26.7 |  | MGD | Fin Perry 2 Flow |  | 5694 | 8.1994 | Perry |  | 0
Plant 1 Filter Flow |  |  | 8.5 |  | MGD | Fin 2 Pumps |  | 1,3 |  | Raw PLT 1 |  | 0
Plant 2 Filter Flow |  |  | 8.5 |  | MGD | Fin Conway 2 Flow |  | 3877 | 5.5829 | Raw PLT 2 |  | 0
Plant 3 Filter Flow |  |  | 9.7 |  | MGD | Fin 2 Pumps |  | 1,3 |  | Raw PLT 3 |  | 0
[12 empty] | Flow | Totalizer
Chemical |  |  | DOSE |  | Calculated |  | Measured |  |  | Decant Weir flow |  |  | 1890683
|  |  | ppm |  | Feed ml/min |  | Feed ml/min |  |  | Sludge Bl.Dwn meter |  |  | 9174.1599
Alum | DESIRED DOSE |  | 63 |  | 1365.651 |  | 2600 |  |  | Thickener Torque 1 |  |  | Sludge Judge |  | feet
[5 empty] | 2654.001 |  | 2600 |  |  | Thickener Torque 2 |  |  | Sludge Judge
[5 empty] | 3002.076 |  | 2600 |  |  | BACKWASH WATER USED
Tank Levels
[5 empty] | 6957.09 |  | 7800 |  | 70.633 |  | BULK
[11 empty] | ALUM 1 | ALUM 2 | ALUM 3 | ALUM 4 | ALUM 5
Polymer | Plant 1 | basin 1 | 0 |  | 0 |  | 0 |  | 0 | Alum
NUMBER OF BASIN | 1 | basin 2 | 0.36 |  | 996.1014 |  | 1000 |  | 0.35879 | Caustic 1
Polymer | Plant 2 | basin 3 | 0.26 |  | 699.046 |  | 700 |  | 0.25846 |  |  | CL2 Pre/Post |  | CL2 Post
NUMBER OF BASIN | 2 | basin 4 | 0.25 |  | 672.1596 |  | 690 |  | 0.25477 |  | CL2
Polymer | Plant 3 | basin 5 | 0.21 |  | 624.9127 |  | 630 |  | 0.21017 | Phosphate
NUMBER OF BASIN | 2 | basin 6 | 0.21 |  | 624.9127 |  | 600 |  | 0.20016 | Fluoride
Polymer |  | Thickener | 800 |  |  |  | 800 |  | 1.5218 | CAL~FLO
Fliter Aid |  | plt1 | 0.06 |  | 966.6818 |  | 980 |  | 0.060827 | Zinc
Fliter Aid |  | plt2 | 0.06 |  | 966.6818 |  | 980 |  | 0.060827 | Polymer
Fliter Aid |  | plt3 | 0.02 |  | 367.7182 |  | 390 |  | 0.021212 | Ammonia
Chlorine |  | Pre 1 | 1 |  | 190.9574 |  | 200 |  | 1.0474 | Hylime LBS/Day
Chlorine |  | Pre 2 | 2.1 |  | 401.0105 |  | 400 |  | 2.0947 | PAC LBS/Day
Chlorine |  | Pre 3 | 1.8 |  | 392.2489 |  | 400 |  | 1.8356 | BI-SULFITE
FILTER AIDE
Caustic |  | Post 1 | 4.6 |  | 268.0085 |  | 251 |  | 4.3081 | ALUM TOWER |  | 0
Caustic |  | Post 2 | 7.2 |  | 239.357 |  | 225 |  | 6.7681
Caustic |  | Pre 1 | 0 |  | 0 |  |  |  | 0
Caustic |  | Pre 2 | 0 |  | 0 |  |  |  | 0
Caustic |  | Pre 3 | 0 |  | 0 |  |  |  | 0
Chemical |  |  |  |  | Calculated |  |  |  | Calculated
|  |  | Plant 1&2 | Plt 3 | Fin 1 ml/min |  |  |  | Fin 2 ml/min
Chlorine |  | Post | 3.8 | 3.6 | 1211.1606 | 3.8506 | 1230 |  | 648.5463 | 3.4658 | 620
Phosphate |  |  | 1.1 |  | 81.345 | 1.1089 | 82 |  | 46.4145 | 1.1376 | 48
Zinc |  |  | 0.1 |  | 11.7658 | 0.10199 | 12 |  | 6.7134 | 0.10427 | 7
Ammonia | All Cl2 / | 5.45 | 0.66327 |  | 247.1756 | 0.67084 | 250 |  | 132.3564 | 0.61137 | 130
Fluoride |  |  | 0.55 |  | 107.9394 | 0.5605 | 110 |  | 61.5889 | 0.51 | 62
grams/min
| Hylime Pounds per Day |  | 0 | Pump Speed |  |  | PPM | 0 |  |  | PLT 1 | PLT 2 | PLT 3 | RAW |  |  | FIN 1 NH3 | [6 empty] | FIN 2 NH3
210 | PAC Pounds per Day |  | 666.0793 | Pump Speed |  | 650 | PPM | 2.958 | Cal~flow Pump % |  |  |  |  | 100 |  |  | (((((D14+D15)*8.34*((D46)/E57)/(E58/100)))/7.74)*3785/1440) | [6 empty] | ((((D16*8.34*(E46/E57)/(E58/100)))/7.74)*3785/1440)
[10 empty] | PPM | 0 | 0 | 0 | 6148.7396
Free Chlorine on Filters |  |  | PLT 1 | 0.59 |  | 0.51 |  | 0.55
Chlorine Strenght % weight/volume |  |  |  |  | Post | 2 | Pre | 0.1 |  | min CT | TARGET CT
Post Chlorine Dose / Ammonia Dose |  |  |  | 4.9 |  | Decant Ph | 5.69 |  | CT PLT 1 | 0.32 | 0.42 | PLT 1
Aquos Ammonia %Strength |  |  |  | 19.5 |  | Decant cl2 | 0.01 |  | CT PLT 2 | 0.32 | 0.42 | PLT 2
CL2 SPG | 1.17 |  | NH3 SPG | 0.928 |  | Decant pump | 17 |  | CT PLT 3 | 0.66 | 0.76 | PLT 3 | -10
| RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [8 empty] | SETTLED | [8 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
|  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW |  |  | DOSE |  |  |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  |  |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST
TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL |  | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLY THICKENER | DECANT | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC
43689.3643 | 2,3,5 | 40 | 5.3 | 10.3 | 11.4 | 27 | 8.5 | 8.5 | 9.7 | 26.7 | ,1,3 | 10.849 | 1,3 | 13.7822 | 24.6312 | 0 | 43689.3643 | 70.633 | 6148.7396 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0474 | 2.0947 | 1.8356 | 0 | 0.35879 | 0.25846 | 0.25477 | 0.21017 | 0.20016 | 1.5218 | 0 | 0.060827 | 0.060827 | 0.021212 | 1.1089 | 0.5605 | 0.10199 | 3.8506 | 0.67084 | 4.3081 | 1.1376 | 0.51 | 0.10427 | 3.4658 | 0.61137 | 6.7681
[18 empty] | 7800 | [6 empty] | 0 | 0 | 0 | 200 | 400 | 400 | 0 | 1000 | 700 | 690 | 630 | 600 | 800 |  | 980 | 980 | 390 | 82 | 110 | 12 | 1230 | 250 | 251 | 48 | 62 | 7 | 620 | 130 | 225
[34 empty] | FINISHED SOUTH 1 |  | END: | 0
[34 empty] | FINISHED SOUTH 2 |  | END: | 0
[34 empty] | FINISHED CONWAY |  | END: | 0
[34 empty] | FINISHED PERRY |  | END: | 0
[34 empty] | RAW PLANT 1 |  | END: | 0
[34 empty] | RAW PLANT 2 |  | END: | 0
[34 empty] | RAW PLANT 3 |  | END: | 0
[34 empty] | DECANT |  | END: | 1890683
[34 empty] | BLOW DOWN |  | END: | 9174.1599
Note on M3: Ctrl+s Will save the sheet
Note on M4: Ctrl+m Will remove all ml/min
Note on M5: Ctrl+o Will remove all Master Meter
Note on D12: PLANT 3 FLOW IS MAX FOR CT CAL. IN LESS BASIN IS DOWN
Note on D20: RAW FLOW X mg/Lx4.18=ml/min Ex. 29.9x61.6x4.18=Total PPM
Note on D26: ((7500*PPM*1440)/(1000*1000*454))/(FLOW*8.34)*#OF BASIN
Note on D30: BASIN 5-6 IS NOT TO BE LOWER THAN 1-4
Note on M39: FROM SCADA TOTAL LBS YESTERDAY
Note on D50: DOSE - AVG FILTER RES PLT 1 & PLT 2 X 8.34 X FIN FLOW PLT 1 PLT 2 /%SOL/(8.34 X SPF) X 3785 / 1440 = ML/MIN
Note on D51: Fin Flow X PPM X 4.35= ML/MIN
Note on D52: PPM X 2.63 / .38 X FLOW= ML/MIM
Note on D53: ML/MIN X 1440 / 3785 / FLOW / 8.34 = PPM
Note on F53: FOLW X 8.34 X ((CL2 mg/l / CL2/NH3) / (NH3% / 100) / 7.74) X 3785 / 1440 = ML/MIN
Note on D54: ML/MIN/2.63*1.9/8.34/FLOW=PPM

## LIME CAL (hidden)
PUMP % | MIL/MIN | FOR CALCULATION FACTOR
5 | 307.4366 | #N/A | #N/A | #N/A | 96
6 | 368.924
7 | 430.4114
8 | 491.8988
9 | 553.3862
10 | 614.8736
11 | 676.361
12 | 737.8484
13 | 799.3358
14 | 860.8232
15 | 922.3106
16 | 983.798
17 | 1045.2854
18 | 1106.7728
19 | 1168.2602
20 | 1229.7476
21 | 1291.235
22 | 1352.7224
23 | 1414.2098
24 | 1475.6972
25 | 1537.1846
26 | 1598.672
27 | 1660.1594
28 | 1721.6468
29 | 1783.1342
30 | 1844.6216
31 | 1906.109
32 | 1967.5964
33 | 2029.0838
34 | 2090.5712
35 | 2152.0586
36 | 2213.546
37 | 2275.0334
38 | 2336.5208
39 | 2398.0082
40 | 2459.4956
41 | 2520.983
42 | 2582.4704
43 | 2643.9578
44 | 2705.4452
45 | 2766.9326
46 | 2828.42
47 | 2889.9074
48 | 2951.3948
49 | 3012.8822
50 | 3074.3696
51 | 3135.857
52 | 3197.3444
53 | 3258.8318
54 | 3320.3192
55 | 3381.8066
56 | 3443.294
57 | 3504.7814
58 | 3566.2688
59 | 3627.7562
60 | 3689.2436
61 | 3750.731
62 | 3812.2184
63 | 3873.7058
64 | 3935.1932
65 | 3996.6806
66 | 4058.168
67 | 4119.6554
68 | 4181.1428
69 | 4242.6302
70 | 4304.1176
71 | 4365.605
72 | 4427.0924
73 | 4488.5798
74 | 4550.0672
75 | 4611.5546
76 | 4673.042
77 | 4734.5294
78 | 4796.0168
79 | 4857.5042
80 | 4918.9916
81 | 4980.479
82 | 5041.9664
83 | 5103.4538
84 | 5164.9412
85 | 5226.4286
86 | 5287.916
87 | 5349.4034
88 | 5410.8908
89 | 5472.3782
90 | 5533.8656
91 | 5595.353
92 | 5656.8404
93 | 5718.3278
94 | 5779.8152
95 | 5841.3026
96 | 5902.79
97 | 5964.2774
98 | 6025.7648
99 | 6087.2522
100 | 6148.7396
101 | 6210.227
102 | 6271.7144
103 | 6333.2018
104 | 6394.6892
105 | 6456.1766
106 | 6517.664
107 | 6579.1514
108 | 6640.6388
109 | 6702.1262
110 | 6763.6136
111 | 6825.101
112 | 6886.5884
113 | 6948.0758
114 | 7009.5632
115 | 7071.0506
116 | 7132.538
117 | 7194.0254
118 | 7255.5128
119 | 7317.0002
120 | 7378.4876
121 | 7439.975
122 | 7501.4624
123 | 7562.9498
124 | 7624.4372
125 | 7685.9246
126 | 7747.412
127 | 7808.8994
128 | 7870.3868
129 | 7931.8742
130 | 7993.3616
131 | 8054.849
132 | 8116.3364
133 | 8177.8238
134 | 8239.3112
135 | 8300.7986
136 | 8362.286
137 | 8423.7734
138 | 8485.2608
139 | 8546.7482
140 | 8608.2356
141 | 8669.723
142 | 8731.2104
143 | 8792.6978
144 | 8854.1852
145 | 8915.6726
146 | 8977.16
147 | 9038.6474
148 | 9100.1348
149 | 9161.6222
150 | 9223.1096
151 | 9284.597
152 | 9346.0844
153 | 9407.5718
154 | 9469.0592
155 | 9530.5466
156 | 9592.034
157 | 9653.5214
158 | 9715.0088
159 | 9776.4962
160 | 9837.9836
161 | 9899.471
162 | 9960.9584
163 | 10022.4458
164 | 10083.9332
165 | 10145.4206
166 | 10206.908
167 | 10268.3954
168 | 10329.8828
169 | 10391.3702
170 | 10452.8576
171 | 10514.345
172 | 10575.8324
173 | 10637.3198
174 | 10698.8072
175 | 10760.2946
176 | 10821.782
177 | 10883.2694
178 | 10944.7568
179 | 11006.2442
180 | 11067.7316
181 | 11129.219
182 | 11190.7064
183 | 11252.1938
184 | 11313.6812
185 | 11375.1686
186 | 11436.656
187 | 11498.1434
188 | 11559.6308
189 | 11621.1182
190 | 11682.6056
191 | 11744.093
192 | 11805.5804
193 | 11867.0678
194 | 11928.5552
195 | 11990.0426
196 | 12051.53
197 | 12113.0174
198 | 12174.5048
199 | 12235.9922
200 | 12297.4796
201 | 12358.967
202 | 12420.4544
203 | 12481.9418
204 | 12543.4292
205 | 12604.9166
206 | 12666.404
207 | 12727.8914
208 | 12789.3788

## CHEM 1 (hidden)
CHEMICAL TRANSFER SHEET PLANT 3 | [7 empty] | CHEMICAL TRANSFER SHEET PLANT 1 and 2
DATE | 2019-08-12 08:45 | TIME | 43689.3643 | OPERATORS |  | CBW/JMM |  | DATE | 2019-08-12 08:45 | TIME | 43689.3643 |  | OPERATORS |  | CBW/JMM
ALUM START 24HR. LEVEL |  |  |  | GAL. |  |  |  |  | PAC TOTAL |  | LB/DAY |  | LIME TOTAL |  |  | GAL/DAY
START |  | GAL. FINISH |  | GAL. |  |  |  |  | AMMONIA |  | GAL/DAY |  | CHLORINE |  |  | GAUDAY
START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER START 24HR. LEVEL |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. |  |  |  | POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | TOTAL GAL. POLYMER USED 24HR.
START |  | GAL. FINISH |  | GAL.
| FINISH 24HR. LEVEL |  |  | GAL.
|  |  |  | TOTAL GAL. ALUM USED 24HR. |  |  | GAL. | CAUSTIC START 24HR. LEVEL |  |  |  | GAL.
[8 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
POLYMER START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL.
POLYMER FINISH 24HR. LEVEL |  |  |  | GAL. | [8 empty] | TOTAL GAL. CAUSTIC USED 24HR.
TOTAL GAL. POLYMER USED 24HR.
[8 empty] | PHOSPHATE START 24HR. LEVEL |  |  |  | GAL.
CAUSTIC START 24HR. LEVEL |  |  |  | GAL. |  |  |  | START |  | GAL. FINISH |  | GAL. |  | START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | PHOSPHATE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. PHOSPHATE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | ZINC CHLORIDE START 24HR. LEVEL |  |  |  |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
CAUSTIC FINISH 24HR. LEVEL |  |  |  | GAL. |  |  |  | ZINC CHLORIDE FINISH 24HR. LEVEL |  |  |  |  | GAL. | TOTAL GAL. ZINC USED 24HR.
|  |  |  | TOTAL GAL. CAUSTIC USED 24HR. |  |  | GAL.
[8 empty] | FILTER AIDE START 24HR. LEVEL |  |  |  | GAL.
PRE HYPOCHLORITE START 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. FINISH |  | GAL.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER AIDE FINISH 24HR. LEVEL |  |  |  | GAL. TOTAL GAL. FILTER AIDE USED 24HR.
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL.
PRE HYPOCHLORITE FINISH 24HR. LEVEL |  |  |  |  | GAL. | FINISH
|  |  | TOTAL GAL. HYPOCHLORITE USED 24HR. |  |  |  | GAL
FILTER AIDE START 24HR. LEVEL
START |  | GAL. FINISH |  | GAL. START |  | GAL. FINISH | GAL. | FILTER CAUSTIC START 24HR. LEVEL | [5 empty] | GAL.
FILTER AIDE FINISH 24HR. LEVEL | [7 empty] | START |  | GAL. FINISH |  | GAL. | START |  | GAL. | FINISH
[8 empty] | FILTER CAUSTIC FINISH 24HR. LEVEL | [6 empty] | GAL.
LIME START |  |  | FT FINISH |  | FT TOTAL | [6 empty] | TOTAL FILT. CAUSTIC USED 24HR. |  |  |  |  | GAL.

## RUN TIME
WEEKLY DATE | 2019-08-12 08:45 | TIME | 43689.3643 | OPERATOR | CBW/JMM
PUMP AND MOTOR RUN TIME LOG
LOCATION | RUN TIMES |  | LOCATION | RUN TIMES
South Pump #1 |  | Hr | Sludge Bl. Dwn Pump #1 |  | Hr
South Pump #2 |  | Hr | Sludge Bl. Dwn Pump #2 |  | Hr
South Pump #3 |  | Hr | Spill Lagoon Pump #1 |  | Hr
South Pump #4 |  | Hr | Spill Lagoon Pump #2 |  | Hr
North Pump #5 |  | Hr | Sludge Spray Pump #1 |  | Hr
North Pump #6 |  | Hr | Sludge Spray Pump #2 |  | Hr
North Pump #7 |  | Hr | Sludge Spray Pump #3 |  | Hr
North Pump #8 |  | Hr
|  | Boge Compressor Lime Pack |  |  | Hr
Finish Vac Pump #1 |  | Hr | Lime Pack Compressor #1 |  | Hr
Finish Vac Pump #2 |  | Hr
|  |  | Plant #3 Compressor #1 |  | Hr
Service Water Pump #1 |  | Hr | Plant #3 Compressor #2 |  | Hr
Service Water Pump #2 |  | Hr | Boge Compressor Plant #3 |  | Hr
Service Water Pump #3 |  | Hr
|  |  | Finished #2 Pump #1 |  | Hr
Hydro Tank Compressor |  | Hr | Finished #2 Pump #2 |  | Hr
|  |  | Finished #2 Pump #3 |  | Hr
Plant #3 Filter Blower #1 |  | Hr
Plant #3 Filter Blower #2 |  | Hr | Raw Header |  | Psi
Plant #3 Backwash pump #1 |  | Hr | Raw Pump #1 |  | Hr
Plant #3 Backwash pump #2 |  | Hr | Raw Pump #2 |  | Hr
Plant #3 Backwash VFD #1 |  | Hr | Raw Pump #3 |  | Hr
Plant #3 Backwash VFD #2 |  | Hr | Raw Pump #4 |  | Hr
Plant #3 Chemical spill #1 |  | Hr | Raw Pump #5 |  | Hr
Plant #3 Chemical spill #2 |  | Hr | Raw Pump #6 |  | Hr
Plant #3 Biulding spill #1 |  | Hr | COMMENTS
Plant #3 Biulding spill #2 |  | Hr
Plant #1/2 Filter Blower #1 |  | Hr
Plant #1/2 Filter Blower #2 |  | Hr
Plant #1/2 backwash pump #1 |  | Hr
Plant #1/2 backwash pump #2 |  | Hr
Plant #1/2 backwash VFD #1 |  | Hr
Plant #1/2 backwash VFD #2 |  | Hr

## 1
DATE: | 2019-01-01 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-01 | [23 empty] | DATE: | 2019-01-01
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-01 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43466.0093 | 1,2,3 | 32 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 15.0898 | 1,3 | 12.564 | 27.6538 | 2.0681 | 43466.0093 | 89.8698 | 8239.3112 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.4838 | 1.5175 | 0.34824 | 0.36657 | 0.34824 | 0.36657 | 0.29444 | 0.29444 | 1.4267 | 0 | 0.070344 | 0.070344 | 0.069544 | 1.12 | 0.54417 | 0.09262 | 3.9868 | 0.73105 | 3.8343 | 1.1494 | 0.59061 | 0.098514 | 3.5821 | 0.64797 | 5.3051 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.05 | 0.276 | 4 | 0.66 | 14.4 | 8.9 | 0.64476 |  | 6.11 | 0.235 | 4 | 0.63 | 14.9 | 8.3 | 0.60939 | 6.1 | 0.224 | 4 | 0.67 | 16.4 | 9.8 | 0.48296 | [13 empty] | 7.34 | 0.049 | 1 | 3.9 | 12.7 |  |  |  | 7.27 | 0.053 | 1 | 3.7 | 15.1 |  |  |  | 4.2 | 4 | 3.3 | [18 empty] | 9520 | [6 empty] | 0 | 0 | 0 | 260 | 260 | 300 | 760 | 800 | 760 | 800 | 720 | 720 | 750 |  | 1040 | 1040 | 1160 | 76 | 98 | 10 | 1230 | 250 | 205 | 44 | 60 | 6 | 610 | 125 | 160 |  | 1:00 | 0.66 | 8.9 | 28.5843 | 18.8656 | 6.05 | 14.4 | 15 | 1.2577 | 10 | 6.5 | 0.52476 | 1:00 | 0.63 | 8.3 | 30.6506 | 19.3099 | 6.11 | 14.9 | 15 | 1.2873 | 10 | 6.5 | 0.48939 | 1:00 | 0.67 | 9.8 | 27.551 | 18.4592 | 6.1 | 16.4 | 10 | 1.8459 | 15 | 6.5 | 0.36296
2:00 | [72 empty] | 43466.316 | 1,2,3 | 32 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 15.0898 | 1,3 | 12.564 | 27.6538 | 2.0434 | 43466.316 | 90.625 | 8362.286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.4838 | 1.5175 | 0.34366 | 0.34366 | 0.34366 | 0.34366 | 0.29444 | 0.29444 | 1.4267 | 3 | 0.070344 | 0.070344 | 0.070743 | 1.12 | 0.55527 | 0.09262 | 3.9702 | 0.74859 | 3.8343 | 1.0972 | 0.55124 | 0.098514 | 3.5921 | 0.64797 | 5.3051 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.25 | 12 | 14 | 8.99 | 115 | 158 | 15.5 | 0.485 |  | 6.07 | 8 | 0.075 | 6.03 | 8 |  | 6 | 8 | [8 empty] | 0.053 | [14 empty] | 0.032 | 1 | 0.32 |  | 0.051 | 0.011 | 2 | 0.31 |  | 0.026 | 2 | 0.43 | [38 empty] | 9600 | [6 empty] | 0 | 0 | 0 | 280 | 260 | 300 | 750 | 750 | 750 | 750 | 720 | 720 | 750 |  | 1040 | 1040 | 1180 | 76 | 100 | 10 | 1250 | 256 | 205 | 42 | 56 | 6 | 610 | 125 | 160 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [127 empty] | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.4 | 0.052 | 1 | 3.8 | 12.8 |  |  |  | 7.37 | 0.056 | 1 | 3.9 | 15.2 |  |  |  | 4.1 | 3.8 | 4.4 | [55 empty] | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.27 | 11 | 14 | 8.66 | 116 | 159 | 15.1 | 0.498 |  | 6 | 10 | 0.072 | 5.96 | 10 |  | 5.97 | 10 | [8 empty] | 0.051 | [14 empty] | 0.028 | 1 | 0.3 |  | 0.05 | 0.01 | 1 | 0.36 |  | 0.025 | 2 | 0.49 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.056 | [9 empty] | 6.12 | 0.281 | 4 | 0.62 | 14.3 | 8.3 | 0.60939 |  | 6.13 | 0.239 | 4 | 0.64 | 14.6 | 8.3 | 0.60939 | 6.12 | 0.247 | 4 | 0.79 | 16.3 | 9.3 | 0.46444 |  |  |  | 0.021 | [9 empty] | 7.22 | 0.084 | 1 | 4 | 13.6 | 22 | 46 | 0.019 | 7.29 | 0.066 | 1 | 4.5 | 14.9 | 21 | 42 | 0.024 | 4 | 3.7 | 3.6 | [55 empty] | 9:00 | 0.62 | 8.3 | 30.6506 | 19.0034 | 6.12 | 14.3 | 15 | 1.2669 | 10 | 6.5 | 0.48939 | 9:00 | 0.64 | 8.3 | 30.6506 | 19.6164 | 6.13 | 14.6 | 15 | 1.3078 | 10 | 6.5 | 0.48939 | 9:00 | 0.79 | 9.3 | 29.0323 | 22.9355 | 6.12 | 16.3 | 10 | 2.2935 | 15 | 6.5 | 0.34444
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.28 | 16 | 15 | 8.72 | 116 | 156 | 15.6 | 0.497 |  | 6.02 | 10 | 0.074 | 6.01 | 11 |  | 5.96 | 11 | [8 empty] | 0.05 | [14 empty] | 0.029 | 1 | 0.39 |  | 0.053 | 0.009 | 1 | 0.39 |  | 0.024 | 1 | 0.44 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.25 | 3 | 0.66 | 15 | 8.3 | 0.44626 |  | 6.12 | 0.225 | 3 | 0.62 | 15 | 8.3 | 0.44626 | 6.1 | 0.218 | 3 | 0.74 | 16.5 | 9.3 | 0.46444 | [13 empty] | 7.31 | 0.06 | 1 | 4 | 13.6 |  |  |  | 7.21 | 0.058 | 1 | 4.2 | 16 |  |  |  | 3.9 | 3.8 | 3.1 | [55 empty] | 13:00 | 0.66 | 8.3 | 30.6506 | 20.2294 | 6.1 | 15 | 10 | 2.0229 | 15 | 6.5 | 0.32626 | 13:00 | 0.62 | 8.3 | 30.6506 | 19.0034 | 6.12 | 15 | 10 | 1.9003 | 15 | 6.5 | 0.32626 | 13:00 | 0.74 | 9.3 | 29.0323 | 21.4839 | 6.1 | 16.5 | 10 | 2.1484 | 15 | 6.5 | 0.34444
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.44 | 18 | 14 | 8.75 | 112 | 158 | 16 | 0.458 |  | 6.05 | 12 | 0.056 | 6.03 | 12 |  | 6 | 12 | [8 empty] | 0.039 | [14 empty] | 0.023 | 1 | 0.35 |  | 0.039 | 0.01 | 1 | 0.36 |  | 0.024 | 1 | 0.44 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.25 | 0.058 | 1 | 4.2 | 13.6 |  |  |  | 7.25 | 0.055 | 1 | 4 | 16 |  |  |  | 3.9 | 3.8 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.23 | 14 | 18 | 8.25 | 115 | 156 | 15.9 | 0.491 |  | 5.96 | 8 | 0.076 | 5.95 | 8 |  | 5.93 | 10 | [8 empty] | 0.051 | [14 empty] | 0.022 | 1 | 0.36 |  | 0.049 | 0.01 | 1 | 0.28 |  | 0.023 | 2 | 0.38 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.032 | [9 empty] | 6.02 | 0.286 | 4 | 0.59 | 14.8 | 9.3 | 0.66835 |  | 6.08 | 0.249 | 4 | 0.55 | 14.9 | 8.4 | 0.61528 | 6.1 | 0.225 | 4 | 0.68 | 16.6 | 10.2 | 0.49778 |  |  |  | 0.008 | [9 empty] | 7.22 | 0.045 | 1 | 3.8 | 13.3 | 20 | 55 | 0.015 | 7.32 | 0.048 | 1 | 4 | 15.6 | 21 | 52 | 0.009 | 3.9 | 3.9 | 3.1 | [55 empty] | 21:00 | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.02 | 14.8 | 15 | 1.076 | 10 | 6.5 | 0.54835 | 21:00 | 0.55 | 8.4 | 30.2857 | 16.6571 | 6.08 | 14.9 | 15 | 1.1105 | 10 | 6.5 | 0.49528 | 21:00 | 0.68 | 10.2 | 26.4706 | 18 | 6.1 | 16.6 | 10 | 1.8 | 15 | 6.5 | 0.37778
22:00 | [72 empty] | DOSE |  | TOTAL | 16.6 | 16.6 | 18.6 | 51.8 | 15.6 | 15.6 | 17.6 | 48.8 | 0 | 30.1795 | 0 | 25.128 | 55.3075 | 4.1115 | TOTAL | 180.4949 | 16601.5972 | 0 | 1300.4405 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0816 | 2.9675 | 3.0349 | 0.69189 | 0.71022 | 0.69189 | 0.71022 | 0.58887 | 0.58887 | 2.8534 | 3 | 0.14069 | 0.14069 | 0.14029 | 2.2399 | 1.0994 | 0.18524 | 7.957 | 1.4796 | 7.6686 | 2.2466 | 1.1418 | 0.19703 | 7.1742 | 1.2959 | 10.6102 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.29 | 16 | 17 | 9 | 116 | 159 | 16.2 | 0.489 |  | 5.92 | 9 | 0.06 | 5.89 | 8 |  | 5.86 | 9 | [8 empty] | 0.047 | [14 empty] | 0.026 | 1 | 0.36 |  | 0.049 | 0.01 | 1 | 0.37 |  | 0.022 | 1 | 0.41 | [22 empty] | AVERAGE | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 |  | 15.0898 |  | 12.564 | 27.6538 | 2.0557 | AVERAGE | 90.2474 | 8300.7986 |  | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5408 | 1.4838 | 1.5175 | 0.34595 | 0.35511 | 0.34595 | 0.35511 | 0.29444 | 0.29444 | 1.4267 | 1.5 | 0.070344 | 0.070344 | 0.070144 | 1.12 | 0.54972 | 0.09262 | 3.9785 | 0.73982 | 3.8343 | 1.1233 | 0.57092 | 0.098514 | 3.5871 | 0.64797 | 5.3051 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.76 | 87 | 92 | 52.37 | 690 | 946 | 94.3 | 2.918 | 0.088 | 36.02 | 57 | 0.413 | 35.87 | 57 | 0 | 35.72 | 60 | 0 | 24.29 | 1.093 | 15 | 2.53 | 58.5 | 34.8 | 2.3688 | 0.291 | 24.44 | 0.948 | 15 | 2.44 | 59.4 | 33.3 | 2.2803 | 24.42 | 0.914 | 15 | 2.88 | 65.8 | 38.6 | 1.9096 | 0.16 | 6 | 2.08 | 0.029 | 0.291 | 0.06 | 7 | 2.07 | 0 | 0.144 | 9 | 2.59 | 0 | 43.74 | 0.348 | 6 | 23.7 | 79.6 | 42 | 101 | 0.034 | 43.71 | 0.336 | 6 | 24.3 | 92.8 | 42 | 94 | 0.033 | 24 | 23 | 20.5 |  |  | MINIMUM | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 |  | 15.0898 |  | 12.564 | 27.6538 | 2.0434 | MINIMUM | 89.8698 | 8239.3112 |  | 650.2203 | [6 empty] | 1.4838 | 1.4838 | 1.5175 | 0.34366 | 0.34366 | 0.34366 | 0.34366 | 0.29444 | 0.29444 | 1.4267 | 0 | 0.070344 | 0.070344 | 0.069544 | 1.12 | 0.54417 | 0.09262 | 3.9702 | 0.73105 | 3.8343 | 1.0972 | 0.55124 | 0.098514 | 3.5821 | 0.64797 | 5.3051 |  | MIN | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.02 | 14.8 | 15 | 1.076 |  |  |  | MIN | 0.55 | 8.4 | 30.2857 | 16.6571 | 6.08 | 14.9 | 15 | 1.1105 |  |  |  | MIN | 0.68 | 10.2 | 26.4706 | 18 | 6.1 | 16.6 | 10 | 1.8 |  |  |  | 1.076
AVERAGE | 6.2933 | 14.5 | 15.3333 | 8.7283 | 115 | 157.6667 | 15.7167 | 0.48633 | 0.044 | 6.0033 | 9.5 | 0.068833 | 5.9783 | 9.5 |  | 5.9533 | 10 |  | 6.0725 | 0.27325 | 3.75 | 0.6325 | 14.625 | 8.7 | 0.59219 | 0.0485 | 6.11 | 0.237 | 3.75 | 0.61 | 14.85 | 8.325 | 0.57008 | 6.105 | 0.2285 | 3.75 | 0.72 | 16.45 | 9.65 | 0.47741 | 0.026667 | 1 | 0.34667 | 0.0145 | 0.0485 | 0.01 | 1.1667 | 0.345 |  | 0.024 | 1.5 | 0.43167 |  | 7.29 | 0.058 | 1 | 3.95 | 13.2667 | 21 | 50.5 | 0.017 | 7.285 | 0.056 | 1 | 4.05 | 15.4667 | 21 | 47 | 0.0165 | 4 | 3.8333 | 3.4167 |  |  | MAXIMUM | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 |  | 15.0898 |  | 12.564 | 27.6538 | 2.0681 | MAXIMUM | 90.625 | 8362.286 |  | 650.2203 | [6 empty] | 1.5979 | 1.4838 | 1.5175 | 0.34824 | 0.36657 | 0.34824 | 0.36657 | 0.29444 | 0.29444 | 1.4267 | 3 | 0.070344 | 0.070344 | 0.070144 | 1.12 | 0.55527 | 0.09262 | 3.9868 | 0.74859 | 3.8343 | 1.1494 | 0.59061 | 0.098514 | 3.5921 | 0.64797 | 5.3051
MINIMUM | 6.23 | 11 | 14 | 8.25 | 112 | 156 | 15.1 | 0.458 | 0.032 | 5.92 | 8 | 0.056 | 5.89 | 8 |  | 5.86 | 8 |  | 6.02 | 0.25 | 3 | 0.59 | 14.3 | 8.3 | 0.44626 | 0.039 | 6.08 | 0.225 | 3 | 0.55 | 14.6 | 8.3 | 0.44626 | 6.1 | 0.218 | 3 | 0.67 | 16.3 | 9.3 | 0.46444 | 0.022 | 1 | 0.3 | 0.008 | 0.039 | 0.009 | 1 | 0.28 |  | 0.022 | 1 | 0.38 |  | 7.22 | 0.045 | 1 | 3.8 | 12.7 | 20 | 46 | 0.015 | 7.21 | 0.048 | 1 | 3.7 | 14.9 | 21 | 42 | 0.009 | 3.9 | 3.7 | 3 | [15 empty] | Ml/Min |  | TOTAL | 19120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 520 | 600 | 1510 | 1550 | 1510 | 1550 | 1440 | 1440 | 1500 | 0 | 2080 | 2080 | 2340 | 152 | 198 | 20 | 2480 | 506 | 410 | 86 | 116 | 12 | 1220 | 250 | 320
MAXIMUM | 6.44 | 18 | 18 | 9 | 116 | 159 | 16.2 | 0.498 | 0.056 | 6.07 | 12 | 0.076 | 6.03 | 12 |  | 6 | 12 |  | 6.12 | 0.286 | 4 | 0.66 | 15 | 9.3 | 0.66835 | 0.053 | 6.13 | 0.249 | 4 | 0.64 | 15 | 8.4 | 0.61528 | 6.12 | 0.247 | 4 | 0.79 | 16.6 | 10.2 | 0.49778 | 0.032 | 1 | 0.39 | 0.021 | 0.053 | 0.011 | 2 | 0.39 |  | 0.026 | 2 | 0.49 |  | 7.4 | 0.084 | 1 | 4.2 | 13.6 | 22 | 55 | 0.019 | 7.37 | 0.066 | 1 | 4.5 | 16 | 21 | 52 | 0.024 | 4.2 | 4 | 4.4 | [17 empty] | AVERAGE | 9560 | [9 empty] | 270 | 260 | 300 | 755 | 775 | 755 | 775 | 720 | 720 | 750 |  | 1040 | 1040 | 1170 | 76 | 99 | 10 | 1240 | 253 | 205 | 43 | 58 | 6 | 610 | 125 | 160
# 0F DAYS IN THE MONTH |  | 31 |  | TOTAL AVG COAG PH: |  |  |  | 5.9783 |  | TOTAL AVG COAG ALK: |  |  |  | 9.6667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.286 |  |  |  |  | TOTAL AVG SETTLED PH: | [6 empty] | 6.0958 | TOTAL MIN SETTLED DISEN.: | [7 empty] | 0.55 | TOTAL FILTER MAX NTU | [6 empty] | 0.032 | [20 empty] | Pump Station MIN |  | 3 | [17 empty] | MINIMUM | 9520 | [9 empty] | 260 | 260 | 300 | 750 | 750 | 750 | 750 | 720 | 720 | 750 |  | 1040 | 1040 | 1160 | 76 | 98 | 10 | 1230 | 250 | 205 | 42 | 56 | 6 | 610 | 125 | 160
[90 empty] | MAXIMUM | 9600 | [9 empty] | 280 | 260 | 300 | 760 | 800 | 760 | 800 | 720 | 720 | 750 |  | 1040 | 1040 | 1180 | 76 | 100 | 10 | 1250 | 256 | 205 | 44 | 60 | 6 | 610 | 125 | 160
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.487 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827078 |  | END: | 23827078 |  |  | Alum | 360 | 9791 | 9791 | 8773 | 8773 | 0 | [44 empty] | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.02 | 14.8 | 15 | 1.076
[73 empty] | FINISHED 2 | 11.194 |  | TOTAL MGD: |  | 12.487 |  |  | FINISHED SOUTH 2 |  | START: | 43831556 |  | END: | 43844043 |  |  | Caustic | 4980 | 6570 | 6570
[73 empty] | TOTAL RAW | 26.985 |  | TOTAL MGD: |  | 4.712 |  |  | FINISHED CONWAY |  | START: | 10221361 |  | END: | 10226073 |  |  | Hypochlorite | 14 |  | 19
[76 empty] | TOTAL MGD: |  | 6.482 |  |  | FINISHED PERRY |  | START: | 33844805 |  | END: | 33851287 |  |  | Phosphate | 2732
[76 empty] | TOTAL MGD: |  | 8.817 |  |  | RAW PLANT 1 |  | START: | 30955169 |  | END: | 30963986 |  |  | Fluoride | 3750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.376 |  |  | RAW PLANT 2 |  | START: | 30915221 |  | END: | 30923597 |  |  | Cal~Flo | 9.04 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.792 |  |  | RAW PLANT 3 |  | START: | 7488275 |  | END: | 7498067 |  |  | Zinc | 967
[76 empty] | TOTAL MGD: |  | 0.877 |  |  | DECANT |  | START: | 1863259 |  | END: | 1864136 |  |  | Polymer | 19
[76 empty] | TOTAL MGD: |  | 1.8797 |  |  | BLOW DOWN |  | START: | 9129.4864 |  | END: | 9131.3661 |  |  | NH3 | 7.71 |  | BI-SUL | 1250
[90 empty] | Lime | 0 |  | FILTER AIDE | 0 | [25 empty] | 1.0202
[82 empty] | BACKWASH WATER USED : |  |  |  |  | 0 |  |  | Cabon | 650
[91 empty] | FINISHED SOUTH 1 |  | END: | 23827078
[91 empty] | FINISHED SOUTH 2 |  | END: | 43844043
[91 empty] | FINISHED CONWAY |  | END: | 10226073
[91 empty] | FINISHED PERRY |  | END: | 33851287
[91 empty] | RAW PLANT 1 |  | END: | 30963986
[91 empty] | RAW PLANT 2 |  | END: | 30923597
[91 empty] | RAW PLANT 3 |  | END: | 7498067
[91 empty] | DECANT |  | END: | 1864136
[91 empty] | BLOW DOWN |  | END: | 9131.3661
Note on AX36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 2
DATE: | 2019-01-02 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CBW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-02 | [23 empty] | DATE: | 2019-01-02
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-02 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43467.0019 | 1,2,3 | 35 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 14.0674 | 1,3 | 14.5325 | 28.5998 | 1.8261 | 43467.0019 | 89.9406 | 8116.3364 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4663 | 1.4663 | 1.4057 | 0.30425 | 0.32115 | 0.30425 | 0.30425 | 0.27382 | 0.27382 | 1.4267 | 7 | 0.068275 | 0.068275 | 0.068863 | 1.0818 | 0.55031 | 0.10199 | 3.9962 | 0.75135 | 3.776 | 1.0647 | 0.54709 | 0.10646 | 3.6452 | 0.67226 | 5.3749 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.286 | 4 | 0.7 | 14.6 | 9 | 0.65066 |  | 5.98 | 0.249 | 4 | 0.78 | 14.9 | 8.7 | 0.56458 | 6.01 | 0.215 | 4 | 0.73 | 16.7 | 10 | 0.49037 | [13 empty] | 7.14 | 0.044 | 1 | 4 | 13.4 |  |  |  | 7.12 | 0.047 | 1 | 4.2 | 15.7 |  |  |  | 3.9 | 3.9 | 3.1 | [18 empty] | 10300 | [6 empty] | 0 | 0 | 0 | 280 | 280 | 300 | 720 | 760 | 720 | 720 | 720 | 720 | 750 |  | 1100 | 1100 | 1240 | 80 | 108 | 12 | 1370 | 280 | 220 | 44 | 60 | 7 | 680 | 140 | 175 |  | 1:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.01 | 14.6 | 15 | 1.3191 | 10 | 6.5 | 0.53066 | 1:00 | 0.78 | 8.7 | 29.2414 | 22.8083 | 5.98 | 14.9 | 13 | 1.7545 | 10 | 6 | 0.44458 | 1:00 | 0.73 | 10 | 27 | 19.71 | 6.01 | 16.7 | 10 | 1.971 | 15 | 6.5 | 0.37037
2:00 | [72 empty] | 43467.3311 | 1,2,3 | 38 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 9.5198 | 1,3 | 11.8843 | 21.4042 | 1.8261 | 43467.3311 | 88.7181 | 9038.6474 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3877 | 1.3616 | 1.4994 | 0.30425 | 0.3296 | 0.30425 | 0.32115 | 0.26622 | 0.21297 | 1.4267 | 7 | 0.068895 | 0.068275 | 0.069973 | 1.0818 | 0.55031 | 0.10199 | 4.0094 | 0.71109 | 4.1193 | 1.0647 | 0.54709 | 0.091255 | 3.598 | 0.62424 | 5.9892 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.29 | 12 | 14 | 9.52 | 118 | 162 | 16.2 | 0.489 |  | 5.99 | 7 | 0.075 | 5.97 | 8 |  | 5.93 | 8 | [8 empty] | 0.05 | [14 empty] | 0.023 | 1 | 0.33 |  | 0.05 | 0.009 | 2 | 0.26 |  | 0.021 | 1 | 0.4 | [38 empty] | 10160 | [6 empty] | 0 | 0 | 0 | 265 | 260 | 320 | 720 | 780 | 720 | 760 | 700 | 560 | 750 |  | 1110 | 1100 | 1260 | 80 | 108 | 12 | 1360 | 265 | 240 | 44 | 60 | 6 | 666 | 130 | 195 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43467.5718 | 1,2,3 | 38 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 9.5198 | 1,3 | 11.8843 | 21.4042 | 1.8261 | 43467.5718 | 90.625 | 8731.2104 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3696 | 1.4267 | 1.5175 | 0.31158 | 0.32075 | 0.30242 | 0.32075 | 0.27808 | 0.22083 | 1.4267 | 7 | 0.060198 | 0.059522 | 0.059952 | 1.0905 | 0.54972 | 0.10188 | 3.8583 | 0.70181 | 4.0962 | 1.0972 | 0.55124 | 0.098514 | 3.734 | 0.57022 | 5.8025 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.16 | 0.051 | 1 | 3.9 | 13.5 |  |  |  | 7.31 | 0.052 | 1 | 4.3 | 15.6 |  |  |  | 3.9 | 3.9 | 3.2 | [18 empty] | 9600 | [6 empty] | 0 | 0 | 0 | 240 | 250 | 300 | 680 | 700 | 660 | 700 | 680 | 540 | 750 |  | 890 | 880 | 1000 | 74 | 99 | 11 | 1210 | 240 | 219 | 42 | 56 | 6 | 620 | 110 | 175 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43467.8275 | 1,2,3 | 30 | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 12.8059 | 1,3 | 9.4032 | 22.2091 | 1.8158 | 43467.8275 | 91.3066 | 8731.2104 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4219 | 1.4219 | 1.5199 | 0.31116 | 0.32104 | 0.30129 | 0.32104 | 0.27977 | 0.28414 | 1.4267 | 3 | 0.060085 | 0.060085 | 0.059835 | 1.1175 | 0.54139 | 0.10034 | 4.0002 | 0.76029 | 4.1336 | 1.1214 | 0.54931 | 0.10572 | 3.7022 | 0.66757 | 5.8001 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.27 | 12 | 13 | 8.89 | 119 | 160 | 15.8 | 0.512 |  | 5.89 | 7 | 0.06 | 5.99 | 8 |  | 5.96 | 7 | [8 empty] | 0.051 | [14 empty] | 0.027 | 1 | 0.39 |  | 0.057 | 0.01 | 1 | 0.33 |  | 0.022 | 1 | 0.4 | [38 empty] | 9000 | [6 empty] | 0 | 0 | 0 | 230 | 230 | 280 | 630 | 650 | 610 | 650 | 640 | 650 | 750 |  | 820 | 820 | 930 | 70 | 90 | 10 | 1157 | 240 | 204 | 40 | 52 | 6 | 590 | 120 | 163 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43467.9767 | 1,2,3 | 30 | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 12.8059 | 1,3 | 9.4032 | 22.2091 | 1.8158 | 43467.9767 | 91.3066 | 8731.2104 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4219 | 1.4219 | 1.5199 | 0.31116 | 0.32104 | 0.30129 | 0.32104 | 0.27977 | 0.28414 | 1.4267 | 3 | 0.060085 | 0.060085 | 0.059835 | 1.1175 | 0.54139 | 0.10034 | 4.0002 | 0.76029 | 4.1336 | 1.1214 | 0.54931 | 0.10572 | 3.7022 | 0.66757 | 5.8001 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.044 | [9 empty] | 6.11 | 0.36 | 4 | 0.62 | 14.7 | 9 | 0.65066 |  | 6.1 | 0.336 | 4 | 0.61 | 14.6 | 9 | 0.65066 | 6.05 | 0.26 | 4 | 0.79 | 16 | 10 | 0.49037 |  |  |  | 0.013 |  |  |  |  | 0.017 |  |  |  | 0.017 | 7.21 | 0.065 | 1 | 4.2 | 14 | 20 | 48 | 0.015 | 7.34 | 0.052 | 1 | 4.4 | 15.3 | 20 | 46 | 0.015 | 3.9 | 4 | 4.1 | [18 empty] | 9000 | [6 empty] | 0 | 0 | 0 | 230 | 230 | 280 | 630 | 650 | 610 | 650 | 640 | 650 | 750 |  | 820 | 820 | 930 | 70 | 90 | 10 | 1157 | 240 | 204 | 40 | 52 | 6 | 590 | 120 | 163 |  | 9:00 | 0.62 | 9 | 28.2667 | 17.5253 | 6.11 | 14.7 | 15 | 1.1684 | 10 | 6.5 | 0.53066 | 9:00 | 0.61 | 9 | 28.2667 | 17.2427 | 6.1 | 14.6 | 15 | 1.1495 | 10 | 6.5 | 0.53066 | 9:00 | 0.79 | 10 | 27 | 21.33 | 6.05 | 16 | 10 | 2.133 | 15 | 6.5 | 0.37037
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.28 | 12 | 14 | 8.95 | 110 | 163 | 16.1 | 0.487 |  | 5.89 | 7 | 0.059 | 5.78 | 8 |  | 5.74 | 7 | [8 empty] | 0.055 | [14 empty] | 0.022 | 1 | 0.35 |  | 0.057 | 0.01 | 1 | 0.29 |  | 0.022 | 1 | 0.52 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.07 | 0.262 | 4 | 0.71 | 14.9 | 9 | 0.65066 |  | 6.07 | 0.364 | 4 | 0.58 | 14.6 | 9 | 0.65066 | 6.1 | 0.291 | 4 | 0.71 | 16.1 | 10 | 0.49037 | [13 empty] | 7.31 | 0.067 | 1 | 4.5 | 13.6 |  |  |  | 7.45 | 0.065 | 1 | 4.4 | 15.1 |  |  |  | 4 | 4 | 2.9 | [55 empty] | 13:00 | 0.71 | 9 | 28.2667 | 20.0693 | 6.07 | 14.9 | 15 | 1.338 | 10 | 6.5 | 0.53066 | 13:00 | 0.58 | 9 | 28.2667 | 16.3947 | 6.07 | 14.6 | 15 | 1.093 | 10 | 6.5 | 0.53066 | 13:00 | 0.71 | 10 | 27 | 19.17 | 6.1 | 16.1 | 10 | 1.917 | 15 | 6.5 | 0.37037
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.29 | 13 | 14 | 8.61 | 115 | 159 | 16.2 | 0.5 |  | 5.98 | 8 | 0.06 | 6 | 8 |  | 5.99 | 8 | [8 empty] | 0.06 | [14 empty] | 0.027 | 1 | 0.36 |  | 0.056 | 0.018 | 1 | 0.31 |  | 0.021 | 1 | 0.42 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.26 | 0.061 | 1 | 4 | 13.8 |  |  |  | 7.3 | 0.063 | 1 | 4 | 15.1 |  |  |  | 4.1 | 4 | 3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.32 | 11 | 13 | 8 | 120 | 161 | 16 | 0.517 |  | 6.07 | 7 | 0.062 | 6 | 8 |  | 6 | 7 | [8 empty] | 0.05 | [14 empty] | 0.023 | 1 | 0.51 |  | 0.05 | 0.021 | 1 | 0.38 |  | 0.022 | 1 | 0.47 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.031 | [9 empty] | 6.17 | 0.276 | 4 | 0.63 | 14.9 | 7.7 | 0.57401 |  | 6.16 | 0.22 | 4 | 0.53 | 15.2 | 7.7 | 0.42267 | 6.14 | 0.27 | 4 | 0.64 | 16.5 | 8.7 | 0.44222 |  |  |  | 0.019 | [9 empty] | 7.67 | 0.061 | 1 | 4.4 | 13.7 | 20 | 54 | 0.012 | 7.52 | 0.058 | 1 | 4.3 | 15.2 | 20 | 52 | 0.012 | 4.1 | 4 | 3 | [55 empty] | 21:00 | 0.63 | 7.7 | 33.039 | 20.8145 | 6.17 | 14.9 | 15 | 1.3876 | 10 | 6.5 | 0.45401 | 21:00 | 0.53 | 7.7 | 33.039 | 17.5106 | 6.16 | 15.2 | 10 | 1.7511 | 15 | 6.5 | 0.30267 | 21:00 | 0.64 | 8.7 | 31.0345 | 19.8621 | 6.14 | 16.5 | 10 | 1.9862 | 15 | 6.5 | 0.32222
22:00 | [72 empty] | DOSE |  | TOTAL | 41.7 | 41.7 | 46.7 | 130.1 | 39.2 | 39.2 | 44.2 | 122.6 | 0 | 58.7189 | 0 | 57.1075 | 115.8264 | 9.1099 | TOTAL | 451.897 | 43348.615 | 0 | 3251.1013 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0675 | 7.0984 | 7.4624 | 1.5424 | 1.6136 | 1.5135 | 1.5882 | 1.3777 | 1.2759 | 7.1334 | 27 | 0.31754 | 0.31624 | 0.31846 | 5.4891 | 2.7331 | 0.50654 | 19.8644 | 3.6848 | 20.2586 | 5.4694 | 2.744 | 0.50768 | 18.3817 | 3.2019 | 28.7667 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.28 | 11 | 14 | 8.65 | 120 | 158 | 16.1 | 0.516 |  | 6.12 | 7 | 0.061 | 6.1 | 7 |  | 6.06 | 7 | [8 empty] | 0.049 | [14 empty] | 0.022 | 1 | 0.28 |  | 0.048 | 0.017 | 1 | 0.34 |  | 0.022 | 1 | 0.36 | [22 empty] | AVERAGE | 8.34 | 8.34 | 9.34 | 26.02 | 7.84 | 7.84 | 8.84 | 24.52 |  | 11.7438 |  | 11.4215 | 23.1653 | 1.822 | AVERAGE | 90.3794 | 8669.723 |  | 650.2203 | 0 | 0 | 0 |  |  |  | 1.4135 | 1.4197 | 1.4925 | 0.30848 | 0.32272 | 0.3027 | 0.31765 | 0.27553 | 0.25518 | 1.4267 | 5.4 | 0.063508 | 0.063248 | 0.063692 | 1.0978 | 0.54662 | 0.10131 | 3.9729 | 0.73697 | 4.0517 | 1.0939 | 0.54881 | 0.10154 | 3.6763 | 0.64037 | 5.7533 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.73 | 71 | 82 | 52.62 | 702 | 963 | 96.4 | 3.021 | 0.075 | 35.94 | 43 | 0.377 | 35.84 | 47 | 0 | 35.68 | 44 | 0 | 24.36 | 1.184 | 16 | 2.66 | 59.1 | 34.7 | 2.526 | 0.315 | 24.31 | 1.169 | 16 | 2.5 | 59.3 | 34.4 | 2.2886 | 24.3 | 1.036 | 16 | 2.87 | 65.3 | 38.7 | 1.9133 | 0.144 | 6 | 2.22 | 0.032 | 0.318 | 0.085 | 7 | 1.91 | 0.017 | 0.13 | 6 | 2.57 | 0.017 | 43.75 | 0.349 | 6 | 25 | 82 | 40 | 102 | 0.027 | 44.04 | 0.337 | 6 | 25.6 | 92 | 40 | 98 | 0.027 | 23.9 | 23.8 | 19.3 |  |  | MINIMUM | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 |  | 9.5198 |  | 9.4032 | 21.4042 | 1.8158 | MINIMUM | 88.7181 | 8116.3364 |  | 634.3612 | [6 empty] | 1.3696 | 1.3616 | 1.4057 | 0.30425 | 0.32075 | 0.30129 | 0.30425 | 0.26622 | 0.21297 | 1.4267 | 3 | 0.060085 | 0.059522 | 0.059835 | 1.0818 | 0.54139 | 0.10034 | 3.8583 | 0.70181 | 3.776 | 1.0647 | 0.54709 | 0.091255 | 3.598 | 0.57022 | 5.3749 |  | MIN | 0.62 | 9 | 28.2667 | 17.5253 | 6.11 | 14.7 | 15 | 1.1684 |  |  |  | MIN | 0.58 | 9 | 28.2667 | 16.3947 | 6.07 | 14.6 | 15 | 1.093 |  |  |  | MIN | 0.71 | 10 | 27 | 19.17 | 6.1 | 16.1 | 10 | 1.917 |  |  |  | 1.093
AVERAGE | 6.2883 | 11.8333 | 13.6667 | 8.77 | 117 | 160.5 | 16.0667 | 0.5035 | 0.0375 | 5.99 | 7.1667 | 0.062833 | 5.9733 | 7.8333 |  | 5.9467 | 7.3333 |  | 6.09 | 0.296 | 4 | 0.665 | 14.775 | 8.675 | 0.6315 | 0.0525 | 6.0775 | 0.29225 | 4 | 0.625 | 14.825 | 8.6 | 0.57214 | 6.075 | 0.259 | 4 | 0.7175 | 16.325 | 9.675 | 0.47833 | 0.024 | 1 | 0.37 | 0.016 | 0.053 | 0.014167 | 1.1667 | 0.31833 | 0.017 | 0.021667 | 1 | 0.42833 | 0.017 | 7.2917 | 0.058167 | 1 | 4.1667 | 13.6667 | 20 | 51 | 0.0135 | 7.34 | 0.056167 | 1 | 4.2667 | 15.3333 | 20 | 49 | 0.0135 | 3.9833 | 3.9667 | 3.2167 |  |  | MAXIMUM | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 14.0674 |  | 14.5325 | 28.5998 | 1.8261 | MAXIMUM | 91.3066 | 9038.6474 |  | 697.7974 | [6 empty] | 1.4663 | 1.4663 | 1.5199 | 0.31158 | 0.3296 | 0.30425 | 0.32115 | 0.27977 | 0.28414 | 1.4267 | 7 | 0.068895 | 0.068275 | 0.069973 | 1.1175 | 0.55031 | 0.10199 | 4.0094 | 0.76029 | 4.1336 | 1.1214 | 0.55124 | 0.10646 | 3.734 | 0.67226 | 5.9892
MINIMUM | 6.27 | 11 | 13 | 8 | 110 | 158 | 15.8 | 0.487 | 0.031 | 5.89 | 7 | 0.059 | 5.78 | 7 |  | 5.74 | 7 |  | 6.01 | 0.262 | 4 | 0.62 | 14.6 | 7.7 | 0.57401 | 0.049 | 5.98 | 0.22 | 4 | 0.53 | 14.6 | 7.7 | 0.42267 | 6.01 | 0.215 | 4 | 0.64 | 16 | 8.7 | 0.44222 | 0.022 | 1 | 0.28 | 0.013 | 0.048 | 0.009 | 1 | 0.26 | 0.017 | 0.021 | 1 | 0.36 | 0.017 | 7.14 | 0.044 | 1 | 3.9 | 13.4 | 20 | 48 | 0.012 | 7.12 | 0.047 | 1 | 4 | 15.1 | 20 | 46 | 0.012 | 3.9 | 3.9 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 48060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245 | 1250 | 1480 | 3380 | 3540 | 3320 | 3480 | 3380 | 3120 | 3750 | 0 | 4740 | 4720 | 5360 | 374 | 495 | 55 | 6254 | 1265 | 1087 | 210 | 280 | 31 | 3146 | 620 | 871
MAXIMUM | 6.32 | 13 | 14 | 9.52 | 120 | 163 | 16.2 | 0.517 | 0.044 | 6.12 | 8 | 0.075 | 6.1 | 8 |  | 6.06 | 8 |  | 6.17 | 0.36 | 4 | 0.71 | 14.9 | 9 | 0.65066 | 0.06 | 6.16 | 0.364 | 4 | 0.78 | 15.2 | 9 | 0.65066 | 6.14 | 0.291 | 4 | 0.79 | 16.7 | 10 | 0.49037 | 0.027 | 1 | 0.51 | 0.019 | 0.057 | 0.021 | 2 | 0.38 | 0.017 | 0.022 | 1 | 0.52 | 0.017 | 7.67 | 0.067 | 1 | 4.5 | 14 | 20 | 54 | 0.015 | 7.52 | 0.065 | 1 | 4.4 | 15.7 | 20 | 52 | 0.015 | 4.1 | 4 | 4.1 | [17 empty] | AVERAGE | 9612 | [9 empty] | 249 | 250 | 296 | 676 | 708 | 664 | 696 | 676 | 624 | 750 |  | 948 | 944 | 1072 | 74.8 | 99 | 11 | 1250.8 | 253 | 217.4 | 42 | 56 | 6.2 | 629.2 | 124 | 174.2
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.97 |  | TOTAL AVG COAG ALK: |  |  |  | 7.4444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.364 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.53 | [5 empty] | 6.0808 |  |  |  |  | 0.027 |  |  |  |  | 0.53 | [6 empty] | 0.027 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 9000 | [9 empty] | 230 | 230 | 280 | 630 | 650 | 610 | 650 | 640 | 540 | 750 |  | 820 | 820 | 930 | 70 | 90 | 10 | 1157 | 240 | 204 | 40 | 52 | 6 | 590 | 110 | 163
[90 empty] | MAXIMUM | 10300 | [9 empty] | 280 | 280 | 320 | 720 | 780 | 720 | 760 | 720 | 720 | 750 |  | 1110 | 1100 | 1260 | 80 | 108 | 12 | 1370 | 280 | 240 | 44 | 60 | 7 | 680 | 140 | 195
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.864 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827078 |  | END: | 23827078 |  |  | Alum | 4970 | 11531 | 11531 | 11885 | 11885 | 0 | [44 empty] | 0.58 | 9 | 28.2667 | 16.3947 | 6.07 | 14.6 | 15 | 1.093
[73 empty] | FINISHED 2 | 10.654 |  | TOTAL MGD: |  | 11.864 |  |  | FINISHED SOUTH 2 |  | START: | 43844043 |  | END: | 43855907 |  |  | Caustic | 4884 | 6517 | 6517
[73 empty] | TOTAL RAW | 25.555 |  | TOTAL MGD: |  | 4.572 |  |  | FINISHED CONWAY |  | START: | 10226073 |  | END: | 10230645 |  |  | Hypochlorite | 22 |  | 42
[76 empty] | TOTAL MGD: |  | 6.082 |  |  | FINISHED PERRY |  | START: | 33851287 |  | END: | 33857369 |  |  | Phosphate | 2643
[76 empty] | TOTAL MGD: |  | 8.34 |  |  | RAW PLANT 1 |  | START: | 30963986 |  | END: | 30972326 |  |  | Fluoride | 4000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.1 |  |  | RAW PLANT 2 |  | START: | 30923597 |  | END: | 30931697 |  |  | Cal~Flo | 12.76 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.115 |  |  | RAW PLANT 3 |  | START: | 7498067 |  | END: | 7507182 |  |  | Zinc | 929
[76 empty] | TOTAL MGD: |  | 0.705 |  |  | DECANT |  | START: | 1864136 |  | END: | 1864841 |  |  | Polymer | 19
[76 empty] | TOTAL MGD: |  | 1.6365 |  |  | BLOW DOWN |  | START: | 9131.3661 |  | END: | 9133.0026 |  |  | NH3 | 7.63 |  | BI-SUL | 1200
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827078
43855907
10230645
33857369
30972326
30931697
7507182
1864841
9133.0026
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CP45: Truck out
Note on CQ45: End of Day
Note on CR45: gal/day
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 3
DATE: | 2019-01-03 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-03 | [23 empty] | DATE: | 2019-01-03
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-03 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43468.0135 | 1,2,3 | 30 | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 12.8059 | 1,3 | 9.4032 | 22.2091 | 1.8158 | 43468.0135 | 91.3066 | 8731.2104 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4219 | 1.4219 | 1.5199 | 0.31116 | 0.32104 | 0.30129 | 0.32104 | 0.27977 | 0.28414 | 1.4267 | 3 | 0.060085 | 0.060085 | 0.059835 | 1.1175 | 0.54139 | 0.10034 | 4.0002 | 0.76029 | 4.1336 | 1.1214 | 0.54931 | 0.10572 | 3.7022 | 0.66757 | 5.8001 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.293 | 4 | 0.56 | 15 | 7.7 | 0.42267 |  | 6.17 | 0.259 | 4 | 0.51 | 15.5 | 7.7 | 0.42267 | 6.15 | 0.298 | 4 | 0.71 | 17 | 8.7 | 0.44222 | [13 empty] | 7.6 | 0.065 | 1 | 3.9 | 13.7 |  |  |  | 7.4 | 0.068 | 1 | 4.2 | 15.3 |  |  |  | 4.1 | 4 | 3.1 | [18 empty] | 9000 | [6 empty] | 0 | 0 | 0 | 230 | 230 | 280 | 630 | 650 | 610 | 650 | 640 | 650 | 750 |  | 820 | 820 | 930 | 70 | 90 | 10 | 1157 | 240 | 204 | 40 | 52 | 6 | 590 | 120 | 163 |  | 1:00 | 0.56 | 7.7 | 33.039 | 18.5018 | 6.19 | 15 | 10 | 1.8502 | 15 | 6.5 | 0.30267 | 1:00 | 0.51 | 7.7 | 33.039 | 16.8499 | 6.17 | 15.5 | 10 | 1.685 | 15 | 6.5 | 0.30267 | 1:00 | 0.71 | 8.7 | 31.0345 | 22.0345 | 6.15 | 17 | 10 | 2.2034 | 15 | 6.5 | 0.32222
2:00 | [72 empty] | 43468.0886 | 1,2,3 | 30 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 9.9504 | 1,3 | 12.7901 | 22.7405 | 1.8158 | 43468.0886 | 90.625 | 8731.2104 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3696 | 1.4267 | 1.5175 | 0.31158 | 0.32075 | 0.30242 | 0.32075 | 0.27808 | 0.26581 | 1.4267 | 3 | 0.060198 | 0.059522 | 0.059952 | 1.0905 | 0.54972 | 0.10188 | 3.8733 | 0.70181 | 4.0962 | 1.0972 | 0.55124 | 0.098514 | 3.634 | 0.57022 | 5.8025 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.33 | 11 | 13 | 8.47 | 122 | 164 | 15.9 | 0.523 |  | 6.1 | 7 | 0.072 | 6.0605 | 7 |  | 6.03 | 7 | [8 empty] | 0.055 | [14 empty] | 0.026 | 1 | 0.26 |  | 0.051 | 0.022 | 1 | 0.37 |  | 0.022 | 1 | 0.47 | [38 empty] | 9600 | [6 empty] | 0 | 0 | 0 | 240 | 250 | 300 | 680 | 700 | 660 | 700 | 680 | 650 | 750 |  | 890 | 880 | 1000 | 74 | 99 | 11 | 1210 | 240 | 219 | 42 | 56 | 6 | 620 | 110 | 175 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43468.3157 | 1,2,3 | 30 | 8 | 8 | 9 | 25 | 7.5 | 7.5 | 8.5 | 23.5 | ,1,3 | 8.8646 | 1,3 | 11.0304 | 19.895 | 1.8158 | 43468.3157 | 90.6601 | 8485.2608 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4244 | 1.4244 | 1.4663 | 0.309 | 0.31376 | 0.2995 | 0.29474 | 0.28312 | 0.27044 | 1.4267 | 5 | 0.058385 | 0.059089 | 0.060206 | 1.0728 | 0.54861 | 0.10596 | 3.9794 | 0.68426 | 4.1044 | 1.0818 | 0.52993 | 0.10199 | 3.6401 | 0.59034 | 5.664 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.62 | 0.061 | 1 | 4.1 | 13.8 |  |  |  | 7.32 | 0.058 | 1 | 4.1 | 15.2 |  |  |  | 4.1 | 4 | 3 | [18 empty] | 9270 | [6 empty] | 0 | 0 | 0 | 240 | 240 | 280 | 650 | 660 | 630 | 620 | 670 | 640 | 750 |  | 830 | 840 | 970 | 70 | 95 | 11 | 1200 | 225 | 211 | 40 | 52 | 6 | 600 | 110 | 165 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43468.5807 | 1,2 | 47 | 7.3 | 7.3 | 8.3 | 22.9 | 6.8 | 6.8 | 7.8 | 21.4 | ,1,3 | 12.6518 | 1,3 | 10.6891 | 23.341 | 1.8158 | 43468.5807 | 90.7101 | 7870.3868 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3747 | 1.4074 | 1.4838 | 0.3178 | 0.3178 | 0.30217 | 0.30217 | 0.29784 | 0.28409 | 1.4267 | 5 | 0.061292 | 0.060516 | 0.060198 | 1.0987 | 0.54776 | 0.10624 | 3.9305 | 0.68762 | 4.1407 | 1.11 | 0.55527 | 0.11114 | 3.6181 | 0.66087 | 5.7982 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.27 | 12 | 13 | 8.71 | 114 | 160 | 15.9 | 0.502 |  | 6.03 | 7 | 0.061 | 5.94 | 7 |  | 5.93 | 7 | [8 empty] | 0.055 | [14 empty] | 0.022 | 1 | 0.3 |  | 0.057 | 0.02 | 1 | 0.36 |  | 0.022 | 1 | 0.42 | [38 empty] | 8496 | [6 empty] | 0 | 0 | 0 | 210 | 215 | 260 | 610 | 610 | 580 | 580 | 650 | 620 | 750 |  | 790 | 780 | 890 | 65 | 86 | 10 | 1060 | 205 | 193 | 38 | 50 | 6 | 540 | 113 | 155 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43468.8175 | 1,2 | 60 | 7.3 | 7.3 | 8.3 | 22.9 | 6.8 | 6.8 | 7.8 | 21.4 | ,1,3 | 8.7566 | 3 | 9.4824 | 18.239 | 1.8288 | 43468.8175 | 89.6851 | 7685.9246 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4139 | 1.4139 | 1.5408 | 0.3178 | 0.3178 | 0.30217 | 0.30217 | 0.29784 | 0.29784 | 1.4267 | 5 | 0.05974 | 0.05974 | 0.060198 | 1.0311 | 0.54776 | 0.095616 | 3.9946 | 0.7547 | 4.1407 | 1.1789 | 0.55527 | 0.09262 | 3.6936 | 0.67841 | 5.3119 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6.05 | 0.342 | 3 | 0.55 | 15.1 | 8.1 | 0.4384 |  | 6.09 | 0.317 | 3 | 0.59 | 15.3 | 8.1 | 0.4384 | 6.1 | 0.287 | 3 | 0.65 | 16.8 | 9.1 | 0.45704 |  |  |  | 0.011 |  |  |  |  | 0.013 |  |  |  | 0.021 | 7.15 | 0.054 | 1 | 4.3 | 13.7 | 20 | 49 | 0.019 | 7.27 | 0.055 | 1 | 4.5 | 15.3 | 20 | 48 | 0.01 | 4 | 3.9 | 4.1 | [18 empty] | 8400 | [6 empty] | 0 | 0 | 0 | 216 | 216 | 270 | 610 | 610 | 580 | 580 | 650 | 650 | 750 |  | 770 | 770 | 890 | 61 | 86 | 9 | 1100 | 225 | 193 | 40 | 50 | 5 | 570 | 116 | 142 |  | 9:00 | 0.55 | 8.1 | 31.4074 | 17.2741 | 6.05 | 15.1 | 10 | 1.7274 | 15 | 6.5 | 0.3184 | 9:00 | 0.59 | 8.1 | 31.4074 | 18.5304 | 6.09 | 15.3 | 10 | 1.853 | 15 | 6.5 | 0.3184 | 9:00 | 0.65 | 9.1 | 29.6703 | 19.2857 | 6.1 | 16.8 | 10 | 1.9286 | 15 | 6.5 | 0.33704
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.24 | 12 | 12 | 8.65 | 111 | 156 | 16.1 | 0.486 |  | 5.97 | 7 | 0.087 | 6.05 | 8 |  | 6.02 | 7 | [8 empty] | 0.057 | [14 empty] | 0.026 | 1 | 0.31 |  | 0.053 | 0.017 | 1 | 0.44 |  | 0.024 | 1 | 0.46 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.04 | 0.352 | 3 | 0.56 | 15.1 | 8 | 0.43447 |  | 6.14 | 0.351 | 3 | 0.6 | 15 | 8 | 0.43447 | 6.03 | 0.305 | 3 | 0.67 | 16.4 | 9 | 0.45333 | [13 empty] | 7.4 | 0.058 | 1 | 4.3 | 14 |  |  |  | 7.37 | 0.054 | 1 | 4.2 | 15.5 |  |  |  | 4 | 3.8 | 2.8 | [55 empty] | 13:00 | 0.56 | 8 | 31.8 | 17.808 | 6.04 | 15.1 | 10 | 1.7808 | 15 | 6.5 | 0.31447 | 13:00 | 0.6 | 8 | 31.8 | 19.08 | 6.14 | 15 | 10 | 1.908 | 15 | 6.5 | 0.31447 | 13:00 | 0.67 | 9 | 30 | 20.1 | 6.03 | 16.4 | 10 | 2.01 | 15 | 6.5 | 0.33333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.25 | 12 | 13 | 8.96 | 110 | 155 | 16.5 | 0.479 |  | 6.06 | 8 | 0.062 | 6.13 | 9 |  | 6.11 | 8 | [8 empty] | 0.06 | [14 empty] | 0.023 | 1 | 0.29 |  | 0.054 | 0.023 | 1 | 0.32 |  | 0.022 | 1 | 0.36 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.31 | 0.064 | 1 | 4.2 | 14 |  |  |  | 7.49 | 0.062 | 1 | 4.2 | 15.6 |  |  |  | 4 | 3.8 | 2.1 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.31 | 12 | 12 | 8.2 | 113 | 158 | 16.5 | 0.506 |  | 6.1 | 8 | 0.056 | 6.13 | 8 |  | 6.13 | 8 | [8 empty] | 0.052 | [14 empty] | 0.022 | 1 | 0.26 |  | 0.05 | 0.02 | 1 | 0.3 |  | 0.025 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.032 | [9 empty] | 6.21 | 0.212 | 4 | 0.56 | 15.4 | 7.3 | 0.40695 |  | 6.23 | 0.221 | 3 | 0.57 | 16 | 7.3 | 0.40695 | 6.2 | 0.205 | 3 | 0.74 | 17.1 | 8.3 | 0.42741 |  |  |  | 0.009 | [9 empty] | 7.52 | 0.059 | 1 | 4.5 | 14.5 | 20 | 52 | 0.009 | 7.32 | 0.064 | 1 | 3.9 | 15.5 | 20 | 54 | 0.012 | 4.1 | 3.8 | 2.8 | [55 empty] | 21:00 | 0.56 | 7.3 | 34.8493 | 19.5156 | 6.21 | 15.4 | 10 | 1.9516 | 15 | 6.5 | 0.28695 | 21:00 | 0.57 | 7.3 | 34.8493 | 19.8641 | 6.23 | 16 | 10 | 1.9864 | 15 | 6.5 | 0.28695 | 21:00 | 0.74 | 8.3 | 32.5301 | 24.0723 | 6.2 | 17.1 | 10 | 2.4072 | 15 | 6.5 | 0.30741
22:00 | [72 empty] | DOSE |  | TOTAL | 38.6 | 38.6 | 43.6 | 120.8 | 36.1 | 36.1 | 41.1 | 113.3 | 0 | 53.0294 | 3 | 53.3952 | 106.4246 | 9.0922 | TOTAL | 452.987 | 41503.993 | 0 | 3044.9339 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0045 | 7.0943 | 7.5283 | 1.5673 | 1.5911 | 1.5075 | 1.5409 | 1.4366 | 1.4023 | 7.1334 | 21 | 0.2997 | 0.29895 | 0.30039 | 5.4106 | 2.7352 | 0.51003 | 19.778 | 3.5887 | 20.6156 | 5.5893 | 2.741 | 0.50999 | 18.2879 | 3.1674 | 28.3767 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.35 | 12 | 12 | 8.4 | 120 | 157 | 16.4 | 0.518 |  | 6.02 | 8 | 0.067 | 6.18 | 8 |  | 6.14 | 8 | [8 empty] | 0.054 | [14 empty] | 0.023 | 1 | 0.35 |  | 0.052 | 0.015 | 1 | 0.31 |  | 0.022 | 1 | 0.36 | [22 empty] | AVERAGE | 7.72 | 7.72 | 8.72 | 24.16 | 7.22 | 7.22 | 8.22 | 22.66 |  | 10.6059 | 3 | 10.679 | 21.2849 | 1.8184 | AVERAGE | 90.5974 | 8300.7986 |  | 608.9868 | 0 | 0 | 0 |  |  |  | 1.4009 | 1.4189 | 1.5057 | 0.31347 | 0.31823 | 0.30151 | 0.30817 | 0.28733 | 0.28046 | 1.4267 | 4.2 | 0.05994 | 0.05979 | 0.060078 | 1.0821 | 0.54705 | 0.10201 | 3.9556 | 0.71773 | 4.1231 | 1.1179 | 0.54821 | 0.102 | 3.6576 | 0.63348 | 5.6753 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.75 | 71 | 75 | 51.39 | 690 | 950 | 97.3 | 3.014 | 0.069 | 36.28 | 45 | 0.405 | 36.4905 | 47 | 0 | 36.36 | 45 | 0 | 24.49 | 1.199 | 14 | 2.23 | 60.6 | 31.1 | 1.7025 | 0.333 | 24.63 | 1.148 | 13 | 2.27 | 61.8 | 31.1 | 1.7025 | 24.48 | 1.095 | 13 | 2.77 | 67.3 | 35.1 | 1.78 | 0.142 | 6 | 1.77 | 0.02 | 0.317 | 0.117 | 6 | 2.1 | 0.013 | 0.137 | 6 | 2.53 | 0.021 | 44.6 | 0.361 | 6 | 25.3 | 83.7 | 40 | 101 | 0.028 | 44.17 | 0.361 | 6 | 25.1 | 92.4 | 40 | 102 | 0.022 | 24.3 | 23.3 | 17.9 |  |  | MINIMUM | 7.3 | 7.3 | 8.3 | 22.9 | 6.8 | 6.8 | 7.8 | 21.4 |  | 8.7566 | 3 | 9.4032 | 18.239 | 1.8158 | MINIMUM | 89.6851 | 7685.9246 |  | 570.9251 | [6 empty] | 1.3696 | 1.4074 | 1.4663 | 0.309 | 0.31376 | 0.2995 | 0.29474 | 0.27808 | 0.26581 | 1.4267 | 3 | 0.058385 | 0.059089 | 0.059835 | 1.0311 | 0.54139 | 0.095616 | 3.8733 | 0.68426 | 4.0962 | 1.0818 | 0.52993 | 0.09262 | 3.6181 | 0.57022 | 5.3119 |  | MIN | 0.55 | 8.1 | 31.4074 | 17.2741 | 6.05 | 15.1 | 10 | 1.7274 |  |  |  | MIN | 0.51 | 7.7 | 33.039 | 16.8499 | 6.17 | 15.5 | 10 | 1.685 |  |  |  | MIN | 0.65 | 9.1 | 29.6703 | 19.2857 | 6.1 | 16.8 | 10 | 1.9286 |  |  |  | 1.685
AVERAGE | 6.2917 | 11.8333 | 12.5 | 8.565 | 115 | 158.3333 | 16.2167 | 0.50233 | 0.0345 | 6.0467 | 7.5 | 0.0675 | 6.0817 | 7.8333 |  | 6.06 | 7.5 |  | 6.1225 | 0.29975 | 3.5 | 0.5575 | 15.15 | 7.775 | 0.42562 | 0.0555 | 6.1575 | 0.287 | 3.25 | 0.5675 | 15.45 | 7.775 | 0.42562 | 6.12 | 0.27375 | 3.25 | 0.6925 | 16.825 | 8.775 | 0.445 | 0.023667 | 1 | 0.295 | 0.01 | 0.052833 | 0.0195 | 1 | 0.35 | 0.013 | 0.022833 | 1 | 0.42167 | 0.021 | 7.4333 | 0.060167 | 1 | 4.2167 | 13.95 | 20 | 50.5 | 0.014 | 7.3617 | 0.060167 | 1 | 4.1833 | 15.4 | 20 | 51 | 0.011 | 4.05 | 3.8833 | 2.9833 |  |  | MAXIMUM | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 |  | 12.8059 | 3 | 12.7901 | 23.341 | 1.8288 | MAXIMUM | 91.3066 | 8731.2104 |  | 634.3612 | [6 empty] | 1.4244 | 1.4267 | 1.5408 | 0.3178 | 0.32104 | 0.30242 | 0.32104 | 0.29784 | 0.29784 | 1.4267 | 5 | 0.061292 | 0.060516 | 0.060206 | 1.1175 | 0.54972 | 0.10624 | 4.0002 | 0.76029 | 4.1407 | 1.1789 | 0.55527 | 0.11114 | 3.7022 | 0.67841 | 5.8025
MINIMUM | 6.24 | 11 | 12 | 8.2 | 110 | 155 | 15.9 | 0.479 | 0.032 | 5.97 | 7 | 0.056 | 5.94 | 7 |  | 5.93 | 7 |  | 6.04 | 0.212 | 3 | 0.55 | 15 | 7.3 | 0.40695 | 0.052 | 6.09 | 0.221 | 3 | 0.51 | 15 | 7.3 | 0.40695 | 6.03 | 0.205 | 3 | 0.65 | 16.4 | 8.3 | 0.42741 | 0.022 | 1 | 0.26 | 0.009 | 0.05 | 0.015 | 1 | 0.3 | 0.013 | 0.022 | 1 | 0.36 | 0.021 | 7.15 | 0.054 | 1 | 3.9 | 13.7 | 20 | 49 | 0.009 | 7.27 | 0.054 | 1 | 3.9 | 15.2 | 20 | 48 | 0.01 | 4 | 3.8 | 2.1 | [15 empty] | MIL/MIN |  | TOTAL | 44766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 1151 | 1390 | 3180 | 3230 | 3060 | 3130 | 3290 | 3210 | 3750 | 0 | 4100 | 4090 | 4680 | 340 | 456 | 51 | 5727 | 1135 | 1020 | 200 | 260 | 29 | 2920 | 569 | 800
MAXIMUM | 6.35 | 12 | 13 | 8.96 | 122 | 164 | 16.5 | 0.523 | 0.037 | 6.1 | 8 | 0.087 | 6.18 | 9 |  | 6.14 | 8 |  | 6.21 | 0.352 | 4 | 0.56 | 15.4 | 8.1 | 0.4384 | 0.06 | 6.23 | 0.351 | 4 | 0.6 | 16 | 8.1 | 0.4384 | 6.2 | 0.305 | 4 | 0.74 | 17.1 | 9.1 | 0.45704 | 0.026 | 1 | 0.35 | 0.011 | 0.057 | 0.023 | 1 | 0.44 | 0.013 | 0.025 | 1 | 0.47 | 0.021 | 7.62 | 0.065 | 1 | 4.5 | 14.5 | 20 | 52 | 0.019 | 7.49 | 0.068 | 1 | 4.5 | 15.6 | 20 | 54 | 0.012 | 4.1 | 4 | 4.1 | [17 empty] | AVERAGE | 8953.2 | [9 empty] | 227.2 | 230.2 | 278 | 636 | 646 | 612 | 626 | 658 | 642 | 750 |  | 820 | 818 | 936 | 68 | 91.2 | 10.2 | 1145.4 | 227 | 204 | 40 | 52 | 5.8 | 584 | 113.8 | 160
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0628 |  | TOTAL AVG COAG ALK: |  |  |  | 7.6111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.352 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.51 | [5 empty] | 6.1333 |  |  |  |  | 0.026 |  |  |  |  | 0.51 | [6 empty] | 0.026 | [16 empty] | Pump Station MIN |  | 2.1 | [17 empty] | MINIMUM | 8400 | [9 empty] | 210 | 215 | 260 | 610 | 610 | 580 | 580 | 640 | 620 | 750 |  | 770 | 770 | 890 | 61 | 86 | 9 | 1060 | 205 | 193 | 38 | 50 | 5 | 540 | 110 | 142
[90 empty] | MAXIMUM | 9600 | [9 empty] | 240 | 250 | 300 | 680 | 700 | 660 | 700 | 680 | 650 | 750 |  | 890 | 880 | 1000 | 74 | 99 | 11 | 1210 | 240 | 219 | 42 | 56 | 6 | 620 | 120 | 175
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.666 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827078 |  | END: | 23827078 |  |  | Alum | 7269 | 11142 | 11142 | 11624 | 11624 | 0 | [44 empty] | 0.51 | 7.7 | 33.039 | 16.8499 | 6.17 | 15.5 | 10 | 1.685
[73 empty] | FINISHED 2 | 11.353 |  | TOTAL MGD: |  | 10.666 |  |  | FINISHED SOUTH 2 |  | START: | 43855907 |  | END: | 43866573 |  |  | Caustic | 4821 | 6492 | 6492
[73 empty] | TOTAL RAW | 25.359 |  | TOTAL MGD: |  | 4.864 |  |  | FINISHED CONWAY |  | START: | 10230645 |  | END: | 10235509 |  |  | Hypochlorite | 21 |  | 38
[76 empty] | TOTAL MGD: |  | 6.489 |  |  | FINISHED PERRY |  | START: | 33857369 |  | END: | 33863858 |  |  | Phosphate | 2641
[76 empty] | TOTAL MGD: |  | 8.283 |  |  | RAW PLANT 1 |  | START: | 30972326 |  | END: | 30980609 |  |  | Fluoride | 3800 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 7.995 |  |  | RAW PLANT 2 |  | START: | 30931697 |  | END: | 30939692 |  |  | Cal~Flo | 17 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.081 |  |  | RAW PLANT 3 |  | START: | 7507182 |  | END: | 7516263 |  |  | Zinc | 940
[76 empty] | TOTAL MGD: |  | 0.825 |  |  | DECANT |  | START: | 1864841 |  | END: | 1865666 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.7438 |  |  | BLOW DOWN |  | START: | 9133.0026 |  | END: | 9134.7464 |  |  | NH3 | 7.39 |  | BI-SUL | 1200
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 600
23827078
43866573
10235509
33863858
30980609
30939692
7516263
1865666
9134.7464
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.comBCOperator:
Note on CN42: PRE
Note on CP42: post
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959

## 4
DATE: | 2019-01-04 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-04 | [23 empty] | DATE: | 2019-01-04
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-04 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43469.0034 | 1,2 | 60 | 8.5 | 7.4 | 9.4 | 25.3 | 8 | 6.9 | 8.9 | 23.8 | ,1,3 | 14.2344 | 1,3 | 13.824 | 28.0584 | 1.8475 | 43469.0034 | 89.875 | 7685.9246 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4021 | 1.3999 | 1.5004 | 0.31767 | 0.31767 | 0.30836 | 0.30836 | 0.29939 | 0.29939 | 1.4267 | 35 | 0.060012 | 0.060404 | 0.059871 | 1.08 | 0.55229 | 0.096971 | 4.0095 | 0.75315 | 4.1124 | 1.1107 | 0.55477 | 0.097407 | 3.7019 | 0.6817 | 5.3111 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.13 | 0.286 | 5 | 0.55 | 15.2 | 8.5 | 0.45412 |  | 6.11 | 0.283 | 5 | 0.52 | 16 | 7.4 | 0.41088 | 6.12 | 0.282 | 5 | 0.69 | 17.2 | 9.4 | 0.46815 | [13 empty] | 7.36 | 0.055 | 1 | 4.1 | 14 |  |  |  | 7.31 | 0.062 | 1 | 4.1 | 15.6 |  |  |  | 4 | 3.9 | 2.9 | [18 empty] | 9300 | [6 empty] | 0 | 0 | 0 | 252 | 217 | 300 | 710 | 710 | 600 | 600 | 740 | 740 | 750 |  | 910 | 790 | 1010 | 70 | 95 | 10 | 1210 | 246 | 210 | 43 | 57 | 6 | 652 | 133 | 162 |  | 1:00 | 0.55 | 8.5 | 29.9294 | 16.4612 | 6.13 | 15.2 | 10 | 1.6461 | 15 | 6.5 | 0.33412 | 1:00 | 0.52 | 7.4 | 34.3784 | 17.8768 | 6.11 | 16 | 10 | 1.7877 | 15 | 6.5 | 0.29088 | 1:00 | 0.69 | 9.4 | 28.7234 | 19.8191 | 6.12 | 17.2 | 10 | 1.9819 | 15 | 6.5 | 0.34815
2:00 | [72 empty] | 43469.1606 | 1,2 | 60 | 8.5 | 7.4 | 9.4 | 25.3 | 8 | 6.9 | 8.9 | 23.8 | ,1,3 | 10.6776 | 1,3 | 12.0744 | 22.752 | 1.8475 | 43469.1606 | 89.875 | 7685.9246 | 0 | 570.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4021 | 1.3999 | 1.5004 | 0.31767 | 0.31767 | 0.30836 | 0.30836 | 0.29939 | 0.29939 | 1.4267 | 35 | 0.060012 | 0.060404 | 0.059871 | 1.08 | 0.55229 | 0.096971 | 4.0095 | 0.75315 | 4.1124 | 1.1107 | 0.55477 | 0.097407 | 3.7019 | 0.6817 | 5.3111 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.21 | 12 | 12 | 8.47 | 122 | 160 | 15.4 | 0.527 |  | 6.1 | 7 | 0.068 | 6.09 | 7 |  | 6.08 | 7 | [8 empty] | 0.058 | [14 empty] | 0.024 | 1 | 0.38 |  | 0.053 | 0.018 | 1 | 0.27 |  | 0.022 | 1 | 0.38 | [38 empty] | 9300 | [6 empty] | 0 | 0 | 0 | 252 | 217 | 300 | 710 | 710 | 600 | 600 | 740 | 740 | 750 |  | 910 | 790 | 1010 | 70 | 95 | 10 | 1210 | 246 | 210 | 43 | 57 | 6 | 652 | 133 | 162 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43469.2875 | 1,2,3 | 60 | 8.3 | 8.3 | 9.4 | 26 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 10.332 | 1,3 | 11.268 | 21.6 | 1.8475 | 43469.2875 | 90.6996 | 7993.3616 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3696 | 1.3125 | 1.5004 | 0.307 | 0.29325 | 0.27492 | 0.27034 | 0.27107 | 0.24275 | 1.4267 | 7 | 0.059522 | 0.060198 | 0.059871 | 1.0905 | 0.54972 | 0.1 | 3.9895 | 0.67256 | 4.1149 | 1.0849 | 0.53531 | 0.097407 | 3.5378 | 0.56381 | 5.3111 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.46 | 0.059 | 1 | 4.1 | 14.3 |  |  |  | 7.55 | 0.06 | 1 | 4.2 | 15.4 |  |  |  | 4 | 3.8 | 2.9 | [18 empty] | 9645 | [6 empty] | 0 | 0 | 0 | 240 | 230 | 300 | 670 | 640 | 600 | 590 | 670 | 600 | 750 |  | 880 | 890 | 1010 | 74 | 99 | 10 | 1260 | 230 | 220 | 42 | 55 | 6 | 620 | 110 | 162 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43469.5496 | 1,2,3 | 60 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 10.8374 | 1,3 | 13.5965 | 24.4339 | 1.8475 | 43469.5496 | 90.7178 | 7993.3616 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3616 | 1.3616 | 1.4057 | 0.27467 | 0.27044 | 0.25777 | 0.24509 | 0.27573 | 0.24568 | 1.5218 | 7 | 0.058965 | 0.059585 | 0.059977 | 1.0953 | 0.55031 | 0.10199 | 4.0167 | 0.72451 | 4.1193 | 1.0889 | 0.54709 | 0.10646 | 3.4971 | 0.57622 | 5.3135 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.27 | 13 | 13 | 9.28 | 122 | 162 | 16.5 | 0.506 |  | 6.03 | 8 | 0.058 | 6.07 | 7 |  | 6.06 | 7 | [8 empty] | 0.049 | [14 empty] | 0.022 | 1 | 0.31 |  | 0.043 | 0.023 | 1 | 0.3 |  | 0.023 | 1 | 0.47 | [38 empty] | 10389 | [6 empty] | 0 | 0 | 0 | 260 | 260 | 300 | 650 | 640 | 610 | 580 | 725 | 646 | 800 |  | 950 | 960 | 1080 | 81 | 108 | 12 | 1400 | 270 | 240 | 45 | 60 | 7 | 620 | 120 | 173 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43469.8497 | 1,2,3 | 41 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 13.0709 | 1,3 | 13.7261 | 26.797 | 1.8576 | 43469.8497 | 90.8138 | 8485.2608 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4139 | 1.4139 | 1.4057 | 0.27044 | 0.27044 | 0.26199 | 0.24932 | 0.27763 | 0.27002 | 1.5218 | 20 | 0.060206 | 0.060206 | 0.061088 | 1.0818 | 0.5605 | 0.093491 | 3.9996 | 0.75135 | 4.1193 | 1.0889 | 0.54709 | 0.10646 | 3.716 | 0.67226 | 5.3135 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.043 | [9 empty] | 6.11 | 0.36 | 5 | 0.51 | 15 | 8.6 | 0.45805 |  | 6.16 | 0.224 | 4 | 0.47 | 15.2 | 8.2 | 0.44233 | 6.17 | 0.2 | 5 | 0.65 | 16.6 | 9.7 | 0.47926 |  |  |  | 0.011 |  |  |  |  | 0.014 |  |  |  | 0.009 | 7.25 | 0.065 | 1 | 4.1 | 14.1 | 20 | 47 | 0.014 | 7.25 | 0.065 | 1 | 4.2 | 15.3 | 21 | 49 | 0.011 | 3.9 | 3.8 | 3.7 | [18 empty] | 10400 | [6 empty] | 0 | 0 | 0 | 270 | 270 | 300 | 640 | 640 | 620 | 590 | 730 | 710 | 800 |  | 970 | 970 | 1100 | 80 | 110 | 11 | 1375 | 280 | 240 | 45 | 60 | 7 | 676 | 140 | 173 |  | 9:00 | 0.51 | 8.6 | 29.5814 | 15.0865 | 6.11 | 15 | 10 | 1.5087 | 15 | 6.5 | 0.33805 | 9:00 | 0.47 | 8.2 | 31.0244 | 14.5815 | 6.16 | 15.2 | 10 | 1.4581 | 15 | 6.5 | 0.32233 | 9:00 | 0.65 | 9.7 | 27.8351 | 18.0928 | 6.17 | 16.6 | 10 | 1.8093 | 15 | 6.5 | 0.35926
10:00 | [72 empty] | 43469.9409 | 1,2,3 | 41 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 13.0709 | 1,3 | 13.7261 | 26.797 | 1.8576 | 43469.9409 | 90.8138 | 8485.2608 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4139 | 1.4139 | 1.4057 | 0.27044 | 0.27044 | 0.26199 | 0.24932 | 0.27763 | 0.27002 | 1.5218 | 20 | 0.060206 | 0.060206 | 0.061088 | 1.0818 | 0.5605 | 0.093491 | 3.9996 | 0.75135 | 4.1193 | 1.0889 | 0.54709 | 0.10646 | 3.716 | 0.67226 | 5.3135 |  | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.28 | 13 | 13 | 9.39 | 106 | 166 | 17 | 0.459 |  | 6.11 | 9 | 0.067 | 6.08 | 8 |  | 6.07 | 8 | [8 empty] | 0.056 | [14 empty] | 0.081 | 1 | 0.32 |  | 0.058 | 0.021 | 1 | 0.2 |  | 0.035 | 1 | 0.52 | [38 empty] | 10400 | [6 empty] | 0 | 0 | 0 | 270 | 270 | 300 | 640 | 640 | 620 | 590 | 730 | 710 | 800 |  | 970 | 970 | 1100 | 80 | 110 | 11 | 1375 | 280 | 240 | 45 | 60 | 7 | 676 | 140 | 173 |  | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.92 | 0.358 | 5 | 0.57 | 15.5 | 9.2 | 0.40931 |  | 6.16 | 0.351 | 5 | 0.42 | 16 | 8.8 | 0.46591 | 6.22 | 0.278 | 5 | 0.65 | 17.2 | 10.3 | 0.50148 | [13 empty] | 7.42 | 0.063 | 1 | 4 | 14.3 |  |  |  | 7.22 | 0.068 | 1 | 4.4 | 15.5 |  |  |  | 3.9 | 3.8 | 2.7 | [55 empty] | 13:00 | 0.57 | 9.2 | 27.6522 | 15.7617 | 5.92 | 15.5 | 8 | 1.9702 | 15 | 6 | 0.28931 | 13:00 | 0.42 | 8.8 | 28.9091 | 12.1418 | 6.16 | 16 | 10 | 1.2142 | 15 | 6.5 | 0.34591 | 13:00 | 0.65 | 10.3 | 26.2136 | 17.0388 | 6.22 | 17.2 | 10 | 1.7039 | 15 | 6.5 | 0.38148
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.29 | 13 | 13 | 9.61 | 118 | 167 | 16.3 | 0.484 |  | 6.03 | 9 | 0.056 | 6.06 | 8 |  | 6.05 | 8 | [8 empty] | 0.056 | [14 empty] | 0.053 | 1 | 0.36 |  | 0.052 | 0.015 | 1 | 0.26 |  | 0.06 | 1 | 0.47 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.23 | 0.065 | 1 | 4 | 14.3 |  |  |  | 7.23 | 0.07 | 1 | 3.9 | 15.2 |  |  |  | 3.8 | 3.8 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.21 | 12 | 14 | 9.71 | 123 | 163 | 16.4 | 0.516 |  | 6.14 | 8 | 0.064 | 6.13 | 9 |  | 6.09 | 8 | [8 empty] | 0.057 | [14 empty] | 0.044 | 1 | 0.4 |  | 0.055 | 0.014 | 1 | 0.32 |  | 0.048 | 1 | 0.5 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.038 | [9 empty] | 6.16 | 0.295 | 4 | 0.55 | 15.2 | 9 | 0.47377 |  | 6.19 | 0.275 | 4 | 0.47 | 16 | 9 | 0.47377 | 6.16 | 0.297 | 3 | 0.53 | 17 | 10 | 0.49037 |  |  |  | 0.012 | [9 empty] | 7.52 | 0.065 | 1 | 4 | 14.4 | 20 | 49 | 0.011 | 7.43 | 0.069 | 1 | 3.9 | 15.6 | 20 | 52 | 0.013 | 3.9 | 3.9 | 2.8 | [55 empty] | 21:00 | 0.55 | 9 | 28.2667 | 15.5467 | 6.16 | 15.2 | 10 | 1.5547 | 15 | 6.5 | 0.35377 | 21:00 | 0.47 | 9 | 28.2667 | 13.2853 | 6.19 | 16 | 10 | 1.3285 | 15 | 6.5 | 0.35377 | 21:00 | 0.53 | 10 | 27 | 14.31 | 6.16 | 17 | 10 | 1.431 | 15 | 6.5 | 0.37037
22:00 | [72 empty] | DOSE |  | TOTAL | 52.3 | 50.1 | 58.2 | 160.6 | 49.3 | 47.1 | 55.2 | 151.6 | 0 | 72.2232 | 0 | 78.215 | 150.4382 | 11.1053 | TOTAL | 542.7952 | 48329.094 | 0 | 3853.7445 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3633 | 8.3017 | 8.7182 | 1.7579 | 1.7399 | 1.6734 | 1.6308 | 1.7008 | 1.6273 | 8.8454 | 124 | 0.35892 | 0.361 | 0.36177 | 6.5094 | 3.3256 | 0.58292 | 24.0245 | 4.4061 | 24.6974 | 6.573 | 3.2861 | 0.61161 | 21.8708 | 3.8479 | 31.8738 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.33 | 12 | 13 | 9.45 | 121 | 166 | 16.6 | 0.514 |  | 6.15 | 8 | 0.055 | 6.11 | 8 |  | 6.1 | 8 | [8 empty] | 0.049 | [14 empty] | 0.031 | 1 | 0.38 |  | 0.045 | 0.012 | 1 | 0.27 |  | 0.036 | 1 | 0.47 | [22 empty] | AVERAGE | 8.7167 | 8.35 | 9.7 | 26.7667 | 8.2167 | 7.85 | 9.2 | 25.2667 |  | 12.0372 |  | 13.0358 | 25.073 | 1.8509 | AVERAGE | 90.4659 | 8054.849 |  | 642.2907 | 0 | 0 | 0 |  |  |  | 1.3939 | 1.3836 | 1.453 | 0.29298 | 0.28999 | 0.2789 | 0.2718 | 0.28347 | 0.27121 | 1.4742 | 20.6667 | 0.05982 | 0.060167 | 0.060294 | 1.0849 | 0.55427 | 0.097153 | 4.0041 | 0.73434 | 4.1162 | 1.0955 | 0.54769 | 0.10194 | 3.6451 | 0.64132 | 5.3123 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.59 | 75 | 78 | 55.91 | 712 | 984 | 98.2 | 3.006 | 0.081 | 36.56 | 49 | 0.368 | 36.54 | 47 | 0 | 36.45 | 46 | 0 | 24.32 | 1.299 | 19 | 2.18 | 60.9 | 35.3 | 1.7953 | 0.325 | 24.62 | 1.133 | 18 | 1.88 | 63.2 | 33.4 | 1.7929 | 24.67 | 1.057 | 18 | 2.52 | 68 | 39.4 | 1.9393 | 0.255 | 6 | 2.15 | 0.023 | 0.306 | 0.103 | 6 | 1.62 | 0.014 | 0.224 | 6 | 2.81 | 0.009 | 44.24 | 0.372 | 6 | 24.3 | 85.4 | 40 | 96 | 0.025 | 43.99 | 0.394 | 6 | 24.7 | 92.6 | 41 | 101 | 0.024 | 23.5 | 23 | 17.7 |  |  | MINIMUM | 8.3 | 7.4 | 9.4 | 25.3 | 7.8 | 6.9 | 8.9 | 23.8 |  | 10.332 |  | 11.268 | 21.6 | 1.8475 | MINIMUM | 89.875 | 7685.9246 |  | 570.9251 | [6 empty] | 1.3616 | 1.3125 | 1.4057 | 0.27044 | 0.27044 | 0.25777 | 0.24509 | 0.27107 | 0.24275 | 1.4267 | 7 | 0.058965 | 0.059585 | 0.059871 | 1.08 | 0.54972 | 0.093491 | 3.9895 | 0.67256 | 4.1124 | 1.0849 | 0.53531 | 0.097407 | 3.4971 | 0.56381 | 5.3111 |  | MIN | 0.51 | 8.6 | 29.5814 | 15.0865 | 6.11 | 15 | 10 | 1.5087 |  |  |  | MIN | 0.42 | 8.8 | 28.9091 | 12.1418 | 6.16 | 16 | 10 | 1.2142 |  |  |  | MIN | 0.53 | 10 | 27 | 14.31 | 6.16 | 17 | 10 | 1.431 |  |  |  | 1.2142
AVERAGE | 6.265 | 12.5 | 13 | 9.3183 | 118.6667 | 164 | 16.3667 | 0.501 | 0.0405 | 6.0933 | 8.1667 | 0.061333 | 6.09 | 7.8333 |  | 6.075 | 7.6667 |  | 6.08 | 0.32475 | 4.75 | 0.545 | 15.225 | 8.825 | 0.44881 | 0.054167 | 6.155 | 0.28325 | 4.5 | 0.47 | 15.8 | 8.35 | 0.44822 | 6.1675 | 0.26425 | 4.5 | 0.63 | 17 | 9.85 | 0.48481 | 0.0425 | 1 | 0.35833 | 0.0115 | 0.051 | 0.017167 | 1 | 0.27 | 0.014 | 0.037333 | 1 | 0.46833 |  | 7.3733 | 0.062 | 1 | 4.05 | 14.2333 | 20 | 48 | 0.0125 | 7.3317 | 0.065667 | 1 | 4.1167 | 15.4333 | 20.5 | 50.5 | 0.012 | 3.9167 | 3.8333 | 2.95 |  |  | MAXIMUM | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 14.2344 |  | 13.824 | 28.0584 | 1.8576 | MAXIMUM | 90.8138 | 8485.2608 |  | 697.7974 | [6 empty] | 1.4139 | 1.4139 | 1.5004 | 0.31767 | 0.31767 | 0.30836 | 0.30836 | 0.29939 | 0.29939 | 1.5218 | 35 | 0.060206 | 0.060404 | 0.061088 | 1.0953 | 0.5605 | 0.10199 | 4.0167 | 0.75315 | 4.1193 | 1.1107 | 0.55477 | 0.10646 | 3.716 | 0.6817 | 5.3135
MINIMUM | 6.21 | 12 | 12 | 8.47 | 106 | 160 | 15.4 | 0.459 | 0.038 | 6.03 | 7 | 0.055 | 6.06 | 7 |  | 6.05 | 7 |  | 5.92 | 0.286 | 4 | 0.51 | 15 | 8.5 | 0.40931 | 0.049 | 6.11 | 0.224 | 4 | 0.42 | 15.2 | 7.4 | 0.41088 | 6.12 | 0.2 | 3 | 0.53 | 16.6 | 9.4 | 0.46815 | 0.022 | 1 | 0.31 | 0.011 | 0.043 | 0.012 | 1 | 0.2 | 0.014 | 0.022 | 1 | 0.38 |  | 7.23 | 0.055 | 1 | 4 | 14 | 20 | 47 | 0.011 | 7.22 | 0.06 | 1 | 3.9 | 15.2 | 20 | 49 | 0.011 | 3.8 | 3.8 | 2.7 | [15 empty] | MIL/MIN |  | TOTAL | 59434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1544 | 1464 | 1800 | 4020 | 3980 | 3650 | 3550 | 4335 | 4146 | 4650 | 0 | 5590 | 5370 | 6310 | 455 | 617 | 64 | 7830 | 1552 | 1360 | 263 | 349 | 39 | 3896 | 776 | 1005
MAXIMUM | 6.33 | 13 | 14 | 9.71 | 123 | 167 | 17 | 0.527 | 0.043 | 6.15 | 9 | 0.068 | 6.13 | 9 |  | 6.1 | 8 |  | 6.16 | 0.36 | 5 | 0.57 | 15.5 | 9.2 | 0.47377 | 0.058 | 6.19 | 0.351 | 5 | 0.52 | 16 | 9 | 0.47377 | 6.22 | 0.297 | 5 | 0.69 | 17.2 | 10.3 | 0.50148 | 0.081 | 1 | 0.4 | 0.012 | 0.058 | 0.023 | 1 | 0.32 | 0.014 | 0.06 | 1 | 0.52 |  | 7.52 | 0.065 | 1 | 4.1 | 14.4 | 20 | 49 | 0.014 | 7.55 | 0.07 | 1 | 4.4 | 15.6 | 21 | 52 | 0.013 | 4 | 3.9 | 3.7 | [17 empty] | AVERAGE | 9905.6667 | [9 empty] | 257.3333 | 244 | 300 | 670 | 663.3333 | 608.3333 | 591.6667 | 722.5 | 691 | 775 |  | 931.6667 | 895 | 1051.6667 | 75.8333 | 102.8333 | 10.6667 | 1305 | 258.6667 | 226.6667 | 43.8333 | 58.1667 | 6.5 | 649.3333 | 129.3333 | 167.5
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0861 |  | TOTAL AVG COAG ALK: |  |  |  | 7.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.36 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.42 | [5 empty] | 6.1342 |  |  |  |  | 0.081 |  |  |  |  | 0.42 | [6 empty] | 0.081 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 9300 | [9 empty] | 240 | 217 | 300 | 640 | 640 | 600 | 580 | 670 | 600 | 750 |  | 880 | 790 | 1010 | 70 | 95 | 10 | 1210 | 230 | 210 | 42 | 55 | 6 | 620 | 110 | 162
[90 empty] | MAXIMUM | 10400 | [9 empty] | 270 | 270 | 300 | 710 | 710 | 620 | 600 | 740 | 740 | 800 |  | 970 | 970 | 1100 | 81 | 110 | 12 | 1400 | 280 | 240 | 45 | 60 | 7 | 676 | 140 | 173
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.175 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827078 |  | END: | 23827078 |  |  | Alum | 4308 | 11148 | 11148 | 11618 | 11618 | 0 | [44 empty] | 0.42 | 8.8 | 28.9091 | 12.1418 | 6.16 | 16 | 10 | 1.2142
[73 empty] | FINISHED 2 | 12.091 |  | TOTAL MGD: |  | 11.175 |  |  | FINISHED SOUTH 2 |  | START: | 43866573 |  | END: | 43877748 |  |  | Caustic | 4715 | 6470 | 6470
[73 empty] | TOTAL RAW | 27.356 |  | TOTAL MGD: |  | 5.066 |  |  | FINISHED CONWAY |  | START: | 10235509 |  | END: | 10240575 |  |  | Hypochlorite | 20 |  | 48
[76 empty] | TOTAL MGD: |  | 7.025 |  |  | FINISHED PERRY |  | START: | 33863858 |  | END: | 33870883 |  |  | Phosphate | 2537
[76 empty] | TOTAL MGD: |  | 8.923 |  |  | RAW PLANT 1 |  | START: | 30980609 |  | END: | 30989532 |  |  | Fluoride | 3800 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.562 |  |  | RAW PLANT 2 |  | START: | 30939692 |  | END: | 30948254 |  |  | Cal~Flo | 13.22 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.871 |  |  | RAW PLANT 3 |  | START: | 7516263 |  | END: | 7526134 |  |  | Zinc | 942
[76 empty] | TOTAL MGD: |  | 0.867 |  |  | DECANT |  | START: | 1865666 |  | END: | 1866533 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.6864 |  |  | BLOW DOWN |  | START: | 9134.7464 |  | END: | 9136.4327 |  |  | NH3 | 7.23 |  | BI-SUL | 1200
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 666
23827078
43877748
10240575
33870883
30989532
30948254
7526134
1866533
9136.4327
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 5
DATE: | 2019-01-05 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-05 | [23 empty] | DATE: | 2019-01-05
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-05 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43470.0028 | 1,2,3 | 41 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 13.0709 | 1,3 | 13.7261 | 26.797 | 1.9339 | 43470.0028 | 90.8138 | 8485.2608 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4139 | 1.4139 | 1.4057 | 0.27044 | 0.27044 | 0.26199 | 0.24932 | 0.27763 | 0.27002 | 1.5218 | 20 | 0.060206 | 0.060206 | 0.061088 | 1.0818 | 0.5605 | 0.093491 | 3.9996 | 0.75135 | 4.1193 | 1.0889 | 0.54709 | 0.10646 | 3.716 | 0.67226 | 5.3135 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.27 | 0.337 | 5 | 0.52 | 15.2 | 9 | 0.47377 |  | 6.25 | 0.371 | 4 | 0.47 | 16 | 9 | 0.47377 | 6.22 | 0.288 | 4 | 0.49 | 17 | 10 | 0.49037 | [13 empty] | 7.7 | 0.062 | 1 | 4.4 | 14.6 |  |  |  | 7.57 | 0.065 | 1 | 3.8 | 15.5 |  |  |  | 3.9 | 3.7 | 2.9 | [18 empty] | 10400 | [6 empty] | 0 | 0 | 0 | 270 | 270 | 300 | 640 | 640 | 620 | 590 | 730 | 710 | 800 |  | 970 | 970 | 1100 | 80 | 110 | 11 | 1375 | 280 | 240 | 45 | 60 | 7 | 676 | 140 | 173 |  | 1:00 | 0.52 | 9 | 28.2667 | 14.6987 | 6.27 | 15.2 | 10 | 1.4699 | 15 | 6.5 | 0.35377 | 1:00 | 0.47 | 9 | 28.2667 | 13.2853 | 6.25 | 16 | 10 | 1.3285 | 15 | 6.5 | 0.35377 | 1:00 | 0.49 | 10 | 27 | 13.23 | 6.22 | 17 | 10 | 1.323 | 15 | 6.5 | 0.37037
2:00 | [72 empty] | 43470.14 | 1,2,3 | 41 | 8.3 | 8.3 | 9.4 | 26 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 13.0709 | 1,3 | 13.7261 | 26.797 | 1.9339 | 43470.14 | 91.2169 | 8485.2608 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4267 | 1.4267 | 1.4004 | 0.27492 | 0.27492 | 0.27034 | 0.27034 | 0.27107 | 0.27107 | 1.5218 | 20 | 0.060874 | 0.060874 | 0.059278 | 1.1052 | 0.54972 | 0.09262 | 4.0237 | 0.76029 | 4.1897 | 1.1107 | 0.55477 | 0.097407 | 3.6991 | 0.6612 | 5.2455 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.29 | 13 | 13 | 9.15 | 123 | 161 | 16.6 | 0.523 |  | 6.13 | 9 | 0.062 | 6.12 | 9 |  | 6.08 | 9 | [8 empty] | 0.054 | [14 empty] | 0.032 | 1 | 0.43 |  | 0.052 | 0.013 | 1 | 0.35 |  | 0.032 | 1 | 0.47 | [38 empty] | 9700 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 280 | 600 | 600 | 590 | 590 | 670 | 670 | 800 |  | 900 | 900 | 1000 | 75 | 99 | 10 | 1270 | 260 | 224 | 43 | 57 | 6 | 630 | 129 | 160 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43470.3516 | 2,3 | 70 | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 12.4805 | 1,3 | 10.273 | 22.7534 | 1.9339 | 43470.3516 | 90.6979 | 7808.8994 | 0 | 602.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3601 | 1.3601 | 1.3028 | 0.27906 | 0.26671 | 0.26177 | 0.23708 | 0.25354 | 0.26228 | 1.5218 | 5 | 0.060085 | 0.059353 | 0.059835 | 1.1175 | 0.54741 | 0.10034 | 3.9214 | 0.69693 | 4.0525 | 1.1214 | 0.52819 | 0.10572 | 3.3641 | 0.58413 | 5.3019 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.81 | 0.061 | 4 | 4.5 | 14.4 |  |  |  | 7.8 | 0.058 | 1 | 3.9 | 15.4 |  |  |  | 3.9 | 3.7 | 3 | [18 empty] | 8940 | [6 empty] | 0 | 0 | 0 | 220 | 220 | 240 | 565 | 540 | 530 | 480 | 580 | 600 | 800 |  | 820 | 810 | 930 | 70 | 91 | 10 | 1140 | 220 | 200 | 40 | 50 | 6 | 540 | 105 | 149 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43470.8248 | 2,3,5 | 70 | 9 | 7.8 | 9.9 | 26.7 | 8.5 | 7.3 | 9.4 | 25.2 | ,1,3 | 9.6178 | 3 | 12.5338 | 22.1515 | 1.9714 | 43470.8248 | 90.6569 | 8116.3364 | 0 | 602.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4139 | 1.4025 | 1.3259 | 0.27805 | 0.26622 | 0.25842 | 0.23843 | 0.2497 | 0.25892 | 1.6169 | 6 | 0.060206 | 0.060708 | 0.060054 | 1.1058 | 0.54825 | 0.10059 | 4.0172 | 0.77954 | 3.7488 | 1.1005 | 0.55291 | 0.1076 | 3.6941 | 0.72794 | 5.2769 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.25 | 13 | 13 | 9.27 | 119 | 166 | 16.4 | 0.505 |  | 6.14 | 10 | 0.063 | 6.16 | 10 |  | 6.13 | 9 | [8 empty] | 0.056 | [14 empty] | 0.032 | 1 | 0.36 |  | 0.054 | 0.013 | 1 | 0.26 |  | 0.033 | 1 | 0.36 | [38 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 270 | 230 | 280 | 658 | 630 | 530 | 489 | 650 | 674 | 850 |  | 970 | 840 | 1070 | 76 | 100 | 11 | 1310 | 270 | 203 | 45 | 60 | 7 | 720 | 150 | 170 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6.2 | 0.446 | 5 | 0.63 | 15.3 | 7.7 | 0.42267 |  | 6.19 | 0.447 | 5 | 0.46 | 15.8 | 7.7 | 0.42267 | 6.21 | 0.321 | 4 | 0.53 | 17.9 | 8.7 | 0.44222 |  |  |  | 0.009 | [9 empty] | 7.61 | 0.066 | 1 | 4.8 | 14.4 | 20 | 52 | 0.013 | 7.7 | 0.063 | 1 | 4.3 | 15.1 | 20 | 52 | 0.008 | 4.1 | 3.7 | 3.6 | [55 empty] | 9:00 | 0.63 | 7.7 | 33.039 | 20.8145 | 6.2 | 15.3 | 10 | 2.0815 | 15 | 6.5 | 0.30267 | 9:00 | 0.46 | 7.7 | 33.039 | 15.1979 | 6.19 | 15.8 | 10 | 1.5198 | 15 | 6.5 | 0.30267 | 9:00 | 0.53 | 8.7 | 31.0345 | 16.4483 | 6.21 | 17.9 | 10 | 1.6448 | 15 | 6.5 | 0.32222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.28 | 12 | 13 | 9.42 | 117 | 163 | 16.6 | 0.492 |  | 6.07 | 9 | 0.056 | 6.1 | 9 |  | 6.09 | 9 | [8 empty] | 0.046 | [14 empty] | 0.029 | 1 | 0.29 |  | 0.052 | 0.016 | 1 | 0.31 |  | 0.034 | 1 | 0.31 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.21 | 0.362 | 5 | 0.68 | 15.8 | 7.8 | 0.4266 |  | 6.24 | 0.369 | 5 | 0.45 | 16.2 | 7.8 | 0.4266 | 6.22 | 0.303 | 4 | 0.48 | 17.1 | 8.7 | 0.44222 | [13 empty] | 7.46 | 0.069 | 1 | 4.3 | 14.2 |  |  |  | 7.67 | 0.071 | 1 | 4.2 | 16.4 |  |  |  | 4.2 | 3.7 | 2.6 | [55 empty] | 13:00 | 0.68 | 7.8 | 32.6154 | 22.1785 | 6.21 | 15.8 | 10 | 2.2178 | 15 | 6.5 | 0.3066 | 13:00 | 0.45 | 7.8 | 32.6154 | 14.6769 | 6.24 | 16.2 | 10 | 1.4677 | 15 | 6.5 | 0.3066 | 13:00 | 0.48 | 8.7 | 31.0345 | 14.8966 | 6.22 | 17.1 | 10 | 1.4897 | 15 | 6.5 | 0.32222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.36 | 13 | 13 | 10.7 | 121 | 170 | 17.1 | 0.499 |  | 6.17 | 10 | 0.057 | 6.18 | 10 |  | 6.11 | 10 | [8 empty] | 0.053 | [14 empty] | 0.033 | 1 | 0.28 |  | 0.055 | 0.021 | 1 | 0.2 |  | 0.035 | 1 | 0.27 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.51 | 0.068 | 1 | 4 | 14.8 |  |  |  | 7.52 | 0.072 | 1 | 4.1 | 15.4 |  |  |  | 4.2 | 3.8 | 2.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.32 | 13 | 13 | 9.78 | 124 | 161 | 16.7 | 0.508 |  | 6.04 | 9 | 0.05 | 6.05 | 9 |  | 6.02 | 9 | [8 empty] | 0.045 | [14 empty] | 0.038 | 1 | 0.27 |  | 0.04 | 0.02 | 1 | 0.2 |  | 0.033 | 1 | 0.32 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.041 | [9 empty] | 6.12 | 0.35 | 5 | 0.52 | 15.2 | 8.3 | 0.44626 |  | 6.22 | 0.343 | 5 | 0.42 | 15.9 | 8.3 | 0.44626 | 6.23 | 0.296 | 4 | 0.49 | 17 | 9.4 | 0.46815 |  |  |  | 0.007 | [9 empty] | 7.6 | 0.069 | 1 | 3.9 | 14.3 | 21 | 53 | 0.012 | 7.56 | 0.068 | 1 | 4 | 15.4 | 21 | 52 | 0.01 | 4.1 | 4.1 | 2.7 | [55 empty] | 21:00 | 0.52 | 8.3 | 30.6506 | 15.9383 | 6.12 | 15.2 | 10 | 1.5938 | 15 | 6.5 | 0.32626 | 21:00 | 0.42 | 8.3 | 30.6506 | 12.8733 | 6.22 | 15.9 | 10 | 1.2873 | 15 | 6.5 | 0.32626 | 21:00 | 0.49 | 9.4 | 28.7234 | 14.0745 | 6.23 | 17 | 10 | 1.4074 | 15 | 6.5 | 0.34815
22:00 | [72 empty] | DOSE |  | TOTAL | 34 | 32.8 | 38 | 104.8 | 32 | 30.8 | 36 | 98.8 | 0 | 48.24 | 3 | 50.2589 | 98.4989 | 7.7731 | TOTAL | 363.3854 | 32895.7574 | 0 | 2600.8811 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6146 | 5.6032 | 5.4348 | 1.1025 | 1.0783 | 1.0525 | 0.99516 | 1.0519 | 1.0623 | 6.1823 | 51 | 0.24137 | 0.24114 | 0.24026 | 4.4103 | 2.2059 | 0.38704 | 15.9619 | 2.9881 | 16.1103 | 4.4215 | 2.183 | 0.41719 | 14.4733 | 2.6455 | 21.1378 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.28 | 12 | 12 | 9.83 | 123 | 167 | 16.4 | 0.514 |  | 6.06 | 9 | 0.06 | 6.04 | 9 |  | 6 | 9 | [8 empty] | 0.049 | [14 empty] | 0.027 | 1 | 0.4 |  | 0.051 | 0.012 | 1 | 0.38 |  | 0.027 | 1 | 0.47 | [22 empty] | AVERAGE | 8.5 | 8.2 | 9.5 | 26.2 | 8 | 7.7 | 9 | 24.7 |  | 12.06 | 3 | 12.5647 | 24.6247 | 1.9433 | AVERAGE | 90.8464 | 8223.9394 |  | 650.2203 | 0 | 0 | 0 |  |  |  | 1.4037 | 1.4008 | 1.3587 | 0.27562 | 0.26958 | 0.26313 | 0.24879 | 0.26299 | 0.26557 | 1.5456 | 12.75 | 0.060343 | 0.060285 | 0.060064 | 1.1026 | 0.55147 | 0.09676 | 3.9905 | 0.74703 | 4.0276 | 1.1054 | 0.54574 | 0.1043 | 3.6183 | 0.66138 | 5.2845 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.78 | 76 | 77 | 58.15 | 727 | 988 | 99.8 | 3.041 | 0.078 | 36.61 | 56 | 0.348 | 36.65 | 56 | 0 | 36.43 | 55 | 0 | 24.8 | 1.495 | 20 | 2.35 | 61.5 | 32.8 | 1.7693 | 0.303 | 24.9 | 1.53 | 19 | 1.8 | 63.9 | 32.8 | 1.7693 | 24.88 | 1.208 | 16 | 1.99 | 69 | 36.8 | 1.843 | 0.191 | 6 | 2.03 | 0.016 | 0.304 | 0.095 | 6 | 1.7 | 0 | 0.194 | 6 | 2.2 | 0 | 45.69 | 0.395 | 9 | 25.9 | 86.7 | 41 | 105 | 0.025 | 45.82 | 0.397 | 6 | 24.3 | 93.2 | 41 | 104 | 0.018 | 24.4 | 22.7 | 17.7 |  |  | MINIMUM | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 |  | 9.6178 | 3 | 10.273 | 22.1515 | 1.9339 | MINIMUM | 90.6569 | 7808.8994 |  | 602.6432 | [6 empty] | 1.3601 | 1.3601 | 1.3028 | 0.27044 | 0.26622 | 0.25842 | 0.23708 | 0.2497 | 0.25892 | 1.5218 | 5 | 0.060085 | 0.059353 | 0.059278 | 1.0818 | 0.54741 | 0.09262 | 3.9214 | 0.69693 | 3.7488 | 1.0889 | 0.52819 | 0.097407 | 3.3641 | 0.58413 | 5.2455 |  | MIN | 0.52 | 9 | 28.2667 | 14.6987 | 6.27 | 15.2 | 10 | 1.4699 |  |  |  | MIN | 0.42 | 8.3 | 30.6506 | 12.8733 | 6.22 | 15.9 | 10 | 1.2873 |  |  |  | MIN | 0.49 | 10 | 27 | 13.23 | 6.22 | 17 | 10 | 1.323 |  |  |  | 1.2873
AVERAGE | 6.2967 | 12.6667 | 12.8333 | 9.6917 | 121.1667 | 164.6667 | 16.6333 | 0.50683 | 0.039 | 6.1017 | 9.3333 | 0.058 | 6.1083 | 9.3333 |  | 6.0717 | 9.1667 |  | 6.2 | 0.37375 | 5 | 0.5875 | 15.375 | 8.2 | 0.44233 | 0.0505 | 6.225 | 0.3825 | 4.75 | 0.45 | 15.975 | 8.2 | 0.44233 | 6.22 | 0.302 | 4 | 0.4975 | 17.25 | 9.2 | 0.46074 | 0.031833 | 1 | 0.33833 | 0.008 | 0.050667 | 0.015833 | 1 | 0.28333 |  | 0.032333 | 1 | 0.36667 |  | 7.615 | 0.065833 | 1.5 | 4.3167 | 14.45 | 20.5 | 52.5 | 0.0125 | 7.6367 | 0.066167 | 1 | 4.05 | 15.5333 | 20.5 | 52 | 0.009 | 4.0667 | 3.7833 | 2.95 |  |  | MAXIMUM | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 13.0709 | 3 | 13.7261 | 26.797 | 1.9714 | MAXIMUM | 91.2169 | 8485.2608 |  | 697.7974 | [6 empty] | 1.4267 | 1.4267 | 1.4057 | 0.27906 | 0.27492 | 0.27034 | 0.27034 | 0.27763 | 0.27107 | 1.6169 | 20 | 0.060874 | 0.060874 | 0.061088 | 1.1175 | 0.5605 | 0.10059 | 4.0237 | 0.77954 | 4.1897 | 1.1214 | 0.55477 | 0.1076 | 3.716 | 0.72794 | 5.3135
MINIMUM | 6.25 | 12 | 12 | 9.15 | 117 | 161 | 16.4 | 0.492 | 0.037 | 6.04 | 9 | 0.05 | 6.04 | 9 |  | 6 | 9 |  | 6.12 | 0.337 | 5 | 0.52 | 15.2 | 7.7 | 0.42267 | 0.045 | 6.19 | 0.343 | 4 | 0.42 | 15.8 | 7.7 | 0.42267 | 6.21 | 0.288 | 4 | 0.48 | 17 | 8.7 | 0.44222 | 0.027 | 1 | 0.27 | 0.007 | 0.04 | 0.012 | 1 | 0.2 |  | 0.027 | 1 | 0.27 |  | 7.46 | 0.061 | 1 | 3.9 | 14.2 | 20 | 52 | 0.012 | 7.52 | 0.058 | 1 | 3.8 | 15.1 | 20 | 52 | 0.008 | 3.9 | 3.7 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 38940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 970 | 1100 | 2463 | 2410 | 2270 | 2149 | 2630 | 2654 | 3250 | 0 | 3660 | 3520 | 4100 | 301 | 400 | 42 | 5095 | 1030 | 867 | 173 | 227 | 26 | 2566 | 524 | 652
MAXIMUM | 6.36 | 13 | 13 | 10.7 | 124 | 170 | 17.1 | 0.523 | 0.041 | 6.17 | 10 | 0.063 | 6.18 | 10 |  | 6.13 | 10 |  | 6.27 | 0.446 | 5 | 0.68 | 15.8 | 9 | 0.47377 | 0.056 | 6.25 | 0.447 | 5 | 0.47 | 16.2 | 9 | 0.47377 | 6.23 | 0.321 | 4 | 0.53 | 17.9 | 10 | 0.49037 | 0.038 | 1 | 0.43 | 0.009 | 0.055 | 0.021 | 1 | 0.38 |  | 0.035 | 1 | 0.47 |  | 7.81 | 0.069 | 4 | 4.8 | 14.8 | 21 | 53 | 0.013 | 7.8 | 0.072 | 1 | 4.3 | 16.4 | 21 | 52 | 0.01 | 4.2 | 4.1 | 3.6 | [17 empty] | AVERAGE | 9735 | [9 empty] | 252.5 | 242.5 | 275 | 615.75 | 602.5 | 567.5 | 537.25 | 657.5 | 663.5 | 812.5 |  | 915 | 880 | 1025 | 75.25 | 100 | 10.5 | 1273.75 | 257.5 | 216.75 | 43.25 | 56.75 | 6.5 | 641.5 | 131 | 163
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0939 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.447 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.42 | [5 empty] | 6.215 |  |  |  |  | 0.038 |  |  |  |  | 0.42 | [6 empty] | 0.038 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 8940 | [9 empty] | 220 | 220 | 240 | 565 | 540 | 530 | 480 | 580 | 600 | 800 |  | 820 | 810 | 930 | 70 | 91 | 10 | 1140 | 220 | 200 | 40 | 50 | 6 | 540 | 105 | 149
[90 empty] | MAXIMUM | 10400 | [9 empty] | 270 | 270 | 300 | 658 | 640 | 620 | 590 | 730 | 710 | 850 |  | 970 | 970 | 1100 | 80 | 110 | 11 | 1375 | 280 | 240 | 45 | 60 | 7 | 720 | 150 | 173
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.059 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827078 |  | END: | 23827078 |  |  | Alum | 588 | 11151 | 11151 | 11615 | 11615 | 0 | [44 empty] | 0.42 | 8.3 | 30.6506 | 12.8733 | 6.22 | 15.9 | 10 | 1.2873
[73 empty] | FINISHED 2 | 11.159 |  | TOTAL MGD: |  | 11.059 |  |  | FINISHED SOUTH 2 |  | START: | 43877748 |  | END: | 43888807 |  |  | Caustic | 4642 | 6460 | 6460
[73 empty] | TOTAL RAW | 25.813 |  | TOTAL MGD: |  | 4.338 |  |  | FINISHED CONWAY |  | START: | 10240575 |  | END: | 10244913 |  |  | Hypochlorite | 20 |  | 48
[76 empty] | TOTAL MGD: |  | 6.821 |  |  | FINISHED PERRY |  | START: | 33870883 |  | END: | 33877704 |  |  | Phosphate | 2488
[76 empty] | TOTAL MGD: |  | 8.262 |  |  | RAW PLANT 1 |  | START: | 30989532 |  | END: | 30997794 |  |  | Fluoride | 3800 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.095 |  |  | RAW PLANT 2 |  | START: | 30948254 |  | END: | 30956349 |  |  | Cal~Flo | 9.7 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.456 |  |  | RAW PLANT 3 |  | START: | 7526134 |  | END: | 7535590 |  |  | Zinc | 935
[76 empty] | TOTAL MGD: |  | 1.093 |  |  | DECANT |  | START: | 1866533 |  | END: | 1867626 |  |  | Polymer | 18
[76 empty] | TOTAL MGD: |  | 1.6915 |  |  | BLOW DOWN |  | START: | 9136.4327 |  | END: | 9138.1242 |  |  | NH3 | 7.19 |  | BI-SUL | 1200
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 602
23827078
43888807
10244913
33877704
30997794
30956349
7535590
1867626
9138.1242
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 6
DATE: | 2019-01-06 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-06 | [23 empty] | DATE: | 2019-01-06
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-06 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43471.0067 | 2,3,5 | 70 | 9 | 7.8 | 9.9 | 26.7 | 8.5 | 7.3 | 9.4 | 25.2 | ,1,3 | 9.6178 | 3 | 12.5338 | 22.1515 | 2.0131 | 43471.0067 | 90.6569 | 8116.3364 | 0 | 602.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4139 | 1.4025 | 1.3259 | 0.27805 | 0.26622 | 0.25842 | 0.23843 | 0.2497 | 0.25892 | 1.6169 | 6 | 0.060206 | 0.060708 | 0.060054 | 1.1058 | 0.54825 | 0.10059 | 4.0172 | 0.77954 | 3.7488 | 1.1005 | 0.55291 | 0.1076 | 3.6941 | 0.72794 | 5.2769 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.21 | 0.379 | 5 | 0.57 | 15.3 | 9 | 0.47377 |  | 6.15 | 0.337 | 5 | 0.47 | 15.6 | 7.8 | 0.4266 | 6.17 | 0.291 | 5 | 0.52 | 16.7 | 9.9 | 0.48667 | [13 empty] | 7.45 | 0.059 | 1 | 4.3 | 14.2 |  |  |  | 7.4 | 0.063 | 1 | 4.2 | 15.3 |  |  |  | 3.9 | 3.9 | 3 | [18 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 270 | 230 | 280 | 658 | 630 | 530 | 489 | 650 | 674 | 850 |  | 970 | 840 | 1070 | 76 | 100 | 11 | 1310 | 270 | 203 | 45 | 60 | 7 | 720 | 150 | 170 |  | 1:00 | 0.57 | 9 | 28.2667 | 16.112 | 6.21 | 15.3 | 10 | 1.6112 | 15 | 6.5 | 0.35377 | 1:00 | 0.47 | 7.8 | 32.6154 | 15.3292 | 6.15 | 15.6 | 10 | 1.5329 | 15 | 6.5 | 0.3066 | 1:00 | 0.52 | 9.9 | 27.2727 | 14.1818 | 6.17 | 16.7 | 10 | 1.4182 | 15 | 6.5 | 0.36667
2:00 | [72 empty] | 43471.3299 | 2,3,5 | 70 | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 | ,1,3 | 11.7533 | 3 | 12.7627 | 24.516 | 2.0131 | 43471.3299 | 91.2553 | 8239.3112 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.3354 | 1.3259 | 0.2774 | 0.24161 | 0.26398 | 0.23266 | 0.2497 | 0.2593 | 1.6645 | 6 | 0.060012 | 0.059353 | 0.060054 | 1.092 | 0.55222 | 0.099335 | 3.8939 | 0.71277 | 3.702 | 1.125 | 0.55291 | 0.1076 | 3.4559 | 0.60661 | 4.7182 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.32 | 13 | 13 | 10.1 | 124 | 169 | 16.1 | 0.521 |  | 6.04 | 9 | 0.07 | 6.04 | 9 |  | 6 | 9 | [8 empty] | 0.049 | [14 empty] | 0.026 | 1 | 0.35 |  | 0.044 | 0.012 | 1 | 0.29 |  | 0.026 | 1 | 0.38 | [38 empty] | 10040 | [6 empty] | 0 | 0 | 0 | 250 | 240 | 280 | 620 | 540 | 590 | 520 | 650 | 675 | 875 |  | 910 | 900 | 1070 | 76 | 102 | 11 | 1250 | 250 | 203 | 46 | 60 | 7 | 640 | 125 | 152 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43471.8369 | 2,3,5 | 35 | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 | ,1,3 | 11.7533 | 3 | 12.7627 | 24.516 | 1.8158 | 43471.8369 | 90.8917 | 8362.286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.391 | 1.3022 | 0.2774 | 0.26846 | 0.25951 | 0.24161 | 0.2497 | 0.26122 | 1.6645 | 6 | 0.060012 | 0.060012 | 0.060054 | 1.1063 | 0.55222 | 0.099335 | 4.0269 | 0.76979 | 3.9573 | 1.1005 | 0.55291 | 0.1076 | 3.727 | 0.68911 | 4.9665 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.38 | 0.06 | 1 | 4 | 14.1 |  |  |  | 7.3 | 0.068 | 1 | 4.1 | 15.1 |  |  |  | 3.9 | 3.9 | 2.9 | [18 empty] | 10000 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 275 | 620 | 600 | 580 | 540 | 650 | 680 | 875 |  | 910 | 910 | 1070 | 77 | 102 | 11 | 1330 | 270 | 217 | 45 | 60 | 7 | 700 | 142 | 160 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43471.9568 | 2,3,5 | 35 | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 | ,1,3 | 11.7533 | 3 | 12.7627 | 24.516 | 1.8158 | 43471.9568 | 90.8917 | 8362.286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.391 | 1.3022 | 0.2774 | 0.26846 | 0.25951 | 0.24161 | 0.2497 | 0.26122 | 1.6645 | 6 | 0.060012 | 0.060012 | 0.060054 | 1.1063 | 0.55222 | 0.099335 | 4.0269 | 0.76979 | 3.9573 | 1.1005 | 0.55291 | 0.1076 | 3.727 | 0.68911 | 4.9665 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.3 | 14 | 14 | 10.4 | 118 | 172 | 16.2 | 0.505 |  | 5.97 | 9 | 0.059 | 5.98 | 9 |  | 5.96 | 9 | [8 empty] | 0.052 | [14 empty] | 0.028 | 1 | 0.37 |  | 0.056 | 0.015 | 1 | 0.29 |  | 0.025 | 1 | 0.35 | [38 empty] | 10000 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 275 | 620 | 600 | 580 | 540 | 650 | 680 | 875 |  | 910 | 910 | 1070 | 77 | 102 | 11 | 1330 | 270 | 217 | 45 | 60 | 7 | 700 | 142 | 160 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6.12 | 0.49 | 5 | 0.67 | 15.2 | 8.5 | 0.45412 |  | 6.07 | 0.462 | 5 | 0.48 | 15.8 | 8.5 | 0.45412 | 6.12 | 0.343 | 4 | 0.58 | 16.8 | 9.9 | 0.48667 |  |  |  | 0.005 |  |  |  |  | 0.01 |  |  |  | 0.011 | 7.2 | 0.062 | 1 | 4.1 | 14.1 | 20 | 51 | 0.008 | 7.22 | 0.058 | 1 | 4.1 | 15 | 21 | 53 | 0.011 | 3.8 | 3.7 | 3.6 | [55 empty] | 9:00 | 0.67 | 8.5 | 29.9294 | 20.0527 | 6.12 | 15.2 | 10 | 2.0053 | 15 | 6.5 | 0.33412 | 9:00 | 0.48 | 8.5 | 29.9294 | 14.3661 | 6.07 | 15.8 | 10 | 1.4366 | 15 | 6.5 | 0.33412 | 9:00 | 0.58 | 9.9 | 27.2727 | 15.8182 | 6.12 | 16.8 | 10 | 1.5818 | 15 | 6.5 | 0.36667
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.31 | 14 | 13 | 10.3 | 120 | 172 | 16.1 | 0.504 |  | 5.98 | 9 | 0.06 | 6 | 9 |  | 5.98 | 9 | [8 empty] | 0.056 | [14 empty] | 0.028 | 1 | 0.37 |  | 0.048 | 0.014 | 1 | 0.32 |  | 0.024 | 1 | 0.38 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.07 | 0.439 | 4 | 0.56 | 15.4 | 8.5 | 0.45412 |  | 6.1 | 0.405 | 4 | 0.4 | 15.6 | 8.5 | 0.45412 | 6.16 | 0.326 | 4 | 0.44 | 15.5 | 9.9 | 0.48667 | [13 empty] | 7.15 | 0.069 | 1 | 4.1 | 14.3 |  |  |  | 7.16 | 0.071 | 1 | 4.1 | 16 |  |  |  | 3.9 | 3.7 | 3.8 | [55 empty] | 13:00 | 0.56 | 8.5 | 29.9294 | 16.7605 | 6.07 | 15.4 | 10 | 1.676 | 15 | 6.5 | 0.33412 | 13:00 | 0.4 | 8.5 | 29.9294 | 11.9718 | 6.1 | 15.6 | 10 | 1.1972 | 15 | 6.5 | 0.33412 | 13:00 | 0.44 | 9.9 | 27.2727 | 12 | 6.16 | 15.5 | 10 | 1.2 | 15 | 6.5 | 0.36667
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.34 | 14 | 13 | 10.4 | 122 | 174 | 16.1 | 0.496 |  | 6.03 | 10 | 0.061 | 6.04 | 10 |  | 6.03 | 10 | [8 empty] | 0.054 | [14 empty] | 0.023 | 1 | 0.26 |  | 0.049 | 0.013 | 1 | 0.21 |  | 0.024 | 1 | 0.33 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.12 | 0.06 | 1 | 4 | 14.1 |  |  |  | 7.15 | 0.064 | 1 | 4.1 | 15.4 |  |  |  | 3.9 | 2.7 | 3.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.35 | 13 | 13 | 9.86 | 124 | 173 | 16.3 | 0.515 |  | 6 | 9 | 0.061 | 6.05 | 10 |  | 6.05 | 10 | [8 empty] | 0.055 | [14 empty] | 0.022 | 1 | 0.36 |  | 0.052 | 0.011 | 1 | 0.33 |  | 0.024 | 1 | 0.38 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.036 | [9 empty] | 6.15 | 0.359 | 5 | 0.58 | 15.5 | 8.5 | 0.45412 |  | 6.15 | 0.347 | 4 | 0.49 | 16 | 8.5 | 0.45412 | 6.15 | 0.27 | 4 | 0.56 | 17 | 9.9 | 0.48667 |  |  |  | 0.009 | [9 empty] | 7.43 | 0.061 | 1 | 4.1 | 14.5 | 21 | 52 | 0.012 | 7.35 | 0.065 | 1 | 4.3 | 15.5 | 20 | 54 | 0.01 | 3.9 | 3.8 | 2.8 | [55 empty] | 21:00 | 0.58 | 8.5 | 29.9294 | 17.3591 | 6.15 | 15.5 | 10 | 1.7359 | 15 | 6.5 | 0.33412 | 21:00 | 0.49 | 8.5 | 29.9294 | 14.6654 | 6.15 | 16 | 10 | 1.4665 | 15 | 6.5 | 0.33412 | 21:00 | 0.56 | 9.9 | 27.2727 | 15.2727 | 6.15 | 17 | 10 | 1.5273 | 15 | 6.5 | 0.36667
22:00 | [72 empty] | DOSE |  | TOTAL | 34.5 | 33.3 | 39.6 | 107.4 | 32.5 | 31.3 | 37.6 | 101.4 | 0 | 44.8776 | 12 | 50.8219 | 95.6995 | 7.6579 | TOTAL | 363.6956 | 33080.2196 | 0 | 2553.304 | 0 | 0 | 0 | 0 | 0 | 0 | 5.587 | 5.5199 | 5.2563 | 1.1103 | 1.0447 | 1.0414 | 0.95431 | 0.9988 | 1.0407 | 6.6103 | 24 | 0.24024 | 0.24008 | 0.24022 | 4.4104 | 2.2049 | 0.3986 | 15.965 | 3.0319 | 15.3654 | 4.4265 | 2.2116 | 0.43039 | 14.604 | 2.7128 | 19.9281 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.34 | 14 | 13 | 10.2 | 130 | 171 | 16.1 | 0.52 |  | 6.14 | 10 | 0.055 | 6.11 | 10 |  | 6.09 | 10 | [8 empty] | 0.044 | [14 empty] | 0.022 | 1 | 0.34 |  | 0.046 | 0.01 | 1 | 0.29 |  | 0.024 | 1 | 0.32 | [22 empty] | AVERAGE | 8.625 | 8.325 | 9.9 | 26.85 | 8.125 | 7.825 | 9.4 | 25.35 |  | 11.2194 | 3 | 12.7055 | 23.9249 | 1.9145 | AVERAGE | 90.9239 | 8270.0549 |  | 638.326 | 0 | 0 | 0 |  |  |  | 1.3967 | 1.38 | 1.3141 | 0.27757 | 0.26119 | 0.26035 | 0.23858 | 0.2497 | 0.26017 | 1.6526 | 6 | 0.06006 | 0.060021 | 0.060054 | 1.1026 | 0.55123 | 0.099649 | 3.9912 | 0.75797 | 3.8414 | 1.1066 | 0.55291 | 0.1076 | 3.651 | 0.67819 | 4.982 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 37.96 | 82 | 79 | 61.26 | 738 | 1031 | 96.9 | 3.061 | 0.073 | 36.16 | 56 | 0.366 | 36.22 | 57 | 0 | 36.11 | 57 | 0 | 24.55 | 1.667 | 19 | 2.38 | 61.4 | 34.5 | 1.8361 | 0.31 | 24.47 | 1.551 | 18 | 1.84 | 63 | 33.3 | 1.789 | 24.6 | 1.23 | 17 | 2.1 | 66 | 39.6 | 1.9467 | 0.149 | 6 | 2.05 | 0.014 | 0.295 | 0.075 | 6 | 1.73 | 0.01 | 0.147 | 6 | 2.14 | 0.011 | 43.73 | 0.371 | 6 | 24.6 | 85.3 | 41 | 103 | 0.02 | 43.58 | 0.389 | 6 | 24.9 | 92.3 | 41 | 107 | 0.021 | 23.3 | 21.7 | 19.9 |  |  | MINIMUM | 8.5 | 7.8 | 9.9 | 26.7 | 8 | 7.3 | 9.4 | 25.2 |  | 9.6178 | 3 | 12.5338 | 22.1515 | 1.8158 | MINIMUM | 90.6569 | 8116.3364 |  | 602.6432 | [6 empty] | 1.391 | 1.3354 | 1.3022 | 0.2774 | 0.24161 | 0.25842 | 0.23266 | 0.2497 | 0.25892 | 1.6169 | 6 | 0.060012 | 0.059353 | 0.060054 | 1.092 | 0.54825 | 0.099335 | 3.8939 | 0.71277 | 3.702 | 1.1005 | 0.55291 | 0.1076 | 3.4559 | 0.60661 | 4.7182 |  | MIN | 0.57 | 9 | 28.2667 | 16.112 | 6.21 | 15.3 | 10 | 1.6112 |  |  |  | MIN | 0.4 | 8.5 | 29.9294 | 11.9718 | 6.1 | 15.6 | 10 | 1.1972 |  |  |  | MIN | 0.44 | 9.9 | 27.2727 | 12 | 6.16 | 15.5 | 10 | 1.2 |  |  |  | 1.1972
AVERAGE | 6.3267 | 13.6667 | 13.1667 | 10.21 | 123 | 171.8333 | 16.15 | 0.51017 | 0.0365 | 6.0267 | 9.3333 | 0.061 | 6.0367 | 9.5 |  | 6.0183 | 9.5 |  | 6.1375 | 0.41675 | 4.75 | 0.595 | 15.35 | 8.625 | 0.45903 | 0.051667 | 6.1175 | 0.38775 | 4.5 | 0.46 | 15.75 | 8.325 | 0.44724 | 6.15 | 0.3075 | 4.25 | 0.525 | 16.5 | 9.9 | 0.48667 | 0.024833 | 1 | 0.34167 | 0.007 | 0.049167 | 0.0125 | 1 | 0.28833 |  | 0.0245 | 1 | 0.35667 | 0.011 | 7.2883 | 0.061833 | 1 | 4.1 | 14.2167 | 20.5 | 51.5 | 0.01 | 7.2633 | 0.064833 | 1 | 4.15 | 15.3833 | 20.5 | 53.5 | 0.0105 | 3.8833 | 3.6167 | 3.3167 |  |  | MAXIMUM | 9 | 8.5 | 9.9 | 26.9 | 8.5 | 8 | 9.4 | 25.4 |  | 11.7533 | 3 | 12.7627 | 24.516 | 2.0131 | MAXIMUM | 91.2553 | 8362.286 |  | 650.2203 | [6 empty] | 1.4139 | 1.4025 | 1.3259 | 0.27805 | 0.26846 | 0.26398 | 0.24161 | 0.2497 | 0.26122 | 1.6645 | 6 | 0.060206 | 0.060708 | 0.060054 | 1.1063 | 0.55222 | 0.10059 | 4.0269 | 0.77954 | 3.9573 | 1.125 | 0.55291 | 0.1076 | 3.727 | 0.72794 | 5.2769
MINIMUM | 6.3 | 13 | 13 | 9.86 | 118 | 169 | 16.1 | 0.496 | 0.036 | 5.97 | 9 | 0.055 | 5.98 | 9 |  | 5.96 | 9 |  | 6.07 | 0.359 | 4 | 0.56 | 15.2 | 8.5 | 0.45412 | 0.044 | 6.07 | 0.337 | 4 | 0.4 | 15.6 | 7.8 | 0.4266 | 6.12 | 0.27 | 4 | 0.44 | 15.5 | 9.9 | 0.48667 | 0.022 | 1 | 0.26 | 0.005 | 0.044 | 0.01 | 1 | 0.21 |  | 0.024 | 1 | 0.32 | 0.011 | 7.12 | 0.059 | 1 | 4 | 14.1 | 20 | 51 | 0.008 | 7.15 | 0.058 | 1 | 4.1 | 15 | 20 | 53 | 0.01 | 3.8 | 2.7 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 39940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 970 | 1110 | 2518 | 2370 | 2280 | 2089 | 2600 | 2709 | 3475 | 0 | 3700 | 3560 | 4280 | 306 | 406 | 44 | 5220 | 1060 | 840 | 181 | 240 | 28 | 2760 | 559 | 642
MAXIMUM | 6.35 | 14 | 14 | 10.4 | 130 | 174 | 16.3 | 0.521 | 0.037 | 6.14 | 10 | 0.07 | 6.11 | 10 |  | 6.09 | 10 |  | 6.21 | 0.49 | 5 | 0.67 | 15.5 | 9 | 0.47377 | 0.056 | 6.15 | 0.462 | 5 | 0.49 | 16 | 8.5 | 0.45412 | 6.17 | 0.343 | 5 | 0.58 | 17 | 9.9 | 0.48667 | 0.028 | 1 | 0.37 | 0.009 | 0.056 | 0.015 | 1 | 0.33 |  | 0.026 | 1 | 0.38 | 0.011 | 7.45 | 0.069 | 1 | 4.3 | 14.5 | 21 | 52 | 0.012 | 7.4 | 0.071 | 1 | 4.3 | 16 | 21 | 54 | 0.011 | 3.9 | 3.9 | 3.8 | [17 empty] | AVERAGE | 9985 | [9 empty] | 255 | 242.5 | 277.5 | 629.5 | 592.5 | 570 | 522.25 | 650 | 677.25 | 868.75 |  | 925 | 890 | 1070 | 76.5 | 101.5 | 11 | 1305 | 265 | 210 | 45.25 | 60 | 7 | 690 | 139.75 | 160.5
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0272 |  | TOTAL AVG COAG ALK: |  |  |  | 9.4444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.49 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.4 | [5 empty] | 6.135 |  |  |  |  | 0.028 |  |  |  |  | 0.4 | [6 empty] | 0.028 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 9900 | [9 empty] | 250 | 230 | 275 | 620 | 540 | 530 | 489 | 650 | 674 | 850 |  | 910 | 840 | 1070 | 76 | 100 | 11 | 1250 | 250 | 203 | 45 | 60 | 7 | 640 | 125 | 152
[90 empty] | MAXIMUM | 10040 | [9 empty] | 270 | 250 | 280 | 658 | 630 | 590 | 540 | 650 | 680 | 875 |  | 970 | 910 | 1070 | 77 | 102 | 11 | 1330 | 270 | 217 | 46 | 60 | 7 | 720 | 150 | 170
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 12.146 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827078 |  | END: | 23827079 |  |  | Alum | 5085 | 9617 | 9617 | 11006 | 11006 | 0 | [44 empty] | 0.4 | 8.5 | 29.9294 | 11.9718 | 6.1 | 15.6 | 10 | 1.1972
[73 empty] | FINISHED 2 | 11.353 |  | TOTAL MGD: |  | 12.145 |  |  | FINISHED SOUTH 2 |  | START: | 43888807 |  | END: | 43900952 |  |  | Caustic | 4548 | 6427 | 6427
[73 empty] | TOTAL RAW | 26.647 |  | TOTAL MGD: |  | 4.464 |  |  | FINISHED CONWAY |  | START: | 10244913 |  | END: | 10249377 |  |  | Hypochlorite | 17 |  | 45
[76 empty] | TOTAL MGD: |  | 6.889 |  |  | FINISHED PERRY |  | START: | 33877704 |  | END: | 33884593 |  |  | Phosphate | 2451
[76 empty] | TOTAL MGD: |  | 8.707 |  |  | RAW PLANT 1 |  | START: | 30997794 |  | END: | 31006501 |  |  | Fluoride | 3800 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.448 |  |  | RAW PLANT 2 |  | START: | 30956349 |  | END: | 30964797 |  |  | Cal~Flo | 6 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.492 |  |  | RAW PLANT 3 |  | START: | 7535590 |  | END: | 7545082 |  |  | Zinc | 941
[76 empty] | TOTAL MGD: |  | 0.651 |  |  | DECANT |  | START: | 1867626 |  | END: | 1868277 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.406 |  |  | BLOW DOWN |  | START: | 9138.1242 |  | END: | 9139.5302 |  |  | NH3 | 7 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 628
23827079
43900952
10249377
33884593
31006501
30964797
7545082
1868277
9139.5302
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 7
DATE: | 2019-01-07 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-07 | [23 empty] | DATE: | 2019-01-07
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-07 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43472.0091 | 2,3,5 | 35 | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 | ,1,3 | 11.7533 | 3 | 12.7627 | 24.516 | 1.8158 | 43472.0091 | 90.8917 | 8362.286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.391 | 1.3022 | 0.2774 | 0.26846 | 0.25951 | 0.24161 | 0.2497 | 0.26122 | 1.6645 | 6 | 0.060012 | 0.060012 | 0.060054 | 1.1063 | 0.55222 | 0.099335 | 4.0269 | 0.76979 | 3.9573 | 1.1005 | 0.55291 | 0.1076 | 3.727 | 0.68911 | 4.9665 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.23 | 0.364 | 5 | 0.57 | 15.5 | 8.5 | 0.45412 |  | 6.2 | 0.376 | 5 | 0.54 | 16.2 | 8.5 | 0.45412 | 6.2 | 0.256 | 5 | 0.55 | 17 | 9.9 | 0.48667 | [13 empty] | 7.46 | 0.068 | 1 | 4.1 | 14.1 |  |  |  | 7.29 | 0.053 | 1 | 4.2 | 15 |  |  |  | 3.9 | 3.8 | 2.9 | [18 empty] | 10000 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 275 | 620 | 600 | 580 | 540 | 650 | 680 | 875 |  | 910 | 910 | 1070 | 77 | 102 | 11 | 1330 | 270 | 217 | 45 | 60 | 7 | 700 | 142 | 160 |  | 1:00 | 0.57 | 8.5 | 29.9294 | 17.0598 | 6.23 | 15.5 | 10 | 1.706 | 15 | 6.5 | 0.33412 | 1:00 | 0.54 | 8.5 | 29.9294 | 16.1619 | 6.2 | 16.2 | 10 | 1.6162 | 15 | 6.5 | 0.33412 | 1:00 | 0.55 | 9.9 | 27.2727 | 15 | 6.2 | 17 | 10 | 1.5 | 15 | 6.5 | 0.36667
2:00 | [72 empty] | 43472.1676 | 2,3,5 | 35 | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 | ,1,3 | 11.7533 | 3 | 12.7627 | 24.516 | 1.8158 | 43472.1676 | 89.9828 | 8362.286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.391 | 1.3022 | 0.2774 | 0.26846 | 0.25951 | 0.24161 | 0.2497 | 0.26122 | 1.6645 | 6 | 0.060012 | 0.060012 | 0.060054 | 1.1063 | 0.55222 | 0.099335 | 4.0269 | 0.76979 | 3.9573 | 1.1005 | 0.55291 | 0.1076 | 3.727 | 0.68911 | 4.9665 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.37 | 11 | 14 | 10.4 | 125 | 174 | 16.1 | 0.524 |  | 6.15 | 8 | 0.053 | 6.08 | 8 |  | 6.05 | 8 | [8 empty] | 0.049 | [14 empty] | 0.024 | 1 | 0.52 |  | 0.049 | 0.011 | 1 | 0.33 |  | 0.023 | 1 | 0.44 | [38 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 275 | 620 | 600 | 580 | 540 | 650 | 680 | 875 |  | 910 | 910 | 1070 | 77 | 102 | 11 | 1330 | 270 | 217 | 45 | 60 | 7 | 700 | 142 | 160 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43472.3025 | 2,3,5 | 35 | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 | ,1,3 | 9.8525 | 3 | 14.639 | 24.4915 | 1.8158 | 43472.3025 | 89.9828 | 8485.2608 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3354 | 1.3632 | 1.3259 | 0.26846 | 0.22371 | 0.24161 | 0.22819 | 0.2497 | 0.26122 | 1.6645 | 7 | 0.060012 | 0.059353 | 0.06 | 1.092 | 0.55222 | 0.099335 | 3.9664 | 0.71277 | 3.9573 | 1.0761 | 0.55291 | 0.1076 | 3.68 | 0.63088 | 4.9665 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.51 | 0.06 | 1 | 4.3 | 13.9 |  |  |  | 7.47 | 0.055 | 1 | 4.2 | 15.1 |  |  |  | 3.9 | 3.8 | 2.9 | [18 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 240 | 245 | 280 | 600 | 500 | 540 | 510 | 650 | 680 | 875 |  | 910 | 900 | 1070 | 76 | 102 | 11 | 1300 | 250 | 217 | 44 | 60 | 7 | 680 | 130 | 160 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43472.8621 | 2,3,5 | 35 | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 | ,1,3 | 9.8525 | 3 | 14.639 | 24.4915 | 1.8158 | 43472.8621 | 90.732 | 8485.2608 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3007 | 1.4163 | 1.2279 | 0.269 | 0.22262 | 0.24117 | 0.2319 | 0.24803 | 0.25795 | 1.5218 | 3 | 0.060295 | 0.060295 | 0.060035 | 1.1046 | 0.55124 | 0.1032 | 4.0173 | 0.75832 | 3.9031 | 1.2155 | 0.54761 | 0.099646 | 3.7009 | 0.66067 | 4.9972 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.38 | 15 | 12 | 11 | 120 | 175 | 16.1 | 0.494 |  | 6.03 | 9 | 0.053 | 6.04 | 9 |  | 5.99 | 9 | [8 empty] | 0.054 | [14 empty] | 0.023 | 1 | 0.32 |  | 0.049 | 0.011 | 1 | 0.2 |  | 0.022 | 1 | 0.38 | [38 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 225 | 245 | 240 | 580 | 480 | 520 | 500 | 600 | 624 | 800 |  | 880 | 880 | 990 | 74 | 98 | 11 | 1260 | 256 | 206 | 46 | 55 | 6 | 620 | 126 | 149 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43472.9928 | 2,3,5 | 35 | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 | ,1,3 | 9.8525 | 3 | 14.639 | 24.4915 | 1.8158 | 43472.9928 | 90.732 | 8485.2608 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3007 | 1.4163 | 1.2279 | 0.269 | 0.22262 | 0.24117 | 0.2319 | 0.24803 | 0.25795 | 1.5218 | 3 | 0.060295 | 0.060295 | 0.060035 | 1.1046 | 0.55124 | 0.1032 | 4.0173 | 0.75832 | 3.9031 | 1.2155 | 0.54761 | 0.099646 | 3.7009 | 0.66067 | 4.9972 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.05 | [9 empty] | 6.1 | 0.425 | 5 | 0.66 | 15.1 | 8.6 | 0.45805 |  | 6.14 | 0.33 | 5 | 0.49 | 15.7 | 8.7 | 0.46198 | 6.18 | 0.35 | 5 | 0.54 | 16.6 | 9.7 | 0.47926 |  |  |  | 0.01 |  |  |  |  | 0.014 |  |  |  | 0.012 | 7.58 | 0.064 | 1 | 4.7 | 14 | 21 | 53 | 0.013 | 7.33 | 0.057 | 1 | 4.7 | 15.1 | 20 | 57 | 0.012 | 3.9 | 3.7 | 3.7 | [18 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 225 | 245 | 240 | 580 | 480 | 520 | 500 | 600 | 624 | 800 |  | 880 | 880 | 990 | 74 | 98 | 11 | 1260 | 256 | 206 | 46 | 55 | 6 | 620 | 126 | 149 |  | 9:00 | 0.66 | 8.6 | 29.5814 | 19.5237 | 6.1 | 15.1 | 10 | 1.9524 | 15 | 6.5 | 0.33805 | 9:00 | 0.49 | 8.7 | 29.2414 | 14.3283 | 6.14 | 15.7 | 10 | 1.4328 | 15 | 6.5 | 0.34198 | 9:00 | 0.54 | 9.7 | 27.8351 | 15.0309 | 6.18 | 16.6 | 10 | 1.5031 | 15 | 6.5 | 0.35926
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.34 | 12 | 14 | 11.5 | 120 | 173 | 16.2 | 0.499 |  | 5.88 | 7 | 0.054 | 5.73 | 7 |  | 6.03 | 7 | [8 empty] | 0.048 | [14 empty] | 0.021 | 1 | 0.39 |  | 0.045 | 0.011 | 1 | 0.28 |  | 0.022 | 1 | 0.38 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.08 | 0.456 | 4 | 0.59 | 15.7 | 8.5 | 0.45412 |  | 6 | 0.464 | 4 | 0.4 | 16 | 8.5 | 0.3873 | 6.12 | 0.375 | 3 | 0.45 | 16.5 | 9.6 | 0.47556 | [13 empty] | 7.27 | 0.07 | 1 | 4.1 | 14.1 |  |  |  | 7.31 | 0.06 | 1 | 3.7 | 15.9 |  |  |  | 3.9 | 3.8 | 2.6 | [55 empty] | 13:00 | 0.59 | 8.5 | 29.9294 | 17.6584 | 6.08 | 15.7 | 10 | 1.7658 | 15 | 6.5 | 0.33412 | 13:00 | 0.4 | 8.5 | 29.9294 | 11.9718 | 6 | 16 | 8 | 1.4965 | 15 | 6 | 0.2673 | 13:00 | 0.45 | 9.6 | 28.125 | 12.6562 | 6.12 | 16.5 | 10 | 1.2656 | 15 | 6.5 | 0.35556
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.36 | 12 | 13 | 11.7 | 119 | 188 | 16.7 | 0.503 |  | 6 | 8 | 0.057 | 5.98 | 8 |  | 5.93 | 8 | [8 empty] | 0.051 | [14 empty] | 0.021 | 1 | 0.33 |  | 0.049 | 0.011 | 1 | 0.24 |  | 0.021 | 1 | 0.45 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.06 | 0.059 | 1 | 4.1 | 14.2 |  |  |  | 7.13 | 0.058 | 1 | 4.2 | 15.2 |  |  |  | 3.9 | 3.8 | 3.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.35 | 12 | 12 | 11.3 | 126 | 180 | 15.9 | 0.521 |  | 6.1 | 8 | 0.06 | 6.08 | 8 |  | 6.05 | 8 | [8 empty] | 0.05 | [14 empty] | 0.021 | 1 | 0.43 |  | 0.048 | 0.016 | 1 | 0.38 |  | 0.021 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.033 | [9 empty] | 6.16 | 0.315 | 4 | 0.65 | 14.8 | 8.2 | 0.60349 |  | 6.17 | 0.308 | 4 | 0.51 | 15.2 | 8.2 | 0.44233 | 6.1 | 0.263 | 3 | 0.65 | 16.1 | 9.2 | 0.46074 |  |  |  | 0.008 | [9 empty] | 7.18 | 0.068 | 1 | 4.3 | 14.2 | 21 | 53 | 0.01 | 7.26 | 0.058 | 1 | 4.1 | 15 | 21 | 56 | 0.009 | 3.9 | 3.7 | 2.8 | [55 empty] | 21:00 | 0.65 | 8.2 | 31.0244 | 20.1659 | 6.16 | 14.8 | 15 | 1.3444 | 10 | 6.5 | 0.48349 | 21:00 | 0.51 | 8.2 | 31.0244 | 15.8224 | 6.17 | 15.2 | 10 | 1.5822 | 15 | 6.5 | 0.32233 | 21:00 | 0.65 | 9.2 | 29.3478 | 19.0761 | 6.1 | 16.1 | 10 | 1.9076 | 15 | 6.5 | 0.34074
22:00 | [72 empty] | DOSE |  | TOTAL | 41.9 | 41.9 | 48.1 | 131.9 | 39.4 | 39.4 | 45.6 | 124.4 | 0 | 53.064 | 15 | 69.4426 | 122.5066 | 9.0792 | TOTAL | 452.3213 | 42180.3544 | 0 | 3251.1013 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7188 | 6.9778 | 6.3862 | 1.3613 | 1.2059 | 1.243 | 1.1752 | 1.2452 | 1.2996 | 8.037 | 25 | 0.30063 | 0.29997 | 0.30018 | 5.5139 | 2.7591 | 0.50441 | 20.055 | 3.769 | 19.678 | 5.7081 | 2.754 | 0.52208 | 18.5359 | 3.3304 | 24.8939 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.39 | 12 | 12 | 11.3 | 125 | 174 | 16.1 | 0.527 |  | 6.12 | 8 | 0.059 | 6.1 | 8 |  | 6.13 | 8 | [8 empty] | 0.051 | [14 empty] | 0.022 | 1 | 0.24 |  | 0.051 | 0.011 | 1 | 0.3 |  | 0.022 | 1 | 0.34 | [22 empty] | AVERAGE | 8.38 | 8.38 | 9.62 | 26.38 | 7.88 | 7.88 | 9.12 | 24.88 |  | 10.6128 | 3 | 13.8885 | 24.5013 | 1.8158 | AVERAGE | 90.4643 | 8436.0709 |  | 650.2203 | 0 | 0 | 0 |  |  |  | 1.3438 | 1.3956 | 1.2772 | 0.27225 | 0.24117 | 0.24859 | 0.23504 | 0.24903 | 0.25992 | 1.6074 | 5 | 0.060125 | 0.059993 | 0.060036 | 1.1028 | 0.55183 | 0.10088 | 4.011 | 0.7538 | 3.9356 | 1.1416 | 0.55079 | 0.10442 | 3.7072 | 0.66609 | 4.9788 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.19 | 74 | 77 | 67.2 | 735 | 1064 | 97.1 | 3.068 | 0.083 | 36.28 | 48 | 0.336 | 36.01 | 48 | 0 | 36.18 | 48 | 0 | 24.57 | 1.56 | 18 | 2.47 | 61.1 | 33.8 | 1.9698 | 0.303 | 24.51 | 1.478 | 18 | 1.94 | 63.1 | 33.9 | 1.7457 | 24.6 | 1.244 | 16 | 2.19 | 66.2 | 38.4 | 1.9022 | 0.132 | 6 | 2.23 | 0.018 | 0.291 | 0.071 | 6 | 1.73 | 0.014 | 0.131 | 6 | 2.45 | 0.012 | 44.06 | 0.389 | 6 | 25.6 | 84.5 | 42 | 106 | 0.023 | 43.79 | 0.341 | 6 | 25.1 | 91.3 | 41 | 113 | 0.021 | 23.4 | 22.6 | 18.6 |  |  | MINIMUM | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 |  | 9.8525 | 3 | 12.7627 | 24.4915 | 1.8158 | MINIMUM | 89.9828 | 8362.286 |  | 650.2203 | [6 empty] | 1.3007 | 1.3632 | 1.2279 | 0.26846 | 0.22262 | 0.24117 | 0.22819 | 0.24803 | 0.25795 | 1.5218 | 3 | 0.060012 | 0.059353 | 0.06 | 1.092 | 0.55124 | 0.099335 | 3.9664 | 0.71277 | 3.9031 | 1.0761 | 0.54761 | 0.099646 | 3.68 | 0.63088 | 4.9665 |  | MIN | 0.65 | 8.2 | 31.0244 | 20.1659 | 6.16 | 14.8 | 15 | 1.3444 |  |  |  | MIN | 0.49 | 8.7 | 29.2414 | 14.3283 | 6.14 | 15.7 | 10 | 1.4328 |  |  |  | MIN | 0.45 | 9.6 | 28.125 | 12.6562 | 6.12 | 16.5 | 10 | 1.2656 |  |  |  | 1.2656
AVERAGE | 6.365 | 12.3333 | 12.8333 | 11.2 | 122.5 | 177.3333 | 16.1833 | 0.51133 | 0.0415 | 6.0467 | 8 | 0.056 | 6.0017 | 8 |  | 6.03 | 8 |  | 6.1425 | 0.39 | 4.5 | 0.6175 | 15.275 | 8.45 | 0.49244 | 0.0505 | 6.1275 | 0.3695 | 4.5 | 0.485 | 15.775 | 8.475 | 0.43643 | 6.15 | 0.311 | 4 | 0.5475 | 16.55 | 9.6 | 0.47556 | 0.022 | 1 | 0.37167 | 0.009 | 0.0485 | 0.011833 | 1 | 0.28833 | 0.014 | 0.021833 | 1 | 0.40833 | 0.012 | 7.3433 | 0.064833 | 1 | 4.2667 | 14.0833 | 21 | 53 | 0.0115 | 7.2983 | 0.056833 | 1 | 4.1833 | 15.2167 | 20.5 | 56.5 | 0.0105 | 3.9 | 3.7667 | 3.1 |  |  | MAXIMUM | 8.5 | 8.5 | 9.9 | 26.9 | 8 | 8 | 9.4 | 25.4 |  | 11.7533 | 3 | 14.639 | 24.516 | 1.8158 | MAXIMUM | 90.8917 | 8485.2608 |  | 650.2203 | [6 empty] | 1.391 | 1.4163 | 1.3259 | 0.2774 | 0.26846 | 0.25951 | 0.24161 | 0.2497 | 0.26122 | 1.6645 | 7 | 0.060295 | 0.060295 | 0.060054 | 1.1063 | 0.55222 | 0.1032 | 4.0269 | 0.76979 | 3.9573 | 1.2155 | 0.55291 | 0.1076 | 3.727 | 0.68911 | 4.9972
MINIMUM | 6.34 | 11 | 12 | 10.4 | 119 | 173 | 15.9 | 0.494 | 0.033 | 5.88 | 7 | 0.053 | 5.73 | 7 |  | 5.93 | 7 |  | 6.08 | 0.315 | 4 | 0.57 | 14.8 | 8.2 | 0.45412 | 0.048 | 6 | 0.308 | 4 | 0.4 | 15.2 | 8.2 | 0.3873 | 6.1 | 0.256 | 3 | 0.45 | 16.1 | 9.2 | 0.46074 | 0.021 | 1 | 0.24 | 0.008 | 0.045 | 0.011 | 1 | 0.2 | 0.014 | 0.021 | 1 | 0.34 | 0.012 | 7.06 | 0.059 | 1 | 4.1 | 13.9 | 21 | 53 | 0.01 | 7.13 | 0.053 | 1 | 3.7 | 15 | 20 | 56 | 0.009 | 3.9 | 3.7 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 48800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 1235 | 1310 | 3000 | 2660 | 2740 | 2590 | 3150 | 3288 | 4225 | 0 | 4490 | 4480 | 5190 | 378 | 502 | 55 | 6480 | 1302 | 1063 | 226 | 290 | 33 | 3320 | 666 | 778
MAXIMUM | 6.39 | 15 | 14 | 11.7 | 126 | 188 | 16.7 | 0.527 | 0.05 | 6.15 | 9 | 0.06 | 6.1 | 9 |  | 6.13 | 9 |  | 6.23 | 0.456 | 5 | 0.66 | 15.7 | 8.6 | 0.60349 | 0.054 | 6.2 | 0.464 | 5 | 0.54 | 16.2 | 8.7 | 0.46198 | 6.2 | 0.375 | 5 | 0.65 | 17 | 9.9 | 0.48667 | 0.024 | 1 | 0.52 | 0.01 | 0.051 | 0.016 | 1 | 0.38 | 0.014 | 0.023 | 1 | 0.46 | 0.012 | 7.58 | 0.07 | 1 | 4.7 | 14.2 | 21 | 53 | 0.013 | 7.47 | 0.06 | 1 | 4.7 | 15.9 | 21 | 57 | 0.012 | 3.9 | 3.8 | 3.7 | [17 empty] | AVERAGE | 9760 | [9 empty] | 238 | 247 | 262 | 600 | 532 | 548 | 518 | 630 | 657.6 | 845 |  | 898 | 896 | 1038 | 75.6 | 100.4 | 11 | 1296 | 260.4 | 212.6 | 45.2 | 58 | 6.6 | 664 | 133.2 | 155.6
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0261 |  | TOTAL AVG COAG ALK: |  |  |  | 8 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.464 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.4 | [5 empty] | 6.14 |  |  |  |  | 0.024 |  |  |  |  | 0.4 | [6 empty] | 0.024 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 9500 | [9 empty] | 225 | 245 | 240 | 580 | 480 | 520 | 500 | 600 | 624 | 800 |  | 880 | 880 | 990 | 74 | 98 | 11 | 1260 | 250 | 206 | 44 | 55 | 6 | 620 | 126 | 149
[90 empty] | MAXIMUM | 10000 | [9 empty] | 250 | 250 | 280 | 620 | 600 | 580 | 540 | 650 | 680 | 875 |  | 910 | 910 | 1070 | 77 | 102 | 11 | 1330 | 270 | 217 | 46 | 60 | 7 | 700 | 142 | 160
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.396 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827079 |  | END: | 23827080 |  |  | Alum | 3223 | 11163 | 11163 | 10248 | 10248 | 0 | [44 empty] | 0.45 | 9.6 | 28.125 | 12.6562 | 6.12 | 16.5 | 10 | 1.2656
[73 empty] | FINISHED 2 | 11.462 |  | TOTAL MGD: |  | 10.395 |  |  | FINISHED SOUTH 2 |  | START: | 43900952 |  | END: | 43911347 |  |  | Caustic | 4496 | 6407 | 6407
[73 empty] | TOTAL RAW | 25.963 |  | TOTAL MGD: |  | 4.692 |  |  | FINISHED CONWAY |  | START: | 10249377 |  | END: | 10254069 |  |  | Hypochlorite | 16 |  | 44
[76 empty] | TOTAL MGD: |  | 6.77 |  |  | FINISHED PERRY |  | START: | 33884593 |  | END: | 33891363 |  |  | Phosphate | 2398
[76 empty] | TOTAL MGD: |  | 8.305 |  |  | RAW PLANT 1 |  | START: | 31006501 |  | END: | 31014806 |  |  | Fluoride | 3500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.314 |  |  | RAW PLANT 2 |  | START: | 30964797 |  | END: | 30973111 |  |  | Cal~Flo | 9.49 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.344 |  |  | RAW PLANT 3 |  | START: | 7545082 |  | END: | 7554426 |  |  | Zinc | 923
[76 empty] | TOTAL MGD: |  | 0.869 |  |  | DECANT |  | START: | 1868277 |  | END: | 1869146 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.8297 |  |  | BLOW DOWN |  | START: | 9139.5302 |  | END: | 9141.3599 |  |  | NH3 | 6.22 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 630
23827080
43911347
10254069
33891363
31014806
30973111
7554426
1869146
9141.3599
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 8
DATE: | 2019-01-08 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-08 | [23 empty] | DATE: | 2019-01-08
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-08 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43473.0072 | 2,3,5 | 35 | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 | ,1,3 | 9.8525 | 3 | 14.639 | 24.4915 | 1.8158 | 43473.0072 | 90.732 | 8485.2608 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3007 | 1.4163 | 1.2279 | 0.269 | 0.22262 | 0.24117 | 0.2319 | 0.24803 | 0.25795 | 1.5218 | 3 | 0.060295 | 0.060295 | 0.060035 | 1.1046 | 0.55124 | 0.1032 | 4.0173 | 0.75832 | 3.9031 | 1.2155 | 0.54761 | 0.099646 | 3.7009 | 0.66067 | 4.9972 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.25 | 0.325 | 4 | 0.61 | 15.5 | 8.2 | 0.44233 |  | 6.22 | 0.317 | 4 | 0.46 | 16.2 | 8.2 | 0.44233 | 6.21 | 0.252 | 4 | 0.52 | 17 | 9.2 | 0.46074 | [13 empty] | 7.56 | 0.051 | 1 | 4.1 | 14.2 |  |  |  | 7.42 | 0.057 | 1 | 4 | 15.1 |  |  |  | 4 | 3.9 | 2.9 | [18 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 225 | 245 | 240 | 580 | 480 | 520 | 500 | 600 | 624 | 800 |  | 880 | 880 | 990 | 74 | 98 | 11 | 1260 | 256 | 206 | 46 | 55 | 6 | 620 | 126 | 149 |  | 1:00 | 0.61 | 8.2 | 31.0244 | 18.9249 | 6.25 | 15.5 | 10 | 1.8925 | 15 | 6.5 | 0.32233 | 1:00 | 0.46 | 8.2 | 31.0244 | 14.2712 | 6.22 | 16.2 | 10 | 1.4271 | 15 | 6.5 | 0.32233 | 1:00 | 0.52 | 9.2 | 29.3478 | 15.2609 | 6.21 | 17 | 10 | 1.5261 | 15 | 6.5 | 0.34074
2:00 | [72 empty] | 43473.1526 | 2,3,5 | 35 | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 | ,1,3 | 9.8525 | 3 | 14.639 | 24.4915 | 1.8158 | 43473.1526 | 90.732 | 8485.2608 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3007 | 1.4163 | 1.2279 | 0.269 | 0.22262 | 0.24117 | 0.2319 | 0.24803 | 0.25795 | 1.5218 | 3 | 0.060295 | 0.060295 | 0.060035 | 1.1046 | 0.55124 | 0.1032 | 4.0173 | 0.75832 | 3.9031 | 1.2155 | 0.54761 | 0.099646 | 3.7009 | 0.66067 | 4.9972 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.38 | 11 | 12 | 10.5 | 126 | 174 | 16.1 | 0.526 |  | 6.16 | 9 | 0.064 | 6.14 | 9 |  | 6.11 | 9 | [8 empty] | 0.05 | [14 empty] | 0.021 | 1 | 0.35 |  | 0.05 | 0.012 | 1 | 0.38 |  | 0.023 | 1 | 0.38 | [38 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 225 | 245 | 240 | 580 | 480 | 520 | 500 | 600 | 624 | 800 |  | 880 | 880 | 990 | 74 | 98 | 11 | 1260 | 256 | 206 | 46 | 55 | 6 | 620 | 126 | 149 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43473.3118 | 2,3,5 | 35 | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 | ,1,3 | 11.507 | 3 | 12.3408 | 23.8478 | 1.8158 | 43473.3118 | 90.7129 | 8731.2104 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2718 | 1.2718 | 1.2279 | 0.269 | 0.21335 | 0.23654 | 0.20871 | 0.24803 | 0.25795 | 1.5218 | 5 | 0.060295 | 0.058924 | 0.060035 | 1.1196 | 0.55124 | 0.1032 | 3.9246 | 0.66649 | 3.9031 | 1.0569 | 0.54761 | 0.099646 | 3.2763 | 0.57677 | 5.0978 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.57 | 0.057 | 1 | 4.4 | 14.2 |  |  |  | 7.55 | 0.058 | 1 | 4.5 | 15.1 |  |  |  | 4 | 3.9 | 3 | [18 empty] | 9498 | [6 empty] | 0 | 0 | 0 | 220 | 220 | 240 | 580 | 460 | 510 | 450 | 600 | 624 | 800 |  | 880 | 860 | 990 | 75 | 98 | 11 | 1200 | 225 | 206 | 40 | 55 | 6 | 560 | 110 | 152 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43473.8223 | 2,3,5 | 35 | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 | ,1,3 | 10.3694 | 3 | 13.5749 | 23.9443 | 1.9944 | 43473.8223 | 90.732 | 8731 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3007 | 1.3007 | 1.2024 | 0.269 | 0.24117 | 0.24117 | 0.2319 | 0.24803 | 0.26043 | 1.5218 | 6 | 0.060295 | 0.060295 | 0.060035 | 1.1046 | 0.56249 | 0.093823 | 4.0173 | 0.77016 | 3.9031 | 1.1098 | 0.54761 | 0.099646 | 3.7021 | 0.7131 | 5.0978 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.47 | 14 | 13 | 10.9 | 124 | 175 | 16.1 | 0.498 |  | 6.04 | 8 | 0.058 | 6.1 | 9 |  | 6.07 | 8 | [8 empty] | 0.054 | [14 empty] | 0.057 | 1 | 0.44 |  | 0.049 | 0.013 | 1 | 0.3 |  | 0.021 | 1 | 0.34 | [38 empty] | 9500 | [6 empty] | 0 | 0 | 0 | 225 | 225 | 235 | 580 | 520 | 520 | 500 | 600 | 630 | 800 |  | 880 | 880 | 990 | 74 | 100 | 10 | 1260 | 260 | 206 | 42 | 55 | 6 | 666 | 136 | 152 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43473.9901 | 2,3,5 | 35 | 8.6 | 8.6 | 9.6 | 26.8 | 8.1 | 8.1 | 9.1 | 25.3 | ,1,3 | 10.3694 | 3 | 13.5749 | 23.9443 | 1.9944 | 43473.9901 | 90.3186 | 8977.16 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3079 | 1.3079 | 1.1984 | 0.26799 | 0.2388 | 0.2388 | 0.22996 | 0.24958 | 0.2575 | 1.5218 | 6 | 0.059922 | 0.059922 | 0.060005 | 1.1069 | 0.55075 | 0.098108 | 4.002 | 0.75747 | 3.8904 | 1.1115 | 0.5521 | 0.095266 | 3.699 | 0.71183 | 5.0982 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.051 | [9 empty] | 6.19 | 0.438 | 4 | 0.54 | 15 | 8.3 | 0.44626 |  | 6.2 | 0.409 | 4 | 0.47 | 15.5 | 8.3 | 0.44626 | 6.2 | 0.298 | 4 | 0.57 | 16.4 | 9.4 | 0.46815 |  |  |  | 0.011 |  |  |  |  | 0.011 |  |  |  | 0.006 | 7.29 | 0.063 | 1 | 4 | 14.1 | 18 | 52 | 0.012 | 7.21 | 0.06 | 1 | 4 | 15.2 | 17 | 51 | 0.008 | 4 | 3.8 | 3.4 | [18 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 238 | 238 | 245 | 606 | 540 | 540 | 520 | 630 | 650 | 800 |  | 920 | 920 | 1035 | 78 | 103 | 11 | 1320 | 269 | 216 | 44 | 58 | 6 | 696 | 142 | 159 |  | 9:00 | 0.54 | 8.3 | 30.6506 | 16.5513 | 6.19 | 15 | 10 | 1.6551 | 15 | 6.5 | 0.32626 | 9:00 | 0.47 | 8.3 | 30.6506 | 14.4058 | 6.2 | 15.5 | 10 | 1.4406 | 15 | 6.5 | 0.32626 | 9:00 | 0.57 | 9.4 | 28.7234 | 16.3723 | 6.2 | 16.4 | 10 | 1.6372 | 15 | 6.5 | 0.34815
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.33 | 13 | 13 | 11.4 | 117 | 174 | 15.9 | 0.48 |  | 6.02 | 7 | 0.06 | 6.06 | 8 |  | 6 | 8 | [8 empty] | 0.057 | [14 empty] | 0.043 | 1 | 0.38 |  | 0.053 | 0.012 | 1 | 0.19 |  | 0.021 | 1 | 0.21 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.18 | 0.419 | 4 | 0.47 | 16.3 | 8.3 | 0.44626 |  | 6.14 | 0.427 | 4 | 0.45 | 15.5 | 8.4 | 0.45019 | 6.14 | 0.313 | 4 | 0.51 | 17 | 9.5 | 0.47185 | [13 empty] | 7.33 | 0.069 | 1 | 4.1 | 14.5 |  |  |  | 7.5 | 0.061 | 1 | 4.5 | 16.2 |  |  |  | 4 | 3.9 | 2.5 | [55 empty] | 13:00 | 0.47 | 8.3 | 30.6506 | 14.4058 | 6.18 | 16.3 | 10 | 1.4406 | 15 | 6.5 | 0.32626 | 13:00 | 0.45 | 8.4 | 30.2857 | 13.6286 | 6.14 | 15.5 | 10 | 1.3629 | 15 | 6.5 | 0.33019 | 13:00 | 0.51 | 9.5 | 28.4211 | 14.4947 | 6.14 | 17 | 10 | 1.4495 | 15 | 6.5 | 0.35185
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.33 | 14 | 13 | 11.2 | 122 | 175 | 16 | 0.507 |  | 6.08 | 8 | 0.06 | 6.12 | 9 |  | 6.12 | 9 | [8 empty] | 0.056 | [14 empty] | 0.038 | 1 | 0.25 |  | 0.054 | 0.015 | 1 | 0.2 |  | 0.056 | 1 | 0.3 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.43 | 0.053 | 1 | 4.3 | 14.7 |  |  |  | 7.35 | 0.06 | 1 | 4.1 | 15.7 |  |  |  | 3.9 | 3.8 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.35 | 13 | 15 | 10.1 | 116 | 171 | 16.1 | 0.524 |  | 6.15 | 8 | 0.059 | 6.17 | 8 |  | 6.13 | 8 | [8 empty] | 0.052 | [14 empty] | 0.033 | 1 | 0.24 |  | 0.052 | 0.021 | 1 | 0.36 |  | 0.044 | 1 | 0.42 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.037 | [9 empty] | 6.28 | 0.361 | 5 | 0.52 | 15.1 | 8.2 | 0.44233 |  | 6.27 | 0.381 | 4 | 0.38 | 15.5 | 8.2 | 0.44233 | 6.25 | 0.295 | 4 | 0.43 | 16.4 | 9.2 | 0.46074 |  |  |  | 0.01 | [9 empty] | 7.62 | 0.058 | 1 | 4.2 | 14.3 | 21 | 52 | 0.009 | 7.56 | 0.062 | 1 | 4.1 | 15.3 | 22 | 52 | 0.008 | 4 | 3.7 | 2.8 | [55 empty] | 21:00 | 0.52 | 8.2 | 31.0244 | 16.1327 | 6.28 | 15.1 | 10 | 1.6133 | 15 | 6.5 | 0.32233 | 21:00 | 0.38 | 8.2 | 31.0244 | 11.7893 | 6.27 | 15.5 | 10 | 1.1789 | 15 | 6.5 | 0.32233 | 21:00 | 0.43 | 9.2 | 29.3478 | 12.6196 | 6.25 | 16.4 | 10 | 1.262 | 15 | 6.5 | 0.34074
22:00 | [72 empty] | DOSE |  | TOTAL | 41.4 | 41.4 | 46.4 | 129.2 | 38.9 | 38.9 | 43.9 | 121.7 | 0 | 51.9509 | 15 | 68.7686 | 120.7195 | 9.4363 | TOTAL | 453.2273 | 43409.892 | 0 | 3251.1013 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4818 | 6.713 | 6.0846 | 1.344 | 1.1386 | 1.1989 | 1.1344 | 1.2417 | 1.2918 | 7.609 | 23 | 0.3011 | 0.29973 | 0.30014 | 5.5404 | 2.7669 | 0.50155 | 19.9786 | 3.7108 | 19.5026 | 5.7092 | 2.7426 | 0.49385 | 18.0792 | 3.323 | 25.2881 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.34 | 13 | 15 | 10.4 | 126 | 176 | 16.1 | 0.526 |  | 6.17 | 8 | 0.057 | 6.18 | 8 |  | 6.13 | 8 | [8 empty] | 0.046 | [14 empty] | 0.034 | 1 | 0.24 |  | 0.05 | 0.016 | 1 | 0.2 |  | 0.04 | 1 | 0.21 | [22 empty] | AVERAGE | 8.28 | 8.28 | 9.28 | 25.84 | 7.78 | 7.78 | 8.78 | 24.34 |  | 10.3902 | 3 | 13.7537 | 24.1439 | 1.8873 | AVERAGE | 90.6455 | 8681.9784 |  | 650.2203 | 0 | 0 | 0 |  |  |  | 1.2964 | 1.3426 | 1.2169 | 0.2688 | 0.22771 | 0.23977 | 0.22687 | 0.24834 | 0.25836 | 1.5218 | 4.6 | 0.06022 | 0.059946 | 0.060029 | 1.1081 | 0.55339 | 0.10031 | 3.9957 | 0.74215 | 3.9005 | 1.1418 | 0.54851 | 0.09877 | 3.6158 | 0.66461 | 5.0576 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.2 | 78 | 81 | 64.5 | 731 | 1045 | 96.3 | 3.061 | 0.088 | 36.62 | 48 | 0.358 | 36.77 | 51 | 0 | 36.56 | 50 | 0 | 24.9 | 1.543 | 17 | 2.14 | 61.9 | 33 | 1.7772 | 0.315 | 24.83 | 1.534 | 16 | 1.76 | 62.7 | 33.1 | 1.7811 | 24.8 | 1.158 | 16 | 2.03 | 66.8 | 37.3 | 1.8615 | 0.226 | 6 | 1.9 | 0.021 | 0.308 | 0.089 | 6 | 1.63 | 0.011 | 0.205 | 6 | 1.86 | 0.006 | 44.8 | 0.351 | 6 | 25.1 | 86 | 39 | 104 | 0.021 | 44.59 | 0.358 | 6 | 25.2 | 92.6 | 39 | 103 | 0.016 | 23.9 | 23 | 17.3 |  |  | MINIMUM | 8.2 | 8.2 | 9.2 | 25.6 | 7.7 | 7.7 | 8.7 | 24.1 |  | 9.8525 | 3 | 12.3408 | 23.8478 | 1.8158 | MINIMUM | 90.3186 | 8485.2608 |  | 650.2203 | [6 empty] | 1.2718 | 1.2718 | 1.1984 | 0.26799 | 0.21335 | 0.23654 | 0.20871 | 0.24803 | 0.2575 | 1.5218 | 3 | 0.059922 | 0.058924 | 0.060005 | 1.1046 | 0.55075 | 0.093823 | 3.9246 | 0.66649 | 3.8904 | 1.0569 | 0.54761 | 0.095266 | 3.2763 | 0.57677 | 4.9972 |  | MIN | 0.47 | 8.3 | 30.6506 | 14.4058 | 6.18 | 16.3 | 10 | 1.4406 |  |  |  | MIN | 0.38 | 8.2 | 31.0244 | 11.7893 | 6.27 | 15.5 | 10 | 1.1789 |  |  |  | MIN | 0.43 | 9.2 | 29.3478 | 12.6196 | 6.25 | 16.4 | 10 | 1.262 |  |  |  | 1.1789
AVERAGE | 6.3667 | 13 | 13.5 | 10.75 | 121.8333 | 174.1667 | 16.05 | 0.51017 | 0.044 | 6.1033 | 8 | 0.059667 | 6.1283 | 8.5 |  | 6.0933 | 8.3333 |  | 6.225 | 0.38575 | 4.25 | 0.535 | 15.475 | 8.25 | 0.44429 | 0.0525 | 6.2075 | 0.3835 | 4 | 0.44 | 15.675 | 8.275 | 0.44528 | 6.2 | 0.2895 | 4 | 0.5075 | 16.7 | 9.325 | 0.46537 | 0.037667 | 1 | 0.31667 | 0.0105 | 0.051333 | 0.014833 | 1 | 0.27167 | 0.011 | 0.034167 | 1 | 0.31 |  | 7.4667 | 0.0585 | 1 | 4.1833 | 14.3333 | 19.5 | 52 | 0.0105 | 7.4317 | 0.059667 | 1 | 4.2 | 15.4333 | 19.5 | 51.5 | 0.008 | 3.9833 | 3.8333 | 2.8833 |  |  | MAXIMUM | 8.6 | 8.6 | 9.6 | 26.8 | 8.1 | 8.1 | 9.1 | 25.3 |  | 11.507 | 3 | 14.639 | 24.4915 | 1.9944 | MAXIMUM | 90.732 | 8977.16 |  | 650.2203 | [6 empty] | 1.3079 | 1.4163 | 1.2279 | 0.269 | 0.24117 | 0.24117 | 0.2319 | 0.24958 | 0.26043 | 1.5218 | 6 | 0.060295 | 0.060295 | 0.060035 | 1.1196 | 0.56249 | 0.1032 | 4.0173 | 0.77016 | 3.9031 | 1.2155 | 0.5521 | 0.099646 | 3.7021 | 0.7131 | 5.0982
MINIMUM | 6.33 | 11 | 12 | 10.1 | 116 | 171 | 15.9 | 0.48 | 0.037 | 6.02 | 7 | 0.057 | 6.06 | 8 |  | 6 | 8 |  | 6.18 | 0.325 | 4 | 0.47 | 15 | 8.2 | 0.44233 | 0.046 | 6.14 | 0.317 | 4 | 0.38 | 15.5 | 8.2 | 0.44233 | 6.14 | 0.252 | 4 | 0.43 | 16.4 | 9.2 | 0.46074 | 0.021 | 1 | 0.24 | 0.01 | 0.049 | 0.012 | 1 | 0.19 | 0.011 | 0.021 | 1 | 0.21 |  | 7.29 | 0.051 | 1 | 4 | 14.1 | 18 | 52 | 0.009 | 7.21 | 0.057 | 1 | 4 | 15.1 | 17 | 51 | 0.008 | 3.9 | 3.7 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 47898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1133 | 1173 | 1200 | 2926 | 2480 | 2610 | 2470 | 3030 | 3152 | 4000 | 0 | 4440 | 4420 | 4995 | 375 | 497 | 54 | 6300 | 1266 | 1040 | 218 | 278 | 30 | 3162 | 640 | 761
MAXIMUM | 6.47 | 14 | 15 | 11.4 | 126 | 176 | 16.1 | 0.526 | 0.051 | 6.17 | 9 | 0.064 | 6.18 | 9 |  | 6.13 | 9 |  | 6.28 | 0.438 | 5 | 0.61 | 16.3 | 8.3 | 0.44626 | 0.057 | 6.27 | 0.427 | 4 | 0.47 | 16.2 | 8.4 | 0.45019 | 6.25 | 0.313 | 4 | 0.57 | 17 | 9.5 | 0.47185 | 0.057 | 1 | 0.44 | 0.011 | 0.054 | 0.021 | 1 | 0.38 | 0.011 | 0.056 | 1 | 0.42 |  | 7.62 | 0.069 | 1 | 4.4 | 14.7 | 21 | 52 | 0.012 | 7.56 | 0.062 | 1 | 4.5 | 16.2 | 22 | 52 | 0.008 | 4 | 3.9 | 3.4 | [17 empty] | AVERAGE | 9579.6 | [9 empty] | 226.6 | 234.6 | 240 | 585.2 | 496 | 522 | 494 | 606 | 630.4 | 800 |  | 888 | 884 | 999 | 75 | 99.4 | 10.8 | 1260 | 253.2 | 208 | 43.6 | 55.6 | 6 | 632.4 | 128 | 152.2
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1083 |  | TOTAL AVG COAG ALK: |  |  |  | 8.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.438 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.38 | [5 empty] | 6.2108 |  |  |  |  | 0.057 |  |  |  |  | 0.38 | [6 empty] | 0.057 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 9498 | [9 empty] | 220 | 220 | 235 | 580 | 460 | 510 | 450 | 600 | 624 | 800 |  | 880 | 860 | 990 | 74 | 98 | 10 | 1200 | 225 | 206 | 40 | 55 | 6 | 560 | 110 | 149
[90 empty] | MAXIMUM | 9900 | [9 empty] | 238 | 245 | 245 | 606 | 540 | 540 | 520 | 630 | 650 | 800 |  | 920 | 920 | 1035 | 78 | 103 | 11 | 1320 | 269 | 216 | 46 | 58 | 6 | 696 | 142 | 159
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.413 |  | TOTAL MGD: |  | 0 |  |  | FINISHED SOUTH 1 |  | START: | 23827080 |  | END: | 23827080 |  |  | Alum | 4034 | 11163 | 11163 | 10248 | 10248 | 0 | [44 empty] | 0.38 | 8.2 | 31.0244 | 11.7893 | 6.27 | 15.5 | 10 | 1.1789
[73 empty] | FINISHED 2 | 11.817 |  | TOTAL MGD: |  | 9.413 |  |  | FINISHED SOUTH 2 |  | START: | 43911347 |  | END: | 43920760 |  |  | Caustic | 4446 | 6372 | 6372
[73 empty] | TOTAL RAW | 26.242 |  | TOTAL MGD: |  | 4.625 |  |  | FINISHED CONWAY |  | START: | 10254069 |  | END: | 10258694 |  |  | Hypochlorite | 19 |  | 38
[76 empty] | TOTAL MGD: |  | 7.192 |  |  | FINISHED PERRY |  | START: | 33891363 |  | END: | 33898555 |  |  | Phosphate | 2373
[76 empty] | TOTAL MGD: |  | 8.368 |  |  | RAW PLANT 1 |  | START: | 31014806 |  | END: | 31023174 |  |  | Fluoride | 3500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.446 |  |  | RAW PLANT 2 |  | START: | 30973111 |  | END: | 30981557 |  |  | Cal~Flo | 14.8 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.428 |  |  | RAW PLANT 3 |  | START: | 7554426 |  | END: | 7563854 |  |  | Zinc | 985
[76 empty] | TOTAL MGD: |  | 0.9 |  |  | DECANT |  | START: | 1869146 |  | END: | 1870046 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.6758 |  |  | BLOW DOWN |  | START: | 9141.3599 |  | END: | 9143.0358 |  |  | NH3 | 13.7 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827080
43920760
10258694
33898555
31023174
30981557
7563854
1870046
9143.0358
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 9
DATE: | 2019-01-09 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-09 | [23 empty] | DATE: | 2019-01-09
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-09 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43474.0068 | 2,3,5 | 35 | 8.6 | 8.6 | 9.6 | 26.8 | 8.1 | 8.1 | 9.1 | 25.3 | ,1,3 | 10.3694 | 3 | 13.5749 | 23.9443 | 1.9944 | 43474.0068 | 90.3186 | 8977.16 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3079 | 1.3079 | 1.1984 | 0.26799 | 0.2388 | 0.2388 | 0.22996 | 0.24958 | 0.2575 | 1.5218 | 6 | 0.059922 | 0.059922 | 0.060005 | 1.1069 | 0.55075 | 0.098108 | 4.002 | 0.75747 | 3.8904 | 1.1115 | 0.5521 | 0.095266 | 3.699 | 0.71183 | 5.0982 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.27 | 0.335 | 5 | 0.58 | 15.5 | 8.6 | 0.45805 |  | 6.24 | 0.327 | 5 | 0.5 | 16 | 8.6 | 0.45805 | 6.24 | 0.282 | 4 | 0.51 | 17 | 9.6 | 0.47556 | [13 empty] | 7.6 | 0.062 | 1 | 4.3 | 14.4 |  |  |  | 7.49 | 0.063 | 1 | 4.3 | 15.2 |  |  |  | 4.1 | 3.8 | 2.8 | [18 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 238 | 238 | 245 | 606 | 540 | 540 | 520 | 630 | 650 | 800 |  | 920 | 920 | 1035 | 78 | 103 | 11 | 1320 | 269 | 216 | 44 | 58 | 6 | 696 | 142 | 159 |  | 1:00 | 0.58 | 8.6 | 29.5814 | 17.1572 | 6.27 | 15.5 | 10 | 1.7157 | 15 | 6.5 | 0.33805 | 1:00 | 0.5 | 8.6 | 29.5814 | 14.7907 | 6.24 | 16 | 10 | 1.4791 | 15 | 6.5 | 0.33805 | 1:00 | 0.51 | 9.6 | 28.125 | 14.3438 | 6.24 | 17 | 10 | 1.4344 | 15 | 6.5 | 0.35556
2:00 | [72 empty] | 43474.123 | 2,3,5 | 35 | 8.6 | 8.6 | 9.6 | 26.8 | 8.1 | 8.1 | 9.1 | 25.3 | ,1,3 | 10.3694 | 3 | 13.5749 | 23.9443 | 1.9944 | 43474.123 | 90.3186 | 8977.16 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3079 | 1.3079 | 1.1984 | 0.26799 | 0.2388 | 0.2388 | 0.22996 | 0.24958 | 0.2575 | 1.5218 | 6 | 0.059922 | 0.059922 | 0.060005 | 1.1069 | 0.55075 | 0.098108 | 4.002 | 0.75747 | 3.8904 | 1.1115 | 0.5521 | 0.095266 | 3.699 | 0.71183 | 5.0982 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.38 | 14 | 15 | 11.8 | 130 | 179 | 16.2 | 0.539 |  | 6.22 | 9 | 0.063 | 6.17 | 9 |  | 6.08 | 9 | [8 empty] | 0.048 | [14 empty] | 0.033 | 1 | 0.27 |  | 0.047 | 0.012 | 1 | 0.37 |  | 0.034 | 1 | 0.45 | [38 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 238 | 238 | 245 | 606 | 540 | 540 | 520 | 630 | 650 | 800 |  | 920 | 920 | 1035 | 78 | 103 | 11 | 1320 | 269 | 216 | 44 | 58 | 6 | 696 | 142 | 159 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43474.3695 | 2,3,5 | 36 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 10.3565 | 3 | 12.7066 | 23.063 | 1.9944 | 43474.3695 | 90.1153 | 8977.16 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3616 | 1.3616 | 1.3119 | 0.27044 | 0.21974 | 0.23664 | 0.21974 | 0.22819 | 0.22819 | 1.5218 | 8 | 0.059585 | 0.059585 | 0.058867 | 1.0818 | 0.55031 | 0.10199 | 3.9962 | 0.75135 | 4.4625 | 1.1131 | 0.54709 | 0.12167 | 3.7352 | 0.64825 | 7.9856 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.58 | 0.06 | 1 | 4.2 | 14.7 |  |  |  | 7.44 | 0.058 | 1 | 4.1 | 15.2 |  |  |  | 4.1 | 3.8 | 2.8 | [18 empty] | 10320 | [6 empty] | 0 | 0 | 0 | 260 | 260 | 280 | 640 | 520 | 560 | 520 | 600 | 600 | 800 |  | 960 | 960 | 1060 | 80 | 108 | 12 | 1370 | 280 | 260 | 46 | 60 | 8 | 680 | 135 | 260 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43475.8459 | 2,3,5 | 38 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 11.4898 | 1,3 | 13.7635 | 25.2533 | 1.9094 | 43475.8459 | 89.9406 | 8854.1852 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3616 | 1.571 | 1.4057 | 0.27044 | 0.23664 | 0.23664 | 0.21974 | 0.22819 | 0.22819 | 1.5218 | 6 | 0.059585 | 0.059585 | 0.059977 | 1.0818 | 0.55031 | 0.10199 | 3.9986 | 0.77818 | 3.7073 | 1.0647 | 0.54709 | 0.10646 | 3.6513 | 0.69627 | 4.9142 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.36 | 12 | 14 | 11.7 | 120 | 177 | 166 | 0.491 |  | 6.06 | 10 | 0.172 | 6.05 | 9 |  | 6.07 | 10 | [8 empty] | 0.049 | [14 empty] | 0.031 | 1 | 0.33 |  | 0.049 | 0.016 | 1 | 0.31 |  | 0.032 | 1 | 0.43 | [38 empty] | 10300 | [6 empty] | 0 | 0 | 0 | 260 | 300 | 300 | 640 | 560 | 560 | 520 | 600 | 600 | 800 |  | 960 | 960 | 1080 | 80 | 108 | 12 | 1410 | 290 | 216 | 44 | 60 | 7 | 700 | 145 | 160 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.046 | [9 empty] | 6.12 | 0.415 | 5 | 0.46 | 15.2 | 8.9 | 0.46984 |  | 6.16 | 0.395 | 4 | 0.45 | 15.9 | 8.6 | 0.45805 | 6.15 | 0.3 | 3 | 0.52 | 16.8 | 10.1 | 0.49407 |  |  |  | 0.009 |  |  |  |  | 0.011 |  |  |  | 0.006 | 7.36 | 0.061 | 1 | 4.1 | 14.1 | 25 | 52 | 0.014 | 7.34 | 0.064 | 1 | 4 | 16.3 | 23 | 55 | 0.012 | 4 | 3.7 | 3.6 | [55 empty] | 9:00 | 0.46 | 8.9 | 28.5843 | 13.1488 | 6.12 | 15.2 | 10 | 1.3149 | 15 | 6.5 | 0.34984 | 9:00 | 0.45 | 8.6 | 29.5814 | 13.3116 | 6.16 | 15.9 | 10 | 1.3312 | 15 | 6.5 | 0.33805 | 9:00 | 0.52 | 10.1 | 26.7327 | 13.901 | 6.15 | 16.8 | 10 | 1.3901 | 15 | 6.5 | 0.37407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.4 | 13 | 14 | 12.8 | 128 | 190 | 16.4 | 0.513 |  | 6.05 | 10 | 0.115 | 5.99 | 10 |  | 6.03 | 11 | [8 empty] | 0.05 | [14 empty] | 0.029 | 1 | 0.31 |  | 0.049 | 0.015 | 1 | 0.35 |  | 0.03 | 2 | 0.32 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.278 | 4 | 0.5 | 15.6 | 8.9 | 0.46984 |  | 6.11 | 0.239 | 3 | 0.43 | 16.3 | 9 | 0.47377 | 6.12 | 0.314 | 3 | 0.41 | 16.6 | 10.1 | 0.49407 | [13 empty] | 7.51 | 0.055 | 1 | 3.8 | 14.1 |  |  |  | 7.49 | 0.058 | 1 | 4.1 | 16.4 |  |  |  | 4 | 3.8 | 2.6 | [55 empty] | 13:00 | 0.5 | 8.9 | 28.5843 | 14.2921 | 6.1 | 15.6 | 10 | 1.4292 | 15 | 6.5 | 0.34984 | 13:00 | 0.43 | 9 | 28.2667 | 12.1547 | 6.11 | 16.3 | 10 | 1.2155 | 15 | 6.5 | 0.35377 | 13:00 | 0.41 | 10.1 | 26.7327 | 10.9604 | 6.12 | 16.6 | 10 | 1.096 | 15 | 6.5 | 0.37407
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.36 | 14 | 13 | 10.4 | 123 | 173 | 16.4 | 0.499 |  | 6.09 | 8 | 0.078 | 6.08 | 9 |  | 6.02 | 9 | [8 empty] | 0.051 | [14 empty] | 0.028 | 1 | 0.22 |  | 0.052 | 0.015 | 1 | 0.16 |  | 0.029 | 1 | 0.27 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.53 | 0.069 | 1 | 3.9 | 14.7 |  |  |  | 7.44 | 0.063 | 1 | 3.8 | 15.1 |  |  |  | 4 | 3.9 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.42 | 16 | 14 | 10.3 | 123 | 170 | 16.1 | 0.509 |  | 6.01 | 10 | 0.078 | 6.03 | 10 |  | 6.01 | 10 | [8 empty] | 0.051 | [14 empty] | 0.028 | 1 | 0.19 |  | 0.05 | 0.016 | 1 | 0.16 |  | 0.029 | 1 | 0.22 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.044 | [9 empty] | 6.22 | 0.466 | 4 | 0.48 | 15.4 | 9 | 0.47377 |  | 6.21 | 0.405 | 4 | 0.44 | 15.4 | 9 | 0.47377 | 6.19 | 0.419 | 4 | 0.45 | 16.4 | 10 | 0.49037 |  |  |  | 0.011 | [9 empty] | 7.44 | 0.064 | 1 | 4 | 14.5 | 22 | 43 | 0.014 | 7.48 | 0.06 | 2 | 3.8 | 15.1 | 23 | 45 | 0.014 | 4 | 3.9 | 2.8 | [55 empty] | 21:00 | 0.48 | 9 | 28.2667 | 13.568 | 6.22 | 15.4 | 10 | 1.3568 | 15 | 6.5 | 0.35377 | 21:00 | 0.44 | 9 | 28.2667 | 12.4373 | 6.21 | 15.4 | 10 | 1.2437 | 15 | 6.5 | 0.35377 | 21:00 | 0.45 | 10 | 27 | 12.15 | 6.19 | 16.4 | 10 | 1.215 | 15 | 6.5 | 0.37037
22:00 | [72 empty] | DOSE |  | TOTAL | 35.2 | 35.2 | 39.2 | 109.6 | 33.2 | 33.2 | 37.2 | 103.6 | 0 | 42.5851 | 9 | 53.6198 | 96.205 | 7.8926 | TOTAL | 360.693 | 35785.6652 | 0 | 2648.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3389 | 5.5484 | 5.1144 | 1.0769 | 0.93398 | 0.95088 | 0.89938 | 0.95554 | 0.97138 | 6.0872 | 26 | 0.23902 | 0.23902 | 0.23885 | 4.3773 | 2.2021 | 0.4002 | 15.9987 | 3.0445 | 15.9507 | 4.4009 | 2.1984 | 0.41867 | 14.7845 | 2.7682 | 23.0962 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.41 | 18 | 14 | 10.5 | 127 | 172 | 15.8 | 0.51 |  | 5.99 | 10 | 0.08 | 6.04 | 12 |  | 5.98 | 12 | [8 empty] | 0.049 | [14 empty] | 0.029 | 1 | 0.22 |  | 0.051 | 0.012 | 1 | 0.21 |  | 0.027 | 1 | 0.29 | [22 empty] | AVERAGE | 8.8 | 8.8 | 9.8 | 27.4 | 8.3 | 8.3 | 9.3 | 25.9 |  | 10.6463 | 3 | 13.405 | 24.0512 | 1.9732 | AVERAGE | 90.1733 | 8946.4163 |  | 662.1145 | 0 | 0 | 0 |  |  |  | 1.3347 | 1.3871 | 1.2786 | 0.26922 | 0.23349 | 0.23772 | 0.22485 | 0.23888 | 0.24285 | 1.5218 | 6.5 | 0.059754 | 0.059754 | 0.059713 | 1.0943 | 0.55053 | 0.10005 | 3.9997 | 0.76112 | 3.9877 | 1.1002 | 0.5496 | 0.10467 | 3.6961 | 0.69204 | 5.774 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.33 | 87 | 84 | 67.5 | 751 | 1061 | 246.9 | 3.061 | 0.09 | 36.42 | 57 | 0.586 | 36.36 | 59 | 0 | 36.19 | 61 | 0 | 24.71 | 1.494 | 18 | 2.02 | 61.7 | 35.4 | 1.8715 | 0.298 | 24.72 | 1.366 | 16 | 1.82 | 63.6 | 35.2 | 1.8636 | 24.7 | 1.315 | 14 | 1.89 | 66.8 | 39.8 | 1.9541 | 0.178 | 6 | 1.54 | 0.02 | 0.298 | 0.086 | 6 | 1.56 | 0.011 | 0.181 | 7 | 1.98 | 0.006 | 45.02 | 0.371 | 6 | 24.3 | 86.5 | 47 | 95 | 0.028 | 44.68 | 0.366 | 7 | 24.1 | 93.3 | 46 | 100 | 0.026 | 24.2 | 22.9 | 17.4 |  |  | MINIMUM | 8.6 | 8.6 | 9.6 | 26.8 | 8.1 | 8.1 | 9.1 | 25.3 |  | 10.3565 | 3 | 12.7066 | 23.063 | 1.9094 | MINIMUM | 89.9406 | 8854.1852 |  | 650.2203 | [6 empty] | 1.3079 | 1.3079 | 1.1984 | 0.26799 | 0.21974 | 0.23664 | 0.21974 | 0.22819 | 0.22819 | 1.5218 | 6 | 0.059585 | 0.059585 | 0.058867 | 1.0818 | 0.55031 | 0.098108 | 3.9962 | 0.75135 | 3.7073 | 1.0647 | 0.54709 | 0.095266 | 3.6513 | 0.64825 | 4.9142 |  | MIN | 0.46 | 8.9 | 28.5843 | 13.1488 | 6.12 | 15.2 | 10 | 1.3149 |  |  |  | MIN | 0.43 | 9 | 28.2667 | 12.1547 | 6.11 | 16.3 | 10 | 1.2155 |  |  |  | MIN | 0.41 | 10.1 | 26.7327 | 10.9604 | 6.12 | 16.6 | 10 | 1.096 |  |  |  | 1.096
AVERAGE | 6.3883 | 14.5 | 14 | 11.25 | 125.1667 | 176.8333 | 41.15 | 0.51017 | 0.045 | 6.07 | 9.5 | 0.097667 | 6.06 | 9.8333 |  | 6.0317 | 10.1667 |  | 6.1775 | 0.3735 | 4.5 | 0.505 | 15.425 | 8.85 | 0.46788 | 0.049667 | 6.18 | 0.3415 | 4 | 0.455 | 15.9 | 8.8 | 0.46591 | 6.175 | 0.32875 | 3.5 | 0.4725 | 16.7 | 9.95 | 0.48852 | 0.029667 | 1 | 0.25667 | 0.01 | 0.049667 | 0.014333 | 1 | 0.26 | 0.011 | 0.030167 | 1.1667 | 0.33 |  | 7.5033 | 0.061833 | 1 | 4.05 | 14.4167 | 23.5 | 47.5 | 0.014 | 7.4467 | 0.061 | 1.1667 | 4.0167 | 15.55 | 23 | 50 | 0.013 | 4.0333 | 3.8167 | 2.9 |  |  | MAXIMUM | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 11.4898 | 3 | 13.7635 | 25.2533 | 1.9944 | MAXIMUM | 90.3186 | 8977.16 |  | 697.7974 | [6 empty] | 1.3616 | 1.571 | 1.4057 | 0.27044 | 0.2388 | 0.2388 | 0.22996 | 0.24958 | 0.2575 | 1.5218 | 8 | 0.059922 | 0.059922 | 0.060005 | 1.1069 | 0.55075 | 0.10199 | 4.002 | 0.77818 | 4.4625 | 1.1131 | 0.5521 | 0.12167 | 3.7352 | 0.71183 | 7.9856
MINIMUM | 6.36 | 12 | 13 | 10.3 | 120 | 170 | 15.8 | 0.491 | 0.044 | 5.99 | 8 | 0.063 | 5.99 | 9 |  | 5.98 | 9 |  | 6.1 | 0.278 | 4 | 0.46 | 15.2 | 8.6 | 0.45805 | 0.048 | 6.11 | 0.239 | 3 | 0.43 | 15.4 | 8.6 | 0.45805 | 6.12 | 0.282 | 3 | 0.41 | 16.4 | 9.6 | 0.47556 | 0.028 | 1 | 0.19 | 0.009 | 0.047 | 0.012 | 1 | 0.16 | 0.011 | 0.027 | 1 | 0.22 |  | 7.36 | 0.055 | 1 | 3.8 | 14.1 | 22 | 43 | 0.014 | 7.34 | 0.058 | 1 | 3.8 | 15.1 | 23 | 45 | 0.012 | 4 | 3.7 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 40420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 1036 | 1070 | 2492 | 2160 | 2200 | 2080 | 2460 | 2500 | 3200 | 0 | 3760 | 3760 | 4210 | 316 | 422 | 46 | 5420 | 1108 | 908 | 178 | 236 | 27 | 2772 | 564 | 738
MAXIMUM | 6.42 | 18 | 15 | 12.8 | 130 | 190 | 166 | 0.539 | 0.046 | 6.22 | 10 | 0.172 | 6.17 | 12 |  | 6.08 | 12 |  | 6.27 | 0.466 | 5 | 0.58 | 15.6 | 9 | 0.47377 | 0.051 | 6.24 | 0.405 | 5 | 0.5 | 16.3 | 9 | 0.47377 | 6.24 | 0.419 | 4 | 0.52 | 17 | 10.1 | 0.49407 | 0.033 | 1 | 0.33 | 0.011 | 0.052 | 0.016 | 1 | 0.37 | 0.011 | 0.034 | 2 | 0.45 |  | 7.6 | 0.069 | 1 | 4.3 | 14.7 | 25 | 52 | 0.014 | 7.49 | 0.064 | 2 | 4.3 | 16.4 | 23 | 55 | 0.014 | 4.1 | 3.9 | 3.6 | [17 empty] | AVERAGE | 10105 | [9 empty] | 249 | 259 | 267.5 | 623 | 540 | 550 | 520 | 615 | 625 | 800 |  | 940 | 940 | 1052.5 | 79 | 105.5 | 11.5 | 1355 | 277 | 227 | 44.5 | 59 | 6.75 | 693 | 141 | 184.5
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0539 |  | TOTAL AVG COAG ALK: |  |  |  | 9.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.466 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.41 | [5 empty] | 6.1775 |  |  |  |  | 0.034 |  |  |  |  | 0.41 | [6 empty] | 0.034 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 9900 | [9 empty] | 238 | 238 | 245 | 606 | 520 | 540 | 520 | 600 | 600 | 800 |  | 920 | 920 | 1035 | 78 | 103 | 11 | 1320 | 269 | 216 | 44 | 58 | 6 | 680 | 135 | 159
[90 empty] | MAXIMUM | 10320 | [9 empty] | 260 | 300 | 300 | 640 | 560 | 560 | 520 | 630 | 650 | 800 |  | 960 | 960 | 1080 | 80 | 108 | 12 | 1410 | 290 | 260 | 46 | 60 | 8 | 700 | 145 | 260
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.904 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827080 |  | END: | 23827081 |  |  | Alum | 6957 | 10934 | 10934 | 9747 | 9747 | 0 | [44 empty] | 0.41 | 10.1 | 26.7327 | 10.9604 | 6.12 | 16.6 | 10 | 1.096
[73 empty] | FINISHED 2 | 13.861 |  | TOTAL MGD: |  | 13.903 |  |  | FINISHED SOUTH 2 |  | START: | 43920760 |  | END: | 43934663 |  |  | Caustic | 8015 | 6367 | 6367
[73 empty] | TOTAL RAW | 29.769 |  | TOTAL MGD: |  | 5.796 |  |  | FINISHED CONWAY |  | START: | 10258694 |  | END: | 10264490 |  |  | Hypochlorite | 18 |  | 48
[76 empty] | TOTAL MGD: |  | 8.065 |  |  | FINISHED PERRY |  | START: | 33898555 |  | END: | 33906620 |  |  | Phosphate | 2382
[76 empty] | TOTAL MGD: |  | 9.579 |  |  | RAW PLANT 1 |  | START: | 31023174 |  | END: | 31032753 |  |  | Fluoride | 3500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.341 |  |  | RAW PLANT 2 |  | START: | 30981557 |  | END: | 30990898 |  |  | Cal~Flo | 10.95 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.849 |  |  | RAW PLANT 3 |  | START: | 7563854 |  | END: | 7574703 |  |  | Zinc | 1005
[76 empty] | TOTAL MGD: |  | 0.96 |  |  | DECANT |  | START: | 1870046 |  | END: | 1871006 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 2.175 |  |  | BLOW DOWN |  | START: | 9143.0358 |  | END: | 9145.2108 |  |  | NH3 | 13.53 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827081
43934663
10264490
33906620
31032753
30990898
7574703
1871006
9145.2108
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 10
DATE: | 2019-01-10 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-10 | [23 empty] | DATE: | 2019-01-10
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-10 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43475.0125 | 2,3,5 | 38 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 11.4898 | 1,3 | 13.7635 | 25.2533 | 1.9094 | 43475.0125 | 89.9406 | 8854.1852 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3616 | 1.571 | 1.4057 | 0.27044 | 0.23664 | 0.23664 | 0.21974 | 0.22819 | 0.22819 | 1.5218 | 6 | 0.059585 | 0.059585 | 0.059977 | 1.0818 | 0.55031 | 0.10199 | 3.9986 | 0.77818 | 3.7073 | 1.0647 | 0.54709 | 0.10646 | 3.6513 | 0.69627 | 4.9142 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.338 | 4 | 0.5 | 15.5 | 9 | 0.47377 |  | 6.1 | 0.325 | 4 | 0.48 | 16 | 9 | 0.47377 | 6.11 | 0.44 | 4 | 0.47 | 16.5 | 10 | 0.49037 | [13 empty] | 7.38 | 0.058 | 1 | 4.2 | 14 |  |  |  | 7.4 | 0.057 | 1 | 3.8 | 16 |  |  |  | 3.8 | 3.9 | 2.9 | [18 empty] | 10300 | [6 empty] | 0 | 0 | 0 | 260 | 300 | 300 | 640 | 560 | 560 | 520 | 600 | 600 | 800 |  | 960 | 960 | 1080 | 80 | 108 | 12 | 1410 | 290 | 216 | 44 | 60 | 7 | 700 | 145 | 160 |  | 1:00 | 0.5 | 9 | 28.2667 | 14.1333 | 6.14 | 15.5 | 10 | 1.4133 | 15 | 6.5 | 0.35377 | 1:00 | 0.48 | 9 | 28.2667 | 13.568 | 6.1 | 16 | 10 | 1.3568 | 15 | 6.5 | 0.35377 | 1:00 | 0.47 | 10 | 27 | 12.69 | 6.11 | 16.5 | 10 | 1.269 | 15 | 6.5 | 0.37037
2:00 | [72 empty] | 43475.3202 | 2,3,5 | 38 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 11.4898 | 1,3 | 13.7635 | 25.2533 | 1.9094 | 43475.3202 | 89.9406 | 8854.1852 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3616 | 1.571 | 1.4057 | 0.27044 | 0.23664 | 0.23664 | 0.21974 | 0.22819 | 0.22819 | 1.5218 | 6 | 0.059585 | 0.059585 | 0.059977 | 1.0818 | 0.55031 | 0.10199 | 3.9986 | 0.77818 | 3.7073 | 1.0647 | 0.54709 | 0.10646 | 3.6513 | 0.69627 | 4.9142 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.35 | 16 | 14 | 9.7 | 125 | 170 | 16.5 | 0.484 |  | 6.06 | 10 | 0.065 | 6.01 | 11 |  | 6 | 10 | [8 empty] | 0.046 | [14 empty] | 0.026 | 1 | 0.2 |  | 0.049 | 0.013 | 1 | 0.2 |  | 0.033 | 1 | 0.25 | [38 empty] | 10300 | [6 empty] | 0 | 0 | 0 | 260 | 300 | 300 | 640 | 560 | 560 | 520 | 600 | 600 | 800 |  | 960 | 960 | 1080 | 80 | 108 | 12 | 1410 | 290 | 216 | 44 | 60 | 7 | 700 | 145 | 160 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43475.8268 | 2,3,5 | 38 | 8.5 | 8.5 | 9.5 | 26.5 | 8 | 8 | 9 | 25 | ,1,3 | 11.4898 | 1,3 | 13.7635 | 25.2533 | 2.3659 | 43475.8268 | 89.9571 | 8423.7734 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.391 | 1.3601 | 0.2774 | 0.24608 | 0.24608 | 0.22371 | 0.2402 | 0.2402 | 1.5218 | 3 | 0.060671 | 0.060671 | 0.059792 | 1.1207 | 0.55222 | 0.10837 | 3.9764 | 0.76409 | 3.6473 | 1.1239 | 0.55824 | 0.096324 | 3.7153 | 0.67919 | 4.7009 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.45 | 0.055 | 1 | 4.2 | 14 |  |  |  | 7.35 | 0.052 | 1 | 4 | 16 |  |  |  | 3.9 | 3.8 | 3.5 | [18 empty] | 9750 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 275 | 620 | 550 | 550 | 500 | 600 | 600 | 800 |  | 920 | 920 | 1020 | 78 | 102 | 12 | 1300 | 268 | 200 | 44 | 58 | 6 | 660 | 134 | 145 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.38 | 12 | 14 | 11.1 | 125 | 174 | 15.4 | 0.502 |  | 6.08 | 10 | 0.077 | 6.04 | 9 |  | 6 | 9 | [8 empty] | 0.05 | [14 empty] | 0.022 | 1 | 0.21 |  | 0.05 | 0.013 | 1 | 0.22 |  | 0.031 | 1 | 0.29 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.031 | [9 empty] | 6.08 | 0.456 | 5 | 0.56 | 14.8 | 8.9 | 0.64476 |  | 6.11 | 0.488 | 5 | 0.54 | 14.9 | 9 | 0.65066 | 6.12 | 0.398 | 4 | 0.52 | 15.9 | 10.1 | 0.49407 |  |  |  | 0.012 | [9 empty] | 7.38 | 0.051 | 1 | 3.7 | 13.6 | 20 | 50 | 0.01 | 7.93 | 0.073 | 1 | 4.8 | 15.2 | 20 | 48 | 0.009 | 3.8 | 3.8 | 3.4 | [55 empty] | 9:00 | 0.56 | 8.9 | 28.5843 | 16.0072 | 6.08 | 14.8 | 15 | 1.0671 | 10 | 6.5 | 0.52476 | 9:00 | 0.54 | 9 | 28.2667 | 15.264 | 6.11 | 14.9 | 15 | 1.0176 | 10 | 6.5 | 0.53066 | 9:00 | 0.52 | 10.1 | 26.7327 | 13.901 | 6.12 | 15.9 | 10 | 1.3901 | 15 | 6.5 | 0.37407
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.44 | 12 | 13 | 10.1 | 123 | 173 | 15.7 | 0.497 |  | 6.03 | 9 | 0.069 | 6.02 | 9 |  | 6.01 | 10 | [8 empty] | 0.051 | [14 empty] | 0.027 | 1 | 0.23 |  | 0.044 | 0.013 | 1 | 0.31 |  | 0.033 | 1 | 0.37 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.06 | 0.31 | 4 | 0.55 | 14.9 | 8.9 | 0.64476 |  | 6.08 | 0.288 | 4 | 0.56 | 15.1 | 9 | 0.47377 | 6.11 | 0.383 | 4 | 0.51 | 16.1 | 10.1 | 0.49407 | [13 empty] | 7.73 | 0.052 | 1 | 4.2 | 13.5 |  |  |  | 7.58 | 0.069 | 1 | 4.3 | 15.6 |  |  |  | 3.9 | 4.2 | 2.7 | [55 empty] | 13:00 | 0.55 | 8.9 | 28.5843 | 15.7213 | 6.06 | 14.9 | 15 | 1.0481 | 10 | 6.5 | 0.52476 | 13:00 | 0.56 | 9 | 28.2667 | 15.8293 | 6.08 | 15.1 | 10 | 1.5829 | 15 | 6.5 | 0.35377 | 13:00 | 0.51 | 10.1 | 26.7327 | 13.6337 | 6.11 | 16.1 | 10 | 1.3634 | 15 | 6.5 | 0.37407
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.43 | 14 | 14 | 9.68 | 124 | 170 | 15.6 | 0.516 |  | 6.1 | 10 | 0.083 | 6.12 | 10 |  | 6.04 | 9 | [8 empty] | 0.052 | [14 empty] | 0.027 | 1 | 0.25 |  | 0.044 | 0.012 | 1 | 0.38 |  | 0.03 | 1 | 0.42 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.92 | 0.054 | 1 | 4.5 | 13.6 |  |  |  | 7.67 | 0.053 | 1 | 4.4 | 15.5 |  |  |  | 4 | 4 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.43 | 20 | 14 | 10.1 | 122 | 171 | 15.2 | 0.504 |  | 6.05 | 10 | 0.078 | 6.04 | 10 |  | 5.98 | 10 | [8 empty] | 0.052 | [14 empty] | 0.029 | 1 | 0.34 |  | 0.051 | 0.013 | 1 | 0.39 |  | 0.03 | 1 | 0.4 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.036 | [9 empty] | 6.15 | 0.308 | 3 | 0.6 | 14.7 | 8.5 | 0.62118 |  | 6.19 | 0.288 | 3 | 0.7 | 14.7 | 8.5 | 0.62118 | 6.19 | 0.306 | 3 | 0.59 | 15.9 | 9.5 | 0.47185 |  |  |  | 0.014 | [9 empty] | 7.52 | 0.064 | 1 | 4.6 | 13.8 | 21 | 49 | 0.008 | 7.46 | 0.06 | 1 | 4.3 | 14.5 | 20 | 46 | 0.011 | 4.2 | 4.2 | 2.9 | [55 empty] | 21:00 | 0.6 | 8.5 | 29.9294 | 17.9576 | 6.15 | 14.7 | 15 | 1.1972 | 10 | 6.5 | 0.50118 | 21:00 | 0.7 | 8.5 | 29.9294 | 20.9506 | 6.19 | 14.7 | 15 | 1.3967 | 10 | 6.5 | 0.50118 | 21:00 | 0.59 | 9.5 | 28.4211 | 16.7684 | 6.19 | 15.9 | 10 | 1.6768 | 15 | 6.5 | 0.35185
22:00 | [72 empty] | DOSE |  | TOTAL | 26.5 | 26.5 | 29.5 | 82.5 | 25 | 25 | 28 | 78 | 0 | 34.4693 | 0 | 41.2906 | 75.7598 | 6.1848 | TOTAL | 269.8383 | 26132.1438 | 0 | 2061.674 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1141 | 4.5331 | 4.1714 | 0.81829 | 0.71936 | 0.71936 | 0.66319 | 0.69657 | 0.69657 | 4.5654 | 15 | 0.17984 | 0.17984 | 0.17975 | 3.2843 | 1.6528 | 0.31235 | 11.9735 | 2.3204 | 11.062 | 3.2533 | 1.6524 | 0.30925 | 11.0178 | 2.0717 | 14.5294 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.43 | 16 | 14 | 9.94 | 125 | 173 | 14.9 | 0.512 |  | 6.06 | 10 | 0.074 | 6.07 | 10 |  | 5.99 | 10 | [8 empty] | 0.05 | [14 empty] | 0.026 | 1 | 0.4 |  | 0.05 | 0.01 | 1 | 0.28 |  | 0.024 | 1 | 0.3 | [22 empty] | AVERAGE | 8.8333 | 8.8333 | 9.8333 | 27.5 | 8.3333 | 8.3333 | 9.3333 | 26 |  | 11.4898 |  | 13.7635 | 25.2533 | 2.0616 | AVERAGE | 89.9461 | 8710.7146 |  | 687.2247 | 0 | 0 | 0 |  |  |  | 1.3714 | 1.511 | 1.3905 | 0.27276 | 0.23979 | 0.23979 | 0.22106 | 0.23219 | 0.23219 | 1.5218 | 5 | 0.059947 | 0.059947 | 0.059916 | 1.0948 | 0.55095 | 0.10412 | 3.9912 | 0.77348 | 3.6873 | 1.0844 | 0.55081 | 0.10308 | 3.6726 | 0.69057 | 4.8431 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.46 | 90 | 83 | 60.62 | 744 | 1031 | 93.3 | 3.015 | 0.067 | 36.38 | 59 | 0.446 | 36.3 | 59 | 0 | 36.02 | 58 | 0 | 24.43 | 1.412 | 16 | 2.21 | 59.9 | 35.3 | 2.3845 | 0.301 | 24.48 | 1.389 | 16 | 2.28 | 60.7 | 35.5 | 2.2194 | 24.53 | 1.527 | 15 | 2.09 | 64.4 | 39.7 | 1.9504 | 0.157 | 6 | 1.63 | 0.026 | 0.288 | 0.074 | 6 | 1.78 | 0 | 0.181 | 6 | 2.03 | 0 | 45.38 | 0.334 | 6 | 25.4 | 82.5 | 41 | 99 | 0.018 | 45.39 | 0.364 | 6 | 25.6 | 92.8 | 40 | 94 | 0.02 | 23.6 | 23.9 | 18.1 |  |  | MINIMUM | 8.5 | 8.5 | 9.5 | 26.5 | 8 | 8 | 9 | 25 |  | 11.4898 |  | 13.7635 | 25.2533 | 1.9094 | MINIMUM | 89.9406 | 8423.7734 |  | 666.0793 | [6 empty] | 1.3616 | 1.391 | 1.3601 | 0.27044 | 0.23664 | 0.23664 | 0.21974 | 0.22819 | 0.22819 | 1.5218 | 3 | 0.059585 | 0.059585 | 0.059792 | 1.0818 | 0.55031 | 0.10199 | 3.9764 | 0.76409 | 3.6473 | 1.0647 | 0.54709 | 0.096324 | 3.6513 | 0.67919 | 4.7009 |  | MIN | 0.55 | 8.9 | 28.5843 | 15.7213 | 6.06 | 14.9 | 15 | 1.0481 |  |  |  | MIN | 0.54 | 9 | 28.2667 | 15.264 | 6.11 | 14.9 | 15 | 1.0176 |  |  |  | MIN | 0.47 | 10 | 27 | 12.69 | 6.11 | 16.5 | 10 | 1.269 |  |  |  | 1.0176
AVERAGE | 6.41 | 15 | 13.8333 | 10.1033 | 124 | 171.8333 | 15.55 | 0.5025 | 0.0335 | 6.0633 | 9.8333 | 0.074333 | 6.05 | 9.8333 |  | 6.0033 | 9.6667 |  | 6.1075 | 0.353 | 4 | 0.5525 | 14.975 | 8.825 | 0.59612 | 0.050167 | 6.12 | 0.34725 | 4 | 0.57 | 15.175 | 8.875 | 0.55485 | 6.1325 | 0.38175 | 3.75 | 0.5225 | 16.1 | 9.925 | 0.48759 | 0.026167 | 1 | 0.27167 | 0.013 | 0.048 | 0.012333 | 1 | 0.29667 |  | 0.030167 | 1 | 0.33833 |  | 7.5633 | 0.055667 | 1 | 4.2333 | 13.75 | 20.5 | 49.5 | 0.009 | 7.565 | 0.060667 | 1 | 4.2667 | 15.4667 | 20 | 47 | 0.01 | 3.9333 | 3.9833 | 3.0167 |  |  | MAXIMUM | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 11.4898 |  | 13.7635 | 25.2533 | 2.3659 | MAXIMUM | 89.9571 | 8854.1852 |  | 697.7974 | [6 empty] | 1.391 | 1.571 | 1.4057 | 0.2774 | 0.24608 | 0.24608 | 0.22371 | 0.2402 | 0.2402 | 1.5218 | 6 | 0.060671 | 0.060671 | 0.059977 | 1.1207 | 0.55222 | 0.10837 | 3.9986 | 0.77818 | 3.7073 | 1.1239 | 0.55824 | 0.10646 | 3.7153 | 0.69627 | 4.9142
MINIMUM | 6.35 | 12 | 13 | 9.68 | 122 | 170 | 14.9 | 0.484 | 0.031 | 6.03 | 9 | 0.065 | 6.01 | 9 |  | 5.98 | 9 |  | 6.06 | 0.308 | 3 | 0.5 | 14.7 | 8.5 | 0.47377 | 0.046 | 6.08 | 0.288 | 3 | 0.48 | 14.7 | 8.5 | 0.47377 | 6.11 | 0.306 | 3 | 0.47 | 15.9 | 9.5 | 0.47185 | 0.022 | 1 | 0.2 | 0.012 | 0.044 | 0.01 | 1 | 0.2 |  | 0.024 | 1 | 0.25 |  | 7.38 | 0.051 | 1 | 3.7 | 13.5 | 20 | 49 | 0.008 | 7.35 | 0.052 | 1 | 3.8 | 14.5 | 20 | 46 | 0.009 | 3.8 | 3.8 | 2.7 | [15 empty] | MIL/MIN |  | TOTAL | 30350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 850 | 875 | 1900 | 1670 | 1670 | 1540 | 1800 | 1800 | 2400 | 0 | 2840 | 2840 | 3180 | 238 | 318 | 36 | 4120 | 848 | 632 | 132 | 178 | 20 | 2060 | 424 | 465
MAXIMUM | 6.44 | 20 | 14 | 11.1 | 125 | 174 | 16.5 | 0.516 | 0.036 | 6.1 | 10 | 0.083 | 6.12 | 11 |  | 6.04 | 10 |  | 6.15 | 0.456 | 5 | 0.6 | 15.5 | 9 | 0.64476 | 0.052 | 6.19 | 0.488 | 5 | 0.7 | 16 | 9 | 0.65066 | 6.19 | 0.44 | 4 | 0.59 | 16.5 | 10.1 | 0.49407 | 0.029 | 1 | 0.4 | 0.014 | 0.051 | 0.013 | 1 | 0.39 |  | 0.033 | 1 | 0.42 |  | 7.92 | 0.064 | 1 | 4.6 | 14 | 21 | 50 | 0.01 | 7.93 | 0.073 | 1 | 4.8 | 16 | 20 | 48 | 0.011 | 4.2 | 4.2 | 3.5 | [17 empty] | AVERAGE | 10116.6667 | [9 empty] | 256.6667 | 283.3333 | 291.6667 | 633.3333 | 556.6667 | 556.6667 | 513.3333 | 600 | 600 | 800 |  | 946.6667 | 946.6667 | 1060 | 79.3333 | 106 | 12 | 1373.3333 | 282.6667 | 210.6667 | 44 | 59.3333 | 6.6667 | 686.6667 | 141.3333 | 155
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0389 |  | TOTAL AVG COAG ALK: |  |  |  | 9.7778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.488 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.47 | [5 empty] | 6.12 |  |  |  |  | 0.033 |  |  |  |  | 0.47 | [6 empty] | 0.033 | [16 empty] | Pump Station MIN |  | 2.7 | [17 empty] | MINIMUM | 9750 | [9 empty] | 250 | 250 | 275 | 620 | 550 | 550 | 500 | 600 | 600 | 800 |  | 920 | 920 | 1020 | 78 | 102 | 12 | 1300 | 268 | 200 | 44 | 58 | 6 | 660 | 134 | 145
[90 empty] | MAXIMUM | 10300 | [9 empty] | 260 | 300 | 300 | 640 | 560 | 560 | 520 | 600 | 600 | 800 |  | 960 | 960 | 1080 | 80 | 108 | 12 | 1410 | 290 | 216 | 44 | 60 | 7 | 700 | 145 | 160
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.073 |  | TOTAL MGD: |  | 0.006 |  |  | FINISHED SOUTH 1 |  | START: | 23827081 |  | END: | 23827087 |  |  | Alum | 5233 | 10937 | 10937 | 11151 | 11151 | 0 | [44 empty] | 0.54 | 9 | 28.2667 | 15.264 | 6.11 | 14.9 | 15 | 1.0176
[73 empty] | FINISHED 2 | 10.9 |  | TOTAL MGD: |  | 11.067 |  |  | FINISHED SOUTH 2 |  | START: | 43934663 |  | END: | 43945730 |  |  | Caustic | 7982 | 6372 | 6372
[73 empty] | TOTAL RAW | 25.72 |  | TOTAL MGD: |  | 4.67 |  |  | FINISHED CONWAY |  | START: | 10264490 |  | END: | 10269160 |  |  | Hypochlorite | 17 |  | 47
[76 empty] | TOTAL MGD: |  | 6.23 |  |  | FINISHED PERRY |  | START: | 33906620 |  | END: | 33912850 |  |  | Phosphate | 2354
[76 empty] | TOTAL MGD: |  | 8.211 |  |  | RAW PLANT 1 |  | START: | 31032753 |  | END: | 31040964 |  |  | Fluoride | 3500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.262 |  |  | RAW PLANT 2 |  | START: | 30990898 |  | END: | 30999160 |  |  | Cal~Flo | 14.6 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.247 |  |  | RAW PLANT 3 |  | START: | 7574703 |  | END: | 7583950 |  |  | Zinc | 962
[76 empty] | TOTAL MGD: |  | 0.884 |  |  | DECANT |  | START: | 1871006 |  | END: | 1871890 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.3944 |  |  | BLOW DOWN |  | START: | 9145.2108 |  | END: | 9146.6051 |  |  | NH3 | 13 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827087
43945730
10269160
33912850
31040964
30999160
7583950
1871890
9146.6051
1 | 1,5,6 |  |  | 28 | 8.8 | 8 |  | 9.6 |  | 26.4 | 8.3 | 7.5 | 9.1 | 24.9 | 7 | 19.4256 | 0 | 0.02772 | 19.4533 | 1 | 0 | 1900 | 650 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | [5 empty] | 0 | 0 |  | 0 | 0.3 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.4 | #DIV/0! | 0
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 11
DATE: | 2019-01-11 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-11 | [23 empty] | DATE: | 2019-01-11
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-11 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43476.01 | 2,3,5 | 38 | 8.5 | 8.5 | 9.5 | 26.5 | 8 | 8 | 9 | 25 | ,1,3 | 11.4898 | 1,3 | 13.7635 | 25.2533 | 2.3659 | 43476.01 | 89.9571 | 8423.7734 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.391 | 1.391 | 1.3601 | 0.2774 | 0.24608 | 0.24608 | 0.22371 | 0.2402 | 0.2402 | 1.5218 | 3 | 0.060671 | 0.060671 | 0.059792 | 1.1207 | 0.55222 | 0.10837 | 3.9764 | 0.76409 | 3.6473 | 1.1239 | 0.55824 | 0.096324 | 3.7153 | 0.67919 | 4.7009 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.15 | 0.31 | 3 | 0.55 | 15 | 8.5 | 0.45412 |  | 6.13 | 0.295 | 3 | 0.68 | 15 | 8.5 | 0.45412 | 6.17 | 0.34 | 3 | 0.55 | 16 | 9.5 | 0.47185 | [13 empty] | 7.36 | 0.058 | 1 | 4.2 | 13 |  |  |  | 7.26 | 0.055 | 1 | 4.2 | 15 |  |  |  | 4.3 | 4.3 | 2.8 | [18 empty] | 9750 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 275 | 620 | 550 | 550 | 500 | 600 | 600 | 800 |  | 920 | 920 | 1020 | 78 | 102 | 12 | 1300 | 268 | 200 | 44 | 58 | 6 | 660 | 134 | 145 |  | 1:00 | 0.55 | 8.5 | 29.9294 | 16.4612 | 6.15 | 15 | 10 | 1.6461 | 15 | 6.5 | 0.33412 | 1:00 | 0.68 | 8.5 | 29.9294 | 20.352 | 6.13 | 15 | 10 | 2.0352 | 15 | 6.5 | 0.33412 | 1:00 | 0.55 | 9.5 | 28.4211 | 15.6316 | 6.17 | 16 | 10 | 1.5632 | 15 | 6.5 | 0.35185
2:00 | [72 empty] | 43476.4426 | 2,3,5 | 35 | 7.7 | 7.7 | 8.7 | 24.1 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 6.1603 | 1,3 | 14.5181 | 20.6784 | 2.3659 | 43476.4426 | 90.495 | 7747.412 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.6074 | 1.5199 | 0.30623 | 0.26671 | 0.21732 | 0.25683 | 0.26228 | 0.2448 | 1.5218 | 6 | 0.060452 | 0.060818 | 0.060478 | 1.1175 | 0.54741 | 0.10034 | 3.9814 | 0.74445 | 3.6473 | 1.1214 | 0.52819 | 0.10572 | 3.6666 | 0.66757 | 4.4479 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.43 | 22 | 16 | 9.71 | 122 | 172 | 15.5 | 0.48 |  | 6.05 | 10 | 0.061 | 6.02 | 11 |  | 6 | 11 | [8 empty] | 0.042 | [14 empty] | 0.027 | 1 | 0.3 |  | 0.042 | 0.013 | 1 | 0.25 |  | 0.028 | 1 | 0.28 | [38 empty] | 8920 | [6 empty] | 0 | 0 | 0 | 240 | 260 | 280 | 620 | 540 | 440 | 520 | 600 | 560 | 800 |  | 825 | 830 | 940 | 70 | 91 | 10 | 1140 | 235 | 180 | 40 | 50 | 6 | 580 | 120 | 125 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43476.808 | 2,3,5 | 35 | 9 | 5 | 10 | 24 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 6.1603 | 1,3 | 14.5181 | 20.6784 | 2.2435 | 43476.808 | 90.057 | 7378.4876 | 0 | 602.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.2983 | 1.3028 | 0.26199 | 0.24509 | 0.25101 |  | 0.11409 | 0.20917 | 1.5218 | 1.5 | 0.069611 | 0.069611 | 0.069486 | 1.1175 | 0.54139 | 0.10034 | 3.9731 | 0.74762 | 3.6473 | 1.1214 | 0.54931 | 0.10572 | 3.4497 | 0.63419 | 4.4479 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.28 | 0.054 | 1 | 4.4 | 13 |  |  |  | 7.3 | 0.052 | 1 | 4.2 | 15 |  |  |  | 4.3 | 4.2 | 3.8 | [18 empty] | 8840 | [6 empty] | 0 | 0 | 0 | 240 | 210 | 240 | 620 | 580 | 660 |  | 600 | 550 | 800 |  | 950 | 950 | 1080 | 70 | 90 | 10 | 1150 | 236 | 180 | 40 | 52 | 6 | 550 | 114 | 125 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.51 | 14 | 15 | 9.99 | 127 | 171 | 15.1 | 0.495 |  | 6.08 | 9 | 0.07 | 6.07 | 10 |  | 6.02 | 10 | [8 empty] | 0.052 | [14 empty] | 0.027 | 1 | 0.35 |  | 0.052 | 0.012 | 1 | 0.39 |  | 0.027 | 1 | 0.44 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.03 | [9 empty] | 6.16 | 0.287 | 3 | 0.65 | 14.4 | 8.5 | 0.62118 |  | 6.17 | 0.298 | 3 | 0.73 | 14.5 | 8.5 | 0.62118 | 6.07 | 0.285 | 3 | 0.65 | 15.6 | 9.5 | 0.47185 |  |  |  | 0.015 | [9 empty] | 7.47 | 0.058 | 1 | 4.5 | 12.5 | 24 | 53 | 0.013 | 7.46 | 0.056 | 1 | 4.7 | 14.7 | 25 | 51 | 0.011 | 4.3 | 4.1 | 3.5 | [55 empty] | 9:00 | 0.65 | 8.5 | 29.9294 | 19.4541 | 6.16 | 14.4 | 15 | 1.2969 | 10 | 6.5 | 0.50118 | 9:00 | 0.73 | 8.5 | 29.9294 | 21.8485 | 6.17 | 14.5 | 15 | 1.4566 | 10 | 6.5 | 0.50118 | 9:00 | 0.65 | 9.5 | 28.4211 | 18.4737 | 6.07 | 15.6 | 10 | 1.8474 | 15 | 6.5 | 0.35185
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.45 | 13 | 14 | 10 | 128 | 172 | 14.5 | 0.515 |  | 6.15 | 10 | 0.086 | 6.13 | 8 |  | 6.03 | 9 | [8 empty] | 0.051 | [14 empty] | 0.023 | 1 | 0.31 |  | 0.052 | 0.011 | 1 | 0.21 |  | 0.028 | 1 | 0.39 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.24 | 0.264 | 4 | 0.59 | 14.5 | 9.6 | 0.68604 |  | 6.2 | 0.248 | 3 | 0.72 | 14.6 | 4.2 | 0.36764 | 6.23 | 0.245 | 3 | 0.59 | 15.3 | 10.7 | 0.5163 | [13 empty] | 7.2 | 0.055 | 1 | 4.2 | 12.6 |  |  |  | 7.25 | 0.054 | 1 | 3.6 | 14.7 |  |  |  | 4.3 | 4.1 | 2.8 | [55 empty] | 13:00 | 0.59 | 9.6 | 26.5 | 15.635 | 6.24 | 14.5 | 15 | 1.0423 | 10 | 6.5 | 0.56604 | 13:00 | 0.72 | 4.2 | 60.5714 | 43.6114 | 6.2 | 14.6 | 15 | 2.9074 | 10 | 6.5 | 0.24764 | 13:00 | 0.59 | 10.7 | 25.2336 | 14.8879 | 6.23 | 15.3 | 10 | 1.4888 | 15 | 6.5 | 0.3963
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.42 | 12 | 15 | 10.2 | 128 | 176 | 14.7 | 0.514 |  | 5.88 | 7 | 0.079 | 5.93 | 7 |  | 5.95 | 8 | [8 empty] | 0.047 | [14 empty] | 0.026 | 1 | 0.29 |  | 0.046 | 0.009 | 1 | 0.21 |  | 0.026 | 1 | 0.26 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.21 | 0.052 | 1 | 4.2 | 12.5 |  |  |  | 7.17 | 0.063 | 1 | 3.7 | 14.3 |  |  |  | 4.2 | 4 | 2.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.35 | 15 | 15 | 10.2 | 123 | 170 | 14.3 | 0.509 |  | 5.93 | 9 | 0.073 | 5.95 | 9 |  | 5.89 | 9 | [8 empty] | 0.054 | [14 empty] | 0.022 | 1 | 0.21 |  | 0.048 | 0.012 | 1 | 0.69 |  | 0.024 | 1 | 0.4 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.034 | [9 empty] | 6.04 | 0.393 | 3 | 0.59 | 13.9 | 9 | 0.65066 |  | 6.11 | 0.308 | 3 | 0.89 | 13.9 | 5 | 0.41481 | 6.09 | 0.391 | 3 | 0.54 | 15.1 | 10 | 0.49037 |  |  |  | 0.015 | [9 empty] | 7.39 | 0.059 | 1 | 4.9 | 12.6 | 21 | 48 | 0.017 | 7.18 | 0.057 | 1 | 4 | 13.5 | 22 | 49 | 0.012 | 4.3 | 4.1 | 2.9 | [55 empty] | 21:00 | 0.59 | 9 | 28.2667 | 16.6773 | 6.04 | 13.9 | 15 | 1.1118 | 10 | 6.5 | 0.53066 | 21:00 | 0.89 | 5 | 50.88 | 45.2832 | 6.11 | 13.9 | 15 | 3.0189 | 10 | 6.5 | 0.29481 | 21:00 | 0.54 | 10 | 27 | 14.58 | 6.09 | 15.1 | 10 | 1.458 | 15 | 6.5 | 0.37037
22:00 | [72 empty] | DOSE |  | TOTAL | 25.2 | 21.2 | 28.2 | 74.6 | 22.4 | 22.4 | 25.4 | 70.2 | 0 | 23.8104 | 0 | 42.7997 | 66.6101 | 6.9754 | TOTAL | 270.5091 | 23549.673 | 0 | 1934.8018 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3585 | 4.2967 | 4.1829 | 0.84562 | 0.75789 | 0.71441 | 0.48055 | 0.61658 | 0.69417 | 4.5654 | 10.5 | 0.19073 | 0.1911 | 0.18976 | 3.3557 | 1.641 | 0.30904 | 11.9308 | 2.2562 | 10.9418 | 3.3667 | 1.6357 | 0.30777 | 10.8316 | 1.981 | 13.5967 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.38 | 16 | 15 | 10.3 | 127 | 177 | 13.9 | 0.52 |  | 6.09 | 10 | 0.08 | 6.07 | 10 |  | 6.02 | 10 | [8 empty] | 0.055 | [14 empty] | 0.021 | 1 | 0.3 |  | 0.05 | 0.011 | 1 | 0.51 |  | 0.024 | 1 | 0.46 | [22 empty] | AVERAGE | 8.4 | 7.0667 | 9.4 | 24.8667 | 7.4667 | 7.4667 | 8.4667 | 23.4 |  | 7.9368 |  | 14.2666 | 22.2034 | 2.3251 | AVERAGE | 90.1697 | 7849.891 |  | 644.9339 | 0 | 0 | 0 |  |  |  | 1.4528 | 1.4322 | 1.3943 | 0.28187 | 0.25263 | 0.23814 | 0.24027 | 0.20553 | 0.23139 | 1.5218 | 3.5 | 0.063578 | 0.0637 | 0.063252 | 1.1186 | 0.54701 | 0.10301 | 3.9769 | 0.75205 | 3.6473 | 1.1222 | 0.54525 | 0.10259 | 3.6105 | 0.66032 | 4.5322 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.54 | 92 | 90 | 60.4 | 755 | 1038 | 88 | 3.033 | 0.064 | 36.18 | 55 | 0.449 | 36.17 | 55 | 0 | 35.91 | 57 | 0 | 24.59 | 1.254 | 13 | 2.38 | 57.8 | 35.6 | 2.412 | 0.301 | 24.61 | 1.149 | 12 | 3.02 | 58 | 26.2 | 1.8578 | 24.56 | 1.261 | 12 | 2.33 | 62 | 39.7 | 1.9504 | 0.146 | 6 | 1.76 | 0.03 | 0.29 | 0.068 | 6 | 2.26 | 0 | 0.157 | 6 | 2.23 | 0 | 43.91 | 0.336 | 6 | 26.4 | 76.2 | 45 | 101 | 0.03 | 43.62 | 0.337 | 6 | 24.4 | 87.2 | 47 | 100 | 0.023 | 25.7 | 24.8 | 18.7 |  |  | MINIMUM | 7.7 | 5 | 8.7 | 24 | 7.2 | 7.2 | 8.2 | 22.6 |  | 6.1603 |  | 13.7635 | 20.6784 | 2.2435 | MINIMUM | 89.9571 | 7378.4876 |  | 602.6432 | [6 empty] | 1.391 | 1.2983 | 1.3028 | 0.26199 | 0.24509 | 0.21732 | 0.22371 | 0.11409 | 0.20917 | 1.5218 | 1.5 | 0.060452 | 0.060671 | 0.059792 | 1.1175 | 0.54139 | 0.10034 | 3.9731 | 0.74445 | 3.6473 | 1.1214 | 0.52819 | 0.096324 | 3.4497 | 0.63419 | 4.4479 |  | MIN | 0.59 | 9.6 | 26.5 | 15.635 | 6.24 | 14.5 | 15 | 1.0423 |  |  |  | MIN | 0.73 | 8.5 | 29.9294 | 21.8485 | 6.17 | 14.5 | 15 | 1.4566 |  |  |  | MIN | 0.54 | 10 | 27 | 14.58 | 6.09 | 15.1 | 10 | 1.458 |  |  |  | 1.0423
AVERAGE | 6.4233 | 15.3333 | 15 | 10.0667 | 125.8333 | 173 | 14.6667 | 0.5055 | 0.032 | 6.03 | 9.1667 | 0.074833 | 6.0283 | 9.1667 |  | 5.985 | 9.5 |  | 6.1475 | 0.3135 | 3.25 | 0.595 | 14.45 | 8.9 | 0.603 | 0.050167 | 6.1525 | 0.28725 | 3 | 0.755 | 14.5 | 6.55 | 0.46444 | 6.14 | 0.31525 | 3 | 0.5825 | 15.5 | 9.925 | 0.48759 | 0.024333 | 1 | 0.29333 | 0.015 | 0.048333 | 0.011333 | 1 | 0.37667 |  | 0.026167 | 1 | 0.37167 |  | 7.3183 | 0.056 | 1 | 4.4 | 12.7 | 22.5 | 50.5 | 0.015 | 7.27 | 0.056167 | 1 | 4.0667 | 14.5333 | 23.5 | 50 | 0.0115 | 4.2833 | 4.1333 | 3.1167 |  |  | MAXIMUM | 9 | 8.5 | 10 | 26.5 | 8 | 8 | 9 | 25 |  | 11.4898 |  | 14.5181 | 25.2533 | 2.3659 | MAXIMUM | 90.495 | 8423.7734 |  | 666.0793 | [6 empty] | 1.4838 | 1.6074 | 1.5199 | 0.30623 | 0.26671 | 0.25101 | 0.25683 | 0.26228 | 0.2448 | 1.5218 | 6 | 0.069611 | 0.069611 | 0.069486 | 1.1207 | 0.55222 | 0.10837 | 3.9814 | 0.76409 | 3.6473 | 1.1239 | 0.55824 | 0.10572 | 3.7153 | 0.67919 | 4.7009
MINIMUM | 6.35 | 12 | 14 | 9.71 | 122 | 170 | 13.9 | 0.48 | 0.03 | 5.88 | 7 | 0.061 | 5.93 | 7 |  | 5.89 | 8 |  | 6.04 | 0.264 | 3 | 0.55 | 13.9 | 8.5 | 0.45412 | 0.042 | 6.11 | 0.248 | 3 | 0.68 | 13.9 | 4.2 | 0.36764 | 6.07 | 0.245 | 3 | 0.54 | 15.1 | 9.5 | 0.47185 | 0.021 | 1 | 0.21 | 0.015 | 0.042 | 0.009 | 1 | 0.21 |  | 0.024 | 1 | 0.26 |  | 7.2 | 0.052 | 1 | 4.2 | 12.5 | 21 | 48 | 0.013 | 7.17 | 0.052 | 1 | 3.6 | 13.5 | 22 | 49 | 0.011 | 4.2 | 4 | 2.8 | [15 empty] | MIL/MIN |  | TOTAL | 27510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 720 | 795 | 1860 | 1670 | 1650 | 1020 | 1800 | 1710 | 2400 | 0 | 2695 | 2700 | 3040 | 218 | 283 | 32 | 3590 | 739 | 560 | 124 | 160 | 18 | 1790 | 368 | 395
MAXIMUM | 6.51 | 22 | 16 | 10.3 | 128 | 177 | 15.5 | 0.52 | 0.034 | 6.15 | 10 | 0.086 | 6.13 | 11 |  | 6.03 | 11 |  | 6.24 | 0.393 | 4 | 0.65 | 15 | 9.6 | 0.68604 | 0.055 | 6.2 | 0.308 | 3 | 0.89 | 15 | 8.5 | 0.62118 | 6.23 | 0.391 | 3 | 0.65 | 16 | 10.7 | 0.5163 | 0.027 | 1 | 0.35 | 0.015 | 0.052 | 0.013 | 1 | 0.69 |  | 0.028 | 1 | 0.46 |  | 7.47 | 0.059 | 1 | 4.9 | 13 | 24 | 53 | 0.017 | 7.46 | 0.063 | 1 | 4.7 | 15 | 25 | 51 | 0.012 | 4.3 | 4.3 | 3.8 | [17 empty] | AVERAGE | 9170 | [9 empty] | 243.3333 | 240 | 265 | 620 | 556.6667 | 550 | 510 | 600 | 570 | 800 |  | 898.3333 | 900 | 1013.3333 | 72.6667 | 94.3333 | 10.6667 | 1196.6667 | 246.3333 | 186.6667 | 41.3333 | 53.3333 | 6 | 596.6667 | 122.6667 | 131.6667
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0144 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2778 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.393 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.1467 |  |  |  |  | 0.028 |  |  |  |  | 0.54 | [6 empty] | 0.028 | [16 empty] | Pump Station MIN |  | 2.8 | [17 empty] | MINIMUM | 8840 | [9 empty] | 240 | 210 | 240 | 620 | 540 | 440 | 500 | 600 | 550 | 800 |  | 825 | 830 | 940 | 70 | 90 | 10 | 1140 | 235 | 180 | 40 | 50 | 6 | 550 | 114 | 125
[90 empty] | MAXIMUM | 9750 | [9 empty] | 250 | 260 | 280 | 620 | 580 | 660 | 520 | 600 | 600 | 800 |  | 950 | 950 | 1080 | 78 | 102 | 12 | 1300 | 268 | 200 | 44 | 58 | 6 | 660 | 134 | 145
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.614 |  | TOTAL MGD: |  | 0.013 |  |  | FINISHED SOUTH 1 |  | START: | 23827087 |  | END: | 23827100 |  |  | Alum | 5830 | 10934 | 10934 | 11145 | 11145 | 0 | [44 empty] | 0.59 | 9.6 | 26.5 | 15.635 | 6.24 | 14.5 | 15 | 1.0423
[73 empty] | FINISHED 2 | 11.591 |  | TOTAL MGD: |  | 10.601 |  |  | FINISHED SOUTH 2 |  | START: | 43945730 |  | END: | 43956331 |  |  | Caustic | 7805 | 8267 | 8267
[73 empty] | TOTAL RAW | 25.395 |  | TOTAL MGD: |  | 4.317 |  |  | FINISHED CONWAY |  | START: | 10269160 |  | END: | 10273477 |  |  | Hypochlorite | 15 |  | 45
[76 empty] | TOTAL MGD: |  | 7.274 |  |  | FINISHED PERRY |  | START: | 33912850 |  | END: | 33920124 |  |  | Phosphate | 2345
[76 empty] | TOTAL MGD: |  | 8.906 |  |  | RAW PLANT 1 |  | START: | 31040964 |  | END: | 31049870 |  |  | Fluoride | 3500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 6.563 |  |  | RAW PLANT 2 |  | START: | 30999160 |  | END: | 31005723 |  |  | Cal~Flo | 11.25 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 9.926 |  |  | RAW PLANT 3 |  | START: | 7583950 |  | END: | 7593876 |  |  | Zinc | 946
[76 empty] | TOTAL MGD: |  | 0.821 |  |  | DECANT |  | START: | 1871890 |  | END: | 1872711 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.6023 |  |  | BLOW DOWN |  | START: | 9146.6051 |  | END: | 9148.2074 |  |  | NH3 | 13 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827100
43956331
10273477
33920124
31049870
31005723
7593876
1872711
9148.2074
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 12
DATE: | 2019-01-12 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-12 | [23 empty] | DATE: | 2019-01-12
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-12 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43477.0052 | 2,3,5 | 35 | 9 | 5 | 10 | 24 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 6.1603 | 1,3 | 14.5181 | 20.6784 | 2.2435 | 43477.0052 | 90.057 | 7378.4876 | 0 | 602.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.2983 | 1.3028 | 0.26199 | 0.24509 | 0.25101 | 0 | 0.11409 | 0.20917 | 1.5218 | 1.5 | 0.069611 | 0.069611 | 0.069486 | 1.1175 | 0.54139 | 0.10034 | 3.9731 | 0.74762 | 3.6473 | 1.1214 | 0.54931 | 0.10572 | 3.4497 | 0.63419 | 4.4479 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.16 | 0.3833 | 3 | 0.68 | 14 | 9 | 0.65066 |  | 6.16 | 0.283 | 3 | 0.85 | 14 | 5 | 0.41481 | 6.09 | 0.396 | 3 | 0.53 | 15 | 10 | 0.49037 | [13 empty] | 7.62 | 0.055 | 1 | 4.2 | 12.5 |  |  |  | 7.28 | 0.052 | 1 | 3.8 | 13 |  |  |  | 4.3 | 3.8 | 3 | [18 empty] | 8840 | [6 empty] | 0 | 0 | 0 | 240 | 210 | 240 | 620 | 580 | 660 | 0 | 600 | 550 | 800 |  | 950 | 950 | 1080 | 70 | 90 | 10 | 1150 | 236 | 180 | 40 | 52 | 6 | 550 | 114 | 125 |  | 1:00 | 0.68 | 9 | 28.2667 | 19.2213 | 6.16 | 14 | 15 | 1.2814 | 10 | 6.5 | 0.53066 | 1:00 | 0.85 | 5 | 50.88 | 43.248 | 6.16 | 14 | 15 | 2.8832 | 10 | 6.5 | 0.29481 | 1:00 | 0.53 | 10 | 27 | 14.31 | 6.09 | 15 | 10 | 1.431 | 15 | 6.5 | 0.37037
2:00 | [72 empty] | 43477.3261 | 2,3,5 | 29 | 9 | 5 | 10 | 24 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 10.9483 | 1 | 10.3176 | 21.2659 | 2.2435 | 43477.3261 | 89.0383 | 7378.4876 | 0 | 602.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9783 | 1.731 | 1.7371 | 0.30425 | 0.27044 | 0.25861 | 0 | 0.12931 | 0.2434 | 1.5218 | 2 | 0.070344 | 0.070344 | 0.069486 | 1.0856 | 0.54741 | 0.10034 | 4.0148 | 0.76029 | 3.1407 | 1.1214 | 0.52819 | 0.10572 | 3.5166 | 0.66757 | 4.4479 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.44 | 18 | 15 | 10 | 127 | 176 | 14.5 | 0.484 |  | 6.11 | 10 | 0.051 | 6.08 | 10 |  | 6 | 10 | [8 empty] | 0.032 | [14 empty] | 0.023 | 1 | 0.28 |  | 0.029 | 0.01 | 1 | 0.45 |  | 0.024 | 1 | 0.38 | [38 empty] | 8740 | [6 empty] | 0 | 0 | 0 | 320 | 280 | 320 | 720 | 640 | 680 | 0 | 680 | 640 | 800 |  | 960 | 960 | 1080 | 68 | 91 | 10 | 1190 | 240 | 155 | 40 | 50 | 6 | 580 | 120 | 125 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43477.792 | 2,3,5 | 29 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.9483 | 1 | 10.3176 | 21.2659 | 2.1528 | 43477.792 | 89.9212 | 7870.3868 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7371 | 1.5199 | 1.5483 | 0.27382 | 0.25101 | 0.2377 | 0 | 0.12447 | 0.24893 | 1.5218 | 3.5 | 0.069486 | 0.069486 | 0.069961 | 1.0934 | 0.54931 | 0.10572 | 3.9995 | 0.75102 | 3.1135 | 1.0995 | 0.5461 | 0.09423 | 3.4842 | 0.63468 | 4.7573 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.35 | 0.054 | 1 | 4 | 12.5 |  |  |  | 7.38 | 0.05 | 1 | 3.8 | 13 |  |  |  | 4.3 | 3.8 | 3 | [18 empty] | 9930 | [6 empty] | 0 | 0 | 0 | 320 | 280 | 320 | 720 | 660 | 750 | 0 | 720 | 720 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1330 | 270 | 175 | 44 | 58 | 6 | 620 | 128 | 150 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.47 | 14 | 18 | 10.7 | 129 | 180 | 14.2 | 0.514 |  | 6.03 | 9 | 0.071 | 5.99 | 9 |  | 5.95 | 10 | [8 empty] | 0.047 | [14 empty] | 0.021 | 1 | 0.29 |  | 0.045 | 0.01 | 1 | 0.2 |  | 0.022 | 1 | 0.29 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.035 | [9 empty] | 6.13 | 0.405 | 4 | 0.65 | 13.9 | 9.3 | 0.66835 |  | 6.15 | 0.308 | 4 | 0.45 | 13.9 | 5.1 | 0.42071 | 6.15 | 0.337 | 3 | 0.61 | 14.9 | 10.4 | 0.69778 |  |  |  | 0.011 | [9 empty] | 7.2 | 0.049 | 1 | 3.9 | 12.1 | 21 | 46 | 0.011 | 7.18 | 0.058 | 1 | 3.7 | 14 | 22 | 50 | 0.011 | 4.2 | 3.7 | 3.2 | [55 empty] | 9:00 | 0.65 | 9.3 | 27.3548 | 17.7806 | 6.13 | 13.9 | 15 | 1.1854 | 10 | 6.5 | 0.54835 | 9:00 | 0.45 | 5.1 | 49.8824 | 22.4471 | 6.15 | 13.9 | 15 | 1.4965 | 10 | 6.5 | 0.30071 | 9:00 | 0.61 | 10.4 | 25.9615 | 15.8365 | 6.15 | 14.9 | 15 | 1.0558 | 10 | 6.5 | 0.57778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.45 | 14 | 14 | 10.9 | 128 | 182 | 13.8 | 0.51 |  | 6.07 | 8 | 0.072 | 6.05 | 8 |  | 5.96 | 9 | [8 empty] | 0.047 | [14 empty] | 0.021 | 1 | 0.39 |  | 0.044 | 0.011 | 1 | 0.31 |  | 0.023 | 1 | 0.41 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.06 | 0.383 | 4 | 0.66 | 13.7 | 9.3 | 0.66835 |  | 6.05 | 0.303 | 3 | 0.53 | 13.9 | 5.1 | 0.42071 | 6.09 | 0.322 | 3 | 0.62 | 14.8 | 10.4 | 0.69778 | [13 empty] | 7.24 | 0.048 | 1 | 4.1 | 12 |  |  |  | 7.21 | 0.055 | 1 | 3.7 | 14.3 |  |  |  | 4.3 | 3.8 | 2.4 | [55 empty] | 13:00 | 0.66 | 9.3 | 27.3548 | 18.0542 | 6.06 | 13.7 | 15 | 1.2036 | 10 | 6.5 | 0.54835 | 13:00 | 0.53 | 5.1 | 49.8824 | 26.4376 | 6.05 | 13.9 | 15 | 1.7625 | 10 | 6.5 | 0.30071 | 13:00 | 0.62 | 10.4 | 25.9615 | 16.0962 | 6.09 | 14.8 | 15 | 1.0731 | 10 | 6.5 | 0.57778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.42 | 15 | 17 | 10.9 | 129 | 181 | 13.9 | 0.518 |  | 6.01 | 8 | 0.077 | 5.98 | 9 |  | 5.97 | 10 | [8 empty] | 0.05 | [14 empty] | 0.016 | 1 | 0.35 |  | 0.049 | 0.013 | 1 | 0.25 |  | 0.052 | 1 | 0.41 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.16 | 0.046 | 1 | 4.3 | 11.9 |  |  |  | 7.1 | 0.052 | 1 | 3.9 | 14.1 |  |  |  | 4.3 | 3.8 | 2.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.41 | 15 | 15 | 11.1 | 129 | 184 | 13.4 | 0.522 |  | 6.12 | 12 | 0.079 | 6.06 | 12 |  | 6.02 | 11 | [8 empty] | 0.05 | [14 empty] | 0.022 | 1 | 0.35 |  | 0.05 | 0.01 | 1 | 0.34 |  | 0.04 | 1 | 0.61 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.034 | [9 empty] | 6.12 | 0.44 | 4 | 0.65 | 12.9 | 10 | 0.70962 |  | 6.13 | 0.371 | 5 | 0.58 | 12.9 | 6 | 0.47377 | 6.13 | 0.422 | 4 | 0.72 | 14.2 | 11 | 0.73111 |  |  |  | 0.009 | [9 empty] | 7.17 | 0.056 | 1 | 4.6 | 11.6 | 22 | 47 | 0.014 | 7.06 | 0.055 | 1 | 4.1 | 13.1 | 22 | 51 | 0.013 | 4.3 | 3.9 | 2.9 | [55 empty] | 21:00 | 0.65 | 10 | 25.44 | 16.536 | 6.12 | 12.9 | 15 | 1.1024 | 10 | 6.5 | 0.58962 | 21:00 | 0.58 | 6 | 42.4 | 24.592 | 6.13 | 12.9 | 15 | 1.6395 | 10 | 6.5 | 0.35377 | 21:00 | 0.72 | 11 | 24.5455 | 17.6727 | 6.13 | 14.2 | 15 | 1.1782 | 10 | 6.5 | 0.61111
22:00 | [72 empty] | DOSE |  | TOTAL | 28 | 16 | 31 | 75 | 22.6 | 22.6 | 25.6 | 70.8 | 0 | 28.057 | 2 | 35.1533 | 63.2102 | 6.6398 | TOTAL | 269.0166 | 22627.362 | 0 | 1871.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1992 | 4.5493 | 4.5881 | 0.84007 | 0.76654 | 0.74731 | 0 | 0.36787 | 0.7015 | 4.5654 | 7 | 0.20944 | 0.20944 | 0.20893 | 3.2964 | 1.6381 | 0.3064 | 11.9873 | 2.2589 | 9.9015 | 3.3422 | 1.6236 | 0.30567 | 10.4505 | 1.9364 | 13.6531 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.44 | 16 | 17 | 11.8 | 130 | 188 | 13.1 | 0.525 |  | 6.01 | 12 | 0.081 | 5.95 | 12 |  | 5.94 | 12 | [8 empty] | 0.051 | [14 empty] | 0.017 | 1 | 0.39 |  | 0.057 | 0.009 | 1 | 0.39 |  | 0.03 | 1 | 0.54 | [22 empty] | AVERAGE | 9.3333 | 5.3333 | 10.3333 | 25 | 7.5333 | 7.5333 | 8.5333 | 23.6 |  | 9.3523 | 1 | 11.7178 | 21.0701 | 2.2133 | AVERAGE | 89.6722 | 7542.454 |  | 623.7885 | 0 | 0 | 0 |  |  |  | 1.7331 | 1.5164 | 1.5294 | 0.28002 | 0.25551 | 0.2491 |  | 0.12262 | 0.23383 | 1.5218 | 2.3333 | 0.069814 | 0.069814 | 0.069644 | 1.0988 | 0.54604 | 0.10213 | 3.9958 | 0.75298 | 3.3005 | 1.1141 | 0.5412 | 0.10189 | 3.4835 | 0.64548 | 4.551 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.63 | 92 | 96 | 65.4 | 772 | 1091 | 82.9 | 3.073 | 0.069 | 36.35 | 59 | 0.431 | 0 | 60 | 0 | 35.84 | 62 | 0 | 24.47 | 1.6113 | 15 | 2.64 | 54.5 | 37.6 | 2.697 | 0.277 | 24.49 | 1.265 | 15 | 2.41 | 54.7 | 21.2 | 1.73 | 24.46 | 1.477 | 13 | 2.48 | 58.9 | 41.8 | 2.617 | 0.12 | 6 | 2.05 | 0.02 | 0.274 | 0.063 | 6 | 1.94 | 0 | 0.191 | 6 | 2.64 | 0 | 43.74 | 0.308 | 6 | 25.1 | 72.6 | 43 | 93 | 0.025 | 43.21 | 0.322 | 6 | 23 | 81.5 | 44 | 101 | 0.024 | 25.7 | 22.8 | 17.1 |  |  | MINIMUM | 9 | 5 | 10 | 24 | 7.2 | 7.2 | 8.2 | 22.6 |  | 6.1603 | 1 | 10.3176 | 20.6784 | 2.1528 | MINIMUM | 89.0383 | 7378.4876 |  | 602.6432 | [6 empty] | 1.4838 | 1.2983 | 1.3028 | 0.26199 | 0.24509 | 0.2377 |  | 0.11409 | 0.20917 | 1.5218 | 1.5 | 0.069486 | 0.069486 | 0.069486 | 1.0856 | 0.54139 | 0.10034 | 3.9731 | 0.74762 | 3.1135 | 1.0995 | 0.52819 | 0.09423 | 3.4497 | 0.63419 | 4.4479 |  | MIN | 0.65 | 10 | 25.44 | 16.536 | 6.12 | 12.9 | 15 | 1.1024 |  |  |  | MIN | 0.45 | 5.1 | 49.8824 | 22.4471 | 6.15 | 13.9 | 15 | 1.4965 |  |  |  | MIN | 0.61 | 10.4 | 25.9615 | 15.8365 | 6.15 | 14.9 | 15 | 1.0558 |  |  |  | 1.0558
AVERAGE | 6.4383 | 15.3333 | 16 | 10.9 | 128.6667 | 181.8333 | 13.8167 | 0.51217 | 0.0345 | 6.0583 | 9.8333 | 0.071833 |  | 10 |  | 5.9733 | 10.3333 |  | 6.1175 | 0.40282 | 3.75 | 0.66 | 13.625 | 9.4 | 0.67425 | 0.046167 | 6.1225 | 0.31625 | 3.75 | 0.6025 | 13.675 | 5.3 | 0.4325 | 6.115 | 0.36925 | 3.25 | 0.62 | 14.725 | 10.45 | 0.65426 | 0.02 | 1 | 0.34167 | 0.01 | 0.045667 | 0.0105 | 1 | 0.32333 |  | 0.031833 | 1 | 0.44 |  | 7.29 | 0.051333 | 1 | 4.1833 | 12.1 | 21.5 | 46.5 | 0.0125 | 7.2017 | 0.053667 | 1 | 3.8333 | 13.5833 | 22 | 50.5 | 0.012 | 4.2833 | 3.8 | 2.85 |  |  | MAXIMUM | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 10.9483 | 1 | 14.5181 | 21.2659 | 2.2435 | MAXIMUM | 90.057 | 7870.3868 |  | 666.0793 | [6 empty] | 1.9783 | 1.731 | 1.7371 | 0.30425 | 0.27044 | 0.25861 |  | 0.12931 | 0.24893 | 1.5218 | 3.5 | 0.070344 | 0.070344 | 0.069961 | 1.1175 | 0.54931 | 0.10572 | 4.0148 | 0.76029 | 3.6473 | 1.1214 | 0.54931 | 0.10572 | 3.5166 | 0.66757 | 4.7573
MINIMUM | 6.41 | 14 | 14 | 10 | 127 | 176 | 13.1 | 0.484 | 0.034 | 6.01 | 8 | 0.051 |  | 8 |  | 5.94 | 9 |  | 6.06 | 0.383 | 3 | 0.65 | 12.9 | 9 | 0.65066 | 0.032 | 6.05 | 0.283 | 3 | 0.45 | 12.9 | 5 | 0.41481 | 6.09 | 0.322 | 3 | 0.53 | 14.2 | 10 | 0.49037 | 0.016 | 1 | 0.28 | 0.009 | 0.029 | 0.009 | 1 | 0.2 |  | 0.022 | 1 | 0.29 |  | 7.16 | 0.046 | 1 | 3.9 | 11.6 | 21 | 46 | 0.011 | 7.06 | 0.05 | 1 | 3.7 | 13 | 22 | 50 | 0.011 | 4.2 | 3.7 | 2.4 | [15 empty] | MIL/MIN |  | TOTAL | 27510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 770 | 880 | 2060 | 1880 | 2090 | 0 | 2000 | 1910 | 2400 | 0 | 2990 | 2990 | 3380 | 216 | 285 | 32 | 3670 | 746 | 510 | 124 | 160 | 18 | 1750 | 362 | 400
MAXIMUM | 6.47 | 18 | 18 | 11.8 | 130 | 188 | 14.5 | 0.525 | 0.035 | 6.12 | 12 | 0.081 |  | 12 |  | 6.02 | 12 |  | 6.16 | 0.44 | 4 | 0.68 | 14 | 10 | 0.70962 | 0.051 | 6.16 | 0.371 | 5 | 0.85 | 14 | 6 | 0.47377 | 6.15 | 0.422 | 4 | 0.72 | 15 | 11 | 0.73111 | 0.023 | 1 | 0.39 | 0.011 | 0.057 | 0.013 | 1 | 0.45 |  | 0.052 | 1 | 0.61 |  | 7.62 | 0.056 | 1 | 4.6 | 12.5 | 22 | 47 | 0.014 | 7.38 | 0.058 | 1 | 4.1 | 14.3 | 22 | 51 | 0.013 | 4.3 | 3.9 | 3.2 | [17 empty] | AVERAGE | 9170 | [9 empty] | 293.3333 | 256.6667 | 293.3333 | 686.6667 | 626.6667 | 696.6667 |  | 666.6667 | 636.6667 | 800 |  | 996.6667 | 996.6667 | 1126.6667 | 72 | 95 | 10.6667 | 1223.3333 | 248.6667 | 170 | 41.3333 | 53.3333 | 6 | 583.3333 | 120.6667 | 133.3333
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0158 |  | TOTAL AVG COAG ALK: |  |  |  | 10.0556 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.44 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.45 | [5 empty] | 6.1183 |  |  |  |  | 0.052 |  |  |  |  | 0.45 | [6 empty] | 0.052 | [16 empty] | Pump Station MIN |  | 2.4 | [17 empty] | MINIMUM | 8740 | [9 empty] | 240 | 210 | 240 | 620 | 580 | 660 |  | 600 | 550 | 800 |  | 950 | 950 | 1080 | 68 | 90 | 10 | 1150 | 236 | 155 | 40 | 50 | 6 | 550 | 114 | 125
[90 empty] | MAXIMUM | 9930 | [9 empty] | 320 | 280 | 320 | 720 | 660 | 750 |  | 720 | 720 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1330 | 270 | 180 | 44 | 58 | 6 | 620 | 128 | 150
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.083 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23827100 |  | END: | 23827109 |  |  | Alum | 3060 | 10937 | 10937 | 10916 | 10916 | 0 | [44 empty] | 0.61 | 10.4 | 25.9615 | 15.8365 | 6.15 | 14.9 | 15 | 1.0558
[73 empty] | FINISHED 2 | 11.115 |  | TOTAL MGD: |  | 11.074 |  |  | FINISHED SOUTH 2 |  | START: | 43956331 |  | END: | 43967405 |  |  | Caustic | 7645 | 8262 | 8262
[73 empty] | TOTAL RAW | 25.569 |  | TOTAL MGD: |  | 4.629 |  |  | FINISHED CONWAY |  | START: | 10273477 |  | END: | 10278106 |  |  | Hypochlorite | 21 |  | 49
[76 empty] | TOTAL MGD: |  | 6.486 |  |  | FINISHED PERRY |  | START: | 33920124 |  | END: | 33926610 |  |  | Phosphate | 2242
[76 empty] | TOTAL MGD: |  | 9.687 |  |  | RAW PLANT 1 |  | START: | 31049870 |  | END: | 31059557 |  |  | Fluoride | 3500 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.236 |  |  | RAW PLANT 2 |  | START: | 31005723 |  | END: | 31010959 |  |  | Cal~Flo | 16.25 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.646 |  |  | RAW PLANT 3 |  | START: | 7593876 |  | END: | 7604522 |  |  | Zinc | 786
[76 empty] | TOTAL MGD: |  | 0.914 |  |  | DECANT |  | START: | 1872711 |  | END: | 1873625 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.4688 |  |  | BLOW DOWN |  | START: | 9148.2074 |  | END: | 9149.6763 |  |  | NH3 | 13 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827109
43967405
10278106
33926610
31059557
31010959
7604522
1873625
9149.6763
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 13
DATE: | 2019-01-13 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-13 | [23 empty] | DATE: | 2019-01-13
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-13 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43478.0093 | 2,3,5 | 29 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.9483 | 1 | 10.3176 | 21.2659 | 2.1528 | 43478.0093 | 89.9212 | 7870.3868 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7371 | 1.5199 | 1.5483 | 0.27382 | 0.25101 | 0.2377 | 0 | 0.12447 | 0.24893 | 1.5218 | 3.5 | 0.069486 | 0.069486 | 0.069961 | 1.0934 | 0.54931 | 0.10572 | 3.9995 | 0.75102 | 3.1135 | 1.0995 | 0.5461 | 0.09423 | 3.4842 | 0.63468 | 4.7573 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.324 | 4 | 0.68 | 14 | 10 | 0.70962 |  | 6.12 | 0.249 | 4 | 0.55 | 14 | 6 | 0.47377 | 6.09 | 0.418 | 4 | 0.65 | 15 | 11 | 0.52741 | [13 empty] | 7.25 | 0.054 | 1 | 4.2 | 12 |  |  |  | 7.21 | 0.052 | 1 | 4 | 14 |  |  |  | 4.3 | 3.8 | 3.1 | [18 empty] | 9930 | [6 empty] | 0 | 0 | 0 | 320 | 280 | 320 | 720 | 660 | 750 | 0 | 720 | 720 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1330 | 270 | 175 | 44 | 58 | 6 | 620 | 128 | 150 |  | 1:00 | 0.68 | 10 | 25.44 | 17.2992 | 6.1 | 14 | 15 | 1.1533 | 10 | 6.5 | 0.58962 | 1:00 | 0.55 | 6 | 42.4 | 23.32 | 6.12 | 14 | 15 | 1.5547 | 10 | 6.5 | 0.35377 | 1:00 | 0.65 | 11 | 24.5455 | 15.9545 | 6.09 | 15 | 10 | 1.5955 | 15 | 6.5 | 0.40741
2:00 | [72 empty] | 43478.3417 | 2,3,5 | 36 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 11.052 | 1,3 | 13.9176 | 24.9696 | 2.1528 | 43478.3417 | 90.374 | 8547 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7371 | 1.9542 | 1.5483 | 0.30425 | 0.25861 | 0.24086 | 0 | 0.11755 | 0.20744 | 1.5218 | 7 | 0.069486 | 0.069486 | 0.071108 | 1.1214 | 0.54931 | 0.10572 | 3.9966 | 0.75102 | 3.1135 | 1.0995 | 0.56493 | 0.09423 | 3.4742 | 0.6198 | 4.7573 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.42 | 18 | 15 | 11.2 | 120 | 184 | 13.8 | 0.478 |  | 6 | 12 | 0.049 | 6.01 | 12 |  | 6 | 12 | [8 empty] | 0.033 | [14 empty] | 0.018 | 1 | 0.3 |  | 0.038 | 0.012 | 1 | 0.32 |  | 0.029 | 1 | 0.55 | [38 empty] | 9980 | [6 empty] | 0 | 0 | 0 | 320 | 360 | 320 | 800 | 680 | 760 | 0 | 680 | 600 | 800 |  | 1080 | 1080 | 1240 | 80 | 104 | 12 | 1320 | 270 | 175 | 44 | 60 | 6 | 620 | 125 | 150 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43478.8082 | 2,3,5 | 36 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 11.052 | 1,3 | 13.9176 | 24.9696 | 2.1744 | 43478.8082 | 90.1023 | 8546.7482 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6285 | 1.6285 | 1.5483 | 0.27573 | 0.25671 | 0.24086 | 0 | 0.11237 | 0.20744 | 1.5218 | 5 | 0.069486 | 0.069486 | 0.070535 | 1.0934 | 0.54931 | 0.10572 | 4.061 | 0.73433 | 3.4694 | 1.0995 | 0.56493 | 0.09423 | 3.5642 | 0.61484 | 5.3599 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.3 | 0.052 | 1 | 4.2 | 12 |  |  |  | 7.25 | 0.054 | 1 | 4.2 | 14 |  |  |  | 4.3 | 3.8 | 3 | [18 empty] | 9950 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 320 | 725 | 675 | 760 | 0 | 650 | 600 | 800 |  | 1080 | 1080 | 1230 | 78 | 104 | 12 | 1300 | 264 | 195 | 44 | 60 | 6 | 620 | 124 | 169 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.58 | 14 | 18 | 11.7 | 129 | 181 | 13.5 | 0.513 |  | 5.86 | 9 | 0.074 | 5.81 | 8 |  | 5.82 | 8 | [8 empty] | 0.051 | [14 empty] | 0.018 | 1 | 0.24 |  | 0.041 | 0.011 | 1 | 0.21 |  | 0.025 | 1 | 0.4 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.035 | [9 empty] | 5.98 | 0.347 | 4 | 0.67 | 13.6 | 10.2 | 0.64123 |  | 5.96 | 0.264 | 4 | 0.59 | 13.5 | 5.5 | 0.40105 | 6.01 | 0.371 | 4 | 0.54 | 15 | 11.2 | 0.53481 |  |  |  | 0.017 | [9 empty] | 7.14 | 0.047 | 1 | 4.2 | 11.5 | 21 | 55 | 0.014 | 7.01 | 0.052 | 1 | 3.4 | 13.5 | 22 | 52 | 0.014 | 4.4 | 3.7 | 3.3 | [55 empty] | 9:00 | 0.67 | 10.2 | 24.9412 | 16.7106 | 5.98 | 13.6 | 13 | 1.2854 | 10 | 6 | 0.52123 | 9:00 | 0.59 | 5.5 | 46.2545 | 27.2902 | 5.96 | 13.5 | 13 | 2.0992 | 10 | 6 | 0.28105 | 9:00 | 0.54 | 11.2 | 24.1071 | 13.0179 | 6.01 | 15 | 10 | 1.3018 | 15 | 6.5 | 0.41481
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.46 | 17 | 17 | 11.6 | 124 | 186 | 13.4 | 0.492 |  | 5.96 | 10 | 0.063 | 5.95 | 9 |  | 5.9 | 9 | [8 empty] | 0.049 | [14 empty] | 0.025 | 1 | 0.54 |  | 0.05 | 0.015 | 1 | 0.42 |  | 0.023 | 1 | 0.5 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.06 | 0.33 | 4 | 0.68 | 13.3 | 10 | 0.70962 |  | 6.03 | 0.26 | 4 | 0.75 | 13.4 | 5.4 | 0.4384 | 6.04 | 0.313 | 4 | 0.8 | 14.2 | 11 | 0.73111 | [13 empty] | 7.26 | 0.048 | 1 | 4.5 | 11.6 |  |  |  | 7.17 | 0.054 | 1 | 3.8 | 13.4 |  |  |  | 4.4 | 3.8 | 2.6 | [55 empty] | 13:00 | 0.68 | 10 | 25.44 | 17.2992 | 6.06 | 13.3 | 15 | 1.1533 | 10 | 6.5 | 0.58962 | 13:00 | 0.75 | 5.4 | 47.1111 | 35.3333 | 6.03 | 13.4 | 15 | 2.3556 | 10 | 6.5 | 0.3184 | 13:00 | 0.8 | 11 | 24.5455 | 19.6364 | 6.04 | 14.2 | 15 | 1.3091 | 10 | 6.5 | 0.61111
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.63 | 16 | 18 | 11.7 | 129 | 185 | 13.4 | 0.512 |  | 6.04 | 10 | 0.064 | 6.01 | 10 |  | 5.95 | 9 | [8 empty] | 0.044 | [14 empty] | 0.038 | 1 | 0.47 |  | 0.043 | 0.015 | 1 | 0.42 |  | 0.021 | 1 | 0.49 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.38 | 0.05 | 1 | 4.7 | 11.3 |  |  |  | 7.19 | 0.053 | 1 | 3.6 | 13.1 |  |  |  | 4.6 | 3.7 | 2.7 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.44 | 19 | 17 | 12.1 | 123 | 193 | 12.9 | 0.505 |  | 6.09 | 10 | 0.083 | 6.08 | 10 |  | 6 | 10 | [8 empty] | 0.048 | [14 empty] | 0.029 | 1 | 0.46 |  | 0.049 | 0.016 | 1 | 0.39 |  | 0.022 | 1 | 0.55 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.044 | [9 empty] | 6.1 | 0.381 | 4 | 0.64 | 12.6 | 10 | 0.70962 |  | 6.12 | 0.322 | 4 | 0.64 | 12.6 | 6 | 0.47377 | 6.1 | 0.437 | 3 | 0.8 | 13.7 | 11 | 0.73111 |  |  |  | 0.011 | [9 empty] | 7.23 | 0.055 | 1 | 4.7 | 11.2 | 22 | 54 | 0.019 | 7.19 | 0.05 | 1 | 4.3 | 12.8 | 22 | 50 | 0.017 | 4.7 | 3.8 | 2.7 | [55 empty] | 21:00 | 0.64 | 10 | 25.44 | 16.2816 | 6.1 | 12.6 | 15 | 1.0854 | 10 | 6.5 | 0.58962 | 21:00 | 0.64 | 6 | 42.4 | 27.136 | 6.12 | 12.6 | 15 | 1.8091 | 10 | 6.5 | 0.35377 | 21:00 | 0.8 | 11 | 24.5455 | 19.6364 | 6.1 | 13.7 | 15 | 1.3091 | 10 | 6.5 | 0.61111
22:00 | [72 empty] | DOSE |  | TOTAL | 30 | 18 | 33 | 81 | 24.6 | 24.6 | 27.6 | 76.8 | 0 | 33.0523 | 1 | 38.1528 | 71.2051 | 6.48 | TOTAL | 270.3975 | 24964.135 | 0 | 1998.2379 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1027 | 5.1027 | 4.6448 | 0.8538 | 0.76633 | 0.71942 | 0 | 0.35438 | 0.66382 | 4.5654 | 15.5 | 0.20846 | 0.20846 | 0.2116 | 3.3081 | 1.6479 | 0.31717 | 12.0571 | 2.2364 | 9.6964 | 3.2984 | 1.676 | 0.28269 | 10.5226 | 1.8693 | 14.8745 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.5 | 17 | 17 | 12.2 | 129 | 189 | 12.6 | 0.524 |  | 6.02 | 10 | 0.08 | 6 | 10 |  | 5.97 | 10 | [8 empty] | 0.05 | [14 empty] | 0.029 | 1 | 0.34 |  | 0.051 | 0.013 | 1 | 0.4 |  | 0.021 | 1 | 0.49 | [22 empty] | AVERAGE | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 11.0174 | 1 | 12.7176 | 23.735 | 2.16 | AVERAGE | 90.1325 | 8321.3783 |  | 666.0793 | 0 | 0 | 0 |  |  |  | 1.7009 | 1.7009 | 1.5483 | 0.2846 | 0.25544 | 0.23981 |  | 0.11813 | 0.22127 | 1.5218 | 5.1667 | 0.069486 | 0.069486 | 0.070535 | 1.1027 | 0.54931 | 0.10572 | 4.019 | 0.74546 | 3.2321 | 1.0995 | 0.55865 | 0.09423 | 3.5075 | 0.62311 | 4.9582 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.03 | 101 | 102 | 70.5 | 754 | 1118 | 79.6 | 3.024 | 0.079 | 35.97 | 61 | 0.413 | 35.86 | 59 | 0 | 35.64 | 58 | 0 | 24.24 | 1.382 | 16 | 2.67 | 53.5 | 40.2 | 2.7701 | 0.275 | 24.23 | 1.095 | 16 | 2.53 | 53.5 | 22.9 | 1.787 | 24.24 | 1.539 | 15 | 2.79 | 57.9 | 44.2 | 2.5244 | 0 | 6 | 2.35 | 0.028 | 0.272 | 0.082 | 6 | 2.16 | 0 | 0.141 | 6 | 2.98 | 0 | 43.56 | 0.306 | 6 | 26.5 | 69.6 | 43 | 109 | 0.033 | 43.02 | 0.315 | 6 | 23.3 | 80.8 | 44 | 102 | 0.031 | 26.7 | 22.6 | 17.4 |  |  | MINIMUM | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 10.9483 | 1 | 10.3176 | 21.2659 | 2.1528 | MINIMUM | 89.9212 | 7870.3868 |  | 666.0793 | [6 empty] | 1.6285 | 1.5199 | 1.5483 | 0.27382 | 0.25101 | 0.2377 |  | 0.11237 | 0.20744 | 1.5218 | 3.5 | 0.069486 | 0.069486 | 0.069961 | 1.0934 | 0.54931 | 0.10572 | 3.9966 | 0.73433 | 3.1135 | 1.0995 | 0.5461 | 0.09423 | 3.4742 | 0.61484 | 4.7573 |  | MIN | 0.64 | 10 | 25.44 | 16.2816 | 6.1 | 12.6 | 15 | 1.0854 |  |  |  | MIN | 0.55 | 6 | 42.4 | 23.32 | 6.12 | 14 | 15 | 1.5547 |  |  |  | MIN | 0.54 | 11.2 | 24.1071 | 13.0179 | 6.01 | 15 | 10 | 1.3018 |  |  |  | 1.0854
AVERAGE | 6.505 | 16.8333 | 17 | 11.75 | 125.6667 | 186.3333 | 13.2667 | 0.504 | 0.0395 | 5.995 | 10.1667 | 0.068833 | 5.9767 | 9.8333 |  | 5.94 | 9.6667 |  | 6.06 | 0.3455 | 4 | 0.6675 | 13.375 | 10.05 | 0.69252 | 0.045833 | 6.0575 | 0.27375 | 4 | 0.6325 | 13.375 | 5.725 | 0.44675 | 6.06 | 0.38475 | 3.75 | 0.6975 | 14.475 | 11.05 | 0.63111 |  | 1 | 0.39167 | 0.014 | 0.045333 | 0.013667 | 1 | 0.36 |  | 0.0235 | 1 | 0.49667 |  | 7.26 | 0.051 | 1 | 4.4167 | 11.6 | 21.5 | 54.5 | 0.0165 | 7.17 | 0.0525 | 1 | 3.8833 | 13.4667 | 22 | 51 | 0.0155 | 4.45 | 3.7667 | 2.9 |  |  | MAXIMUM | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 11.052 | 1 | 13.9176 | 24.9696 | 2.1744 | MAXIMUM | 90.374 | 8547 |  | 666.0793 | [6 empty] | 1.7371 | 1.9542 | 1.5483 | 0.30425 | 0.25861 | 0.24086 |  | 0.12447 | 0.24893 | 1.5218 | 7 | 0.069486 | 0.069486 | 0.071108 | 1.1214 | 0.54931 | 0.10572 | 4.061 | 0.75102 | 3.4694 | 1.0995 | 0.56493 | 0.09423 | 3.5642 | 0.63468 | 5.3599
MINIMUM | 6.42 | 14 | 15 | 11.2 | 120 | 181 | 12.6 | 0.478 | 0.035 | 5.86 | 9 | 0.049 | 5.81 | 8 |  | 5.82 | 8 |  | 5.98 | 0.324 | 4 | 0.64 | 12.6 | 10 | 0.64123 | 0.033 | 5.96 | 0.249 | 4 | 0.55 | 12.6 | 5.4 | 0.40105 | 6.01 | 0.313 | 3 | 0.54 | 13.7 | 11 | 0.52741 |  | 1 | 0.24 | 0.011 | 0.038 | 0.011 | 1 | 0.21 |  | 0.021 | 1 | 0.4 |  | 7.14 | 0.047 | 1 | 4.2 | 11.2 | 21 | 54 | 0.014 | 7.01 | 0.05 | 1 | 3.4 | 12.8 | 22 | 50 | 0.014 | 4.3 | 3.7 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 29860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 940 | 960 | 2245 | 2015 | 2270 | 0 | 2050 | 1920 | 2400 | 0 | 3240 | 3240 | 3690 | 236 | 312 | 36 | 3950 | 804 | 545 | 132 | 178 | 18 | 1860 | 377 | 469
MAXIMUM | 6.63 | 19 | 18 | 12.2 | 129 | 193 | 13.8 | 0.524 | 0.044 | 6.09 | 12 | 0.083 | 6.08 | 12 |  | 6 | 12 |  | 6.1 | 0.381 | 4 | 0.68 | 14 | 10.2 | 0.70962 | 0.051 | 6.12 | 0.322 | 4 | 0.75 | 14 | 6 | 0.47377 | 6.1 | 0.437 | 4 | 0.8 | 15 | 11.2 | 0.73111 |  | 1 | 0.54 | 0.017 | 0.051 | 0.016 | 1 | 0.42 |  | 0.029 | 1 | 0.55 |  | 7.38 | 0.055 | 1 | 4.7 | 12 | 22 | 55 | 0.019 | 7.25 | 0.054 | 1 | 4.3 | 14 | 22 | 52 | 0.017 | 4.7 | 3.8 | 3.3 | [17 empty] | AVERAGE | 9953.3333 | [9 empty] | 313.3333 | 313.3333 | 320 | 748.3333 | 671.6667 | 756.6667 |  | 683.3333 | 640 | 800 |  | 1080 | 1080 | 1230 | 78.6667 | 104 | 12 | 1316.6667 | 268 | 181.6667 | 44 | 59.3333 | 6 | 620 | 125.6667 | 156.3333
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 5.9706 |  | TOTAL AVG COAG ALK: |  |  |  | 9.8889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.437 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.54 | [5 empty] | 6.0592 |  |  |  |  | 0.029 |  |  |  |  | 0.54 | [23 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 9930 | [9 empty] | 300 | 280 | 320 | 720 | 660 | 750 |  | 650 | 600 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1300 | 264 | 175 | 44 | 58 | 6 | 620 | 124 | 150
[90 empty] | MAXIMUM | 9980 | [9 empty] | 320 | 360 | 320 | 800 | 680 | 760 |  | 720 | 720 | 800 |  | 1080 | 1080 | 1240 | 80 | 104 | 12 | 1330 | 270 | 195 | 44 | 60 | 6 | 620 | 128 | 169
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.821 |  | TOTAL MGD: |  | 0.011 |  |  | FINISHED SOUTH 1 |  | START: | 23827109 |  | END: | 23827120 |  |  | Alum | 7279 | 10392 | 10392 | 9604 | 9604 | 0 | [44 empty] | 0.64 | 10 | 25.44 | 16.2816 | 6.1 | 12.6 | 15 | 1.0854
[73 empty] | FINISHED 2 | 12.1 |  | TOTAL MGD: |  | 10.81 |  |  | FINISHED SOUTH 2 |  | START: | 43967405 |  | END: | 43978215 |  |  | Caustic | 7460 | 8213 | 8213
[73 empty] | TOTAL RAW | 27.833 |  | TOTAL MGD: |  | 4.58 |  |  | FINISHED CONWAY |  | START: | 10278106 |  | END: | 10282686 |  |  | Hypochlorite | 20 |  | 48
[76 empty] | TOTAL MGD: |  | 7.52 |  |  | FINISHED PERRY |  | START: | 33926610 |  | END: | 33934130 |  |  | Phosphate | 2210
[76 empty] | TOTAL MGD: |  | 10.581 |  |  | RAW PLANT 1 |  | START: | 31059557 |  | END: | 31070138 |  |  | Fluoride | 3100 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.704 |  |  | RAW PLANT 2 |  | START: | 31010959 |  | END: | 31016663 |  |  | Cal~Flo | 12.5 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.548 |  |  | RAW PLANT 3 |  | START: | 7604522 |  | END: | 7616070 |  |  | Zinc | 786
[76 empty] | TOTAL MGD: |  | 1.065 |  |  | DECANT |  | START: | 1873625 |  | END: | 1874690 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.4847 |  |  | BLOW DOWN |  | START: | 9149.6763 |  | END: | 9151.161 |  |  | NH3 | 13 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827120
43978215
10282686
33934130
31070138
31016663
7616070
1874690
9151.161
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 14
DATE: | 2019-01-14 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-14 | [23 empty] | DATE: | 2019-01-14
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-14 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43479.0123 | 2,3,5 | 36 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 11.052 | 1,3 | 13.9176 | 24.9696 | 2.1744 | 43479.0123 | 90.1023 | 8546.7482 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6285 | 1.6285 | 1.5483 | 0.27573 | 0.25671 | 0.24086 | 0 | 0.11237 | 0.20744 | 1.5218 | 5 | 0.069486 | 0.069486 | 0.070535 | 1.0934 | 0.54931 | 0.10572 | 4.061 | 0.73433 | 3.4694 | 1.0995 | 0.56493 | 0.09423 | 3.5642 | 0.61484 | 5.3599 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.345 | 3 | 0.62 | 13.5 | 10 | 0.70962 |  | 6.15 | 0.32 | 3 | 0.55 | 13.5 | 6 | 0.47377 | 6.09 | 0.44 | 3 | 0.74 | 14.5 | 11 | 0.73111 | [13 empty] | 7.29 | 0.052 | 1 | 4.4 | 11.5 |  |  |  | 7.15 | 0.05 | 1 | 4.2 | 13.5 |  |  |  | 4.5 | 3.9 | 2.7 | [18 empty] | 9950 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 320 | 725 | 675 | 760 | 0 | 650 | 600 | 800 |  | 1080 | 1080 | 1230 | 78 | 104 | 12 | 1300 | 264 | 195 | 44 | 60 | 6 | 620 | 124 | 169 |  | 1:00 | 0.62 | 10 | 25.44 | 15.7728 | 6.1 | 13.5 | 15 | 1.0515 | 10 | 6.5 | 0.58962 | 1:00 | 0.55 | 6 | 42.4 | 23.32 | 6.15 | 13.5 | 15 | 1.5547 | 10 | 6.5 | 0.35377 | 1:00 | 0.74 | 11 | 24.5455 | 18.1636 | 6.09 | 14.5 | 15 | 1.2109 | 10 | 6.5 | 0.61111
2:00 | [72 empty] | 43479.3456 | 2,3,5 | 34 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.5538 | 1,3 | 11.4034 | 21.9571 | 2.1744 | 43479.3456 | 89.8307 | 8423.7734 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7371 | 1.9542 | 1.7418 | 0.33467 | 0.31946 | 0.25354 | 0 | 0.11755 | 0.2351 | 1.5218 | 7 | 0.069486 | 0.069486 | 0.069961 | 1.0653 | 0.54931 | 0.10572 | 4.0016 | 0.75102 | 3.4694 | 1.0495 | 0.56493 | 0.09423 | 3.5042 | 0.6198 | 5.3599 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.44 | 20 | 17 | 11.6 | 122 | 186 | 13.2 | 0.466 |  | 6.05 | 10 | 0.052 | 6.07 | 11 |  | 6 | 11 | [8 empty] | 0.038 | [14 empty] | 0.027 | 1 | 0.35 |  | 0.039 | 0.013 | 1 | 0.38 |  | 0.021 | 1 | 0.45 | [38 empty] | 9920 | [6 empty] | 0 | 0 | 0 | 320 | 360 | 360 | 880 | 840 | 800 | 0 | 680 | 680 | 800 |  | 1080 | 1080 | 1220 | 76 | 104 | 12 | 1320 | 270 | 195 | 42 | 60 | 6 | 620 | 125 | 169 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43479.8165 | 2,3,5 | 34 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.5538 | 1,3 | 11.4034 | 21.9571 | 2.2392 | 43479.8165 | 89.7401 | 8546.7482 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6285 | 1.6285 | 1.645 | 0.30425 | 0.30425 | 0.2472 | 0.2472 | 0.24 | 0.24202 | 1.5218 | 2 | 0.069486 | 0.069486 | 0.069961 | 1.0934 | 0.54931 | 0.10572 | 3.991 | 0.73989 | 3.4694 | 1.0995 | 0.5461 | 0.09423 | 3.465 | 0.61484 | 5.3599 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.19 | 0.054 | 1 | 4.2 | 11 |  |  |  | 7.2 | 0.052 | 1 | 4 | 13 |  |  |  | 4.5 | 3.8 | 3.4 | [18 empty] | 9910 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 340 | 800 | 800 | 780 | 780 | 700 | 700 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1300 | 266 | 195 | 44 | 58 | 6 | 600 | 124 | 169 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.51 | 15 | 16 | 11.6 | 127 | 188 | 12.8 | 0.512 |  | 6 | 11 | 0.07 | 5.97 | 10 |  | 5.94 | 11 | [8 empty] | 0.05 | [14 empty] | 0.029 | 1 | 0.32 |  | 0.053 | 0.011 | 1 | 0.34 |  | 0.02 | 1 | 0.43 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.04 | 0.337 | 4 | 0.63 | 12.5 | 10.3 | 0.72731 |  | 6.06 | 0.283 | 4 | 0.7 | 12.8 | 5.6 | 0.45019 | 6.07 | 0.347 | 4 | 0.69 | 13.2 | 11.2 | 0.74222 |  |  |  | 0.02 | [9 empty] | 7.37 | 0.055 | 1 | 4.6 | 11.1 | 24 | 57 | 0.014 | 7.41 | 0.061 | 1 | 3.9 | 12.7 | 29 | 53 | 0.011 | 4.4 | 3.7 | 3.2 | [55 empty] | 9:00 | 0.63 | 10.3 | 24.699 | 15.5604 | 6.04 | 12.5 | 15 | 1.0374 | 10 | 6.5 | 0.60731 | 9:00 | 0.7 | 5.6 | 45.4286 | 31.8 | 6.06 | 12.8 | 15 | 2.12 | 10 | 6.5 | 0.33019 | 9:00 | 0.69 | 11.2 | 24.1071 | 16.6339 | 6.07 | 13.2 | 15 | 1.1089 | 10 | 6.5 | 0.62222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.53 | 16 | 15 | 12.2 | 129 | 190 | 12.8 | 0.499 |  | 6.08 | 10 | 0.073 | 6.12 | 10 |  | 6.03 | 10 | [8 empty] | 0.052 | [14 empty] | 0.026 | 1 | 0.37 |  | 0.05 | 0.012 | 1 | 0.38 |  | 0.022 | 1 | 0.54 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.06 | 0.309 | 4 | 0.67 | 12.5 | 10.2 | 0.72142 |  | 6.1 | 0.265 | 4 | 0.76 | 12.7 | 5.4 | 0.4384 | 6.09 | 0.34 | 4 | 0.68 | 13.1 | 11 | 0.73111 | [13 empty] | 7.68 | 0.053 | 1 | 4.5 | 11 |  |  |  | 7.29 | 0.059 | 1 | 3.6 | 12.8 |  |  |  | 4.4 | 3.7 | 2.6 | [55 empty] | 13:00 | 0.67 | 10.2 | 24.9412 | 16.7106 | 6.06 | 12.5 | 15 | 1.114 | 10 | 6.5 | 0.60142 | 13:00 | 0.76 | 5.4 | 47.1111 | 35.8044 | 6.1 | 12.7 | 15 | 2.387 | 10 | 6.5 | 0.3184 | 13:00 | 0.68 | 11 | 24.5455 | 16.6909 | 6.09 | 13.1 | 15 | 1.1127 | 10 | 6.5 | 0.61111
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.48 | 14 | 15 | 11.7 | 128 | 187 | 12.9 | 0.509 |  | 6.11 | 8 | 0.068 | 6.09 | 8 |  | 6.02 | 9 | [8 empty] | 0.05 | [14 empty] | 0.023 | 1 | 0.4 |  | 0.056 | 0.012 | 1 | 0.45 |  | 0.019 | 1 | 0.55 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.99 | 0.052 | 1 | 5 | 10.9 |  |  |  | 7.38 | 0.056 | 1 | 4 | 12.7 |  |  |  | 4.4 | 3.8 | 2.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.43 | 16 | 15 | 12 | 126 | 190 | 12.4 | 0.519 |  | 6.02 | 10 | 0.076 | 6.02 | 10 |  | 6 | 10 | [8 empty] | 0.052 | [14 empty] | 0.024 | 1 | 0.51 |  | 0.057 | 0.013 | 1 | 0.45 |  | 0.018 | 1 | 0.57 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.042 | [9 empty] | 6.1 | 0.305 | 3 | 0.76 | 11.7 | 10 | 0.70962 |  | 6.14 | 0.235 | 3 | 0.9 | 11.9 | 6 | 0.47377 | 6.12 | 0.297 | 3 | 0.9 | 13.1 | 11 | 0.73111 |  |  |  | 0.019 | [9 empty] | 7.63 | 0.056 | 1 | 4.9 | 10.6 | 23 | 49 | 0.017 | 7.37 | 0.055 | 1 | 4.4 | 12.3 | 22 | 51 | 0.01 | 4.1 | 3.9 | 2.8 | [55 empty] | 21:00 | 0.76 | 10 | 25.44 | 19.3344 | 6.1 | 11.7 | 15 | 1.289 | 10 | 6.5 | 0.58962 | 21:00 | 0.9 | 6 | 42.4 | 38.16 | 6.14 | 11.9 | 15 | 2.544 | 10 | 6.5 | 0.35377 | 21:00 | 0.9 | 11 | 24.5455 | 22.0909 | 6.12 | 13.1 | 15 | 1.4727 | 10 | 6.5 | 0.61111
22:00 | [72 empty] | DOSE |  | TOTAL | 30 | 18 | 33 | 81 | 24.6 | 24.6 | 27.6 | 76.8 | 0 | 32.1595 | 0 | 36.7243 | 68.8838 | 6.588 | TOTAL | 269.6731 | 25517.2698 | 0 | 1998.2379 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9941 | 5.2112 | 4.9351 | 0.91465 | 0.88042 | 0.74161 | 0.2472 | 0.46992 | 0.68456 | 4.5654 | 14 | 0.20846 | 0.20846 | 0.21046 | 3.252 | 1.6479 | 0.31717 | 12.0537 | 2.2252 | 10.4081 | 3.2484 | 1.676 | 0.28269 | 10.5335 | 1.8495 | 16.0797 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.49 | 15 | 15 | 12.1 | 132 | 191 | 12.4 | 0.52 |  | 6 | 10 | 0.079 | 5.99 | 10 |  | 5.97 | 10 | [8 empty] | 0.05 | [14 empty] | 0.017 | 1 | 0.59 |  | 0.054 | 0.013 | 1 | 0.51 |  | 0.017 | 1 | 0.57 | [22 empty] | AVERAGE | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 10.7198 |  | 12.2414 | 22.9613 | 2.196 | AVERAGE | 89.891 | 8505.7566 |  | 666.0793 | 0 | 0 | 0 |  |  |  | 1.6647 | 1.7371 | 1.645 | 0.30488 | 0.29347 | 0.2472 | 0.082401 | 0.15664 | 0.22819 | 1.5218 | 4.6667 | 0.069486 | 0.069486 | 0.070153 | 1.084 | 0.54931 | 0.10572 | 4.0179 | 0.74175 | 3.4694 | 1.0828 | 0.55865 | 0.09423 | 3.5112 | 0.6165 | 5.3599 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.88 | 96 | 93 | 71.2 | 764 | 1132 | 76.5 | 3.025 | 0.083 | 36.26 | 59 | 0.418 | 36.26 | 59 | 0 | 35.96 | 61 | 0 | 24.3 | 1.296 | 14 | 2.68 | 50.2 | 40.5 | 2.868 | 0.292 | 24.45 | 1.103 | 14 | 2.91 | 50.9 | 23 | 1.8361 | 24.37 | 1.424 | 14 | 3.01 | 53.9 | 44.2 | 2.9356 | 0.146 | 6 | 2.54 | 0.039 | 0.309 | 0.074 | 6 | 2.51 | 0 | 0.117 | 6 | 3.11 | 0 | 45.15 | 0.322 | 6 | 27.6 | 66.1 | 47 | 106 | 0.031 | 43.8 | 0.333 | 6 | 24.1 | 77 | 51 | 104 | 0.021 | 26.3 | 22.8 | 17.3 |  |  | MINIMUM | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 10.5538 |  | 11.4034 | 21.9571 | 2.1744 | MINIMUM | 89.7401 | 8423.7734 |  | 666.0793 | [6 empty] | 1.6285 | 1.6285 | 1.5483 | 0.27573 | 0.25671 | 0.24086 | 0 | 0.11237 | 0.20744 | 1.5218 | 2 | 0.069486 | 0.069486 | 0.069961 | 1.0653 | 0.54931 | 0.10572 | 3.991 | 0.73433 | 3.4694 | 1.0495 | 0.5461 | 0.09423 | 3.465 | 0.61484 | 5.3599 |  | MIN | 0.63 | 10.3 | 24.699 | 15.5604 | 6.04 | 12.5 | 15 | 1.0374 |  |  |  | MIN | 0.55 | 6 | 42.4 | 23.32 | 6.15 | 13.5 | 15 | 1.5547 |  |  |  | MIN | 0.69 | 11.2 | 24.1071 | 16.6339 | 6.07 | 13.2 | 15 | 1.1089 |  |  |  | 1.0374
AVERAGE | 6.48 | 16 | 15.5 | 11.8667 | 127.3333 | 188.6667 | 12.75 | 0.50417 | 0.0415 | 6.0433 | 9.8333 | 0.069667 | 6.0433 | 9.8333 |  | 5.9933 | 10.1667 |  | 6.075 | 0.324 | 3.5 | 0.67 | 12.55 | 10.125 | 0.71699 | 0.048667 | 6.1125 | 0.27575 | 3.5 | 0.7275 | 12.725 | 5.75 | 0.45903 | 6.0925 | 0.356 | 3.5 | 0.7525 | 13.475 | 11.05 | 0.73389 | 0.024333 | 1 | 0.42333 | 0.0195 | 0.0515 | 0.012333 | 1 | 0.41833 |  | 0.0195 | 1 | 0.51833 |  | 7.525 | 0.053667 | 1 | 4.6 | 11.0167 | 23.5 | 53 | 0.0155 | 7.3 | 0.0555 | 1 | 4.0167 | 12.8333 | 25.5 | 52 | 0.0105 | 4.3833 | 3.8 | 2.8833 |  |  | MAXIMUM | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 |  | 11.052 |  | 13.9176 | 24.9696 | 2.2392 | MAXIMUM | 90.1023 | 8546.7482 |  | 666.0793 | [6 empty] | 1.7371 | 1.9542 | 1.7418 | 0.33467 | 0.31946 | 0.25354 | 0.2472 | 0.24 | 0.24202 | 1.5218 | 7 | 0.069486 | 0.069486 | 0.070535 | 1.0934 | 0.54931 | 0.10572 | 4.061 | 0.75102 | 3.4694 | 1.0995 | 0.56493 | 0.09423 | 3.5642 | 0.6198 | 5.3599
MINIMUM | 6.43 | 14 | 15 | 11.6 | 122 | 186 | 12.4 | 0.466 | 0.041 | 6 | 8 | 0.052 | 5.97 | 8 |  | 5.94 | 9 |  | 6.04 | 0.305 | 3 | 0.62 | 11.7 | 10 | 0.70962 | 0.038 | 6.06 | 0.235 | 3 | 0.55 | 11.9 | 5.4 | 0.4384 | 6.07 | 0.297 | 3 | 0.68 | 13.1 | 11 | 0.73111 | 0.017 | 1 | 0.32 | 0.019 | 0.039 | 0.011 | 1 | 0.34 |  | 0.017 | 1 | 0.43 |  | 7.19 | 0.052 | 1 | 4.2 | 10.6 | 23 | 49 | 0.014 | 7.15 | 0.05 | 1 | 3.6 | 12.3 | 22 | 51 | 0.01 | 4.1 | 3.7 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 29780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 960 | 1020 | 2405 | 2315 | 2340 | 780 | 2030 | 1980 | 2400 | 0 | 3240 | 3240 | 3670 | 232 | 312 | 36 | 3920 | 800 | 585 | 130 | 178 | 18 | 1840 | 373 | 507
MAXIMUM | 6.53 | 20 | 17 | 12.2 | 132 | 191 | 13.2 | 0.52 | 0.042 | 6.11 | 11 | 0.079 | 6.12 | 11 |  | 6.03 | 11 |  | 6.1 | 0.345 | 4 | 0.76 | 13.5 | 10.3 | 0.72731 | 0.052 | 6.15 | 0.32 | 4 | 0.9 | 13.5 | 6 | 0.47377 | 6.12 | 0.44 | 4 | 0.9 | 14.5 | 11.2 | 0.74222 | 0.029 | 1 | 0.59 | 0.02 | 0.057 | 0.013 | 1 | 0.51 |  | 0.022 | 1 | 0.57 |  | 7.99 | 0.056 | 1 | 5 | 11.5 | 24 | 57 | 0.017 | 7.41 | 0.061 | 1 | 4.4 | 13.5 | 29 | 53 | 0.011 | 4.5 | 3.9 | 3.4 | [17 empty] | AVERAGE | 9926.6667 | [9 empty] | 306.6667 | 320 | 340 | 801.6667 | 771.6667 | 780 | 260 | 676.6667 | 660 | 800 |  | 1080 | 1080 | 1223.3333 | 77.3333 | 104 | 12 | 1306.6667 | 266.6667 | 195 | 43.3333 | 59.3333 | 6 | 613.3333 | 124.3333 | 169
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0267 |  | TOTAL AVG COAG ALK: |  |  |  | 9.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.44 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.55 | [5 empty] | 6.0933 |  |  |  |  | 0.029 |  |  |  |  | 0.55 | [6 empty] | 0.029 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 9910 | [9 empty] | 300 | 300 | 320 | 725 | 675 | 760 | 0 | 650 | 600 | 800 |  | 1080 | 1080 | 1220 | 76 | 104 | 12 | 1300 | 264 | 195 | 42 | 58 | 6 | 600 | 124 | 169
[90 empty] | MAXIMUM | 9950 | [9 empty] | 320 | 360 | 360 | 880 | 840 | 800 | 780 | 700 | 700 | 800 |  | 1080 | 1080 | 1230 | 78 | 104 | 12 | 1320 | 270 | 195 | 44 | 60 | 6 | 620 | 125 | 169
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.155 |  | TOTAL MGD: |  | 0.01 |  |  | FINISHED SOUTH 1 |  | START: | 23827120 |  | END: | 23827130 |  |  | Alum | 5692 | 10392 | 10392 | 8460 | 8460 | 0 | [44 empty] | 0.63 | 10.3 | 24.699 | 15.5604 | 6.04 | 12.5 | 15 | 1.0374
[73 empty] | FINISHED 2 | 11.758 |  | TOTAL MGD: |  | 11.145 |  |  | FINISHED SOUTH 2 |  | START: | 43978215 |  | END: | 43989360 |  |  | Caustic | 7318 | 8200 | 8200
[73 empty] | TOTAL RAW | 26.612 |  | TOTAL MGD: |  | 4.681 |  |  | FINISHED CONWAY |  | START: | 10282686 |  | END: | 10287367 |  |  | Hypochlorite | 18 |  | 47
[76 empty] | TOTAL MGD: |  | 7.077 |  |  | FINISHED PERRY |  | START: | 33934130 |  | END: | 33941207 |  |  | Phosphate | 2168
[76 empty] | TOTAL MGD: |  | 10.366 |  |  | RAW PLANT 1 |  | START: | 31070138 |  | END: | 31080504 |  |  | Fluoride | 3100 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.603 |  |  | RAW PLANT 2 |  | START: | 31016663 |  | END: | 31022266 |  |  | Cal~Flo | 17 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.643 |  |  | RAW PLANT 3 |  | START: | 7616070 |  | END: | 7626713 |  |  | Zinc | 791
[76 empty] | TOTAL MGD: |  | 0.895 |  |  | DECANT |  | START: | 1874690 |  | END: | 1875585 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.5426 |  |  | BLOW DOWN |  | START: | 9151.161 |  | END: | 9152.7036 |  |  | NH3 | 12.5 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827130
43989360
10287367
33941207
31080504
31022266
7626713
1875585
9152.7036
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 15
DATE: | 2019-01-15 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 20 |  | 16 | [33 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 4 |  | 5 | [23 empty] | 6:00 - 18:00 |  | 20 |  | 16 | [37 empty] | 6:00 - 18:00 |  | 20 |  | 16
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 4 |  | 5 | [37 empty] | 18:00 - 6:00 |  | 4 |  | 5
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-15 | [23 empty] | DATE: | 2019-01-15
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-15 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43480.0127 | 2,3,5 | 34 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.5538 | 1,3 | 11.4034 | 21.9571 | 2.2392 | 43480.0127 | 89.7401 | 8546.7482 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6285 | 1.6285 | 1.645 | 0.30425 | 0.30425 | 0.2472 | 0.19 | 0.24 | 0.24202 | 1.5218 | 2 | 0.069486 | 0.069486 | 0.069961 | 1.0934 | 0.54931 | 0.10572 | 3.991 | 0.73989 | 3.4694 | 1.0995 | 0.5461 | 0.09423 | 3.465 | 0.61484 | 5.3599 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.06 | 0.318 | 3 | 0.76 | 12.5 | 10 | 0.70962 |  | 6.12 | 0.234 | 3 | 0.82 | 12.8 | 6 | 0.47377 | 6.13 | 0.325 | 3 | 0.78 | 13 | 11 | 0.73111 | [13 empty] | 7.34 | 0.052 | 1 | 4.4 | 11 |  |  |  | 7.37 | 0.054 | 1 | 4.3 | 13 |  |  |  | 4.9 | 3.9 | 2.7 | [18 empty] | 9910 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 340 | 800 | 800 | 780 | 300 | 700 | 700 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1300 | 266 | 195 | 44 | 58 | 6 | 600 | 124 | 169 |  | 1:00 | 0.76 | 10 | 25.44 | 19.3344 | 6.06 | 12.5 | 15 | 1.289 | 10 | 6.5 | 0.58962 | 1:00 | 0.82 | 6 | 42.4 | 34.768 | 6.12 | 12.8 | 15 | 2.3179 | 10 | 6.5 | 0.35377 | 1:00 | 0.78 | 11 | 24.5455 | 19.1455 | 6.13 | 13 | 15 | 1.2764 | 10 | 6.5 | 0.61111
2:00 | [72 empty] | 43480.1168 | 2,3,5 | 34 | 10 | 6 | 11 | 27 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.5538 | 1,3 | 11.4034 | 21.9571 | 2.2392 | 43480.1168 | 89.7401 | 8546.7482 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6285 | 1.6285 | 1.645 | 0.30425 | 0.30425 | 0.2472 | 0.19 | 0.24 | 0.24202 | 1.5218 | 2 | 0.069486 | 0.069486 | 0.069961 | 1.0934 | 0.54931 | 0.10572 | 3.991 | 0.73989 | 3.4694 | 1.0995 | 0.5461 | 0.09423 | 3.465 | 0.61484 | 5.3599 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.46 | 18 | 15 | 11.8 | 120 | 188 | 13 | 0.467 |  | 6.07 | 10 | 0.053 | 6.09 | 10 |  | 6.01 | 10 | [8 empty] | 0.038 | [14 empty] | 0.02 | 1 | 0.48 |  | 0.041 | 0.016 | 1 | 0.44 |  | 0.016 | 1 | 0.55 | [38 empty] | 9910 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 340 | 800 | 800 | 780 | 300 | 700 | 700 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1300 | 266 | 195 | 44 | 58 | 6 | 600 | 124 | 169 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43480.3252 | 2,3,5 | 31 | 9 | 6 | 10 | 25 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 12.24 | 1,3 | 11.2291 | 23.4691 | 2.2392 | 43480.3252 | 89.9756 | 8669.723 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 1.3616 | 1.6868 | 0.37186 | 0.32115 | 0.50708 | 0.19016 | 0.2434 | 0.2434 | 1.5218 | 2.5 | 0.069516 | 0.069516 | 0.068863 | 1.0818 | 0.55031 | 0.10199 | 4.0021 | 0.72451 | 3.0895 | 1.0647 | 0.54709 | 0.10646 | 3.5271 | 0.60023 | 4.7607 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.25 | 0.052 | 1 | 4.2 | 11 |  |  |  | 7.28 | 0.055 | 1 | 4.2 | 13 |  |  |  | 4.7 | 3.9 | 3.3 | [18 empty] | 9200 | [6 empty] | 0 | 0 | 0 | 300 | 260 | 360 | 880 | 760 | 800 | 300 | 640 | 640 | 800 |  | 1120 | 1120 | 1240 | 80 | 108 | 12 | 1320 | 270 | 180 | 44 | 60 | 7 | 620 | 125 | 155 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 19:20 | 2,3,5 | 31 | 10.5 | 6 | 11.5 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 12.24 | 1,3 | 11.2291 | 23.4691 | 2.196 | 19:20 | 89.6787 | 7993.3616 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 1.571 | 1.4994 | 0.29701 | 0.26079 | 0.31693 | 0.31693 | 0.2811 | 0.2811 | 1.5218 | 2.5 | 0.070137 | 0.070137 | 0.069418 | 1.0818 | 0.55031 | 0.10199 | 3.9876 | 0.74061 | 3.6902 | 1.1131 | 0.54709 | 0.12167 | 3.4991 | 0.59543 | 5.4056 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.5 | 17 | 16 | 12 | 127 | 189 | 12.5 | 0.511 |  | 5.97 | 8 | 0.07 | 5.96 | 9 |  | 5.94 | 8 | [8 empty] | 0.049 | [14 empty] | 0.021 | 1 | 0.42 |  | 0.05 | 0.02 | 1 | 0.32 |  | 0.016 | 1 | 0.55 | [38 empty] | 10270 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 320 | 820 | 720 | 500 | 500 | 850 | 850 | 800 |  | 1130 | 1130 | 1250 | 80 | 108 | 12 | 1350 | 276 | 215 | 46 | 60 | 8 | 610 | 124 | 176 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.035 | [9 empty] | 6.1 | 0.27 | 4 | 0.72 | 11.9 | 8.7 | 0.63297 |  | 6.14 | 0.23 | 3 | 0.84 | 12.1 | 5.3 | 0.4325 | 6.12 | 0.266 | 4 | 0.81 | 12.9 | 9.5 | 0.64778 |  |  |  | 0.016 | [9 empty] | 7.66 | 0.053 | 1 | 4.7 | 10.6 | 21 | 52 | 0.012 | 7.86 | 0.054 | 1 | 5 | 12.5 | 20 | 50 | 0.012 | 4.7 | 3.8 | 3.3 | [55 empty] | 9:00 | 0.72 | 8.7 | 29.2414 | 21.0538 | 6.1 | 11.9 | 15 | 1.4036 | 10 | 6.5 | 0.51297 | 9:00 | 0.84 | 5.3 | 48 | 40.32 | 6.14 | 12.1 | 15 | 2.688 | 10 | 6.5 | 0.3125 | 9:00 | 0.81 | 9.5 | 28.4211 | 23.0211 | 6.12 | 12.9 | 15 | 1.5347 | 10 | 6.5 | 0.52778
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.51 | 18 | 16 | 12.2 | 125 | 190 | 12.6 | 0.489 |  | 6.08 | 9 | 0.062 | 6.07 | 9 |  | 6.02 | 9 | [8 empty] | 0.047 | [14 empty] | 0.023 | 1 | 0.48 |  | 0.042 | 0.016 | 1 | 0.55 |  | 0.06 | 1 | 0.61 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.11 | 0.343 | 4 | 0.67 | 12.1 | 9.2 | 0.66245 |  | 6.15 | 0.344 | 3 | 0.85 | 12.3 | 5.3 | 0.4325 | 6.3 | 0.435 | 4 | 0.79 | 12.7 | 9.9 | 0.67 | [13 empty] | 7.7 | 0.051 | 1 | 4.6 | 10.4 |  |  |  | 7.45 | 0.052 | 1 | 4.2 | 12.6 |  |  |  | 4.9 | 4.1 | 2.5 | [55 empty] | 13:00 | 0.67 | 9.2 | 27.6522 | 18.527 | 6.11 | 12.1 | 15 | 1.2351 | 10 | 6.5 | 0.54245 | 13:00 | 0.85 | 5.3 | 48 | 40.8 | 6.15 | 12.3 | 15 | 2.72 | 10 | 6.5 | 0.3125 | 13:00 | 0.79 | 9.9 | 27.2727 | 21.5455 | 6.3 | 12.7 | 15 | 1.4364 | 10 | 6.5 | 0.55
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.47 | 15 | 17 | 12.1 | 129 | 190 | 12.3 | 0.504 |  | 6.12 | 8 | 0.07 | 6.13 | 9 |  | 6.05 | 10 | [8 empty] | 0.044 | [14 empty] | 0.029 | 1 | 0.36 |  | 0.046 | 0.011 | 1 | 0.37 |  | 0.04 | 1 | 0.57 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.45 | 0.05 | 1 | 4.5 | 10.4 |  |  |  | 7.31 | 0.055 | 1 | 4.1 | 12.6 |  |  |  | 5 | 4.1 | 3.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.5 | 15 | 16 | 11.5 | 131 | 191 | 11.9 | 0.52 |  | 6.09 | 10 | 0.071 | 6.08 | 10 |  | 6.02 | 10 | [8 empty] | 0.048 | [14 empty] | 0.022 | 1 | 0.39 |  | 0.05 | 0.017 | 1 | 0.39 |  | 0.035 | 1 | 0.58 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.034 | [9 empty] | 6.15 | 0.322 | 4 | 0.68 | 11.5 | 10.5 | 0.7391 |  | 6.19 | 0.325 | 4 | 0.81 | 11.4 | 6 | 0.47377 | 6.19 | 0.494 | 4 | 0.93 | 12.4 | 11.5 | 0.75889 |  |  |  | 0.014 | [9 empty] | 7.37 | 0.051 | 1 | 4.7 | 10.5 | 22 | 49 | 0.019 | 7.3 | 0.055 | 1 | 4.1 | 12 | 21 | 55 | 0.014 | 4.9 | 4.1 | 3.2 | [55 empty] | 21:00 | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.15 | 11.5 | 15 | 1.0984 | 10 | 6.5 | 0.6191 | 21:00 | 0.81 | 6 | 42.4 | 34.344 | 6.19 | 11.4 | 15 | 2.2896 | 10 | 6.5 | 0.35377 | 21:00 | 0.93 | 11.5 | 23.4783 | 21.8348 | 6.19 | 12.4 | 15 | 1.4557 | 10 | 6.5 | 0.63889
22:00 | [72 empty] | DOSE |  | TOTAL | 39.5 | 24 | 43.5 | 107 | 33.4 | 33.4 | 37.4 | 104.2 | 0 | 45.5875 | 0 | 45.265 | 90.8525 | 8.9136 | TOTAL | 359.1344 | 33756.581 | 0 | 2664.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3991 | 6.1896 | 6.4762 | 1.2774 | 1.1904 | 1.3184 | 0.88708 | 1.0045 | 1.0085 | 6.0872 | 9 | 0.27862 | 0.27862 | 0.2782 | 4.3503 | 2.1992 | 0.41543 | 15.9716 | 2.9449 | 13.7183 | 4.3768 | 2.1864 | 0.4166 | 13.9563 | 2.4253 | 20.8861 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 18 | 15 | 11.9 | 130 | 190 | 11.8 | 0.52 |  | 6 | 10 | 0.082 | 5.98 | 10 |  | 5.95 | 10 | [8 empty] | 0.054 | [14 empty] | 0.022 | 1 | 0.38 |  | 0.054 | 0.018 | 1 | 0.56 |  | 0.03 | 1 | 0.66 | [22 empty] | AVERAGE | 9.875 | 6 | 10.875 | 26.75 | 8.35 | 8.35 | 9.35 | 26.05 |  | 11.3969 |  | 11.3162 | 22.7131 | 2.2284 | AVERAGE | 89.7836 | 8439.1453 |  | 666.0793 | 0 | 0 | 0 |  |  |  | 1.5998 | 1.5474 | 1.6191 | 0.31934 | 0.29761 | 0.3296 | 0.22177 | 0.25113 | 0.25213 | 1.5218 | 2.25 | 0.069656 | 0.069656 | 0.069551 | 1.0876 | 0.54981 | 0.10386 | 3.9929 | 0.73623 | 3.4296 | 1.0942 | 0.5466 | 0.10415 | 3.4891 | 0.60634 | 5.2215 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.97 | 101 | 95 | 71.5 | 762 | 1138 | 74.1 | 3.011 | 0.069 | 36.33 | 55 | 0.408 | 36.31 | 57 | 0 | 35.99 | 57 | 0 | 24.42 | 1.253 | 15 | 2.83 | 48 | 38.4 | 2.7442 | 0.28 | 24.6 | 1.133 | 13 | 3.32 | 48.6 | 22.6 | 1.8125 | 24.74 | 1.52 | 15 | 3.31 | 51 | 41.9 | 2.8078 | 0.137 | 6 | 2.51 | 0.03 | 0.283 | 0.098 | 6 | 2.63 | 0 | 0.197 | 6 | 3.52 | 0 | 44.77 | 0.309 | 6 | 27.1 | 63.9 | 43 | 101 | 0.031 | 44.57 | 0.325 | 6 | 25.9 | 75.7 | 41 | 105 | 0.026 | 29.1 | 23.9 | 18.4 |  |  | MINIMUM | 9 | 6 | 10 | 25 | 8.2 | 8.2 | 9.2 | 25.6 |  | 10.5538 |  | 11.2291 | 21.9571 | 2.196 | MINIMUM | 89.6787 | 7993.3616 |  | 666.0793 | [6 empty] | 1.571 | 1.3616 | 1.4994 | 0.29701 | 0.26079 | 0.2472 | 0.19 | 0.24 | 0.24202 | 1.5218 | 2 | 0.069486 | 0.069486 | 0.068863 | 1.0818 | 0.54931 | 0.10199 | 3.9876 | 0.72451 | 3.0895 | 1.0647 | 0.5461 | 0.09423 | 3.465 | 0.59543 | 4.7607 |  | MIN | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.15 | 11.5 | 15 | 1.0984 |  |  |  | MIN | 0.81 | 6 | 42.4 | 34.344 | 6.19 | 11.4 | 15 | 2.2896 |  |  |  | MIN | 0.78 | 11 | 24.5455 | 19.1455 | 6.13 | 13 | 15 | 1.2764 |  |  |  | 1.0984
AVERAGE | 6.495 | 16.8333 | 15.8333 | 11.9167 | 127 | 189.6667 | 12.35 | 0.50183 | 0.0345 | 6.055 | 9.1667 | 0.068 | 6.0517 | 9.5 |  | 5.9983 | 9.5 |  | 6.105 | 0.31325 | 3.75 | 0.7075 | 12 | 9.6 | 0.68604 | 0.046667 | 6.15 | 0.28325 | 3.25 | 0.83 | 12.15 | 5.65 | 0.45314 | 6.185 | 0.38 | 3.75 | 0.8275 | 12.75 | 10.475 | 0.70194 | 0.022833 | 1 | 0.41833 | 0.015 | 0.047167 | 0.016333 | 1 | 0.43833 |  | 0.032833 | 1 | 0.58667 |  | 7.4617 | 0.0515 | 1 | 4.5167 | 10.65 | 21.5 | 50.5 | 0.0155 | 7.4283 | 0.054167 | 1 | 4.3167 | 12.6167 | 20.5 | 52.5 | 0.013 | 4.85 | 3.9833 | 3.0667 |  |  | MAXIMUM | 10.5 | 6 | 11.5 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 12.24 |  | 11.4034 | 23.4691 | 2.2392 | MAXIMUM | 89.9756 | 8669.723 |  | 666.0793 | [6 empty] | 1.6285 | 1.6285 | 1.6868 | 0.37186 | 0.32115 | 0.50708 | 0.31693 | 0.2811 | 0.2811 | 1.5218 | 2.5 | 0.070137 | 0.070137 | 0.069961 | 1.0934 | 0.55031 | 0.10572 | 4.0021 | 0.74061 | 3.6902 | 1.1131 | 0.54709 | 0.12167 | 3.5271 | 0.61484 | 5.4056
MINIMUM | 6.46 | 15 | 15 | 11.5 | 120 | 188 | 11.8 | 0.467 | 0.034 | 5.97 | 8 | 0.053 | 5.96 | 9 |  | 5.94 | 8 |  | 6.06 | 0.27 | 3 | 0.67 | 11.5 | 8.7 | 0.63297 | 0.038 | 6.12 | 0.23 | 3 | 0.81 | 11.4 | 5.3 | 0.4325 | 6.12 | 0.266 | 3 | 0.78 | 12.4 | 9.5 | 0.64778 | 0.02 | 1 | 0.36 | 0.014 | 0.041 | 0.011 | 1 | 0.32 |  | 0.016 | 1 | 0.55 |  | 7.25 | 0.05 | 1 | 4.2 | 10.4 | 21 | 49 | 0.012 | 7.28 | 0.052 | 1 | 4.1 | 12 | 20 | 50 | 0.012 | 4.7 | 3.8 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 39290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1160 | 1360 | 3300 | 3080 | 2860 | 1400 | 2890 | 2890 | 3200 | 0 | 4410 | 4410 | 4930 | 316 | 424 | 48 | 5270 | 1078 | 785 | 178 | 236 | 27 | 2430 | 497 | 669
MAXIMUM | 6.53 | 18 | 17 | 12.2 | 131 | 191 | 13 | 0.52 | 0.035 | 6.12 | 10 | 0.082 | 6.13 | 10 |  | 6.05 | 10 |  | 6.15 | 0.343 | 4 | 0.76 | 12.5 | 10.5 | 0.7391 | 0.054 | 6.19 | 0.344 | 4 | 0.85 | 12.8 | 6 | 0.47377 | 6.3 | 0.494 | 4 | 0.93 | 13 | 11.5 | 0.75889 | 0.029 | 1 | 0.48 | 0.016 | 0.054 | 0.02 | 1 | 0.56 |  | 0.06 | 1 | 0.66 |  | 7.7 | 0.053 | 1 | 4.7 | 11 | 22 | 52 | 0.019 | 7.86 | 0.055 | 1 | 5 | 13 | 21 | 55 | 0.014 | 5 | 4.1 | 3.4 | [17 empty] | AVERAGE | 9822.5 | [9 empty] | 300 | 290 | 340 | 825 | 770 | 715 | 350 | 722.5 | 722.5 | 800 |  | 1102.5 | 1102.5 | 1232.5 | 79 | 106 | 12 | 1317.5 | 269.5 | 196.25 | 44.5 | 59 | 6.75 | 607.5 | 124.25 | 167.25
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.035 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.494 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.67 | [5 empty] | 6.1467 |  |  |  |  | 0.06 |  |  |  |  | 0.67 | [6 empty] | 0.06 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 9200 | [9 empty] | 300 | 260 | 320 | 800 | 720 | 500 | 300 | 640 | 640 | 800 |  | 1080 | 1080 | 1220 | 78 | 104 | 12 | 1300 | 266 | 180 | 44 | 58 | 6 | 600 | 124 | 155
[90 empty] | MAXIMUM | 10270 | [9 empty] | 300 | 300 | 360 | 880 | 800 | 800 | 500 | 850 | 850 | 800 |  | 1130 | 1130 | 1250 | 80 | 108 | 12 | 1350 | 276 | 215 | 46 | 60 | 8 | 620 | 125 | 176
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.652 |  | TOTAL MGD: |  | 0.012 |  |  | FINISHED SOUTH 1 |  | START: | 23827130 |  | END: | 23827142 |  |  | Alum | 7660 | 10174 | 10174 | 10295 | 10295 | 0 | [44 empty] | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.15 | 11.5 | 15 | 1.0984
[73 empty] | FINISHED 2 | 11.421 |  | TOTAL MGD: |  | 10.64 |  |  | FINISHED SOUTH 2 |  | START: | 43989360 |  | END: | 44000000 |  |  | Caustic | 7283 | 8200 | 8200
[73 empty] | TOTAL RAW | 26.769 |  | TOTAL MGD: |  | 4.573 |  |  | FINISHED CONWAY |  | START: | 10287367 |  | END: | 10291940 |  |  | Hypochlorite | 17 |  | 39
[76 empty] | TOTAL MGD: |  | 6.848 |  |  | FINISHED PERRY |  | START: | 33941207 |  | END: | 33948055 |  |  | Phosphate | 2156
[76 empty] | TOTAL MGD: |  | 9.846 |  |  | RAW PLANT 1 |  | START: | 31080504 |  | END: | 31090350 |  |  | Fluoride | 3000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.886 |  |  | RAW PLANT 2 |  | START: | 31022266 |  | END: | 31028152 |  |  | Cal~Flo | 13.1 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.037 |  |  | RAW PLANT 3 |  | START: | 7626713 |  | END: | 7637750 |  |  | Zinc | 781
[76 empty] | TOTAL MGD: |  | 1.079 |  |  | DECANT |  | START: | 1875585 |  | END: | 1876664 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.1015 |  |  | BLOW DOWN |  | START: | 9152.7036 |  | END: | 9153.8051 |  |  | NH3 | 12 |  | BI-SUL | 1100
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827142
44000000
10291940
33948055
31090350
31028152
7637750
1876664
9153.8051
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 16
DATE: | 2019-01-16 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 3 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 3 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 3
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-16 | [23 empty] | DATE: | 2019-01-16
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-16 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43481.0139 | 2,3,5 | 31 | 10.5 | 6 | 11.5 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 12.24 | 1,3 | 11.2291 | 23.4691 | 2.196 |  | 89.6787 | 7993.3616 | 0 | 666.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 1.571 | 1.571 | 1.4994 | 0.29701 | 0.26079 | 0.31693 | 0.31693 | 0.2811 | 0.2811 | 1.5218 | 2.5 | 0.070137 | 0.070137 | 0.069418 | 1.0818 | 0.55031 | 0.10199 | 3.9876 | 0.74061 | 3.6902 | 1.1131 | 0.54709 | 0.12167 | 3.4991 | 0.59543 | 5.4056 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.05 | 0.355 | 3 | 0.7 | 12 | 10.5 | 0.7391 |  | 6.1 | 0.252 | 3 | 0.75 | 12 | 6 | 0.47377 | 6.03 | 0.478 | 3 | 0.8 | 13 | 11.5 | 0.75889 | [13 empty] | 7.33 | 0.05 | 1 | 4.5 | 10.5 |  |  |  | 7.18 | 0.052 | 1 | 4 | 12 |  |  |  | 4.8 | 4.3 | 2.2 | [18 empty] | 10270 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 320 | 820 | 720 | 500 | 500 | 850 | 850 | 800 |  | 1130 | 1130 | 1250 | 80 | 108 | 12 | 1350 | 276 | 215 | 46 | 60 | 8 | 610 | 124 | 176 |  | 1:00 | 0.7 | 10.5 | 24.2286 | 16.96 | 6.05 | 12 | 15 | 1.1307 | 10 | 6.5 | 0.6191 | 1:00 | 0.75 | 6 | 42.4 | 31.8 | 6.1 | 12 | 15 | 2.12 | 10 | 6.5 | 0.35377 | 1:00 | 0.8 | 11.5 | 23.4783 | 18.7826 | 6.03 | 13 | 15 | 1.2522 | 10 | 6.5 | 0.63889
2:00 | [72 empty] | 43481.369 | 2,3,5 | 37 | 10.5 | 6 | 11.5 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 10.9483 | 1,3 | 15.0494 | 25.9978 | 1.7366 | 43481.369 | 88.6308 | 8731.2104 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6234 | 1.571 | 1.6399 | 0.32598 | 0.29882 | 0.38031 | 0.19016 | 0.27118 | 0.27779 | 1.5218 | 3 | 0.070137 | 0.070137 | 0.069418 | 1.0953 | 0.55031 | 0.093491 | 3.9752 | 0.73793 | 3.6902 | 1.0889 | 0.54709 | 0.10646 | 3.7212 | 0.60023 | 5.4056 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.48 | 18 | 16 | 12.2 | 122 | 190 | 12.2 | 0.474 |  | 6.03 | 10 | 0.056 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.039 | [14 empty] | 0.027 | 1 | 0.4 |  | 0.043 | 0.017 | 1 | 0.52 |  | 0.027 | 1 | 0.6 | [38 empty] | 10150 | [6 empty] | 0 | 0 | 0 | 310 | 300 | 350 | 900 | 825 | 600 | 300 | 820 | 840 | 800 |  | 1130 | 1130 | 1250 | 81 | 108 | 11 | 1310 | 275 | 215 | 45 | 60 | 7 | 650 | 125 | 176 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43481.4486 | 2,3,5 | 30 | 9.5 | 6 | 10.5 | 26 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 10.9483 | 1,3 | 15.0494 | 25.9978 | 1.7366 | 43481.4486 | 88.5838 | 8731.2104 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.4838 | 1.5004 | 0.30425 | 0.28023 | 0.31693 | 0.1648 | 0.26803 | 0.27527 | 1.4267 | 3 | 0.070344 | 0.070344 | 0.071134 | 1.1052 | 0.54972 | 0.10188 | 4.0275 | 0.74567 | 3.7034 | 1.1107 | 0.53531 | 0.097407 | 3.5216 | 0.58944 | 5.4094 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.28 | 0.048 | 1 | 4.4 | 10.5 |  |  |  | 7.21 | 0.05 | 1 | 4 | 12 |  |  |  | 4.8 | 4.2 | 2.2 | [18 empty] | 9420 | [6 empty] | 0 | 0 | 0 | 280 | 260 | 300 | 760 | 700 | 500 | 260 | 740 | 760 | 750 |  | 1040 | 1040 | 1200 | 75 | 99 | 11 | 1220 | 255 | 198 | 43 | 55 | 6 | 570 | 115 | 165 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43481.6187 | 2,3,5 | 30 | 9 | 6 | 10.5 | 25.5 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 10.9483 | 1,3 | 15.0494 | 25.9978 | 1.7366 | 43481.6187 | 90.3207 | 8731.2104 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.4838 | 1.5004 | 0.32115 | 0.2958 | 0.31693 | 0.1648 | 0.26803 | 0.27527 | 1.4267 | 3 | 0.070344 | 0.070344 | 0.071134 | 1.1052 | 0.54972 | 0.10188 | 4.0275 | 0.74567 | 3.7034 | 1.1107 | 0.53531 | 0.097407 | 3.5216 | 0.58944 | 5.4094 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.54 | 16 | 17 | 12 | 134 | 191 | 11.7 | 0.541 |  | 6 | 8 | 0.056 | 6.01 | 8 |  | 5.96 | 8 | [8 empty] | 0.046 | [14 empty] | 0.027 | 1 | 0.4 |  | 0.047 | 0.018 | 1 | 0.7 |  | 0.023 | 1 | 0.39 | [38 empty] | 9420 | [6 empty] | 0 | 0 | 0 | 280 | 260 | 300 | 760 | 700 | 500 | 260 | 740 | 760 | 750 |  | 1040 | 1040 | 1200 | 75 | 99 | 11 | 1220 | 255 | 198 | 43 | 55 | 6 | 570 | 115 | 165 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43481.8322 | 2,3,5 | 30 | 9 | 6 | 10.5 | 25.5 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 8.5421 | 1,3 | 15.5477 | 24.0898 | 1.7366 | 43481.8322 | 90.129 | 8362.286 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.3696 | 1.6005 | 0.33806 | 0.2958 | 0.21551 | 0.15212 | 0.26079 | 0.26803 | 1.4267 | 1.5 | 0.070344 | 0.070344 | 0.069949 | 1.0905 | 0.54972 | 0.10188 | 3.7428 | 0.65794 | 3.4602 | 1.0849 | 0.53531 | 0.097407 | 3.4928 | 0.56381 | 5.4094 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.068 | [9 empty] | 6.05 | 0.364 | 4 | 0.66 | 11.2 | 10.5 | 0.7391 |  | 6.14 | 0.244 | 4 | 0.89 | 12.1 | 6 | 0.47377 | 6.09 | 0.525 | 4 | 0.72 | 12.4 | 11.5 | 0.75889 |  |  |  | 0.014 | [9 empty] | 7.44 | 0.055 | 1 | 4.7 | 10.8 | 24 | 60 | 0.013 | 7.19 | 0.056 | 1 | 4 | 11.9 | 26 | 58 | 0.017 | 4.9 | 4 | 3.2 | [18 empty] | 9400 | [6 empty] | 0 | 0 | 0 | 280 | 240 | 320 | 800 | 700 | 340 | 240 | 720 | 740 | 750 |  | 1040 | 1040 | 1180 | 74 | 99 | 11 | 1150 | 225 | 185 | 42 | 55 | 6 | 580 | 110 | 165 |  | 9:00 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.05 | 11.2 | 15 | 1.0661 | 10 | 6.5 | 0.6191 | 9:00 | 0.89 | 6 | 42.4 | 37.736 | 6.14 | 12.1 | 15 | 2.5157 | 10 | 6.5 | 0.35377 | 9:00 | 0.72 | 11.5 | 23.4783 | 16.9043 | 6.09 | 12.4 | 15 | 1.127 | 10 | 6.5 | 0.63889
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.56 | 16 | 19 | 12.1 | 134 | 190 | 12.2 | 0.539 |  | 6.08 | 8 | 0.055 | 6.09 | 8 |  | 6.05 | 8 | [8 empty] | 0.048 | [14 empty] | 0.021 | 1 | 0.39 |  | 0.047 | 0.016 | 1 | 0.79 |  | 0.021 | 1 | 0.57 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.17 | 0.325 | 4 | 0.6 | 12 | 9.5 | 0.68014 |  | 6.2 | 0.283 | 4 | 0.92 | 13 | 6 | 0.47377 | 6.14 | 0.444 | 4 | 0.74 | 13 | 10.5 | 0.70333 | [13 empty] | 7.56 | 0.059 | 1 | 4.9 | 10.2 |  |  |  | 7.18 | 0.053 | 1 | 4.3 | 13.3 |  |  |  | 4.9 | 3.9 | 2.3 | [55 empty] | 13:00 | 0.6 | 9.5 | 26.7789 | 16.0674 | 6.17 | 12 | 15 | 1.0712 | 10 | 6.5 | 0.56014 | 13:00 | 0.92 | 6 | 42.4 | 39.008 | 6.2 | 13 | 15 | 2.6005 | 10 | 6.5 | 0.35377 | 13:00 | 0.74 | 10.5 | 25.7143 | 19.0286 | 6.14 | 13 | 15 | 1.2686 | 10 | 6.5 | 0.58333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.56 | 16 | 18 | 12 | 135 | 195 | 12.2 | 0.537 |  | 6.13 | 8 | 0.053 | 6.09 | 8 |  | 6.07 | 8 | [8 empty] | 0.044 | [14 empty] | 0.02 | 1 | 0.4 |  | 0.043 | 0.012 | 1 | 0.65 |  | 0.023 | 1 | 0.54 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.68 | 0.058 | 1 | 4.8 | 10.5 |  |  |  | 7.55 | 0.056 | 1 | 4.5 | 12.5 |  |  |  | 4.9 | 3.9 | 2.3 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.48 | 15 | 15 | 12 | 129 | 191 | 12.1 | 0.52 |  | 6.09 | 10 | 0.057 | 6.09 | 10 |  | 6.06 | 10 | [8 empty] | 0.052 | [14 empty] | 0.02 | 1 | 0.31 |  | 0.051 | 0.021 | 1 | 0.45 |  | 0.021 | 1 | 0.52 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.037 | [9 empty] | 6.24 | 0.424 | 5 | 0.7 | 11.8 | 9 | 0.65066 |  | 6.22 | 0.33 | 5 | 0.83 | 12.6 | 6 | 0.47377 | 6.19 | 0.443 | 5 | 0.72 | 13.2 | 10.5 | 0.70333 |  |  |  | 0.009 | [9 empty] | 7.54 | 0.063 | 1 | 4.9 | 10.4 | 20 | 47 | 0.011 | 7.33 | 0.059 | 1 | 4.2 | 11.8 | 22 | 50 | 0.015 | 5 | 3.9 | 2.5 | [55 empty] | 21:00 | 0.7 | 9 | 28.2667 | 19.7867 | 6.24 | 11.8 | 15 | 1.3191 | 10 | 6.5 | 0.53066 | 21:00 | 0.83 | 6 | 42.4 | 35.192 | 6.22 | 12.6 | 15 | 2.3461 | 10 | 6.5 | 0.35377 | 21:00 | 0.72 | 10.5 | 25.7143 | 18.5143 | 6.19 | 13.2 | 15 | 1.2343 | 10 | 6.5 | 0.58333
22:00 | [72 empty] | DOSE |  | TOTAL | 48.5 | 30 | 54.5 | 133 | 40.4 | 40.4 | 45.7 | 126.5 | 0 | 53.627 | 0 | 71.9251 | 125.5522 | 9.1426 | TOTAL | 447.3429 | 42549.2788 | 0 | 3346.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9881 | 7.4792 | 7.7406 | 1.5864 | 1.4314 | 1.5466 | 0.98881 | 1.3491 | 1.3775 | 7.3236 | 13 | 0.3513 | 0.3513 | 0.35105 | 5.4781 | 2.7498 | 0.50113 | 19.7606 | 3.6278 | 18.2474 | 5.5083 | 2.7001 | 0.52036 | 17.7563 | 2.9383 | 27.0396 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.48 | 16 | 15 | 12.3 | 123 | 183 | 12.2 | 0.498 |  | 6.12 | 10 | 0.054 | 6.11 | 9 |  | 6.06 | 10 | [8 empty] | 0.047 | [14 empty] | 0.017 | 1 | 0.37 |  | 0.045 | 0.021 | 1 | 0.49 |  | 0.02 | 1 | 0.67 | [22 empty] | AVERAGE | 9.7 | 6 | 10.9 | 26.6 | 8.08 | 8.08 | 9.14 | 25.3 |  | 10.7254 |  | 14.385 | 25.1104 | 1.8285 | AVERAGE | 89.4686 | 8509.8558 |  | 669.2511 | 0 | 0 | 0 |  |  |  | 1.5976 | 1.4958 | 1.5481 | 0.31729 | 0.28629 | 0.30932 | 0.19776 | 0.26983 | 0.27549 | 1.4647 | 2.6 | 0.070261 | 0.070261 | 0.070211 | 1.0956 | 0.54996 | 0.10023 | 3.9521 | 0.72556 | 3.6495 | 1.1017 | 0.54002 | 0.10407 | 3.5513 | 0.58767 | 5.4079 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.1 | 97 | 100 | 72.6 | 777 | 1140 | 72.6 | 3.109 | 0.105 | 36.45 | 54 | 0.331 | 36.44 | 53 | 0 | 36.2 | 54 | 0 | 24.51 | 1.468 | 16 | 2.66 | 47 | 39.5 | 2.809 | 0.276 | 24.66 | 1.109 | 16 | 3.39 | 49.7 | 24 | 1.8951 | 24.45 | 1.89 | 16 | 2.98 | 51.6 | 44 | 2.9244 | 0.132 | 6 | 2.27 | 0.023 | 0.276 | 0.105 | 6 | 3.6 | 0 | 0.135 | 6 | 3.29 | 0 | 44.83 | 0.333 | 6 | 28.2 | 62.9 | 44 | 107 | 0.024 | 43.64 | 0.326 | 6 | 25 | 73.5 | 48 | 108 | 0.032 | 29.3 | 24.2 | 14.7 |  |  | MINIMUM | 9 | 6 | 10.5 | 25.5 | 7.8 | 7.8 | 8.9 | 24.5 |  | 8.5421 |  | 11.2291 | 23.4691 | 1.7366 | MINIMUM | 88.5838 | 7993.3616 |  | 586.7841 | [6 empty] | 1.571 | 1.3696 | 1.4994 | 0.29701 | 0.26079 | 0.21551 | 0.15212 | 0.26079 | 0.26803 | 1.4267 | 1.5 | 0.070137 | 0.070137 | 0.069418 | 1.0818 | 0.54972 | 0.093491 | 3.7428 | 0.65794 | 3.4602 | 1.0849 | 0.53531 | 0.097407 | 3.4928 | 0.56381 | 5.4056 |  | MIN | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.05 | 11.2 | 15 | 1.0661 |  |  |  | MIN | 0.75 | 6 | 42.4 | 31.8 | 6.1 | 12 | 15 | 2.12 |  |  |  | MIN | 0.72 | 11.5 | 23.4783 | 16.9043 | 6.09 | 12.4 | 15 | 1.127 |  |  |  | 1.0661
AVERAGE | 6.5167 | 16.1667 | 16.6667 | 12.1 | 129.5 | 190 | 12.1 | 0.51817 | 0.0525 | 6.075 | 9 | 0.055167 | 6.0733 | 8.8333 |  | 6.0333 | 9 |  | 6.1275 | 0.367 | 4 | 0.665 | 11.75 | 9.875 | 0.70225 | 0.046 | 6.165 | 0.27725 | 4 | 0.8475 | 12.425 | 6 | 0.47377 | 6.1125 | 0.4725 | 4 | 0.745 | 12.9 | 11 | 0.73111 | 0.022 | 1 | 0.37833 | 0.0115 | 0.046 | 0.0175 | 1 | 0.6 |  | 0.0225 | 1 | 0.54833 |  | 7.4717 | 0.0555 | 1 | 4.7 | 10.4833 | 22 | 53.5 | 0.012 | 7.2733 | 0.054333 | 1 | 4.1667 | 12.25 | 24 | 54 | 0.016 | 4.8833 | 4.0333 | 2.45 |  |  | MAXIMUM | 10.5 | 6 | 11.5 | 28 | 8.5 | 8.5 | 9.5 | 26.5 |  | 12.24 |  | 15.5477 | 25.9978 | 2.196 | MAXIMUM | 90.3207 | 8731.2104 |  | 697.7974 | [6 empty] | 1.6234 | 1.571 | 1.6399 | 0.33806 | 0.29882 | 0.38031 | 0.31693 | 0.2811 | 0.2811 | 1.5218 | 3 | 0.070344 | 0.070344 | 0.071134 | 1.1052 | 0.55031 | 0.10199 | 4.0275 | 0.74567 | 3.7034 | 1.1131 | 0.54709 | 0.12167 | 3.7212 | 0.60023 | 5.4094
MINIMUM | 6.48 | 15 | 15 | 12 | 122 | 183 | 11.7 | 0.474 | 0.037 | 6 | 8 | 0.053 | 6.01 | 8 |  | 5.96 | 8 |  | 6.05 | 0.325 | 3 | 0.6 | 11.2 | 9 | 0.65066 | 0.039 | 6.1 | 0.244 | 3 | 0.75 | 12 | 6 | 0.47377 | 6.03 | 0.443 | 3 | 0.72 | 12.4 | 10.5 | 0.70333 | 0.017 | 1 | 0.31 | 0.009 | 0.043 | 0.012 | 1 | 0.45 |  | 0.02 | 1 | 0.39 |  | 7.28 | 0.048 | 1 | 4.4 | 10.2 | 20 | 47 | 0.011 | 7.18 | 0.05 | 1 | 4 | 11.8 | 22 | 50 | 0.015 | 4.8 | 3.9 | 2.2 | [15 empty] | MIL/MIN |  | TOTAL | 48660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1450 | 1360 | 1590 | 4040 | 3645 | 2440 | 1560 | 3870 | 3950 | 3850 | 0 | 5380 | 5380 | 6080 | 385 | 513 | 56 | 6250 | 1286 | 1011 | 219 | 285 | 33 | 2980 | 589 | 847
MAXIMUM | 6.56 | 18 | 19 | 12.3 | 135 | 195 | 12.2 | 0.541 | 0.068 | 6.13 | 10 | 0.057 | 6.11 | 10 |  | 6.07 | 10 |  | 6.24 | 0.424 | 5 | 0.7 | 12 | 10.5 | 0.7391 | 0.052 | 6.22 | 0.33 | 5 | 0.92 | 13 | 6 | 0.47377 | 6.19 | 0.525 | 5 | 0.8 | 13.2 | 11.5 | 0.75889 | 0.027 | 1 | 0.4 | 0.014 | 0.051 | 0.021 | 1 | 0.79 |  | 0.027 | 1 | 0.67 |  | 7.68 | 0.063 | 1 | 4.9 | 10.8 | 24 | 60 | 0.013 | 7.55 | 0.059 | 1 | 4.5 | 13.3 | 26 | 58 | 0.017 | 5 | 4.3 | 3.2 | [17 empty] | AVERAGE | 9732 | [9 empty] | 290 | 272 | 318 | 808 | 729 | 488 | 312 | 774 | 790 | 770 |  | 1076 | 1076 | 1216 | 77 | 102.6 | 11.2 | 1250 | 257.2 | 202.2 | 43.8 | 57 | 6.6 | 596 | 117.8 | 169.4
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0606 |  | TOTAL AVG COAG ALK: |  |  |  | 8.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.525 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.6 | [5 empty] | 6.135 |  |  |  |  | 0.027 |  |  |  |  | 0.6 | [6 empty] | 0.027 | [16 empty] | Pump Station MIN |  | 2.2 | [17 empty] | MINIMUM | 9400 | [9 empty] | 280 | 240 | 300 | 760 | 700 | 340 | 240 | 720 | 740 | 750 |  | 1040 | 1040 | 1180 | 74 | 99 | 11 | 1150 | 225 | 185 | 42 | 55 | 6 | 570 | 110 | 165
[90 empty] | MAXIMUM | 10270 | [9 empty] | 310 | 300 | 350 | 900 | 825 | 600 | 500 | 850 | 850 | 800 |  | 1130 | 1130 | 1250 | 81 | 108 | 12 | 1350 | 276 | 215 | 46 | 60 | 8 | 650 | 125 | 176
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.009 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23827142 |  | END: | 23827151 |  |  | Alum | 7350 | 10200 | 10200 | 11200 | 11200 | 0 | [44 empty] | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.05 | 11.2 | 15 | 1.0661
[73 empty] | FINISHED 2 | 11.89 |  | TOTAL MGD: |  | 11 |  |  | FINISHED SOUTH 2 |  | START: | 44000000 |  | END: | 44011000 |  |  | Caustic | 7182 | 8147 | 8147
[73 empty] | TOTAL RAW | 27.294 |  | TOTAL MGD: |  | 4.856 |  |  | FINISHED CONWAY |  | START: | 10291940 |  | END: | 10296796 |  |  | Hypochlorite | 14.5 |  | 43.5
[76 empty] | TOTAL MGD: |  | 7.034 |  |  | FINISHED PERRY |  | START: | 33948055 |  | END: | 33955089 |  |  | Phosphate | 2055
[76 empty] | TOTAL MGD: |  | 10.085 |  |  | RAW PLANT 1 |  | START: | 31090350 |  | END: | 31100435 |  |  | Fluoride | 2950 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.829 |  |  | RAW PLANT 2 |  | START: | 31028152 |  | END: | 31033981 |  |  | Cal~Flo | 9.38 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.38 |  |  | RAW PLANT 3 |  | START: | 7637750 |  | END: | 7649130 |  |  | Zinc | 786
[76 empty] | TOTAL MGD: |  | 0.836 |  |  | DECANT |  | START: | 1876664 |  | END: | 1877500 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.5335 |  |  | BLOW DOWN |  | START: | 9153.8051 |  | END: | 9155.3386 |  |  | NH3 | 12.06 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 587
23827151
44011000
10296796
33955089
31100435
31033981
7649130
1877500
9155.3386
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 17
DATE: | 2019-01-17 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 3 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 3 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 3
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-17 | [23 empty] | DATE: | 2019-01-17
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-17 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43482.0222 | 2,3,5 | 30 | 9 | 6 | 10.5 | 25.5 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 9.7042 | 1,3 | 10.1822 | 19.8864 | 1.8795 | 43482.0222 | 90.129 | 8362.286 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.1984 | 1.6005 | 0.32327 | 0.2789 | 0.20283 | 0.14579 | 0.26803 | 0.27165 | 1.4267 | 1.5 | 0.070344 | 0.070344 | 0.069949 | 1.0905 | 0.54972 | 0.10188 | 3.6551 | 0.64332 | 3.4602 | 1.0849 | 0.53531 | 0.097407 | 3.4928 | 0.56381 | 5.4094 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.17 | 0.431 | 4 | 0.62 | 11.5 | 9.5 | 0.68014 |  | 6.21 | 0.348 | 4 | 0.68 | 12.3 | 5.5 | 0.44429 | 6.18 | 0.471 | 4 | 0.75 | 12.9 | 10.4 | 0.69778 | [13 empty] | 7.32 | 0.063 | 1 | 4.3 | 10.3 |  |  |  | 7.21 | 0.068 | 1 | 4 | 11.8 |  |  |  | 5 | 4 | 2.6 | [18 empty] | 9400 | [6 empty] | 0 | 0 | 0 | 280 | 210 | 320 | 765 | 660 | 320 | 230 | 740 | 750 | 750 |  | 1040 | 1040 | 1180 | 74 | 99 | 11 | 1120 | 220 | 185 | 42 | 55 | 6 | 580 | 110 | 165 |  | 1:00 | 0.62 | 9.5 | 26.7789 | 16.6029 | 6.17 | 11.5 | 15 | 1.1069 | 10 | 6.5 | 0.56014 | 1:00 | 0.68 | 5.5 | 46.2545 | 31.4531 | 6.21 | 12.3 | 15 | 2.0969 | 10 | 6.5 | 0.32429 | 1:00 | 0.75 | 10.4 | 25.9615 | 19.4712 | 6.18 | 12.9 | 15 | 1.2981 | 10 | 6.5 | 0.57778
2:00 | [72 empty] | 43482.3738 | 2,3,5 | 30 | 9 | 6 | 10.5 | 25.5 | 7.8 | 7.8 | 8.9 | 24.5 | ,1,3 | 8.5723 | 1,3 | 18.3398 | 26.9122 | 1.8288 | 43482.3738 | 90.129 | 8362.286 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.0843 | 1.6005 | 0.2958 | 0.28735 | 0.26622 | 0.30425 | 0.27165 | 0.27165 | 1.4267 | 5 | 0.070344 | 0.070344 | 0.071134 | 1.1052 | 0.54972 | 0.10188 | 3.6066 | 0.64332 | 3.4602 | 1.1107 | 0.53531 | 0.097407 | 3.4491 | 0.56381 | 5.4094 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.51 | 15 | 15 | 12.1 | 126 | 190 | 11.9 | 0.495 |  | 6.13 | 10 | 0.051 | 6.12 | 10 |  | 6.1 | 10 | [8 empty] | 0.045 | [14 empty] | 0.018 | 1 | 0.41 |  | 0.049 | 0.013 | 1 | 0.38 |  | 0.02 | 1 | 0.63 | [38 empty] | 9400 | [6 empty] | 0 | 0 | 0 | 260 | 190 | 320 | 700 | 680 | 420 | 480 | 750 | 750 | 750 |  | 1040 | 1040 | 1200 | 75 | 99 | 11 | 1100 | 220 | 185 | 43 | 55 | 6 | 550 | 110 | 165 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43482.5776 | 2,3,5 | 30 | 8 | 6 | 9.5 | 23.5 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 8.3318 | 1,3 | 11.3702 | 19.7021 | 1.8288 | 43482.5776 | 91.0368 | 8239.3112 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5456 | 0.98917 | 1.6285 | 0.29712 | 0.28523 | 0.25354 | 0.28523 | 0.28023 | 0.28023 | 1.3411 | 5 | 0.069611 | 0.069611 | 0.067556 | 1.0696 | 0.54139 | 0.10034 | 3.6212 | 0.64941 | 3.4041 | 1.0934 | 0.52819 | 0.10572 | 3.4783 | 0.55631 | 5.3375 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.36 | 0.061 | 1 | 4.3 | 10.2 |  |  |  | 7.33 | 0.067 | 1 | 4.1 | 11.3 |  |  |  | 4.8 | 4 | 3.6 | [18 empty] | 8750 | [6 empty] | 0 | 0 | 0 | 250 | 160 | 300 | 625 | 600 | 400 | 450 | 700 | 700 | 705 |  | 950 | 950 | 1050 | 67 | 90 | 10 | 1020 | 205 | 168 | 39 | 50 | 6 | 512 | 100 | 150 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43482.6936 | 2,3,5 | 30 | 8 | 6 | 9.5 | 23.5 | 7.1 | 7.1 | 8.1 | 22.3 | ,1,3 | 8.3318 | 1,3 | 11.3702 | 19.7021 | 1.8288 | 43482.6936 | 91.0368 | 8239.3112 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5673 | 1.0031 | 1.6486 | 0.29712 | 0.28523 | 0.099198 | 0.25354 | 0.28023 | 0.28023 | 1.3411 | 5 | 0.070591 | 0.070591 | 0.06839 | 1.0847 | 0.54902 | 0.10175 | 3.6667 | 0.65856 | 3.4521 | 1.1069 | 0.53471 | 0.10703 | 3.5135 | 0.56318 | 5.4034 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.52 | 14 | 15 | 12.6 | 119 | 190 | 11.8 | 0.528 |  | 6.18 | 7 | 0.058 | 6.17 | 8 |  | 6.11 | 8 | [8 empty] | 0.051 | [14 empty] | 0.016 | 1 | 0.35 |  | 0.048 | 0.02 | 1 | 0.38 |  | 0.019 | 1 | 0.58 | [38 empty] | 8750 | [6 empty] | 0 | 0 | 0 | 250 | 160 | 300 | 625 | 600 | 313 | 800 | 700 | 700 | 705 |  | 950 | 950 | 1050 | 67 | 90 | 10 | 1020 | 205 | 168 | 39 | 50 | 6 | 512 | 100 | 150 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43482.8059 | 2,5 | 75 | 8 | 6 | 9.5 | 23.5 | 7.2 | 7.2 | 8.2 | 22.6 | ,1,3 | 9.661 | 1,3 | 13.3258 | 22.9867 | 1.8288 | 43482.8059 | 90.8287 | 7501.4624 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6074 | 0.98917 | 1.6285 | 0.33753 | 0.30425 | 0.08874 | 0.19649 | 0.28023 | 0.28023 | 1.3411 | 4.5 | 0.070344 | 0.069611 | 0.069486 | 1.0856 | 0.54139 | 0.10034 | 3.7196 | 0.57022 | 3.5054 | 1.0653 | 0.52819 | 0.10572 | 3.2615 | 0.50068 | 5.3375 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.042 | [9 empty] | 6.16 | 0.42 | 5 | 0.59 | 10.9 | 9.5 | 0.68014 |  | 6.22 | 0.415 | 4 | 0.61 | 11.7 | 6 | 0.47377 | 6.2 | 0.418 | 4 | 0.7 | 12.5 | 10.5 | 0.70333 |  |  |  | 0.014 | [9 empty] | 7.38 | 0.054 | 1 | 4.1 | 10.4 | 23 | 60 | 0.013 | 7.27 | 0.063 | 1 | 3.9 | 11.6 | 22 | 62 | 0.013 | 4.6 | 3.8 | 2.6 | [18 empty] | 8730 | [6 empty] | 0 | 0 | 0 | 260 | 160 | 300 | 710 | 640 | 280 | 620 | 700 | 700 | 705 |  | 960 | 950 | 1080 | 68 | 90 | 10 | 1040 | 180 | 173 | 38 | 50 | 6 | 500 | 90 | 150 |  | 9:00 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.16 | 10.9 | 15 | 1.0533 | 10 | 6.5 | 0.56014 | 9:00 | 0.61 | 6 | 42.4 | 25.864 | 6.22 | 11.7 | 15 | 1.7243 | 10 | 6.5 | 0.35377 | 9:00 | 0.7 | 10.5 | 25.7143 | 18 | 6.2 | 12.5 | 15 | 1.2 | 10 | 6.5 | 0.58333
10:00 | [72 empty] | 43482.8911 | 1,2,3 | 33 | 9.5 | 6 | 10.5 | 26 | 7.7 | 7.7 | 10 | 25.4 | ,1,3 | 12.685 | 1,3 | 13.4798 | 26.1648 | 1.8288 | 43482.8911 | 90.8407 | 7993.3616 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6186 | 1.0406 | 1.7805 | 0.29825 | 0.27022 | 0.098247 | 0.20759 | 0.28252 | 0.28252 | 1.5218 | 4.5 | 0.068517 | 0.068517 | 0.06964 | 1.1046 | 0.52311 | 0.1032 | 3.6834 | 0.62206 | 3.7515 | 1.1034 | 0.51974 | 0.10114 | 3.217 | 0.5246 | 5.2521 |  | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.54 | 15 | 15 | 12.7 | 131 | 191 | 11.8 | 0.537 |  | 6.03 | 8 | 0.057 | 6.02 | 8 |  | 6.08 | 8 | [8 empty] | 0.048 | [14 empty] | 0.021 | 1 | 0.35 |  | 0.046 | 0.016 | 1 | 0.42 |  | 0.019 | 1 | 0.47 | [38 empty] | 9660 | [6 empty] | 0 | 0 | 0 | 280 | 180 | 400 | 745 | 675 | 310 | 655 | 780 | 780 | 800 |  | 1000 | 1000 | 1320 | 74 | 93 | 11 | 1100 | 210 | 198 | 48 | 60 | 7 | 600 | 115 | 180 |  | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.33 | 0.352 | 4 | 0.72 | 11.6 | 8 | 0.5917 |  | 6.31 | 0.327 | 4 | 0.61 | 12.5 | 6 | 0.47377 | 6.26 | 0.455 | 4 | 0.63 | 13 | 9.5 | 0.64778 | [13 empty] | 7.59 | 0.062 | 1 | 4.4 | 9.9 |  |  |  | 7.4 | 0.067 | 1 | 4 | 12.5 |  |  |  | 4.6 | 3.8 | 2.5 | [55 empty] | 13:00 | 0.72 | 8 | 31.8 | 22.896 | 6.33 | 11.6 | 15 | 1.5264 | 10 | 6.5 | 0.4717 | 13:00 | 0.61 | 6 | 42.4 | 25.864 | 6.31 | 12.5 | 15 | 1.7243 | 10 | 6.5 | 0.35377 | 13:00 | 0.63 | 9.5 | 28.4211 | 17.9053 | 6.26 | 13 | 15 | 1.1937 | 10 | 6.5 | 0.52778
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.54 | 15 | 15 | 12.3 | 131 | 188 | 11.9 | 0.527 |  | 6.32 | 9 | 0.06 | 6.25 | 9 |  | 6.29 | 9 | [8 empty] | 0.049 | [14 empty] | 0.024 | 1 | 0.46 |  | 0.048 | 0.016 | 1 | 0.48 |  | 0.02 | 1 | 0.47 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.62 | 0.068 | 1 | 4.7 | 10.4 |  |  |  | 7.87 | 0.071 | 1 | 4.8 | 11.8 |  |  |  | 4.5 | 3.7 | 2.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.55 | 16 | 15 | 12.5 | 129 | 190 | 12 | 0.502 |  | 6.18 | 8 | 0.049 | 6.19 | 8 |  | 6.16 | 8 | [8 empty] | 0.044 | [14 empty] | 0.046 | 1 | 0.46 |  | 0.045 | 0.034 | 1 | 0.39 |  | 0.02 | 1 | 0.48 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.038 | [9 empty] | 6.34 | 0.4 | 5 | 0.63 | 11.4 | 8 | 0.5917 |  | 6.33 | 0.31 | 4 | 0.43 | 12.2 | 6 | 0.47377 | 6.32 | 0.487 | 6 | 0.71 | 12.7 | 9.5 | 0.64778 |  |  |  | 0.013 | [9 empty] | 7.53 | 0.067 | 1 | 4.5 | 10.5 | 20 | 57 | 0.026 | 7.41 | 0.051 | 1 | 3.9 | 11.8 | 22 | 59 | 0.017 | 4.5 | 3.6 | 2.6 | [55 empty] | 21:00 | 0.63 | 8 | 31.8 | 20.034 | 6.34 | 11.4 | 15 | 1.3356 | 10 | 6.5 | 0.4717 | 21:00 | 0.43 | 6 | 42.4 | 18.232 | 6.33 | 12.2 | 15 | 1.2155 | 10 | 6.5 | 0.35377 | 21:00 | 0.71 | 9.5 | 28.4211 | 20.1789 | 6.32 | 12.7 | 15 | 1.3453 | 10 | 6.5 | 0.52778
22:00 | [72 empty] | DOSE |  | TOTAL | 51.5 | 36 | 60 | 147.5 | 44.8 | 44.8 | 52.3 | 141.9 | 0 | 57.2861 | 0 | 78.0682 | 135.3542 | 11.0235 | TOTAL | 544.0009 | 48698.0184 | 0 | 3520.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4206 | 6.3047 | 9.887 | 1.8491 | 1.7112 | 1.0088 | 1.3929 | 1.6629 | 1.6665 | 8.3984 | 25.5 | 0.41975 | 0.41902 | 0.41615 | 6.5402 | 3.2544 | 0.6094 | 21.9527 | 3.7869 | 21.0336 | 6.5645 | 3.1814 | 0.61443 | 20.4122 | 3.2724 | 32.1493 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.45 | 15 | 16 | 13.1 | 119 | 192 | 12.1 | 0.501 |  | 6.14 | 8 | 0.06 | 6.12 | 9 |  | 6.06 | 8 | [8 empty] | 0.051 | [14 empty] | 0.035 | 1 | 0.43 |  | 0.048 | 0.027 | 1 | 0.42 |  | 0.018 | 1 | 0.63 | [22 empty] | AVERAGE | 8.5833 | 6 | 10 | 24.5833 | 7.4667 | 7.4667 | 8.7167 | 23.65 |  | 9.5477 |  | 13.0114 | 22.559 | 1.8372 | AVERAGE | 90.6668 | 8116.3364 |  | 586.7841 | 0 | 0 | 0 |  |  |  | 1.5701 | 1.0508 | 1.6478 | 0.30818 | 0.2852 | 0.16813 | 0.23215 | 0.27715 | 0.27775 | 1.3997 | 4.25 | 0.069958 | 0.069836 | 0.069359 | 1.09 | 0.54239 | 0.10157 | 3.6588 | 0.63115 | 3.5056 | 1.0941 | 0.53024 | 0.1024 | 3.402 | 0.5454 | 5.3582 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.11 | 90 | 91 | 75.3 | 755 | 1141 | 71.5 | 3.09 | 0.08 | 36.98 | 50 | 0.335 | 36.87 | 52 | 0 | 5.942 | 5 | 0 | 25 | 1.603 | 18 | 2.56 | 45.4 | 35 | 2.5437 | 0.288 | 25.07 | 1.4 | 16 | 2.33 | 48.7 | 23.5 | 1.8656 | 24.96 | 1.831 | 18 | 2.79 | 51.1 | 39.9 | 2.6967 | 0.16 | 6 | 2.46 | 0.027 | 0.284 | 0.126 | 6 | 2.47 | 0 | 0.1 | 6 | 3.26 | 0 | 44.8 | 0.375 | 6 | 26.3 | 61.7 | 43 | 117 | 0.039 | 44.49 | 0.387 | 6 | 24.7 | 70.8 | 44 | 121 | 0.03 | 28 | 22.9 | 16.4 |  |  | MINIMUM | 8 | 6 | 9.5 | 23.5 | 7.1 | 7.1 | 8.1 | 22.3 |  | 8.3318 |  | 10.1822 | 19.7021 | 1.8288 | MINIMUM | 90.129 | 7501.4624 |  | 586.7841 | [6 empty] | 1.4838 | 0.98917 | 1.6005 | 0.2958 | 0.27022 | 0.08874 | 0.14579 | 0.26803 | 0.27165 | 1.3411 | 1.5 | 0.068517 | 0.068517 | 0.067556 | 1.0696 | 0.52311 | 0.10034 | 3.6066 | 0.57022 | 3.4041 | 1.0653 | 0.51974 | 0.097407 | 3.217 | 0.50068 | 5.2521 |  | MIN | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.16 | 10.9 | 15 | 1.0533 |  |  |  | MIN | 0.43 | 6 | 42.4 | 18.232 | 6.33 | 12.2 | 15 | 1.2155 |  |  |  | MIN | 0.63 | 9.5 | 28.4211 | 17.9053 | 6.26 | 13 | 15 | 1.1937 |  |  |  | 1.0533
AVERAGE | 6.5183 | 15 | 15.1667 | 12.55 | 125.8333 | 190.1667 | 11.9167 | 0.515 | 0.04 | 6.1633 | 8.3333 | 0.055833 | 6.145 | 8.6667 |  | 6.1333 | 8.5 |  | 6.25 | 0.40075 | 4.5 | 0.64 | 11.35 | 8.75 | 0.63592 | 0.048 | 6.2675 | 0.35 | 4 | 0.5825 | 12.175 | 5.875 | 0.4664 | 6.24 | 0.45775 | 4.5 | 0.6975 | 12.775 | 9.975 | 0.67417 | 0.026667 | 1 | 0.41 | 0.0135 | 0.047333 | 0.021 | 1 | 0.41167 |  | 0.019333 | 1 | 0.54333 |  | 7.4667 | 0.0625 | 1 | 4.3833 | 10.2833 | 21.5 | 58.5 | 0.0195 | 7.415 | 0.0645 | 1 | 4.1167 | 11.8 | 22 | 60.5 | 0.015 | 4.6667 | 3.8167 | 2.7333 |  |  | MAXIMUM | 9.5 | 6 | 10.5 | 26 | 7.8 | 7.8 | 10 | 25.4 |  | 12.685 |  | 18.3398 | 26.9122 | 1.8795 | MAXIMUM | 91.0368 | 8362.286 |  | 586.7841 | [6 empty] | 1.6186 | 1.1984 | 1.7805 | 0.33753 | 0.30425 | 0.26622 | 0.30425 | 0.28252 | 0.28252 | 1.5218 | 5 | 0.070591 | 0.070591 | 0.071134 | 1.1052 | 0.54972 | 0.1032 | 3.7196 | 0.65856 | 3.7515 | 1.1107 | 0.53531 | 0.10703 | 3.5135 | 0.56381 | 5.4094
MINIMUM | 6.45 | 14 | 15 | 12.1 | 119 | 188 | 11.8 | 0.495 | 0.038 | 6.03 | 7 | 0.049 | 6.02 | 8 |  | 6.06 | 8 |  | 6.16 | 0.352 | 4 | 0.59 | 10.9 | 8 | 0.5917 | 0.044 | 6.21 | 0.31 | 4 | 0.43 | 11.7 | 5.5 | 0.44429 | 6.18 | 0.418 | 4 | 0.63 | 12.5 | 9.5 | 0.64778 | 0.016 | 1 | 0.35 | 0.013 | 0.045 | 0.013 | 1 | 0.38 |  | 0.018 | 1 | 0.47 |  | 7.32 | 0.054 | 1 | 4.1 | 9.9 | 20 | 57 | 0.013 | 7.21 | 0.051 | 1 | 3.9 | 11.3 | 22 | 59 | 0.013 | 4.5 | 3.6 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 54690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1580 | 1060 | 1940 | 4170 | 3855 | 2043 | 3235 | 4370 | 4380 | 4415 | 0 | 5940 | 5930 | 6880 | 425 | 561 | 63 | 6400 | 1240 | 1077 | 249 | 320 | 37 | 3254 | 625 | 960
MAXIMUM | 6.55 | 16 | 16 | 13.1 | 131 | 192 | 12.1 | 0.537 | 0.042 | 6.32 | 10 | 0.06 | 6.25 | 10 |  | 6.29 | 10 |  | 6.34 | 0.431 | 5 | 0.72 | 11.6 | 9.5 | 0.68014 | 0.051 | 6.33 | 0.415 | 4 | 0.68 | 12.5 | 6 | 0.47377 | 6.32 | 0.487 | 6 | 0.75 | 13 | 10.5 | 0.70333 | 0.046 | 1 | 0.46 | 0.014 | 0.049 | 0.034 | 1 | 0.48 |  | 0.02 | 1 | 0.63 |  | 7.62 | 0.068 | 1 | 4.7 | 10.5 | 23 | 60 | 0.026 | 7.87 | 0.071 | 1 | 4.8 | 12.5 | 22 | 62 | 0.017 | 5 | 4 | 3.6 | [17 empty] | AVERAGE | 9115 | [9 empty] | 263.3333 | 176.6667 | 323.3333 | 695 | 642.5 | 340.5 | 539.1667 | 728.3333 | 730 | 735.8333 |  | 990 | 988.3333 | 1146.6667 | 70.8333 | 93.5 | 10.5 | 1066.6667 | 206.6667 | 179.5 | 41.5 | 53.3333 | 6.1667 | 542.3333 | 104.1667 | 160
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1472 |  | TOTAL AVG COAG ALK: |  |  |  | 8.5 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.487 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.43 | [5 empty] | 6.2525 |  |  |  |  | 0.046 |  |  |  |  | 0.43 | [6 empty] | 0.046 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 8730 | [9 empty] | 250 | 160 | 300 | 625 | 600 | 280 | 230 | 700 | 700 | 705 |  | 950 | 950 | 1050 | 67 | 90 | 10 | 1020 | 180 | 168 | 38 | 50 | 6 | 500 | 90 | 150
[90 empty] | MAXIMUM | 9660 | [9 empty] | 280 | 210 | 400 | 765 | 680 | 420 | 800 | 780 | 780 | 800 |  | 1040 | 1040 | 1320 | 75 | 99 | 11 | 1120 | 220 | 198 | 48 | 60 | 7 | 600 | 115 | 180
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 9.813 |  | TOTAL MGD: |  | 0.01 |  |  | FINISHED SOUTH 1 |  | START: | 23827151 |  | END: | 23827161 |  |  | Alum | 8195 | 10200 | 10200 | 11200 | 11200 | 0 | [44 empty] | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.16 | 10.9 | 15 | 1.0533
[73 empty] | FINISHED 2 | 11.417 |  | TOTAL MGD: |  | 9.803 |  |  | FINISHED SOUTH 2 |  | START: | 44011000 |  | END: | 44020803 |  |  | Caustic | 7138 | 8132 | 8132
[73 empty] | TOTAL RAW | 25.273 |  | TOTAL MGD: |  | 4.236 |  |  | FINISHED CONWAY |  | START: | 10296796 |  | END: | 10301032 |  |  | Hypochlorite | 19 |  | 35.5
[76 empty] | TOTAL MGD: |  | 7.181 |  |  | FINISHED PERRY |  | START: | 33955089 |  | END: | 33962270 |  |  | Phosphate | 1993
[76 empty] | TOTAL MGD: |  | 9.502 |  |  | RAW PLANT 1 |  | START: | 31100435 |  | END: | 31109937 |  |  | Fluoride | 2950 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.505 |  |  | RAW PLANT 2 |  | START: | 31033981 |  | END: | 31039486 |  |  | Cal~Flo | 14.29 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.266 |  |  | RAW PLANT 3 |  | START: | 7649130 |  | END: | 7659396 |  |  | Zinc | 781
[76 empty] | TOTAL MGD: |  | 0.922 |  |  | DECANT |  | START: | 1877500 |  | END: | 1878422 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.5069 |  |  | BLOW DOWN |  | START: | 9155.3386 |  | END: | 9156.8455 |  |  | NH3 | 11.92 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 585
23827161
44020803
10301032
33962270
31109937
31039486
7659396
1878422
9156.8455
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 18
DATE: | 2019-01-18 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 18 |  | 14 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 18 |  | 14 | [37 empty] | 6:00 - 18:00 |  | 18 |  | 14
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-18 | [23 empty] | DATE: | 2019-01-18
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-18 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [7 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  | 5.625 |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43483.0319 | 1,2,3 | 33 | 9.5 | 6 | 10.5 | 26 | 7.7 | 7.7 | 10 | 25.4 | ,1,3 | 12.685 | 1,3 | 13.4798 | 26.1648 | 1.9519 | 43483.0319 | 90.8407 | 8116.3364 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7343 | 1.0406 | 1.6915 | 0.29825 | 0.28824 | 0.098247 | 0.21234 | 0.28252 | 0.28252 | 1.5218 | 4.5 | 0.068517 | 0.068517 | 0.06964 | 1.1046 | 0.52311 | 0.1032 | 3.7723 | 0.62206 | 3.6567 | 1.1034 | 0.51974 | 0.10114 | 3.217 | 0.5246 | 5.2521 |  |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.463 | 4 | 0.61 | 11.3 | 9.9 | 0.70373 |  | 6.22 | 0.303 | 5 | 0.43 | 12.1 | 5.7 | 0.45608 | 6.24 | 0.501 | 5 | 0.89 | 12.8 | 10.8 | 0.72 | [13 empty] | 7.41 | 0.06 | 1 | 4 | 10.4 |  |  |  | 7.32 | 0.057 | 1 | 3.9 | 11.7 |  |  |  | 4.5 | 3.5 | 2.7 | [18 empty] | 9660 | [6 empty] | 0 | 0 | 0 | 300 | 180 | 380 | 745 | 720 | 310 | 670 | 780 | 780 | 800 |  | 1000 | 1000 | 1320 | 74 | 93 | 11 | 1130 | 210 | 193 | 48 | 60 | 7 | 600 | 115 | 180 |  |  | 1:00 | 0.61 | 9.9 | 25.697 | 15.6752 | 6.19 | 11.3 | 15 | 1.045 | 10 | 6.5 | 0.58373 | 1:00 | 0.43 | 5.7 | 44.6316 | 19.1916 | 6.22 | 12.1 | 15 | 1.2794 | 10 | 6.5 | 0.33608 | 1:00 | 0.89 | 10.8 | 25 | 22.25 | 6.24 | 12.8 | 15 | 1.4833 | 10 | 6.5 | 0.6
2:00 | [72 empty] | 43483.2855 | 3,2,5 | 38 | 11 | 5 | 12 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 7.9013 | 1,3 | 9.6091 | 17.5104 | 1.872 | 43483.2855 | 90.8138 | 8608.2356 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7281 | 0.99499 | 1.7805 | 0.28696 | 0.27659 | 0.11409 | 0.26622 | 0.26939 | 0.26939 | 1.4267 | 5 | 0.070137 | 0.070137 | 0.069418 | 1.0953 | 0.5605 | 0.093491 | 3.6551 | 0.60376 | 3.6902 | 1.0889 | 0.54709 | 0.10646 | 3.5431 | 0.59543 | 5.9278 |  |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.49 | 16 | 16 | 13.4 | 129 | 191 | 11.8 | 0.481 |  | 6.09 | 8 | 0.054 | 6.15 | 9 |  | 6.11 | 9 | [8 empty] | 0.047 | [14 empty] | 0.029 | 1 | 0.49 |  | 0.046 | 0.022 | 1 | 0.38 |  | 0.017 | 1 | 0.58 | [38 empty] | 10400 | [6 empty] | 0 | 0 | 0 | 330 | 190 | 380 | 830 | 800 | 300 | 700 | 850 | 850 | 750 |  | 1130 | 1130 | 1250 | 81 | 110 | 11 | 1200 | 225 | 215 | 45 | 60 | 7 | 615 | 124 | 193 |  |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43483.491 | 3,2,5 | 38 | 11.5 | 5 | 12.5 | 29 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 7.9013 | 1,3 | 9.6091 | 17.5104 | 1.872 | 43483.491 | 88.947 | 8608.2356 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7281 | 0.99499 | 1.7805 | 0.27449 | 0.26457 | 0.11409 | 0.2472 | 0.25861 | 0.25861 | 1.4267 | 5 | 0.070137 | 0.070137 | 0.069418 | 1.0953 | 0.5605 | 0.093491 | 3.6551 | 0.60376 | 3.6902 | 1.0889 | 0.54709 | 0.10646 | 3.5431 | 0.59543 | 5.9278 |  |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.12 | 0.058 | 1 | 4.1 | 9.9 |  |  |  | 7.32 | 0.059 | 1 | 4.1 | 11.4 |  |  |  | 4.3 | 3.6 | 2.2 | [18 empty] | 10550 | [6 empty] | 0 | 0 | 0 | 330 | 190 | 380 | 830 | 800 | 300 | 650 | 850 | 850 | 750 |  | 1130 | 1130 | 1250 | 81 | 110 | 11 | 1200 | 225 | 215 | 45 | 60 | 7 | 615 | 124 | 193 |  |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43483.6429 | 3,2,5 | 42 | 11.5 | 5 | 12.5 | 29 | 8.8 | 8.8 | 9.9 | 27.5 | ,1,3 | 12.1723 | 1,3 | 10.9282 | 23.1005 | 1.872 | 43483.6429 | 88.947 | 8608.2356 | 0 | 586.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6692 | 0.96107 | 1.7086 | 0.27449 | 0.26457 | 0 | 0.27382 | 0.25861 | 0.25861 | 1.4267 | 5 | 0.067746 | 0.067746 | 0.066613 | 1.0711 | 0.54139 | 0.098514 | 3.5453 | 0.64797 | 3.5644 | 1.0449 | 0.52499 | 0.10216 | 3.4238 | 0.57137 | 5.6883 |  |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.52 | 16 | 16 | 13.7 | 129 | 192 | 11.8 | 0.499 |  | 6.09 | 8 | 0.05 | 6.12 | 8 |  | 6.09 | 9 | [8 empty] | 0.046 | [14 empty] | 0.03 | 1 | 0.47 |  | 0.047 | 0.021 | 1 | 0.45 |  | 0.017 | 1 | 0.61 | [38 empty] | 10550 | [6 empty] | 0 | 0 | 0 | 330 | 190 | 380 | 830 | 800 | 0 | 720 | 850 | 850 | 750 |  | 1130 | 1130 | 1250 | 82 | 110 | 12 | 1200 | 250 | 215 | 45 | 60 | 7 | 615 | 124 | 193 |  |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43483.8201 | 3,2,5 | 47 | 12 | 5 | 13 | 30 | 9.2 | 9.2 | 10.3 | 28.7 | ,1,3 | 11.5877 | 1,3 | 16.2893 | 27.877 | 1.872 | 43483.8201 | 90.8557 | 8977.16 | 0 | 745.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5483 | 0.96766 | 1.7286 | 0.27256 | 0.25671 | 0 | 0.27382 | 0.20478 | 0.23404 | 1.4267 | 3 | 0.068815 | 0.068815 | 0.070685 | 1.0995 | 0.55081 | 0.09423 | 3.693 | 0.57022 | 4.1706 | 1.0713 | 0.53824 | 0.098195 | 3.6216 | 0.48718 | 5.694 |  |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.044 | [9 empty] | 6.15 | 0.519 | 5 | 0.8 | 11.1 | 11 | 0.76858 |  | 6.19 | 0.292 | 4 | 0.6 | 11.8 | 5 | 0.41481 | 6.2 | 0.506 | 5 | 0.8 | 12.7 | 12 | 0.78667 |  |  |  | 0.007 | [9 empty] | 7.55 | 0.055 | 1 | 4.6 | 10.5 | 21 | 56 |  | 7.33 | 0.056 | 1 | 3.9 | 12 | 23 | 58 |  | 4.2 | 3.6 | 2.09 | [18 empty] | 11148 | [6 empty] | 0 | 0 | 0 | 320 | 200 | 400 | 860 | 810 | 0 | 720 | 700 | 800 | 750 |  | 1200 | 1200 | 1380 | 88 | 117 | 12 | 1300 | 230 | 263 | 48 | 64 | 7 | 680 | 110 | 201 |  |  | 9:00 | 0.8 | 11 | 23.1273 | 18.5018 | 6.15 | 11.1 | 15 | 1.2335 | 10 | 6.5 | 0.64858 | 9:00 | 0.6 | 5 | 50.88 | 30.528 | 6.19 | 11.8 | 15 | 2.0352 | 10 | 6.5 | 0.29481 | 9:00 | 0.8 | 12 | 22.5 | 18 | 6.2 | 12.7 | 15 | 1.2 | 10 | 6.5 | 0.66667
10:00 | [128 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.5 | 16 | 16 | 13.6 | 128 | 191 | 11.8 | 0.498 |  | 6.2 | 8 | 0.055 | 6.21 | 8 |  | 6.2 | 9 | [8 empty] | 0.046 | [14 empty] | 0.032 | 1 | 0.4 |  | 0.049 | 0.022 | 1 | 0.48 |  | 0.019 | 1 | 0.6 | [76 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [128 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.27 | 0.403 | 5 | 0.7 | 11.9 | 11 | 0.76858 |  | 6.24 | 0.205 | 3 | 0.56 | 12.9 | 5 | 0.41481 | 6.25 | 0.526 | 5 | 0.81 | 12.8 | 12.5 | 0.81444 | [13 empty] | 7.29 | 0.058 | 1 | 4.1 | 10.3 |  |  |  | 7.2 | 0.058 | 1 | 3.8 | 12.6 |  |  |  | 4.3 | 3.6 | 2.1 | [56 empty] | 13:00 | 0.7 | 11 | 23.1273 | 16.1891 | 6.27 | 11.9 | 15 | 1.0793 | 10 | 6.5 | 0.64858 | 13:00 | 0.56 | 5 | 50.88 | 28.4928 | 6.24 | 12.9 | 15 | 1.8995 | 10 | 6.5 | 0.29481 | 13:00 | 0.81 | 12.5 | 21.6 | 17.496 | 6.25 | 12.8 | 15 | 1.1664 | 10 | 6.5 | 0.69444
14:00 | [126 empty] | #REF! |  | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.5 | 16 | 16 | 15.2 | 129 | 203 | 11.9 | 0.469 |  | 6.08 | 9 | 0.052 | 6.06 | 8 |  | 6.02 | 9 | [8 empty] | 0.04 | [14 empty] | 0.032 | 1 | 0.46 |  | 0.041 | 0.023 | 1 | 0.48 |  | 0.02 | 1 | 0.61 | [76 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [128 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.2 | 0.056 | 1 | 4.1 | 10.1 |  |  |  | 7.19 | 0.059 | 1 | 3.8 | 12.1 |  |  |  | 4.3 | 3.5 | 2.7 | [56 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [128 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.44 | 15 | 16 | 15.1 | 114 | 204 | 11.8 | 0.473 |  | 5.96 | 8 | 0.058 | 6.08 | 8 |  | 6.02 | 8 | [8 empty] | 0.045 | [14 empty] | 0.024 | 1 | 0.44 |  | 0.047 | 0.016 | 1 | 0.54 |  | 0.018 | 1 | 0.44 | [76 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [128 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.039 | [9 empty] | 6.16 | 0.502 | 4 | 0.75 | 11.9 | 12.2 | 0.83934 |  | 6.15 | 0.3 | 3 | 0.85 | 12.7 | 4.8 | 0.40302 | 6.13 | 0.54 | 4 | 0.75 | 13.3 | 13.1 | 0.84778 |  |  |  | 0.021 | [9 empty] | 7.13 | 0.052 | 1 | 4.3 | 10.8 | 20 | 58 | 0.017 | 7.12 | 0.056 | 1 | 4.1 | 11.9 | 20 | 60 | 0.024 | 4.4 | 3.7 | 2.4 | [56 empty] | 21:00 | 0.75 | 12.2 | 20.8525 | 15.6393 | 6.16 | 11.9 | 15 | 1.0426 | 10 | 6.5 | 0.71934 | 21:00 | 0.85 | 4.8 | 53 | 45.05 | 6.15 | 12.7 | 15 | 3.0033 | 10 | 6.5 | 0.28302 | 21:00 | 0.75 | 13.1 | 20.6107 | 15.458 | 6.13 | 13.3 | 15 | 1.0305 | 10 | 6.5 | 0.72778
22:00 | [72 empty] | DOSE |  | TOTAL | 55.5 | 26 | 60.5 | 142 | 42.7 | 42.7 | 49.2 | 134.6 | 0 | 52.2475 | 0 | 59.9155 | 112.163 | 9.4399 | TOTAL | 450.4042 | 42918.2032 | 0 | 3092.511 | 0 | 0 | 0 | 0 | 0 | 0 | 8.408 | 4.9593 | 8.6897 | 1.4067 | 1.3507 | 0.32643 | 1.2734 | 1.2739 | 1.3032 | 7.2285 | 22.5 | 0.34535 | 0.34535 | 0.34578 | 5.4658 | 2.7363 | 0.48293 | 18.3206 | 3.0478 | 18.7721 | 5.3975 | 2.6771 | 0.51443 | 17.3487 | 2.774 | 28.4899 |  |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.4 | 16 | 15 | 15.5 | 114 | 206 | 11.8 | 0.464 |  | 6.04 | 8 | 0.051 | 6.5 | 6 |  | 6.02 | 8 | [8 empty] | 0.045 | [14 empty] | 0.024 | 1 | 0.42 |  | 0.044 | 0.016 | 1 | 0.54 |  | 0.053 | 1 | 0.58 | [22 empty] | AVERAGE | 11.1 | 5.2 | 12.1 | 28.4 | 8.54 | 8.54 | 9.84 | 26.92 |  | 10.4495 |  | 11.9831 | 22.4326 | 1.888 | AVERAGE | 90.0808 | 8583.6406 |  | 618.5022 | 0 | 0 | 0 |  |  |  | 1.6816 | 0.99185 | 1.7379 | 0.28135 | 0.27013 | 0.065287 | 0.25468 | 0.25478 | 0.26063 | 1.4457 | 4.5 | 0.06907 | 0.06907 | 0.069155 | 1.0932 | 0.54726 | 0.096586 | 3.6641 | 0.60955 | 3.7544 | 1.0795 | 0.53543 | 0.10289 | 3.4697 | 0.5548 | 5.698 |  |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.85 | 95 | 95 | 86.5 | 743 | 1187 | 70.9 | 2.884 | 0.083 | 36.46 | 49 | 0.32 | 37.12 | 47 | 0 | 36.46 | 52 | 0 | 24.77 | 1.887 | 18 | 2.86 | 46.2 | 44.1 | 3.0802 | 0.269 | 24.8 | 1.1 | 15 | 2.44 | 49.5 | 20.5 | 1.6887 | 24.82 | 2.073 | 19 | 3.25 | 51.6 | 48.4 | 3.1689 | 0.171 | 6 | 2.68 | 0.028 | 0.274 | 0.12 | 6 | 2.87 | 0 | 0.144 | 6 | 3.42 | 0 | 43.7 | 0.339 | 6 | 25.2 | 62 | 41 | 114 | 0.017 | 43.48 | 0.345 | 6 | 23.6 | 71.7 | 43 | 118 | 0.024 | 26 | 21.5 | 14.19 |  |  | MINIMUM | 9.5 | 5 | 10.5 | 26 | 7.7 | 7.7 | 9.5 | 25.4 |  | 7.9013 |  | 9.6091 | 17.5104 | 1.872 | MINIMUM | 88.947 | 8116.3364 |  | 586.7841 | [6 empty] | 1.5483 | 0.96107 | 1.6915 | 0.27256 | 0.25671 | 0 | 0.21234 | 0.20478 | 0.23404 | 1.4267 | 3 | 0.067746 | 0.067746 | 0.066613 | 1.0711 | 0.52311 | 0.093491 | 3.5453 | 0.57022 | 3.5644 | 1.0449 | 0.51974 | 0.098195 | 3.217 | 0.48718 | 5.2521 |  |  | MIN | 0.75 | 12.2 | 20.8525 | 15.6393 | 6.16 | 11.9 | 15 | 1.0426 |  |  |  | MIN | 0.43 | 5.7 | 44.6316 | 19.1916 | 6.22 | 12.1 | 15 | 1.2794 |  |  |  | MIN | 0.75 | 13.1 | 20.6107 | 15.458 | 6.13 | 13.3 | 15 | 1.0305 |  |  |  | 1.0305
AVERAGE | 6.475 | 15.8333 | 15.8333 | 14.4167 | 123.8333 | 197.8333 | 11.8167 | 0.48067 | 0.0415 | 6.0767 | 8.1667 | 0.053333 | 6.1867 | 7.8333 |  | 6.0767 | 8.6667 |  | 6.1925 | 0.47175 | 4.5 | 0.715 | 11.55 | 11.025 | 0.77006 | 0.044833 | 6.2 | 0.275 | 3.75 | 0.61 | 12.375 | 5.125 | 0.42218 | 6.205 | 0.51825 | 4.75 | 0.8125 | 12.9 | 12.1 | 0.79222 | 0.0285 | 1 | 0.44667 | 0.014 | 0.045667 | 0.02 | 1 | 0.47833 |  | 0.024 | 1 | 0.57 |  | 7.2833 | 0.0565 | 1 | 4.2 | 10.3333 | 20.5 | 57 | 0.017 | 7.2467 | 0.0575 | 1 | 3.9333 | 11.95 | 21.5 | 59 | 0.024 | 4.3333 | 3.5833 | 2.365 |  |  | MAXIMUM | 12 | 6 | 13 | 30 | 9.2 | 9.2 | 10.3 | 28.7 |  | 12.685 |  | 16.2893 | 27.877 | 1.9519 | MAXIMUM | 90.8557 | 8977.16 |  | 745.3744 | [6 empty] | 1.7343 | 1.0406 | 1.7805 | 0.29825 | 0.28824 | 0.11409 | 0.27382 | 0.28252 | 0.28252 | 1.5218 | 5 | 0.070137 | 0.070137 | 0.070685 | 1.1046 | 0.5605 | 0.1032 | 3.7723 | 0.64797 | 4.1706 | 1.1034 | 0.54709 | 0.10646 | 3.6216 | 0.59543 | 5.9278
MINIMUM | 6.4 | 15 | 15 | 13.4 | 114 | 191 | 11.8 | 0.464 | 0.039 | 5.96 | 8 | 0.05 | 6.06 | 6 |  | 6.02 | 8 |  | 6.15 | 0.403 | 4 | 0.61 | 11.1 | 9.9 | 0.70373 | 0.04 | 6.15 | 0.205 | 3 | 0.43 | 11.8 | 4.8 | 0.40302 | 6.13 | 0.501 | 4 | 0.75 | 12.7 | 10.8 | 0.72 | 0.024 | 1 | 0.4 | 0.007 | 0.041 | 0.016 | 1 | 0.38 |  | 0.017 | 1 | 0.44 |  | 7.12 | 0.052 | 1 | 4 | 9.9 | 20 | 56 | 0.017 | 7.12 | 0.056 | 1 | 3.8 | 11.4 | 20 | 58 | 0.024 | 4.2 | 3.5 | 2.09 | [15 empty] | MIL/MIN |  | TOTAL | 52308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1610 | 950 | 1920 | 4095 | 3930 | 910 | 3460 | 4030 | 4130 | 3800 | 0 | 5590 | 5590 | 6450 | 406 | 540 | 57 | 6030 | 1140 | 1101 | 231 | 304 | 35 | 3125 | 597 | 960
MAXIMUM | 6.52 | 16 | 16 | 15.5 | 129 | 206 | 11.9 | 0.499 | 0.044 | 6.2 | 9 | 0.058 | 6.5 | 9 |  | 6.2 | 9 |  | 6.27 | 0.519 | 5 | 0.8 | 11.9 | 12.2 | 0.83934 | 0.047 | 6.24 | 0.303 | 5 | 0.85 | 12.9 | 5.7 | 0.45608 | 6.25 | 0.54 | 5 | 0.89 | 13.3 | 13.1 | 0.84778 | 0.032 | 1 | 0.49 | 0.021 | 0.049 | 0.023 | 1 | 0.54 |  | 0.053 | 1 | 0.61 |  | 7.55 | 0.06 | 1 | 4.6 | 10.8 | 21 | 58 | 0.017 | 7.33 | 0.059 | 1 | 4.1 | 12.6 | 23 | 60 | 0.024 | 4.5 | 3.7 | 2.7 | [17 empty] | AVERAGE | 10461.6 | [9 empty] | 322 | 190 | 384 | 819 | 786 | 182 | 692 | 806 | 826 | 760 |  | 1118 | 1118 | 1290 | 81.2 | 108 | 11.4 | 1206 | 228 | 220.2 | 46.2 | 60.8 | 7 | 625 | 119.4 | 192
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1133 |  | TOTAL AVG COAG ALK: |  |  |  | 8.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.54 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.43 | [5 empty] | 6.1992 |  |  |  |  | 0.053 |  |  |  |  | 0.43 | [6 empty] | 0.053 | [16 empty] | Pump Station MIN |  | 2.09 | [17 empty] | MINIMUM | 9660 | [9 empty] | 300 | 180 | 380 | 745 | 720 | 0 | 650 | 700 | 780 | 750 |  | 1000 | 1000 | 1250 | 74 | 93 | 11 | 1130 | 210 | 193 | 45 | 60 | 7 | 600 | 110 | 180
[90 empty] | MAXIMUM | 11148 | [9 empty] | 330 | 200 | 400 | 860 | 810 | 310 | 720 | 850 | 850 | 800 |  | 1200 | 1200 | 1380 | 88 | 117 | 12 | 1300 | 250 | 263 | 48 | 64 | 7 | 680 | 124 | 201
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [51 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.084 |  | TOTAL MGD: |  | 0.008 |  |  | FINISHED SOUTH 1 |  | START: | 23827161 |  | END: | 23827169 |  |  | Alum | 8827 | 10200 | 10200 | 11500 | 11500 | 0 | [45 empty] | 0.75 | 13.1 | 20.6107 | 15.458 | 6.13 | 13.3 | 15 | 1.0305
[73 empty] | FINISHED 2 | 12.273 |  | TOTAL MGD: |  | 10.076 |  |  | FINISHED SOUTH 2 |  | START: | 44020803 |  | END: | 44030879 |  |  | Caustic | 7051 | 8104 | 8104
[73 empty] | TOTAL RAW | 27.372 |  | TOTAL MGD: |  | 4.547 |  |  | FINISHED CONWAY |  | START: | 10301032 |  | END: | 10305579 |  |  | Hypochlorite | 18 |  | 46.5
[76 empty] | TOTAL MGD: |  | 7.726 |  |  | FINISHED PERRY |  | START: | 33962270 |  | END: | 33969996 |  |  | Phosphate | 1999
[76 empty] | TOTAL MGD: |  | 10.695 |  |  | RAW PLANT 1 |  | START: | 31109937 |  | END: | 31120632 |  |  | Fluoride | 2950 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 4.986 |  |  | RAW PLANT 2 |  | START: | 31039486 |  | END: | 31044472 |  |  | Cal~Flo | 10.5 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.691 |  |  | RAW PLANT 3 |  | START: | 7659396 |  | END: | 7671087 |  |  | Zinc | 786
[76 empty] | TOTAL MGD: |  | 1.115 |  |  | DECANT |  | START: | 1878422 |  | END: | 1879537 |  |  | Polymer | 17
[76 empty] | TOTAL MGD: |  | 1.4839 |  |  | BLOW DOWN |  | START: | 9156.8455 |  | END: | 9158.3294 |  |  | NH3 | 11.76 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 760
23827169
44030879
10305579
33969996
31120632
31044472
7671087
1879537
9158.3294
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 19
DATE: | 2019-01-19 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-19 | [23 empty] | DATE: | 2019-01-19
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-19 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43484.0379 | 3,2,5 | 47 | 12 | 5 | 13 | 30 | 9.2 | 9.2 | 10.3 | 28.7 | ,1,3 | 10.1851 | 1,3 | 16.5499 | 26.735 | 3.3003 | 43484.0379 | 90.8557 | 8977.16 | 0 | 745.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6934 | 0.8709 | 1.7935 | 0.28207 | 0.26622 | 0 | 0.27763 | 0.21356 | 0.23989 | 1.4267 | 3 | 0.068815 | 0.068815 | 0.070685 | 1.0995 | 0.55081 | 0.09423 | 3.693 | 0.57022 | 4.3609 | 1.0713 | 0.53824 | 0.098195 | 3.6216 | 0.48718 | 6.0906 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.17 | 0.542 | 5 | 0.76 | 12 | 12.3 | 0.84524 |  | 6.21 | 0.309 | 4 | 0.64 | 12.9 | 5 | 0.41481 | 6.2 | 0.576 | 5 | 0.78 | 13.1 | 13.4 | 0.86444 | [13 empty] | 7.31 | 0.063 | 1 | 4.2 | 10.5 |  |  |  | 7.14 | 0.061 | 1 | 3.8 | 11.9 |  |  |  | 4.3 | 3.6 | 2.6 | [18 empty] | 11148 | [6 empty] | 0 | 0 | 0 | 350 | 180 | 415 | 890 | 840 | 0 | 730 | 730 | 820 | 750 |  | 1200 | 1200 | 1380 | 88 | 117 | 12 | 1300 | 230 | 275 | 48 | 64 | 7 | 680 | 110 | 215 |  | 1:00 | 0.76 | 12.3 | 20.6829 | 15.719 | 6.17 | 12 | 15 | 1.0479 | 10 | 6.5 | 0.72524 | 1:00 | 0.64 | 5 | 50.88 | 32.5632 | 6.21 | 12.9 | 15 | 2.1709 | 10 | 6.5 | 0.29481 | 1:00 | 0.78 | 13.4 | 20.1493 | 15.7164 | 6.2 | 13.1 | 15 | 1.0478 | 10 | 6.5 | 0.74444
2:00 | [72 empty] | 43484.3188 | 3,2,5 | 51 | 12 | 5 | 13 | 30 | 9.2 | 9.2 | 10.3 | 28.7 | ,1,3 | 10.6517 | 1,3 | 13.2883 | 23.94 | 2.1902 | 43484.3188 | 90.4645 | 9100.1348 | 0 | 745.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6934 | 0.91928 | 1.8151 | 0.28523 | 0.26939 | 0 | 0.30425 | 0.21941 | 0.24867 | 1.4267 | 5 | 0.068815 | 0.068815 | 0.069149 | 1.0995 | 0.55081 | 0.09423 | 3.773 | 0.57022 | 4.2023 | 1.1159 | 0.54665 | 0.098195 | 3.5788 | 0.48718 | 6.3455 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.61 | 16 | 16 | 15.7 | 115 | 205 | 11.8 | 0.462 |  | 5.95 | 8 | 0.055 | 6.2 | 12 |  | 6.06 | 9 | [8 empty] | 0.048 | [14 empty] | 0.022 | 1 | 0.57 |  | 0.046 | 0.012 | 1 | 0.53 |  | 0.031 | 1 | 0.7 | [38 empty] | 11100 | [6 empty] | 0 | 0 | 0 | 350 | 190 | 420 | 900 | 850 | 0 | 800 | 750 | 850 | 750 |  | 1200 | 1200 | 1350 | 88 | 117 | 12 | 1300 | 230 | 265 | 50 | 65 | 7 | 650 | 110 | 224 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43484.5733 | 3,2,5 | 51 | 12 | 5 | 13 | 30 | 9.2 | 9.2 | 10.3 | 28.7 | ,1,3 | 10.6517 | 1,3 | 13.2883 | 23.94 | 2.1902 | 43484.5733 | 90.4645 | 9100.1348 | 0 | 745.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6934 | 0.91928 | 1.8151 | 0.28523 | 0.26939 | 0 | 0.30425 | 0.21941 | 0.24867 | 1.4267 | 5 | 0.068815 | 0.068815 | 0.069149 | 1.0995 | 0.55081 | 0.09423 | 3.773 | 0.57022 | 4.2023 | 1.1159 | 0.54665 | 0.098195 | 3.5788 | 0.48718 | 6.3455 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.28 | 0.065 | 1 | 4.3 | 10.2 |  |  |  | 7.26 | 0.063 | 1 | 3.9 | 11.8 |  |  |  | 4.3 | 3.8 | 3.4 | [18 empty] | 11100 | [6 empty] | 0 | 0 | 0 | 350 | 190 | 420 | 900 | 850 | 0 | 800 | 750 | 850 | 750 |  | 1200 | 1200 | 1350 | 88 | 117 | 12 | 1300 | 230 | 265 | 50 | 65 | 7 | 650 | 110 | 224 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43484.8297 | 3,2,5 | 51 | 11 | 5 | 12 | 28 | 8 | 8 | 10 | 26 | ,1,3 | 10.9483 | 1,3 | 16.3699 | 27.3182 | 2.1902 | 43484.8297 | 90.7702 | 8731.2104 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2256 | 0.89025 | 1.8695 | 0.29388 | 0.27659 | 0 | 0.31186 | 0.23136 | 0.26305 | 1.4267 | 5 | 0.065947 | 0.065947 | 0.070168 | 1.0345 | 0.51432 | 0.090304 | 3.5601 | 0.52745 | 4.2855 | 1.2414 | 0.64101 | 0.10114 | 3.4983 | 0.54741 | 5.8356 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.6 | 16 | 16 | 15.5 | 124 | 205 | 12 | 0.487 |  | 6.09 | 8 | 0.052 | 6.06 | 9 |  | 6.03 | 9 | [8 empty] | 0.045 | [14 empty] | 0.02 | 1 | 0.56 |  | 0.044 | 0.016 | 1 | 0.55 |  | 0.026 | 1 | 0.72 | [38 empty] | 10395 | [6 empty] | 0 | 0 | 0 | 400 | 160 | 420 | 850 | 800 | 0 | 820 | 730 | 830 | 750 |  | 1000 | 1000 | 1330 | 72 | 95 | 10 | 1040 | 185 | 235 | 54 | 74 | 7 | 620 | 120 | 200 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.045 | [9 empty] | 6.13 | 0.469 | 5 | 0.76 | 12 | 12 | 0.82755 |  | 6.17 | 0.254 | 3 | 0.69 | 13 | 5 | 0.41481 | 6.16 | 0.518 | 5 | 0.8 | 13.5 | 13 | 0.84222 |  |  |  | 0.01 | [9 empty] | 7.5 | 0.063 | 1 | 4.3 | 10.3 | 21 | 56 | 0.021 | 7.2 | 0.061 | 1 | 3.8 | 12.2 | 21 | 58 | 0.012 | 4.3 | 3.7 | 3.3 | [55 empty] | 9:00 | 0.76 | 12 | 21.2 | 16.112 | 6.13 | 12 | 15 | 1.0741 | 10 | 6.5 | 0.70755 | 9:00 | 0.69 | 5 | 50.88 | 35.1072 | 6.17 | 13 | 15 | 2.3405 | 10 | 6.5 | 0.29481 | 9:00 | 0.8 | 13 | 20.7692 | 16.6154 | 6.16 | 13.5 | 15 | 1.1077 | 10 | 6.5 | 0.72222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.6 | 16 | 16 | 15.8 | 122 | 200 | 12 | 0.475 |  | 6 | 8 | 0.053 | 6.01 | 8 |  | 6.02 | 8 | [8 empty] | 0.043 | [14 empty] | 0.022 | 1 | 0.58 |  | 0.043 | 0.016 | 1 | 0.59 |  | 0.03 | 1 | 0.69 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.04 | 0.473 | 5 | 0.76 | 12.9 | 12 | 0.82755 |  | 6 | 0.273 | 3 | 0.66 | 13.5 | 5 | 0.3755 | 6.02 | 0.473 | 5 | 0.79 | 13.6 | 13 | 0.84222 | [13 empty] | 7.86 | 0.063 | 1 | 4.3 | 11 |  |  |  | 7.32 | 0.066 | 1 | 3.8 | 12.6 |  |  |  | 4.3 | 3.7 | 3.3 | [55 empty] | 13:00 | 0.76 | 12 | 21.2 | 16.112 | 6.04 | 12.9 | 15 | 1.0741 | 10 | 6.5 | 0.70755 | 13:00 | 0.66 | 5 | 50.88 | 33.5808 | 6 | 13.5 | 13 | 2.5831 | 10 | 6 | 0.2555 | 13:00 | 0.79 | 13 | 20.7692 | 16.4077 | 6.02 | 13.6 | 15 | 1.0938 | 10 | 6.5 | 0.72222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.58 | 16 | 17 | 16.1 | 125 | 203 | 12.3 | 0.483 |  | 6 | 9 | 0.056 | 6 | 9 |  | 6.01 | 9 | [8 empty] | 0.048 | [14 empty] | 0.022 | 1 | 0.57 |  | 0.049 | 0.016 | 1 | 0.56 |  | 0.033 | 1 | 0.63 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.46 | 0.063 | 1 | 4.4 | 11.2 |  |  |  | 7.3 | 0.063 | 1 | 3.6 | 12.8 |  |  |  | 4.6 | 3.4 | 2.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 17 | 17 | 15.7 | 114 | 203 | 12.4 | 0.467 |  | 5.94 | 10 | 0.049 | 6.06 | 10 |  | 6.13 | 10 | [8 empty] | 0.046 | [14 empty] | 0.021 | 1 | 0.61 |  | 0.045 | 0.016 | 1 | 0.58 |  | 0.021 | 1 | 0.7 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.048 | [9 empty] | 6.21 | 0.52 | 5 | 0.82 | 13.1 | 11 | 0.76858 |  | 6.12 | 0.309 | 3 | 0.82 | 13.4 | 5 | 0.41481 | 6.18 | 0.58 | 5 | 0.93 | 14.1 | 12 | 0.78667 |  |  |  | 0.028 |  |  |  |  | 0.028 |  |  |  | 0.013 | 7.49 | 0.062 | 1 | 4.4 | 11.1 | 20 | 56 | 0.016 | 7.36 | 0.055 | 1 | 4.2 | 12.4 | 21 | 57 | 0.02 | 4.6 | 3.3 | 2.5 | [55 empty] | 21:00 | 0.82 | 11 | 23.1273 | 18.9644 | 6.21 | 13.1 | 15 | 1.2643 | 10 | 6.5 | 0.64858 | 21:00 | 0.82 | 5 | 50.88 | 41.7216 | 6.12 | 13.4 | 15 | 2.7814 | 10 | 6.5 | 0.29481 | 21:00 | 0.93 | 12 | 22.5 | 20.925 | 6.18 | 14.1 | 15 | 1.395 | 10 | 6.5 | 0.66667
22:00 | [72 empty] | DOSE |  | TOTAL | 47 | 20 | 51 | 118 | 35.6 | 35.6 | 40.9 | 112.1 | 0 | 42.4368 | 0 | 59.4965 | 101.9333 | 9.8711 | TOTAL | 362.555 | 35908.64 | 0 | 2933.9207 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3059 | 3.5997 | 7.2931 | 1.1464 | 1.0816 | 0 | 1.198 | 0.88374 | 1.0003 | 5.7067 | 18 | 0.27239 | 0.27239 | 0.27915 | 4.3328 | 2.1667 | 0.373 | 14.799 | 2.2381 | 17.051 | 4.5446 | 2.2725 | 0.39573 | 14.2774 | 2.0089 | 24.6173 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.63 | 18 | 17 | 15.6 | 109 | 200 | 13.1 | 0.455 |  | 6.14 | 10 | 0.049 | 6.09 | 10 |  | 6.04 | 10 | [8 empty] | 0.044 | [14 empty] | 0.022 | 1 | 0.65 |  | 0.046 | 0.011 | 1 | 0.46 |  | 0.02 | 1 | 0.71 | [22 empty] | AVERAGE | 11.75 | 5 | 12.75 | 29.5 | 8.9 | 8.9 | 10.225 | 28.025 |  | 10.6092 |  | 14.8741 | 25.4833 | 2.4678 | AVERAGE | 90.6388 | 8977.16 |  | 733.4802 | 0 | 0 | 0 |  |  |  | 1.8265 | 0.89993 | 1.8233 | 0.2866 | 0.2704 |  | 0.2995 | 0.22093 | 0.25007 | 1.4267 | 4.5 | 0.068098 | 0.068098 | 0.069788 | 1.0832 | 0.54169 | 0.093249 | 3.6998 | 0.55953 | 4.2627 | 1.1361 | 0.56814 | 0.098931 | 3.5694 | 0.50223 | 6.1543 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.64 | 99 | 99 | 94.4 | 709 | 1216 | 73.6 | 2.829 | 0.093 | 36.12 | 53 | 0.314 | 36.42 | 58 | 0 | 36.29 | 55 | 0 | 24.55 | 2.004 | 20 | 3.1 | 50 | 47.3 | 3.2689 | 0.274 | 24.5 | 1.145 | 13 | 2.81 | 52.8 | 20 | 1.6199 | 24.56 | 2.147 | 20 | 3.3 | 54.3 | 51.4 | 3.3356 | 0.129 | 6 | 3.54 | 0.038 | 0.273 | 0.087 | 6 | 3.27 | 0.028 | 0.161 | 6 | 4.15 | 0.013 | 44.9 | 0.379 | 6 | 25.9 | 64.3 | 41 | 112 | 0.037 | 43.58 | 0.369 | 6 | 23.1 | 73.7 | 42 | 115 | 0.032 | 26.4 | 21.5 | 17.5 |  |  | MINIMUM | 11 | 5 | 12 | 28 | 8 | 8 | 10 | 26 |  | 10.1851 |  | 13.2883 | 23.94 | 2.1902 | MINIMUM | 90.4645 | 8731.2104 |  | 697.7974 | [6 empty] | 1.6934 | 0.8709 | 1.7935 | 0.28207 | 0.26622 |  | 0.27763 | 0.21356 | 0.23989 | 1.4267 | 3 | 0.065947 | 0.065947 | 0.069149 | 1.0345 | 0.51432 | 0.090304 | 3.5601 | 0.52745 | 4.2023 | 1.0713 | 0.53824 | 0.098195 | 3.4983 | 0.48718 | 5.8356 |  | MIN | 0.76 | 12.3 | 20.6829 | 15.719 | 6.17 | 12 | 15 | 1.0479 |  |  |  | MIN | 0.64 | 5 | 50.88 | 32.5632 | 6.21 | 12.9 | 15 | 2.1709 |  |  |  | MIN | 0.78 | 13.4 | 20.1493 | 15.7164 | 6.2 | 13.1 | 15 | 1.0478 |  |  |  | 1.0478
AVERAGE | 6.6067 | 16.5 | 16.5 | 15.7333 | 118.1667 | 202.6667 | 12.2667 | 0.4715 | 0.0465 | 6.02 | 8.8333 | 0.052333 | 6.07 | 9.6667 |  | 6.0483 | 9.1667 |  | 6.1375 | 0.501 | 5 | 0.775 | 12.5 | 11.825 | 0.81723 | 0.045667 | 6.125 | 0.28625 | 3.25 | 0.7025 | 13.2 | 5 | 0.40498 | 6.14 | 0.53675 | 5 | 0.825 | 13.575 | 12.85 | 0.83389 | 0.0215 | 1 | 0.59 | 0.019 | 0.0455 | 0.0145 | 1 | 0.545 | 0.028 | 0.026833 | 1 | 0.69167 | 0.013 | 7.4833 | 0.063167 | 1 | 4.3167 | 10.7167 | 20.5 | 56 | 0.0185 | 7.2633 | 0.0615 | 1 | 3.85 | 12.2833 | 21 | 57.5 | 0.016 | 4.4 | 3.5833 | 2.9167 |  |  | MAXIMUM | 12 | 5 | 13 | 30 | 9.2 | 9.2 | 10.3 | 28.7 |  | 10.9483 |  | 16.5499 | 27.3182 | 3.3003 | MAXIMUM | 90.8557 | 9100.1348 |  | 745.3744 | [6 empty] | 2.2256 | 0.91928 | 1.8695 | 0.29388 | 0.27659 |  | 0.31186 | 0.23136 | 0.26305 | 1.4267 | 5 | 0.068815 | 0.068815 | 0.070685 | 1.0995 | 0.55081 | 0.09423 | 3.773 | 0.57022 | 4.3609 | 1.2414 | 0.64101 | 0.10114 | 3.6216 | 0.54741 | 6.3455
MINIMUM | 6.58 | 16 | 16 | 15.5 | 109 | 200 | 11.8 | 0.455 | 0.045 | 5.94 | 8 | 0.049 | 6 | 8 |  | 6.01 | 8 |  | 6.04 | 0.469 | 5 | 0.76 | 12 | 11 | 0.76858 | 0.043 | 6 | 0.254 | 3 | 0.64 | 12.9 | 5 | 0.3755 | 6.02 | 0.473 | 5 | 0.78 | 13.1 | 12 | 0.78667 | 0.02 | 1 | 0.56 | 0.01 | 0.043 | 0.011 | 1 | 0.46 | 0.028 | 0.02 | 1 | 0.63 | 0.013 | 7.28 | 0.062 | 1 | 4.2 | 10.2 | 20 | 56 | 0.016 | 7.14 | 0.055 | 1 | 3.6 | 11.8 | 21 | 57 | 0.012 | 4.3 | 3.3 | 2.4 | [15 empty] | MIL/MIN |  | TOTAL | 43743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1450 | 720 | 1675 | 3540 | 3340 | 0 | 3150 | 2960 | 3350 | 3000 | 0 | 4600 | 4600 | 5410 | 336 | 446 | 46 | 4940 | 875 | 1040 | 202 | 268 | 28 | 2600 | 450 | 863
MAXIMUM | 6.63 | 18 | 17 | 16.1 | 125 | 205 | 13.1 | 0.487 | 0.048 | 6.14 | 10 | 0.056 | 6.2 | 12 |  | 6.13 | 10 |  | 6.21 | 0.542 | 5 | 0.82 | 13.1 | 12.3 | 0.84524 | 0.048 | 6.21 | 0.309 | 4 | 0.82 | 13.5 | 5 | 0.41481 | 6.2 | 0.58 | 5 | 0.93 | 14.1 | 13.4 | 0.86444 | 0.022 | 1 | 0.65 | 0.028 | 0.049 | 0.016 | 1 | 0.59 | 0.028 | 0.033 | 1 | 0.72 | 0.013 | 7.86 | 0.065 | 1 | 4.4 | 11.2 | 21 | 56 | 0.021 | 7.36 | 0.066 | 1 | 4.2 | 12.8 | 21 | 58 | 0.02 | 4.6 | 3.8 | 3.4 | [17 empty] | AVERAGE | 10935.75 | [9 empty] | 362.5 | 180 | 418.75 | 885 | 835 |  | 787.5 | 740 | 837.5 | 750 |  | 1150 | 1150 | 1352.5 | 84 | 111.5 | 11.5 | 1235 | 218.75 | 260 | 50.5 | 67 | 7 | 650 | 112.5 | 215.75
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0461 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.58 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.64 | [5 empty] | 6.1342 |  |  |  |  | 0.033 |  |  |  |  | 0.64 | [6 empty] | 0.033 | [16 empty] | Pump Station MIN |  | 2.4 | [17 empty] | MINIMUM | 10395 | [9 empty] | 350 | 160 | 415 | 850 | 800 |  | 730 | 730 | 820 | 750 |  | 1000 | 1000 | 1330 | 72 | 95 | 10 | 1040 | 185 | 235 | 48 | 64 | 7 | 620 | 110 | 200
[90 empty] | MAXIMUM | 11148 | [9 empty] | 400 | 190 | 420 | 900 | 850 |  | 820 | 750 | 850 | 750 |  | 1200 | 1200 | 1380 | 88 | 117 | 12 | 1300 | 230 | 275 | 54 | 74 | 7 | 680 | 120 | 224
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.115 |  | TOTAL MGD: |  | 0.005 |  |  | FINISHED SOUTH 1 |  | START: | 23827169 |  | END: | 23827174 |  |  | Alum | 4043 | 10200 | 10200 | 11700 | 11700 | 0 | [44 empty] | 0.78 | 13.4 | 20.1493 | 15.7164 | 6.2 | 13.1 | 15 | 1.0478
[73 empty] | FINISHED 2 | 13.438 |  | TOTAL MGD: |  | 11.11 |  |  | FINISHED SOUTH 2 |  | START: | 44030879 |  | END: | 44041989 |  |  | Caustic | 6940 | 8075 | 8075
[73 empty] | TOTAL RAW | 29.545 |  | TOTAL MGD: |  | 4.795 |  |  | FINISHED CONWAY |  | START: | 10305579 |  | END: | 10310374 |  |  | Hypochlorite | 16 |  | 45
[76 empty] | TOTAL MGD: |  | 8.643 |  |  | FINISHED PERRY |  | START: | 33969996 |  | END: | 33978639 |  |  | Phosphate | 1957
[76 empty] | TOTAL MGD: |  | 11.863 |  |  | RAW PLANT 1 |  | START: | 31120632 |  | END: | 31132495 |  |  | Fluoride | 2950 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 4.847 |  |  | RAW PLANT 2 |  | START: | 31044472 |  | END: | 31049319 |  |  | Cal~Flo | 6.37 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.835 |  |  | RAW PLANT 3 |  | START: | 7671087 |  | END: | 7683922 |  |  | Zinc | 805
[76 empty] | TOTAL MGD: |  | 1.298 |  |  | DECANT |  | START: | 1879537 |  | END: | 1880835 |  |  | Polymer | 16
[76 empty] | TOTAL MGD: |  | 1.8357 |  |  | BLOW DOWN |  | START: | 9158.3294 |  | END: | 9160.1651 |  |  | NH3 | 11.59 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 720
23827174
44041989
10310374
33978639
31132495
31049319
7683922
1880835
9160.1651
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 20
DATE: | 2019-01-20 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-20 | [23 empty] | DATE: | 2019-01-20
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-20 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43485.0008 | 3,2,5 | 51 | 11 | 5 | 12 | 28 | 8 | 8 | 10 | 26 | ,1,3 | 10.5264 | 1,3 | 12.4128 | 22.9392 | 2.5907 | 43485.0008 | 90.7702 | 8731.2104 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0031 | 0.89025 | 1.8695 | 0.29388 | 0.27659 | 0 | 0.31186 | 0.23136 | 0.26305 | 1.4267 | 6 | 0.065947 | 0.065947 | 0.070168 | 1.0345 | 0.51432 | 0.090304 | 3.7312 | 0.52745 | 4.2855 | 1.2414 | 0.64101 | 0.10114 | 3.5895 | 0.54741 | 5.9815 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.25 | 0.497 | 5 | 0.93 | 13.5 | 11 | 0.76858 |  | 6.2 | 0.285 | 3 | 0.45 | 13.8 | 5 | 0.41481 | 6.23 | 0.52 | 5 | 0.76 | 14 | 12 | 0.78667 | [13 empty] | 7.24 | 0.067 | 1 | 3.8 | 11.3 |  |  |  | 7.22 | 0.057 | 1 | 3.5 | 12.8 |  |  |  | 4.6 | 3.4 | 2.5 | [18 empty] | 10395 | [6 empty] | 0 | 0 | 0 | 360 | 160 | 420 | 850 | 800 | 0 | 820 | 730 | 830 | 750 |  | 1000 | 1000 | 1330 | 72 | 95 | 10 | 1100 | 185 | 235 | 54 | 74 | 7 | 640 | 120 | 205 |  | 1:00 | 0.93 | 11 | 23.1273 | 21.5084 | 6.25 | 13.5 | 15 | 1.4339 | 10 | 6.5 | 0.64858 | 1:00 | 0.45 | 5 | 50.88 | 22.896 | 6.2 | 13.8 | 15 | 1.5264 | 10 | 6.5 | 0.29481 | 1:00 | 0.76 | 12 | 22.5 | 17.1 | 6.23 | 14 | 15 | 1.14 | 10 | 6.5 | 0.66667
2:00 | [72 empty] | 43485.3405 | 3,2,5 | 34 | 10.5 | 5 | 11 | 26.5 | 7.4 | 7.4 | 9.5 | 24.3 | ,1,3 | 10.9829 | 1,3 | 13.3517 | 24.3346 | 2.5907 | 43485.3405 | 89.8648 | 8362.286 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8046 | 0.60152 | 1.7336 | 0.32598 | 0.28976 | 0 | 0.39552 | 0.2593 | 0.26968 | 1.4267 | 6 | 0.071294 | 0.069868 | 0.066641 | 1.1184 | 0.55017 | 0.097626 | 3.8338 | 0.61645 | 4.3373 | 1.0647 | 0.54709 | 0.10646 | 3.9332 | 0.48018 | 5.8356 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.55 | 18 | 17 | 15.5 | 115 | 201 | 12.5 | 0.443 |  | 5.98 | 10 | 0.047 | 6.07 | 10 |  | 6.05 | 10 | [8 empty] | 0.046 | [14 empty] | 0.016 | 1 | 0.51 |  | 0.045 | 0.013 | 1 | 0.32 |  | 0.02 | 1 | 0.61 | [38 empty] | 9740 | [6 empty] | 0 | 0 | 0 | 300 | 100 | 370 | 900 | 800 | 0 | 1040 | 750 | 780 | 750 |  | 1000 | 980 | 1200 | 72 | 94 | 10 | 1080 | 200 | 220 | 44 | 60 | 7 | 640 | 100 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43485.8405 | 3,2,5 | 34 | 10.5 | 5 | 11 | 26.5 | 7.4 | 7.4 | 9.5 | 24.3 | ,1,3 | 10.9829 | 1,3 | 13.3517 | 24.3346 | 2.5907 | 43485.8405 | 89.8648 | 8362.286 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8046 | 0.60152 | 1.7336 | 0.32598 | 0.28976 | 0 | 0.39552 | 0.2593 | 0.26968 | 1.4267 | 6 | 0.071294 | 0.069868 | 0.066641 | 1.1184 | 0.55017 | 0.097626 | 3.8338 | 0.61645 | 4.3373 | 1.0647 | 0.54709 | 0.10646 | 3.9332 | 0.48018 | 5.8356 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.31 | 0.064 | 1 | 4.2 | 11 |  |  |  | 7.27 | 0.056 | 1 | 4.2 | 12.6 |  |  |  | 4.4 | 3.6 | 3.3 | [18 empty] | 9740 | [6 empty] | 0 | 0 | 0 | 300 | 100 | 370 | 900 | 800 | 0 | 1040 | 750 | 780 | 750 |  | 1000 | 980 | 1200 | 72 | 94 | 10 | 1080 | 200 | 220 | 44 | 60 | 7 | 640 | 100 | 190 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.6 | 18 | 17 | 15.3 | 117 | 198 | 12.7 | 0.453 |  | 6 | 8 | 0.046 | 6.01 | 9 |  | 6.03 | 9 | [8 empty] | 0.041 | [14 empty] | 0.018 | 1 | 0.49 |  | 0.044 | 0.014 | 1 | 0.4 |  | 0.02 | 1 | 0.68 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.047 | [9 empty] | 6.25 | 0.463 | 5 | 0.79 | 12.6 | 10 | 0.70962 |  | 6.21 | 0.285 | 3 | 0.43 | 13.2 | 5 | 0.41481 | 6.23 | 0.53 | 5 | 0.76 | 14 | 11 | 0.73111 |  |  |  | 0.012 | [9 empty] | 7.39 | 0.066 | 1 | 4.2 | 11.5 | 21 | 56 | 0.02 | 7.37 | 0.063 | 1 | 3.9 | 12.6 | 22 | 57 | 0.013 | 4.4 | 3.6 | 3.1 | [55 empty] | 9:00 | 0.79 | 10 | 25.44 | 20.0976 | 6.25 | 12.6 | 15 | 1.3398 | 10 | 6.5 | 0.58962 | 9:00 | 0.43 | 5 | 50.88 | 21.8784 | 6.21 | 13.2 | 15 | 1.4586 | 10 | 6.5 | 0.29481 | 9:00 | 0.76 | 11 | 24.5455 | 18.6545 | 6.23 | 14 | 15 | 1.2436 | 10 | 6.5 | 0.61111
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.62 | 18 | 17 | 15.8 | 119 | 194 | 12.8 | 0.466 |  | 6.09 | 10 | 0.054 | 6 | 10 |  | 6.1 | 10 | [8 empty] | 0.04 | [14 empty] | 0.018 | 1 | 0.5 |  | 0.043 | 0.013 | 1 | 0.43 |  | 0.022 | 1 | 0.69 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.18 | 0.432 | 4 | 0.76 | 12.4 | 10 | 0.70962 |  | 6.14 | 0.283 | 3 | 0.45 | 13.1 | 5 | 0.41481 | 6.14 | 0.496 | 5 | 0.77 | 13.7 | 11 | 0.73111 | [13 empty] | 7.98 | 0.063 | 1 | 4.5 | 11.1 |  |  |  | 7.8 | 0.061 | 1 | 4 | 13 |  |  |  | 4.3 | 3.4 | 2.8 | [55 empty] | 13:00 | 0.76 | 10 | 25.44 | 19.3344 | 6.18 | 12.4 | 15 | 1.289 | 10 | 6.5 | 0.58962 | 13:00 | 0.45 | 5 | 50.88 | 22.896 | 6.14 | 13.1 | 15 | 1.5264 | 10 | 6.5 | 0.29481 | 13:00 | 0.77 | 11 | 24.5455 | 18.9 | 6.14 | 13.7 | 15 | 1.26 | 10 | 6.5 | 0.61111
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.6 | 17 | 17 | 15.9 | 118 | 194 | 12.7 | 0.46 |  | 6.19 | 8 | 0.05 | 6.13 | 9 |  | 6.2 | 8 | [8 empty] | 0.043 | [14 empty] | 0.039 | 1 | 0.55 |  | 0.045 | 0.03 | 1 | 0.42 |  | 0.028 | 1 | 0.68 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.55 | 0.066 | 1 | 4.2 | 11.5 |  |  |  | 7.7 | 0.063 | 1 | 4 | 13 |  |  |  | 4.3 | 3.4 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.57 | 17 | 17 | 15.4 | 106 | 198 | 12.8 | 0.427 |  | 6.1 | 10 | 0.048 | 6.13 | 9 |  | 6.06 | 9 | [8 empty] | 0.044 | [14 empty] | 0.043 | 1 | 0.68 |  | 0.046 | 0.01 | 1 | 0.33 |  | 0.021 | 1 | 0.86 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.041 | [9 empty] | 6.25 | 0.445 | 5 | 0.66 | 12.7 | 10.5 | 0.7391 |  | 6.24 | 0.403 | 4 | 0.4 | 13.6 | 5 | 0.41481 | 6.27 | 0.514 | 5 | 0.75 | 14.2 | 11 | 0.73111 |  |  |  | 0.012 | [9 empty] | 7.19 | 0.067 | 1 | 4.1 | 11 | 20 | 54 | 0.016 | 7.39 | 0.061 | 1 | 3.9 | 12.5 | 21 | 56 | 0.011 | 4.2 | 3.4 | 2.8 | [55 empty] | 21:00 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.25 | 12.7 | 15 | 1.0661 | 10 | 6.5 | 0.6191 | 21:00 | 0.4 | 5 | 50.88 | 20.352 | 6.24 | 13.6 | 15 | 1.3568 | 10 | 6.5 | 0.29481 | 21:00 | 0.75 | 11 | 24.5455 | 18.4091 | 6.27 | 14.2 | 15 | 1.2273 | 10 | 6.5 | 0.61111
22:00 | [72 empty] | DOSE |  | TOTAL | 32 | 15 | 34 | 81 | 22.8 | 22.8 | 29 | 74.6 | 0 | 32.4922 | 0 | 39.1162 | 71.6083 | 7.7721 | TOTAL | 270.4998 | 25455.7824 | 0 | 1966.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6122 | 2.0933 | 5.3368 | 0.94584 | 0.85611 | 0 | 1.1029 | 0.74996 | 0.8024 | 4.2801 | 18 | 0.20854 | 0.20568 | 0.20345 | 3.2712 | 1.6147 | 0.28556 | 11.3989 | 1.7604 | 12.9601 | 3.3708 | 1.7352 | 0.31407 | 11.4559 | 1.5078 | 17.6528 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 17 | 17 | 15.2 | 111 | 195 | 12.8 | 0.441 |  | 6.12 | 9 | 0.05 | 6.1 | 9 |  | 6.13 | 9 | [8 empty] | 0.046 | [14 empty] | 0.032 | 1 | 0.53 |  | 0.046 | 0.016 | 1 | 0.27 |  | 0.02 | 1 | 0.67 | [22 empty] | AVERAGE | 10.6667 | 5 | 11.3333 | 27 | 7.6 | 7.6 | 9.6667 | 24.8667 |  | 10.8307 |  | 13.0387 | 23.8694 | 2.5907 | AVERAGE | 90.1666 | 8485.2608 |  | 655.5066 | 0 | 0 | 0 |  |  |  | 1.8707 | 0.69776 | 1.7789 | 0.31528 | 0.28537 |  | 0.36764 | 0.24999 | 0.26747 | 1.4267 | 6 | 0.069512 | 0.068561 | 0.067817 | 1.0904 | 0.53822 | 0.095185 | 3.7996 | 0.58678 | 4.32 | 1.1236 | 0.5784 | 0.10469 | 3.8186 | 0.50259 | 5.8843 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.47 | 105 | 102 | 93.1 | 686 | 1180 | 76.3 | 2.69 | 0.088 | 36.48 | 55 | 0.295 | 36.44 | 56 | 0 | 36.57 | 55 | 0 | 24.93 | 1.837 | 19 | 3.14 | 51.2 | 41.5 | 2.9269 | 0.26 | 24.79 | 1.256 | 13 | 1.73 | 53.7 | 20 | 1.6592 | 24.87 | 2.06 | 20 | 3.04 | 55.9 | 45 | 2.98 | 0.166 | 6 | 3.26 | 0.024 | 0.269 | 0.096 | 6 | 2.17 | 0 | 0.131 | 6 | 4.19 | 0 | 44.66 | 0.393 | 6 | 25 | 67.4 | 41 | 110 | 0.036 | 44.75 | 0.361 | 6 | 23.5 | 76.5 | 43 | 113 | 0.024 | 26.2 | 20.8 | 17.3 |  |  | MINIMUM | 10.5 | 5 | 11 | 26.5 | 7.4 | 7.4 | 9.5 | 24.3 |  | 10.5264 |  | 12.4128 | 22.9392 | 2.5907 | MINIMUM | 89.8648 | 8362.286 |  | 634.3612 | [6 empty] | 1.8046 | 0.60152 | 1.7336 | 0.29388 | 0.27659 |  | 0.31186 | 0.23136 | 0.26305 | 1.4267 | 6 | 0.065947 | 0.065947 | 0.066641 | 1.0345 | 0.51432 | 0.090304 | 3.7312 | 0.52745 | 4.2855 | 1.0647 | 0.54709 | 0.10114 | 3.5895 | 0.48018 | 5.8356 |  | MIN | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.25 | 12.7 | 15 | 1.0661 |  |  |  | MIN | 0.4 | 5 | 50.88 | 20.352 | 6.24 | 13.6 | 15 | 1.3568 |  |  |  | MIN | 0.76 | 12 | 22.5 | 17.1 | 6.23 | 14 | 15 | 1.14 |  |  |  | 1.0661
AVERAGE | 6.5783 | 17.5 | 17 | 15.5167 | 114.3333 | 196.6667 | 12.7167 | 0.44833 | 0.044 | 6.08 | 9.1667 | 0.049167 | 6.0733 | 9.3333 |  | 6.095 | 9.1667 |  | 6.2325 | 0.45925 | 4.75 | 0.785 | 12.8 | 10.375 | 0.73173 | 0.043333 | 6.1975 | 0.314 | 3.25 | 0.4325 | 13.425 | 5 | 0.41481 | 6.2175 | 0.515 | 5 | 0.76 | 13.975 | 11.25 | 0.745 | 0.027667 | 1 | 0.54333 | 0.012 | 0.044833 | 0.016 | 1 | 0.36167 |  | 0.021833 | 1 | 0.69833 |  | 7.4433 | 0.0655 | 1 | 4.1667 | 11.2333 | 20.5 | 55 | 0.018 | 7.4583 | 0.060167 | 1 | 3.9167 | 12.75 | 21.5 | 56.5 | 0.012 | 4.3667 | 3.4667 | 2.8833 |  |  | MAXIMUM | 11 | 5 | 12 | 28 | 8 | 8 | 10 | 26 |  | 10.9829 |  | 13.3517 | 24.3346 | 2.5907 | MAXIMUM | 90.7702 | 8731.2104 |  | 697.7974 | [6 empty] | 2.0031 | 0.89025 | 1.8695 | 0.32598 | 0.28976 |  | 0.39552 | 0.2593 | 0.26968 | 1.4267 | 6 | 0.071294 | 0.069868 | 0.070168 | 1.1184 | 0.55017 | 0.097626 | 3.8338 | 0.61645 | 4.3373 | 1.2414 | 0.64101 | 0.10646 | 3.9332 | 0.54741 | 5.9815
MINIMUM | 6.53 | 17 | 17 | 15.2 | 106 | 194 | 12.5 | 0.427 | 0.041 | 5.98 | 8 | 0.046 | 6 | 9 |  | 6.03 | 8 |  | 6.18 | 0.432 | 4 | 0.66 | 12.4 | 10 | 0.70962 | 0.04 | 6.14 | 0.283 | 3 | 0.4 | 13.1 | 5 | 0.41481 | 6.14 | 0.496 | 5 | 0.75 | 13.7 | 11 | 0.73111 | 0.016 | 1 | 0.49 | 0.012 | 0.043 | 0.01 | 1 | 0.27 |  | 0.02 | 1 | 0.61 |  | 7.19 | 0.063 | 1 | 3.8 | 11 | 20 | 54 | 0.016 | 7.22 | 0.056 | 1 | 3.5 | 12.5 | 21 | 56 | 0.011 | 4.2 | 3.4 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 29875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 360 | 1160 | 2650 | 2400 | 0 | 2900 | 2230 | 2390 | 2250 | 0 | 3000 | 2960 | 3730 | 216 | 283 | 30 | 3260 | 585 | 675 | 142 | 194 | 21 | 1920 | 320 | 585
MAXIMUM | 6.62 | 18 | 17 | 15.9 | 119 | 201 | 12.8 | 0.466 | 0.047 | 6.19 | 10 | 0.054 | 6.13 | 10 |  | 6.2 | 10 |  | 6.25 | 0.497 | 5 | 0.93 | 13.5 | 11 | 0.76858 | 0.046 | 6.24 | 0.403 | 4 | 0.45 | 13.8 | 5 | 0.41481 | 6.27 | 0.53 | 5 | 0.77 | 14.2 | 12 | 0.78667 | 0.043 | 1 | 0.68 | 0.012 | 0.046 | 0.03 | 1 | 0.43 |  | 0.028 | 1 | 0.86 |  | 7.98 | 0.067 | 1 | 4.5 | 11.5 | 21 | 56 | 0.02 | 7.8 | 0.063 | 1 | 4.2 | 13 | 22 | 57 | 0.013 | 4.6 | 3.6 | 3.3 | [17 empty] | AVERAGE | 9958.3333 | [9 empty] | 320 | 120 | 386.6667 | 883.3333 | 800 |  | 966.6667 | 743.3333 | 796.6667 | 750 |  | 1000 | 986.6667 | 1243.3333 | 72 | 94.3333 | 10 | 1086.6667 | 195 | 225 | 47.3333 | 64.6667 | 7 | 640 | 106.6667 | 195
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0828 |  | TOTAL AVG COAG ALK: |  |  |  | 9.2222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.53 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.4 | [5 empty] | 6.2158 |  |  |  |  | 0.043 |  |  |  |  | 0.4 | [6 empty] | 0.043 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 9740 | [9 empty] | 300 | 100 | 370 | 850 | 800 |  | 820 | 730 | 780 | 750 |  | 1000 | 980 | 1200 | 72 | 94 | 10 | 1080 | 185 | 220 | 44 | 60 | 7 | 640 | 100 | 190
[90 empty] | MAXIMUM | 10395 | [9 empty] | 360 | 160 | 420 | 900 | 800 |  | 1040 | 750 | 830 | 750 |  | 1000 | 1000 | 1330 | 72 | 95 | 10 | 1100 | 200 | 235 | 54 | 74 | 7 | 640 | 120 | 205
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.628 |  | TOTAL MGD: |  | 0.002 |  |  | FINISHED SOUTH 1 |  | START: | 23827174 |  | END: | 23827176 |  |  | Alum | 366 | 10200 | 10200 | 11700 | 11700 | 0 | [44 empty] | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.25 | 12.7 | 15 | 1.0661
[73 empty] | FINISHED 2 | 12.282 |  | TOTAL MGD: |  | 10.626 |  |  | FINISHED SOUTH 2 |  | START: | 44041989 |  | END: | 44052615 |  |  | Caustic | 6854 | 8080 | 8080
[73 empty] | TOTAL RAW | 27.113 |  | TOTAL MGD: |  | 4.471 |  |  | FINISHED CONWAY |  | START: | 10310374 |  | END: | 10314845 |  |  | Hypochlorite | 14 |  | 43.5
[76 empty] | TOTAL MGD: |  | 7.811 |  |  | FINISHED PERRY |  | START: | 33978639 |  | END: | 33986450 |  |  | Phosphate | 1946
[76 empty] | TOTAL MGD: |  | 10.664 |  |  | RAW PLANT 1 |  | START: | 31132495 |  | END: | 31143159 |  |  | Fluoride | 2950 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 4.866 |  |  | RAW PLANT 2 |  | START: | 31049319 |  | END: | 31054185 |  |  | Cal~Flo | 11.03 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.583 |  |  | RAW PLANT 3 |  | START: | 7683922 |  | END: | 7695505 |  |  | Zinc | 804
[76 empty] | TOTAL MGD: |  | 1.106 |  |  | DECANT |  | START: | 1880835 |  | END: | 1881941 |  |  | Polymer | 15
[76 empty] | TOTAL MGD: |  | 1.6616 |  |  | BLOW DOWN |  | START: | 9160.1651 |  | END: | 9161.8267 |  |  | NH3 | 11.45 |  | BI-SUL | 1020
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827176
44052615
10314845
33986450
31143159
31054185
7695505
1881941
9161.8267
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 21
DATE: | 2019-01-21 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-21 | [23 empty] | DATE: | 2019-01-21
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-21 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43486.009 | 3,2,5 | 34 | 10.5 | 5 | 11 | 26.5 | 7.4 | 7.4 | 9.5 | 24.3 | ,1,3 | 10.9829 | 1,3 | 13.3517 | 24.3346 | 2.2445 | 43486.009 | 89.8648 | 8362.286 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8046 | 0.60152 | 1.7336 | 0.32598 | 0.28976 | 0 | 0.39552 | 0.2593 | 0.26968 | 1.4267 | 6 | 0.071294 | 0.069868 | 0.066641 | 1.1184 | 0.55017 | 0.097626 | 3.8338 | 0.61645 | 4.3373 | 1.0647 | 0.54709 | 0.10646 | 3.9332 | 0.48018 | 5.8356 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.15 | 0.42 | 4 | 0.69 | 12.3 | 10.5 | 0.7391 |  | 6.25 | 0.36 | 3 | 0.33 | 13 | 5 | 0.41481 | 6.24 | 0.427 | 4 | 0.78 | 13.8 | 11 | 0.73111 | [13 empty] | 7.4 | 0.061 | 1 | 4.1 | 11.3 |  |  |  | 7.37 | 0.064 | 1 | 3.8 | 12.2 |  |  |  | 4.1 | 3.4 | 2.7 | [18 empty] | 9740 | [6 empty] | 0 | 0 | 0 | 300 | 100 | 370 | 900 | 800 | 0 | 1040 | 750 | 780 | 750 |  | 1000 | 980 | 1200 | 72 | 94 | 10 | 1080 | 200 | 220 | 44 | 60 | 7 | 640 | 100 | 190 |  | 1:00 | 0.69 | 10.5 | 24.2286 | 16.7177 | 6.15 | 12.3 | 15 | 1.1145 | 10 | 6.5 | 0.6191 | 1:00 | 0.33 | 5 | 50.88 | 16.7904 | 6.25 | 13 | 15 | 1.1194 | 10 | 6.5 | 0.29481 | 1:00 | 0.78 | 11 | 24.5455 | 19.1455 | 6.24 | 13.8 | 15 | 1.2764 | 10 | 6.5 | 0.61111
2:00 | [72 empty] | 43486.3344 | 3,2,5 | 35 | 10.6 | 5 | 11.6 | 27.2 | 8.2 | 8.2 | 9.2 | 25.6 | ,1,3 | 10.2643 | 1,3 | 11.0506 | 21.3149 | 2.2406 | 43486.3344 | 88.9904 | 8362.286 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5199 | 0.6514 | 1.7418 | 0.31573 | 0.30138 | 0 | 0.37271 | 0.2295 | 0.26228 | 1.4267 | 6 | 0.063052 | 0.063052 | 0.068815 | 1.0934 | 0.52819 | 0.096912 | 3.7129 | 0.69817 | 3.9141 | 1.0995 | 0 | 0.09423 | 3.9126 | 0.52559 | 6.0259 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.61 | 16 | 17 | 15 | 115 | 192 | 12.4 | 0.449 |  | 6.02 | 9 | 0.054 | 6.12 | 9 |  | 6.08 | 9 | [8 empty] | 0.042 | [14 empty] | 0.028 | 1 | 0.5 |  | 0.049 | 0.013 | 1 | 0.25 |  | 0.035 | 1 | 0.64 | [38 empty] | 9900 | [6 empty] | 0 | 0 | 0 | 280 | 120 | 360 | 880 | 840 | 0 | 980 | 700 | 800 | 750 |  | 980 | 980 | 1200 | 78 | 100 | 11 | 1200 | 251 | 220 | 44 | 0 | 6 | 660 | 106 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43486.6566 | 3,2,5 | 42 | 11.5 | 5 | 12.5 | 29 | 8.8 | 8.8 | 9.8 | 27.4 | ,1,3 | 10.8979 | 1,3 | 11.3717 | 22.2696 | 2.2406 | 43486.6566 | 88.947 | 8854.1852 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5175 | 0.75874 | 1.726 | 0.31417 | 0.29764 | 0.099262 | 0.3613 | 0.22819 | 0.26165 | 1.5218 | 6 | 0.059952 | 0.059952 | 0.067293 | 1.0972 | 0.55124 | 0.098514 | 3.4853 | 0.68685 | 3.8959 | 1.1025 | 0.53034 | 0.1032 | 3.7587 | 0.65168 | 6.0441 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.23 | 0.058 | 1 | 4.1 | 10.6 |  |  |  | 7.32 | 0.061 | 1 | 3.9 | 11.6 |  |  |  | 3.8 | 3.4 | 3 | [18 empty] | 10550 | [6 empty] | 0 | 0 | 0 | 300 | 150 | 380 | 950 | 900 | 261 | 950 | 750 | 860 | 800 |  | 1000 | 1000 | 1250 | 84 | 112 | 12 | 1200 | 265 | 235 | 47 | 60 | 7 | 670 | 140 | 203 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43486.8188 | 3,2,5 | 47 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 11.5963 | 1,3 | 14.4202 | 26.0165 | 2.2406 | 43486.8188 | 90.8463 | 9407.5718 | 0 | 729.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7805 | 0.69242 | 1.7629 | 0.3296 | 0.33594 | 0.089485 | 0.37286 | 0.22526 | 0.25744 | 1.5218 | 1.5 | 0.059206 | 0.060085 | 0.069995 | 1.0728 | 0.54861 | 0.096324 | 3.5925 | 0.60823 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.7819 | 0.54199 | 6.009 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.53 | 16 | 17 | 15.1 | 115 | 191 | 12.2 | 0.448 |  | 6.08 | 9 | 0.052 | 6.09 | 9 |  | 6.13 | 9 | [8 empty] | 0.04 | [14 empty] | 0.028 | 1 | 0.47 |  | 0.044 | 0.012 | 1 | 0.24 |  | 0.036 | 1 | 0.63 | [38 empty] | 11184 | [6 empty] | 0 | 0 | 0 | 360 | 140 | 400 | 1040 | 1060 | 240 | 1000 | 770 | 880 | 800 |  | 1010 | 1025 | 1340 | 84 | 114 | 12 | 1240 | 240 | 248 | 46 | 62 | 7 | 720 | 120 | 208 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.034 | [9 empty] | 6.19 | 0.467 | 4 | 0.74 | 11.8 | 10.5 | 0.7391 |  | 6.23 | 0.308 | 3 | 0.4 | 12.7 | 5 | 0.41481 | 6.24 | 0.402 | 4 | 0.73 | 13.5 | 11 | 0.73111 |  |  |  | 0.011 | [9 empty] | 7.49 | 0.054 | 1 | 4 | 12.1 | 24 | 65 | 0.022 | 7.45 | 0.06 | 1 | 3.9 | 11.6 | 22 | 64 | 0.012 | 4.1 | 3.3 | 3 | [55 empty] | 9:00 | 0.74 | 10.5 | 24.2286 | 17.9291 | 6.19 | 11.8 | 15 | 1.1953 | 10 | 6.5 | 0.6191 | 9:00 | 0.4 | 5 | 50.88 | 20.352 | 6.23 | 12.7 | 15 | 1.3568 | 10 | 6.5 | 0.29481 | 9:00 | 0.73 | 11 | 24.5455 | 17.9182 | 6.24 | 13.5 | 15 | 1.1945 | 10 | 6.5 | 0.61111
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.58 | 17 | 17 | 15.2 | 116 | 190 | 12 | 0.445 |  | 6.1 | 9 | 0.054 | 6.09 | 8 |  | 6.08 | 9 | [8 empty] | 0.046 | [14 empty] | 0.03 | 1 | 0.4 |  | 0.05 | 0.018 | 1 | 0.26 |  | 0.039 | 1 | 0.64 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.2 | 0.396 | 3 | 0.73 | 12 | 10.5 | 0.7391 |  | 6.22 | 0.298 | 2 | 0.4 | 13.1 | 5 | 0.41481 | 6.22 | 0.46 | 4 | 0.8 | 13.3 | 11 | 0.73111 | [13 empty] | 7.44 | 0.058 | 1 | 4.3 | 10.7 |  |  |  | 7.33 | 0.064 | 1 | 3.8 | 12.3 |  |  |  | 4.1 | 3.3 | 2.4 | [55 empty] | 13:00 | 0.73 | 10.5 | 24.2286 | 17.6869 | 6.2 | 12 | 15 | 1.1791 | 10 | 6.5 | 0.6191 | 13:00 | 0.4 | 5 | 50.88 | 20.352 | 6.22 | 13.1 | 15 | 1.3568 | 10 | 6.5 | 0.29481 | 13:00 | 0.8 | 11 | 24.5455 | 19.6364 | 6.22 | 13.3 | 15 | 1.3091 | 10 | 6.5 | 0.61111
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.53 | 16 | 17 | 15 | 114 | 187 | 12 | 0.45 |  | 6.13 | 8 | 0.054 | 6.1 | 8 |  | 6.11 | 9 | [8 empty] | 0.045 | [14 empty] | 0.03 | 1 | 0.41 |  | 0.043 | 0.02 | 1 | 0.3 |  | 0.039 | 1 | 0.66 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17;00 | [53 empty] | 7.33 | 0.061 | 1 | 4.4 | 11 |  |  |  | 7.24 | 0.066 | 1 | 3 | 12 |  |  |  | 4.1 | 3.3 | 2.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.58 | 16 | 17 | 15 | 113 | 187 | 11.8 | 0.449 |  | 6.05 | 9 | 0.049 | 5.99 | 9 |  | 5.98 | 9 | [8 empty] | 0.047 | [14 empty] | 0.023 | 1 | 0.46 |  | 0.048 | 0.04 | 1 | 0.44 |  | 0.027 | 1 | 0.53 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.041 | [9 empty] | 6.18 | 0.518 | 4 | 0.76 | 11.6 | 12 | 0.82755 |  | 6.21 | 0.328 | 3 | 0.6 | 12.7 | 5.3 | 0.4325 | 6.2 | 0.447 | 4 | 0.8 | 13 | 13 | 0.84222 |  |  |  | 0.012 |  |  |  |  | 0.017 |  |  |  | 0.014 | 7.42 | 0.062 | 1 | 4.5 | 10.1 | 20 | 61 | 0.016 | 7.38 | 0.064 | 1 | 3.9 | 11.5 | 20 | 60 | 0.019 | 4.1 | 3.2 | 2.3 | [55 empty] | 21:00 | 0.76 | 12 | 21.2 | 16.112 | 6.18 | 11.6 | 15 | 1.0741 | 10 | 6.5 | 0.70755 | 21:00 | 0.6 | 5.3 | 48 | 28.8 | 6.21 | 12.7 | 15 | 1.92 | 10 | 6.5 | 0.3125 | 21:00 | 0.8 | 13 | 20.7692 | 16.6154 | 6.2 | 13 | 15 | 1.1077 | 10 | 6.5 | 0.72222
22:00 | [72 empty] | DOSE |  | TOTAL | 44.6 | 20.1 | 48.1 | 112.8 | 33.4 | 33.4 | 38.6 | 105.4 | 0 | 43.7414 | 0 | 50.1941 | 93.9355 | 8.9664 | TOTAL | 358.6485 | 34986.329 | 0 | 2632.5991 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6225 | 2.7041 | 6.9643 | 1.2855 | 1.2247 | 0.18875 | 1.5024 | 0.94225 | 1.0511 | 5.897 | 19.5 | 0.2535 | 0.25296 | 0.27274 | 4.3817 | 2.1782 | 0.38938 | 14.6245 | 2.6097 | 16.1675 | 4.3137 | 1.6092 | 0.40404 | 15.3864 | 2.1994 | 23.9146 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.47 | 17 | 17 | 15.1 | 113 | 189 | 11.6 | 0.447 |  | 6.12 | 9 | 0.051 | 6.09 | 9 |  | 6.09 | 9 | [8 empty] | 0.046 | [14 empty] | 0.022 | 1 | 0.42 |  | 0.044 | 0.021 | 1 | 0.39 |  | 0.024 | 1 | 0.65 | [22 empty] | AVERAGE | 11.15 | 5.025 | 12.025 | 28.2 | 8.35 | 8.35 | 9.65 | 26.35 |  | 10.9354 |  | 12.5485 | 23.4839 | 2.2416 | AVERAGE | 89.6621 | 8746.5822 |  | 658.1498 | 0 | 0 | 0 |  |  |  | 1.6556 | 0.67602 | 1.7411 | 0.32137 | 0.30618 | 0.047187 | 0.3756 | 0.23556 | 0.26276 | 1.4742 | 4.875 | 0.063376 | 0.063239 | 0.068186 | 1.0954 | 0.54455 | 0.097344 | 3.6561 | 0.65243 | 4.0419 | 1.0784 | 0.40229 | 0.10101 | 3.8466 | 0.54986 | 5.9786 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.3 | 98 | 102 | 90.4 | 686 | 1136 | 72 | 2.688 | 0.075 | 36.5 | 53 | 0.314 | 36.48 | 52 | 0 | 36.47 | 54 | 0 | 24.72 | 1.801 | 15 | 2.92 | 47.7 | 43.5 | 3.0449 | 0.266 | 24.91 | 1.294 | 11 | 1.73 | 51.5 | 20.3 | 1.6769 | 24.9 | 1.736 | 16 | 3.11 | 53.6 | 46 | 3.0356 | 0.161 | 6 | 2.66 | 0.023 | 0.278 | 0.124 | 6 |  | 0.017 | 0.2 | 6 | 3.75 | 0.014 | 44.31 | 0.354 | 6 | 25.4 | 65.8 | 44 | 126 | 0.038 | 44.09 | 0.379 | 6 | 22.3 | 71.2 | 42 | 124 | 0.031 | 24.3 | 19.9 | 15.6 |  |  | MINIMUM | 10.5 | 5 | 11 | 26.5 | 7.4 | 7.4 | 9.2 | 24.3 |  | 10.2643 |  | 11.0506 | 21.3149 | 2.2406 | MINIMUM | 88.947 | 8362.286 |  | 634.3612 | [6 empty] | 1.5175 | 0.60152 | 1.726 | 0.31417 | 0.28976 | 0 | 0.3613 | 0.22526 | 0.25744 | 1.4267 | 1.5 | 0.059206 | 0.059952 | 0.066641 | 1.0728 | 0.52819 | 0.096324 | 3.4853 | 0.60823 | 3.8959 | 1.047 | 0 | 0.09423 | 3.7587 | 0.48018 | 5.8356 |  | MIN | 0.76 | 12 | 21.2 | 16.112 | 6.18 | 11.6 | 15 | 1.0741 |  |  |  | MIN | 0.33 | 5 | 50.88 | 16.7904 | 6.25 | 13 | 15 | 1.1194 |  |  |  | MIN | 0.8 | 13 | 20.7692 | 16.6154 | 6.2 | 13 | 15 | 1.1077 |  |  |  | 1.0741
AVERAGE | 6.55 | 16.3333 | 17 | 15.0667 | 114.3333 | 189.3333 | 12 | 0.448 | 0.0375 | 6.0833 | 8.8333 | 0.052333 | 6.08 | 8.6667 |  | 6.0783 | 9 |  | 6.18 | 0.45025 | 3.75 | 0.73 | 11.925 | 10.875 | 0.76121 | 0.044333 | 6.2275 | 0.3235 | 2.75 | 0.4325 | 12.875 | 5.075 | 0.41923 | 6.225 | 0.434 | 4 | 0.7775 | 13.4 | 11.5 | 0.75889 | 0.026833 | 1 | 0.44333 | 0.0115 | 0.046333 | 0.020667 | 1 |  | 0.017 | 0.033333 | 1 | 0.625 | 0.014 | 7.385 | 0.059 | 1 | 4.2333 | 10.9667 | 22 | 63 | 0.019 | 7.3483 | 0.063167 | 1 | 3.7167 | 11.8667 | 21 | 62 | 0.0155 | 4.05 | 3.3167 | 2.6 |  |  | MAXIMUM | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 |  | 11.5963 |  | 14.4202 | 26.0165 | 2.2445 | MAXIMUM | 90.8463 | 9407.5718 |  | 729.5154 | [6 empty] | 1.8046 | 0.75874 | 1.7629 | 0.3296 | 0.33594 | 0.099262 | 0.39552 | 0.2593 | 0.26968 | 1.5218 | 6 | 0.071294 | 0.069868 | 0.069995 | 1.1184 | 0.55124 | 0.098514 | 3.8338 | 0.69817 | 4.3373 | 1.1025 | 0.54709 | 0.10646 | 3.9332 | 0.65168 | 6.0441
MINIMUM | 6.47 | 16 | 17 | 15 | 113 | 187 | 11.6 | 0.445 | 0.034 | 6.02 | 8 | 0.049 | 5.99 | 8 |  | 5.98 | 9 |  | 6.15 | 0.396 | 3 | 0.69 | 11.6 | 10.5 | 0.7391 | 0.04 | 6.21 | 0.298 | 2 | 0.33 | 12.7 | 5 | 0.41481 | 6.2 | 0.402 | 4 | 0.73 | 13 | 11 | 0.73111 | 0.022 | 1 | 0.4 | 0.011 | 0.043 | 0.012 | 1 |  | 0.017 | 0.024 | 1 | 0.53 | 0.014 | 7.23 | 0.054 | 1 | 4 | 10.1 | 20 | 61 | 0.016 | 7.24 | 0.06 | 1 | 3 | 11.5 | 20 | 60 | 0.012 | 3.8 | 3.2 | 2.2 | [15 empty] | MIL/MIN |  | TOTAL | 41374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 510 | 1510 | 3770 | 3600 | 501 | 3970 | 2970 | 3320 | 3100 | 0 | 3990 | 3985 | 4990 | 318 | 420 | 45 | 4720 | 956 | 923 | 181 | 182 | 27 | 2690 | 466 | 791
MAXIMUM | 6.61 | 17 | 17 | 15.2 | 116 | 192 | 12.4 | 0.45 | 0.041 | 6.13 | 9 | 0.054 | 6.12 | 9 |  | 6.13 | 9 |  | 6.2 | 0.518 | 4 | 0.76 | 12.3 | 12 | 0.82755 | 0.047 | 6.25 | 0.36 | 3 | 0.6 | 13.1 | 5.3 | 0.4325 | 6.24 | 0.46 | 4 | 0.8 | 13.8 | 13 | 0.84222 | 0.03 | 1 | 0.5 | 0.012 | 0.05 | 0.04 | 1 |  | 0.017 | 0.039 | 1 | 0.66 | 0.014 | 7.49 | 0.062 | 1 | 4.5 | 12.1 | 24 | 65 | 0.022 | 7.45 | 0.066 | 1 | 3.9 | 12.3 | 22 | 64 | 0.019 | 4.1 | 3.4 | 3 | [17 empty] | AVERAGE | 10343.5 | [9 empty] | 310 | 127.5 | 377.5 | 942.5 | 900 | 125.25 | 992.5 | 742.5 | 830 | 775 |  | 997.5 | 996.25 | 1247.5 | 79.5 | 105 | 11.25 | 1180 | 239 | 230.75 | 45.25 | 45.5 | 6.75 | 672.5 | 116.5 | 197.75
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0806 |  | TOTAL AVG COAG ALK: |  |  |  | 8.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.518 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.33 | [5 empty] | 6.2108 |  |  |  |  | 0.04 |  |  |  |  | 0.33 | [6 empty] | 0.04 | [16 empty] | Pump Station MIN |  | 2.2 | [17 empty] | MINIMUM | 9740 | [9 empty] | 280 | 100 | 360 | 880 | 800 | 0 | 950 | 700 | 780 | 750 |  | 980 | 980 | 1200 | 72 | 94 | 10 | 1080 | 200 | 220 | 44 | 0 | 6 | 640 | 100 | 190
[90 empty] | MAXIMUM | 11184 | [9 empty] | 360 | 150 | 400 | 1040 | 1060 | 261 | 1040 | 770 | 880 | 800 |  | 1010 | 1025 | 1340 | 84 | 114 | 12 | 1240 | 265 | 248 | 47 | 62 | 7 | 720 | 140 | 208
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.194 |  | TOTAL MGD: |  | 0.012 |  |  | FINISHED SOUTH 1 |  | START: | 23827176 |  | END: | 23827188 |  |  | Alum | 4011 | 8976 | 8976 | 11500 | 11500 | 0 | [44 empty] | 0.76 | 12 | 21.2 | 16.112 | 6.18 | 11.6 | 15 | 1.0741
[73 empty] | FINISHED 2 | 12.897 |  | TOTAL MGD: |  | 11.182 |  |  | FINISHED SOUTH 2 |  | START: | 44052615 |  | END: | 44063797 |  |  | Caustic | 6785 | 8036 | 8036
[73 empty] | TOTAL RAW | 28.606 |  | TOTAL MGD: |  | 4.472 |  |  | FINISHED CONWAY |  | START: | 10314845 |  | END: | 10319317 |  |  | Hypochlorite | 17 |  | 46
[76 empty] | TOTAL MGD: |  | 8.425 |  |  | FINISHED PERRY |  | START: | 33986450 |  | END: | 33994875 |  |  | Phosphate | 1902
[76 empty] | TOTAL MGD: |  | 11.318 |  |  | RAW PLANT 1 |  | START: | 31143159 |  | END: | 31154477 |  |  | Fluoride | 2900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.124 |  |  | RAW PLANT 2 |  | START: | 31054185 |  | END: | 31059309 |  |  | Cal~Flo | 7.15 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.164 |  |  | RAW PLANT 3 |  | START: | 7695505 |  | END: | 7707669 |  |  | Zinc | 809
[76 empty] | TOTAL MGD: |  | 0.962 |  |  | DECANT |  | START: | 1881941 |  | END: | 1882903 |  |  | Polymer | 15
[76 empty] | TOTAL MGD: |  | 1.0524 |  |  | BLOW DOWN |  | START: | 9161.8267 |  | END: | 9162.8791 |  |  | NH3 | 11.29 |  | BI-SUL | 1010
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 737
23827188
44063797
10319317
33994875
31154477
31059309
7707669
1882903
9162.8791
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 22
DATE: | 2019-01-22 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 14 |  | 18 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 17 |  | 21 | [23 empty] | 6:00 - 18:00 |  | 14 |  | 18 | [37 empty] | 6:00 - 18:00 |  | 14 |  | 18
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 17 |  | 21 | [37 empty] | 18:00 - 6:00 |  | 17 |  | 21
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-22 | [23 empty] | DATE: | 2019-01-22
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-22 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43487.0254 | 3,2,5 | 47 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 11.5963 | 1,3 | 14.4202 | 26.0165 | 1.9536 | 43487.0254 | 90.8463 | 9469.0592 | 0 | 729.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9041 | 0.79133 | 1.7629 | 0.3296 | 0.33594 | 0.089485 | 0.37286 | 0.22526 | 0.25744 | 1.5218 | 1.5 | 0.059206 | 0.060085 | 0.05 | 1.0728 | 0.54861 | 0.096324 | 3.5925 | 0.60823 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.7819 | 0.54199 | 6.2112 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.1 | 0.503 | 4 | 0.74 | 11.5 | 12 | 0.82755 |  | 6.2 | 0.627 | 5 | 0.39 | 12.5 | 5.3 | 0.4325 | 6.24 | 0.523 | 5 | 0.75 | 13 | 13 | 0.84222 | [13 empty] | 7.39 | 0.059 | 1 | 4.2 | 10.8 |  |  |  | 7.19 | 0.062 | 1 | 4 | 11.1 |  |  |  | 4.3 | 3.1 | 2.4 | [18 empty] | 11184 | [6 empty] | 0 | 0 | 0 | 385 | 160 | 400 | 1040 | 1060 | 240 | 1000 | 770 | 880 | 800 |  | 1010 | 1025 | 1050 | 84 | 114 | 12 | 1240 | 240 | 248 | 46 | 62 | 7 | 720 | 120 | 215 |  | 1:00 | 0.74 | 12 | 21.2 | 15.688 | 6.1 | 11.5 | 15 | 1.0459 | 10 | 6.5 | 0.70755 | 1:00 | 0.39 | 5.3 | 48 | 18.72 | 6.2 | 12.5 | 15 | 1.248 | 10 | 6.5 | 0.3125 | 1:00 | 0.75 | 13 | 20.7692 | 15.5769 | 6.24 | 13 | 15 | 1.0385 | 10 | 6.5 | 0.72222
2:00 | [72 empty] | 43487.3234 | 3,2,5 | 50 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 10.0368 | 1,3 | 12.1493 | 22.1861 | 2.4048 | 43487.3234 | 90.164 | 9592.034 | 0 | 729.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9041 | 0.79133 | 1.7629 | 0.3296 | 0.33277 | 0.29828 | 0.59657 | 0.22819 | 0.25159 | 1.52 | 1 | 0.059792 | 0.059792 | 0.054847 | 1.0856 | 0.54861 | 0.096324 | 3.6796 | 0.60823 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.8568 | 0.56006 | 6.2112 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.44 | 16 | 17 | 15 | 106 | 189 | 11.2 | 0.401 |  | 6.23 | 10 | 0.047 | 6.14 | 9 |  | 6.16 | 10 | [8 empty] | 0.045 | [14 empty] | 0.018 | 1 | 0.4 |  | 0.043 | 0.018 | 1 | 0.37 |  | 0.023 | 1 | 0.65 | [38 empty] | 11100 | [6 empty] | 0 | 0 | 0 | 385 | 160 | 400 | 1040 | 1050 | 400 | 800 | 780 | 860 | 800 |  | 1020 | 1020 | 1050 | 85 | 114 | 12 | 1300 | 240 | 248 | 46 | 62 | 7 | 710 | 124 | 215 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43487.6561 | 3,2,5 | 50 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 10.0368 | 1,3 | 12.1493 | 22.1861 | 2.4048 | 43487.6561 | 85.2903 | 9592.034 | 0 | 729.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9041 | 0.79133 | 1.7629 | 0.3296 | 0.33277 | 0.29828 | 0.522 | 0.22819 | 0.25159 | 1.52 | 1 | 0.059792 | 0.059792 | 0.054847 | 1.0856 | 0.54861 | 0.096324 | 3.6796 | 0.60823 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.8568 | 0.56006 | 6.2112 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.3 | 0.061 | 1 | 4.3 | 9.6 |  |  |  | 7.22 | 0.062 | 1 | 4.1 | 10.7 |  |  |  | 4.2 | 3.3 | 3.3 | [18 empty] | 10500 | [6 empty] | 0 | 0 | 0 | 385 | 160 | 400 | 1040 | 1050 | 400 | 700 | 780 | 860 | 800 |  | 1020 | 1020 | 1050 | 85 | 114 | 12 | 1300 | 240 | 248 | 46 | 62 | 7 | 710 | 124 | 215 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43487.8231 | 3,2,5 | 50 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 12.9658 | 1,3 | 13.8355 | 26.8013 | 2.4048 | 43487.8231 | 85.7776 | 9223.1096 | 0 | 729.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0278 | 0.79133 | 1.6747 | 0.31693 | 0.27573 | 0.22371 | 0.261 | 0.20478 | 0.22819 | 1.5218 | 4.5 | 0.059792 | 0.060378 | 0.050146 | 1.1239 | 0.54861 | 0.096324 | 3.6268 | 0.58289 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.8823 | 0.60974 | 6.2112 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.57 | 16 | 16 | 15 | 107 | 189 | 11 | 0.425 |  | 6.2 | 8 | 0.052 | 6.1 | 8 |  | 6.098 | 8 | [8 empty] | 0.043 | [14 empty] | 0.019 | 1 | 0.65 |  | 0.044 | 0.02 | 1 | 0.48 |  | 0.023 | 1 | 0.6 | [38 empty] | 10560 | [6 empty] | 0 | 0 | 0 | 410 | 160 | 380 | 1000 | 870 | 300 | 350 | 700 | 780 | 800 |  | 1020 | 1030 | 960 | 88 | 114 | 12 | 1220 | 230 | 248 | 46 | 62 | 7 | 740 | 135 | 215 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.037 | [9 empty] | 6.18 | 0.543 | 4 | 0.86 | 10.9 | 12 | 0.82755 |  | 6.23 | 0.626 | 3 | 0.39 | 12 | 5.3 | 0.4325 | 6.24 | 0.63 | 4 | 0.86 | 12.6 | 13 | 0.84222 |  |  |  | 0.01 | [9 empty] | 7.5 | 0.056 | 1 | 4.2 | 11 | 23 | 65 | 0.015 | 7.32 | 0.055 | 1 | 3.9 | 10.6 | 25 | 60 | 0.01 | 4.2 | 3.5 | 3.1 | [55 empty] | 9:00 | 0.86 | 12 | 21.2 | 18.232 | 6.18 | 10.9 | 15 | 1.2155 | 10 | 6.5 | 0.70755 | 9:00 | 0.39 | 5.3 | 48 | 18.72 | 6.23 | 12 | 15 | 1.248 | 10 | 6.5 | 0.3125 | 9:00 | 0.86 | 13 | 20.7692 | 17.8615 | 6.24 | 12.6 | 15 | 1.1908 | 10 | 6.5 | 0.72222
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.56 | 16 | 17 | 15 | 105 | 189 | 11 | 0.435 |  | 6.07 | 8 | 0.053 | 6.109 | 9 |  | 6.06 | 8 | [8 empty] | 0.042 | [14 empty] | 0.02 | 1 | 0.63 |  | 0.043 | 0.02 | 1 | 0.46 |  | 0.03 | 1 | 0.63 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.17 | 0.51 | 4 | 0.84 | 11.4 | 12 | 0.82755 |  | 6.13 | 0.532 | 3 | 0.39 | 12.3 | 5.3 | 0.4325 | 6.28 | 0.569 | 4 | 0.8 | 12.5 | 13 | 0.84222 | [13 empty] | 7.32 | 0.059 | 1 | 4.2 | 9.7 |  |  |  | 7.34 | 0.061 | 1 | 3.8 | 11.4 |  |  |  | 4.2 | 3.6 | 2.4 | [55 empty] | 13:00 | 0.84 | 12 | 21.2 | 17.808 | 6.17 | 11.4 | 15 | 1.1872 | 10 | 6.5 | 0.70755 | 13:00 | 0.39 | 5.3 | 48 | 18.72 | 6.13 | 12.3 | 15 | 1.248 | 10 | 6.5 | 0.3125 | 13:00 | 0.8 | 13 | 20.7692 | 16.6154 | 6.28 | 12.5 | 15 | 1.1077 | 10 | 6.5 | 0.72222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.57 | 16 | 17 | 14.9 | 106 | 188 | 11 | 0.441 |  | 6.17 | 8 | 0.058 | 6.1 | 8 |  | 6.12 | 8 | [8 empty] | 0.046 | [14 empty] | 0.018 | 1 | 0.6 |  | 0.044 | 0.019 | 1 | 0.36 |  | 0.031 | 1 | 0.69 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.52 | 0.056 | 1 | 4.1 | 10 |  |  |  | 7.54 | 0.063 | 1 | 4 | 11 |  |  |  | 4.2 | 3.6 | 2.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.58 | 17 | 17 | 14.5 | 106 | 185 | 10.9 | 0.428 |  | 6.25 | 10 | 0.054 | 6.36 | 12 |  | 6.3 | 10 | [8 empty] | 0.047 | [14 empty] | 0.024 | 1 | 0.49 |  | 0.046 | 0.012 | 1 | 0.58 |  | 0.019 | 1 | 0.54 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.031 | [9 empty] | 6.27 | 0.375 | 5 | 0.78 | 10.9 | 12 | 0.82755 |  | 6.32 | 0.441 | 4 | 0.72 | 11.9 | 5.5 | 0.44429 | 6.33 | 0.467 | 5 | 0.75 | 12.4 | 13 | 0.84222 |  |  |  | 0.014 | [9 empty] | 7.7 | 0.063 | 1 | 4.3 | 10 | 21 | 62 | 0.005 | 7.6 | 0.065 | 1 | 4 | 10.9 | 22 | 60 | 0.013 | 4.3 | 3.5 | 2.6 | [55 empty] | 21:00 | 0.78 | 12 | 21.2 | 16.536 | 6.27 | 10.9 | 15 | 1.1024 | 10 | 6.5 | 0.70755 | 21:00 | 0.72 | 5.5 | 46.2545 | 33.3033 | 6.32 | 11.9 | 15 | 2.2202 | 10 | 6.5 | 0.32429 | 21:00 | 0.75 | 13 | 20.7692 | 15.5769 | 6.33 | 12.4 | 15 | 1.0385 | 10 | 6.5 | 0.72222
22:00 | [72 empty] | DOSE |  | TOTAL | 48 | 20.4 | 52 | 120.4 | 36 | 36 | 40.4 | 112.4 | 0 | 44.6357 | 0 | 52.5542 | 97.1899 | 9.168 | TOTAL | 352.0782 | 37876.2368 | 0 | 2918.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7402 | 3.1653 | 6.9633 | 1.3057 | 1.2772 | 0.90977 | 1.7524 | 0.88642 | 0.98881 | 6.0836 | 8 | 0.23858 | 0.24005 | 0.20984 | 4.3678 | 2.1944 | 0.3853 | 14.5786 | 2.4076 | 16.0804 | 4.188 | 2.127 | 0.40056 | 15.3777 | 2.2718 | 24.8448 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.48 | 17 | 17 | 14.6 | 104 | 185 | 11.1 | 0.417 |  | 6.24 | 9 | 0.052 | 6.24 | 10 |  | 6.22 | 9 | [8 empty] | 0.046 | [14 empty] | 0.021 | 1 | 0.59 |  | 0.047 | 0.013 | 1 | 0.45 |  | 0.018 | 1 | 0.61 | [22 empty] | AVERAGE | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 |  | 11.1589 |  | 13.1386 | 24.2975 | 2.292 | AVERAGE | 88.0196 | 9469.0592 |  | 729.5154 | 0 | 0 | 0 |  |  |  | 1.9351 | 0.79133 | 1.7408 | 0.32643 | 0.3193 | 0.22744 | 0.43811 | 0.22161 | 0.2472 | 1.5209 | 2 | 0.059646 | 0.060012 | 0.05246 | 1.092 | 0.54861 | 0.096324 | 3.6446 | 0.6019 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.8444 | 0.56796 | 6.2112 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.2 | 98 | 101 | 89 | 634 | 1125 | 66.2 | 2.547 | 0.068 | 37.16 | 53 | 0.316 | 37.049 | 56 | 0 | 36.958 | 53 | 0 | 24.72 | 1.931 | 17 | 3.22 | 44.7 | 48 | 3.3102 | 0.269 | 24.88 | 2.226 | 15 | 1.89 | 48.7 | 21.4 | 1.7418 | 25.09 | 2.189 | 18 | 3.16 | 50.5 | 52 | 3.3689 | 0.12 | 6 | 3.36 | 0.024 | 0.267 | 0.102 | 6 | 2.7 | 0 | 0.144 | 6 | 3.72 | 0 | 44.73 | 0.354 | 6 | 25.3 | 61.1 | 44 | 127 | 0.02 | 44.21 | 0.368 | 6 | 23.8 | 65.7 | 47 | 120 | 0.023 | 25.4 | 20.6 | 16.2 |  |  | MINIMUM | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 |  | 10.0368 |  | 12.1493 | 22.1861 | 1.9536 | MINIMUM | 85.2903 | 9223.1096 |  | 729.5154 | [6 empty] | 1.9041 | 0.79133 | 1.6747 | 0.31693 | 0.27573 | 0.089485 | 0.261 | 0.20478 | 0.22819 | 1.52 | 1 | 0.059206 | 0.059792 | 0.05 | 1.0728 | 0.54861 | 0.096324 | 3.5925 | 0.58289 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.7819 | 0.54199 | 6.2112 |  | MIN | 0.74 | 12 | 21.2 | 15.688 | 6.1 | 11.5 | 15 | 1.0459 |  |  |  | MIN | 0.39 | 5.3 | 48 | 18.72 | 6.2 | 12.5 | 15 | 1.248 |  |  |  | MIN | 0.75 | 13 | 20.7692 | 15.5769 | 6.24 | 13 | 15 | 1.0385 |  |  |  | 1.0385
AVERAGE | 6.5333 | 16.3333 | 16.8333 | 14.8333 | 105.6667 | 187.5 | 11.0333 | 0.4245 | 0.034 | 6.1933 | 8.8333 | 0.052667 | 6.1748 | 9.3333 |  | 6.1597 | 8.8333 |  | 6.18 | 0.48275 | 4.25 | 0.805 | 11.175 | 12 | 0.82755 | 0.044833 | 6.22 | 0.5565 | 3.75 | 0.4725 | 12.175 | 5.35 | 0.43545 | 6.2725 | 0.54725 | 4.5 | 0.79 | 12.625 | 13 | 0.84222 | 0.02 | 1 | 0.56 | 0.012 | 0.0445 | 0.017 | 1 | 0.45 |  | 0.024 | 1 | 0.62 |  | 7.455 | 0.059 | 1 | 4.2167 | 10.1833 | 22 | 63.5 | 0.01 | 7.3683 | 0.061333 | 1 | 3.9667 | 10.95 | 23.5 | 60 | 0.0115 | 4.2333 | 3.4333 | 2.7 |  |  | MAXIMUM | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 |  | 12.9658 |  | 14.4202 | 26.8013 | 2.4048 | MAXIMUM | 90.8463 | 9592.034 |  | 729.5154 | [6 empty] | 2.0278 | 0.79133 | 1.7629 | 0.3296 | 0.33594 | 0.29828 | 0.59657 | 0.22819 | 0.25744 | 1.5218 | 4.5 | 0.059792 | 0.060378 | 0.054847 | 1.1239 | 0.54861 | 0.096324 | 3.6796 | 0.60823 | 4.0201 | 1.047 | 0.53174 | 0.10014 | 3.8823 | 0.60974 | 6.2112
MINIMUM | 6.44 | 16 | 16 | 14.5 | 104 | 185 | 10.9 | 0.401 | 0.031 | 6.07 | 8 | 0.047 | 6.1 | 8 |  | 6.06 | 8 |  | 6.1 | 0.375 | 4 | 0.74 | 10.9 | 12 | 0.82755 | 0.042 | 6.13 | 0.441 | 3 | 0.39 | 11.9 | 5.3 | 0.4325 | 6.24 | 0.467 | 4 | 0.75 | 12.4 | 13 | 0.84222 | 0.018 | 1 | 0.4 | 0.01 | 0.043 | 0.012 | 1 | 0.36 |  | 0.018 | 1 | 0.54 |  | 7.3 | 0.056 | 1 | 4.1 | 9.6 | 21 | 62 | 0.005 | 7.19 | 0.055 | 1 | 3.8 | 10.6 | 22 | 60 | 0.01 | 4.2 | 3.1 | 2.4 | [15 empty] | MIL/MIN |  | TOTAL | 43344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1565 | 640 | 1580 | 4120 | 4030 | 1340 | 2850 | 3030 | 3380 | 3200 | 0 | 4070 | 4095 | 4110 | 342 | 456 | 48 | 5060 | 950 | 992 | 184 | 248 | 28 | 2880 | 503 | 860
MAXIMUM | 6.58 | 17 | 17 | 15 | 107 | 189 | 11.2 | 0.441 | 0.037 | 6.25 | 10 | 0.058 | 6.36 | 12 |  | 6.3 | 10 |  | 6.27 | 0.543 | 5 | 0.86 | 11.5 | 12 | 0.82755 | 0.047 | 6.32 | 0.627 | 5 | 0.72 | 12.5 | 5.5 | 0.44429 | 6.33 | 0.63 | 5 | 0.86 | 13 | 13 | 0.84222 | 0.024 | 1 | 0.65 | 0.014 | 0.047 | 0.02 | 1 | 0.58 |  | 0.031 | 1 | 0.69 |  | 7.7 | 0.063 | 1 | 4.3 | 11 | 23 | 65 | 0.015 | 7.6 | 0.065 | 1 | 4.1 | 11.4 | 25 | 60 | 0.013 | 4.3 | 3.6 | 3.3 | [17 empty] | AVERAGE | 10836 | [9 empty] | 391.25 | 160 | 395 | 1030 | 1007.5 | 335 | 712.5 | 757.5 | 845 | 800 |  | 1017.5 | 1023.75 | 1027.5 | 85.5 | 114 | 12 | 1265 | 237.5 | 248 | 46 | 62 | 7 | 720 | 125.75 | 215
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1759 |  | TOTAL AVG COAG ALK: |  |  |  | 9 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.63 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.39 | [5 empty] | 6.2242 |  |  |  |  | 0.031 |  |  |  |  | 0.39 | [6 empty] | 0.031 | [16 empty] | Pump Station MIN |  | 2.4 | [17 empty] | MINIMUM | 10500 | [9 empty] | 385 | 160 | 380 | 1000 | 870 | 240 | 350 | 700 | 780 | 800 |  | 1010 | 1020 | 960 | 84 | 114 | 12 | 1220 | 230 | 248 | 46 | 62 | 7 | 710 | 120 | 215
[90 empty] | MAXIMUM | 11184 | [9 empty] | 410 | 160 | 400 | 1040 | 1060 | 400 | 1000 | 780 | 880 | 800 |  | 1020 | 1030 | 1050 | 88 | 114 | 12 | 1300 | 240 | 248 | 46 | 62 | 7 | 740 | 135 | 215
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.396 |  | TOTAL MGD: |  | 0.014 |  |  | FINISHED SOUTH 1 |  | START: | 23827188 |  | END: | 23827202 |  |  | Alum | 5879 | 11000 | 11000 | 11000 | 11000 | 0 | [44 empty] | 0.75 | 13 | 20.7692 | 15.5769 | 6.24 | 13 | 15 | 1.0385
[73 empty] | FINISHED 2 | 13.366 |  | TOTAL MGD: |  | 11.382 |  |  | FINISHED SOUTH 2 |  | START: | 44063797 |  | END: | 44075179 |  |  | Caustic | 6647 | 8014 | 8014
[73 empty] | TOTAL RAW | 30.02 |  | TOTAL MGD: |  | 4.516 |  |  | FINISHED CONWAY |  | START: | 10319317 |  | END: | 10323833 |  |  | Hypochlorite | 16 |  | 48
[76 empty] | TOTAL MGD: |  | 8.85 |  |  | FINISHED PERRY |  | START: | 33994875 |  | END: | 34003725 |  |  | Phosphate | 1843
[76 empty] | TOTAL MGD: |  | 11.934 |  |  | RAW PLANT 1 |  | START: | 31154477 |  | END: | 31166411 |  |  | Fluoride | 2900 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 5.293 |  |  | RAW PLANT 2 |  | START: | 31059309 |  | END: | 31064602 |  |  | Cal~Flo | 11.3 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.793 |  |  | RAW PLANT 3 |  | START: | 7707669 |  | END: | 7720462 |  |  | Zinc | 801
[76 empty] | TOTAL MGD: |  | 1.231 |  |  | DECANT |  | START: | 1882903 |  | END: | 1884134 |  |  | Polymer | 15
[76 empty] | TOTAL MGD: |  | 1.7415 |  |  | BLOW DOWN |  | START: | 9162.8791 |  | END: | 9164.6206 |  |  | NH3 | 11.11 |  | BI-SUL | 1000
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 717
23827202
44075179
10323833
34003725
31166411
31064602
7720462
1884134
9164.6206
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 23
DATE: | 2019-01-23 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-23 | [23 empty] | DATE: | 2019-01-23
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-23 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43488.0055 | 3,2,5 | 50 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 11.5747 | 1,3 | 12.5323 | 24.107 | 2.4048 | 43488.0055 | 85.7776 | 8977.16 | 0 | 729.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0773 | 0.84079 | 1.6747 | 0.31693 | 0.27573 | 0.22371 | 0.261 | 0.20478 | 0.22819 | 1.5218 | 4.5 | 0.059792 | 0.060378 | 0.050146 | 1.1239 | 0.54861 | 0.096324 | 3.6268 | 0.58289 | 3.6473 | 1.047 | 0.53174 | 0.10014 | 3.8823 | 0.60974 | 5.7779 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.37 | 0.531 | 4 | 0.73 | 11.9 | 12 | 0.82755 |  | 6.41 | 0.462 | 4 | 0.61 | 12.7 | 5.2 | 0.4266 | 6.31 | 0.503 | 4 | 0.81 | 13 | 13 | 0.84222 | [13 empty] | 7.61 | 0.064 | 1 | 4.3 | 9.6 |  |  |  | 7.54 | 0.06 | 1 | 4.1 | 11.2 |  |  |  | 4.3 | 3.6 | 2.7 | [18 empty] | 10560 | [6 empty] | 0 | 0 | 0 | 420 | 170 | 380 | 1000 | 870 | 300 | 350 | 700 | 780 | 800 |  | 1020 | 1030 | 960 | 88 | 114 | 12 | 1220 | 230 | 225 | 46 | 62 | 7 | 740 | 135 | 200 |  | 1:00 | 0.73 | 12 | 21.2 | 15.476 | 6.37 | 11.9 | 15 | 1.0317 | 10 | 6.5 | 0.70755 | 1:00 | 0.61 | 5.2 | 48.9231 | 29.8431 | 6.41 | 12.7 | 15 | 1.9895 | 10 | 6.5 | 0.3066 | 1:00 | 0.81 | 13 | 20.7692 | 16.8231 | 6.31 | 13 | 15 | 1.1215 | 10 | 6.5 | 0.72222
2:00 | [72 empty] | 43488.321 | 3,2,5 | 50 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 11.5747 | 1,3 | 12.5323 | 24.107 | 2.9059 | 43488.321 | 83.8282 | 8915.6726 | 0 | 761.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8547 | 1.2365 | 1.7629 | 0.31059 | 0.30742 | 0.261 | 0.261 | 0.23404 | 0.24867 | 1.5218 | 5 | 0.059792 | 0.059792 | 0.052235 | 1.0983 | 0.54861 | 0.096324 | 3.7029 | 0.66906 | 3.6473 | 1.047 | 0.5489 | 0.11444 | 3.7016 | 0.63232 | 5.7779 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.36 | 16 | 17 | 15 | 103 | 181 | 10.9 | 0.404 |  | 6.05 | 9 | 0.051 | 6.2 | 9 |  | 6.14 | 9 | [8 empty] | 0.044 | [14 empty] | 0.02 | 1 | 0.57 |  | 0.043 | 0.013 | 1 | 0.43 |  | 0.017 | 1 | 0.6 | [38 empty] | 10320 | [6 empty] | 0 | 0 | 0 | 375 | 250 | 400 | 980 | 970 | 350 | 350 | 800 | 850 | 800 |  | 1020 | 1020 | 1000 | 86 | 114 | 12 | 1250 | 264 | 225 | 46 | 64 | 8 | 700 | 140 | 200 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43488.4403 | 3,2,5 | 50 | 12 | 5.1 | 13 | 30.1 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 11.5747 | 1,3 | 12.5323 | 24.107 | 2.9059 | 43488.4403 | 79.6855 | 8915.6726 | 0 | 761.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 2.102 | 1.2365 | 1.7629 | 0.31059 | 0.30742 | 0.261 | 0.261 | 0.23404 | 0.24867 | 1.5218 | 5 | 0.059792 | 0.059792 | 0.052235 | 1.0983 | 0.54861 | 0.096324 | 3.7029 | 0.66906 | 3.6473 | 1.047 | 0.5489 | 0.11444 | 3.7016 | 0.63232 | 5.7779 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.49 | 0.062 | 1 | 4.2 | 9.1 |  |  |  | 7.46 | 0.063 | 1 | 4 | 10.8 |  |  |  | 4.2 | 3.9 | 3.2 | [18 empty] | 9810 | [6 empty] | 0 | 0 | 0 | 425 | 250 | 400 | 980 | 970 | 350 | 350 | 800 | 850 | 800 |  | 1020 | 1020 | 1000 | 86 | 114 | 12 | 1250 | 264 | 225 | 46 | 64 | 8 | 700 | 140 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43488.6497 | 3,2,5 | 50 | 10.5 | 8 | 11.5 | 30 | 9 | 9 | 10.1 | 28.1 | ,1,3 | 11.5747 | 1,3 | 12.5323 | 24.107 | 2.9059 | 43488.6497 | 79.9511 | 7685.9246 | 0 | 761.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 1.731 | 1.3848 | 1.5425 | 0.25354 | 0.25354 | 0.19966 | 0.19966 | 0.23149 | 0.23149 | 1.5218 | 5 | 0.059792 | 0.059792 | 0.052235 | 1.0983 | 0.54861 | 0.096324 | 3.7029 | 0.66906 | 3.6473 | 1.047 | 0.5489 | 0.11444 | 3.7016 | 0.63232 | 5.7779 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.59 | 18 | 17 | 14.2 | 91 | 169 | 11.6 | 0.384 |  | 6.2 | 12 | 0.061 | 6.18 | 12 |  | 6.18 | 12 | [8 empty] | 0.04 | [14 empty] | 0.027 | 1 | 0.65 |  | 0.045 | 0.009 | 1 | 0.56 |  | 0.036 | 1 | 0.52 | [38 empty] | 9810 | [6 empty] | 0 | 0 | 0 | 350 | 280 | 350 | 700 | 700 | 420 | 420 | 700 | 700 | 800 |  | 1020 | 1020 | 1000 | 86 | 114 | 12 | 1250 | 264 | 225 | 46 | 64 | 8 | 700 | 140 | 200 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43488.8645 | 2,3,5 | 50 | 10 | 8 | 11 | 29 | 9 | 9 | 10.5 | 28.5 | ,1,3 | 9.1699 | 1,3 | 13.1976 | 22.3675 | 2.9059 | 43488.8645 | 79.5886 | 7624.4372 | 0 | 761.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8794 | 1.7805 | 1.6957 | 0.30425 | 0.25861 | 0.2472 | 0.20917 | 0.22127 | 0.27659 | 1.5218 | 0.5 | 0.060965 | 0.060965 | 0.050246 | 1.0473 | 0.51974 | 0.096324 | 3.6255 | 0.60823 | 3.6635 | 1.0509 | 0.57748 | 0.096324 | 3.5236 | 0.54306 | 5.5577 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.06 | [9 empty] | 6.34 | 0.391 | 3 | 0.75 | 11.1 | 12 | 0.82755 |  | 6.33 | 0.371 | 7 | 0.74 | 9.9 | 5.1 | 0.52094 | 6.28 | 0.39 | 4 | 0.9 | 12.4 | 13 | 0.84222 |  |  |  | 0.036 | [9 empty] | 7.33 | 0.059 | 1 | 4.4 | 9.9 | 27 | 58 | 0.037 | 7.37 | 0.069 | 2 | 4 | 11.3 | 24 | 60 | 0.026 | 4.3 | 3.8 | 3.2 | [18 empty] | 9440 | [6 empty] | 0 | 0 | 0 | 380 | 360 | 400 | 800 | 680 | 520 | 440 | 640 | 800 | 800 |  | 1040 | 1040 | 1000 | 82 | 108 | 12 | 1180 | 240 | 226 | 48 | 70 | 7 | 620 | 125 | 200 |  | 9:00 | 0.75 | 12 | 21.2 | 15.9 | 6.34 | 11.1 | 15 | 1.06 | 10 | 6.5 | 0.70755 | 9:00 | 0.74 | 5.1 | 49.8824 | 36.9129 | 6.33 | 9.9 | 20 | 1.8456 | 5 | 6.5 | 0.40094 | 9:00 | 0.9 | 13 | 20.7692 | 18.6923 | 6.28 | 12.4 | 15 | 1.2462 | 10 | 6.5 | 0.72222
10:00 | [72 empty] | 43488.975 | 2,3,5 | 50 | 10 | 8 | 11 | 29 | 9 | 9 | 10.5 | 28.5 | ,1,3 | 9.1699 | 1,3 | 13.1976 | 22.3675 | 2.9059 | 43488.975 | 75.3731 | 7624.4372 | 0 | 761.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8794 | 1.7805 | 1.6957 | 0.28904 | 0.2434 | 0.20917 | 0.20917 | 0.22127 | 0.24893 | 1.5218 | 0.5 | 0.060965 | 0.060965 | 0.050246 | 1.0473 | 0.51974 | 0.096324 | 3.6255 | 0.60823 | 3.6635 | 1.0509 | 0.57748 | 0.096324 | 3.5236 | 0.54306 | 5.5577 |  | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.47 | 18 | 17 | 13.7 | 90 | 171 | 11.5 | 0.389 |  | 6.19 | 11 | 0.06 | 6.2 | 12 |  | 6.22 | 12 | [8 empty] | 0.042 | [14 empty] | 0.026 | 1 | 0.6 |  | 0.044 | 0.011 | 1 | 0.55 |  | 0.037 | 1 | 0.57 | [38 empty] | 8940 | [6 empty] | 0 | 0 | 0 | 380 | 360 | 400 | 760 | 640 | 440 | 440 | 640 | 720 | 800 |  | 1040 | 1040 | 1000 | 82 | 108 | 12 | 1180 | 240 | 226 | 48 | 70 | 7 | 620 | 125 | 200 |  | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.21 | 0.352 | 3 | 0.78 | 11.5 | 12 | 0.82755 |  | 6.18 | 0.296 | 3 | 0.72 | 11 | 5.2 | 0.4266 | 6.24 | 0.384 | 4 | 0.82 | 13.2 | 13 | 0.84222 | [13 empty] | 7.34 | 0.054 | 1 | 4.2 | 9.9 |  |  |  | 7.29 | 0.058 | 1 | 4 | 13 |  |  |  | 4.3 | 3.8 | 2.5 | [55 empty] | 13:00 | 0.78 | 12 | 21.2 | 16.536 | 6.21 | 11.5 | 15 | 1.1024 | 10 | 6.5 | 0.70755 | 13:00 | 0.72 | 5.2 | 48.9231 | 35.2246 | 6.18 | 11 | 15 | 2.3483 | 10 | 6.5 | 0.3066 | 13:00 | 0.82 | 13 | 20.7692 | 17.0308 | 6.24 | 13.2 | 15 | 1.1354 | 10 | 6.5 | 0.72222
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.55 | 20 | 18 | 14.2 | 90 | 175 | 11.8 | 0.365 |  | 6.05 | 12 | 0.053 | 6.16 | 12 |  | 6.06 | 12 | [8 empty] | 0.039 | [14 empty] | 0.023 | 1 | 0.58 |  | 0.039 | 0.016 | 1 | 0.62 |  | 0.04 | 1 | 0.55 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.45 | 0.052 | 1 | 4.4 | 10 |  |  |  | 7.32 | 0.054 | 1 | 4.1 | 13 |  |  |  | 4.2 | 3.9 | 2.9 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.62 | 16 | 16 | 14.1 | 100 | 173 | 11.8 | 0.395 |  | 6.12 | 11 | 0.07 | 6.13 | 10 |  | 6.11 | 10 | [8 empty] | 0.042 | [14 empty] | 0.021 | 1 | 0.61 |  | 0.038 | 0.016 | 1 | 0.66 |  | 0.031 | 1 | 0.83 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.035 | [9 empty] | 6.14 | 0.38 | 3 | 0.95 | 11.4 | 10 | 0.70962 |  | 6.21 | 0.366 | 4 | 0.99 | 10.7 | 8 | 0.5917 | 6.22 | 0.411 | 3 | 0.83 | 13.3 | 11.4 | 0.75333 |  |  |  | 0.008 | [9 empty] | 7.2 | 0.06 | 1 | 4.5 | 9.7 | 20 | 47 | 0.016 | 7.22 | 0.058 | 1 | 4.6 | 12.2 | 21 | 46 | 0.012 | 4.4 | 4.1 | 2.5 | [55 empty] | 21:00 | 0.95 | 10 | 25.44 | 24.168 | 6.14 | 11.4 | 15 | 1.6112 | 10 | 6.5 | 0.58962 | 21:00 | 0.99 | 8 | 31.8 | 31.482 | 6.21 | 10.7 | 15 | 2.0988 | 10 | 6.5 | 0.4717 | 21:00 | 0.83 | 11.4 | 23.6842 | 19.6579 | 6.22 | 13.3 | 15 | 1.3105 | 10 | 6.5 | 0.63333
22:00 | [72 empty] | DOSE |  | TOTAL | 66.5 | 39.3 | 72.5 | 178.3 | 54 | 54 | 61.4 | 169.4 | 0 | 64.6387 | 0 | 76.5245 | 141.1632 | 16.9344 | TOTAL | 484.204 | 49743.3042 | 0 | 4535.6828 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5238 | 8.2596 | 10.1344 | 1.7849 | 1.6461 | 1.4017 | 1.401 | 1.3469 | 1.4825 | 9.1308 | 20.5 | 0.3611 | 0.36168 | 0.30734 | 6.5134 | 3.2339 | 0.57795 | 21.9864 | 3.8065 | 21.9161 | 6.2898 | 3.3334 | 0.63612 | 22.0343 | 3.5928 | 34.2269 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 17 | 16 | 14.2 | 92 | 172 | 11.7 | 0.396 |  | 6.08 | 10 | 0.065 | 6.03 | 10 |  | 6 | 10 | [8 empty] | 0.039 | [14 empty] | 0.023 | 1 | 0.64 |  | 0.041 | 0.015 | 1 | 0.7 |  | 0.026 | 1 | 0.59 | [22 empty] | AVERAGE | 11.0833 | 6.55 | 12.0833 | 29.7167 | 9 | 9 | 10.2333 | 28.2333 |  | 10.7731 |  | 12.7541 | 23.5272 | 2.8224 | AVERAGE | 80.7007 | 8290.5507 |  | 755.9471 | 0 | 0 | 0 |  |  |  | 1.9206 | 1.3766 | 1.6891 | 0.29749 | 0.27435 | 0.23362 | 0.2335 | 0.22448 | 0.24709 | 1.5218 | 3.4167 | 0.060183 | 0.060281 | 0.051224 | 1.0856 | 0.53899 | 0.096324 | 3.6644 | 0.63442 | 3.6527 | 1.0483 | 0.55557 | 0.10602 | 3.6724 | 0.5988 | 5.7045 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.12 | 105 | 101 | 85.4 | 566 | 1041 | 69.3 | 2.333 | 0.095 | 36.69 | 65 | 0.36 | 36.9 | 65 | 0 | 36.71 | 65 | 0 | 25.06 | 1.654 | 13 | 3.21 | 45.9 | 46 | 3.1923 | 0.246 | 25.13 | 1.495 | 18 | 3.06 | 44.3 | 23.5 | 1.9658 | 25.05 | 1.688 | 15 | 3.36 | 51.9 | 50.4 | 3.28 | 0.14 | 6 | 3.65 | 0.044 | 0.25 | 0.08 | 6 | 3.52 | 0 | 0.187 | 6 | 3.66 | 0 | 44.42 | 0.351 | 6 | 26 | 58.2 | 47 | 105 | 0.053 | 44.2 | 0.362 | 7 | 24.8 | 71.5 | 45 | 106 | 0.038 | 25.7 | 23.1 | 17 |  |  | MINIMUM | 10 | 5.1 | 11 | 29 | 9 | 9 | 10.1 | 28.1 |  | 9.1699 |  | 12.5323 | 22.3675 | 2.4048 | MINIMUM | 75.3731 | 7624.4372 |  | 729.5154 | [6 empty] | 1.731 | 0.84079 | 1.5425 | 0.25354 | 0.2434 | 0.19966 | 0.19966 | 0.20478 | 0.22819 | 1.5218 | 0.5 | 0.059792 | 0.059792 | 0.050146 | 1.0473 | 0.51974 | 0.096324 | 3.6255 | 0.58289 | 3.6473 | 1.047 | 0.53174 | 0.096324 | 3.5236 | 0.54306 | 5.5577 |  | MIN | 0.73 | 12 | 21.2 | 15.476 | 6.37 | 11.9 | 15 | 1.0317 |  |  |  | MIN | 0.74 | 5.1 | 49.8824 | 36.9129 | 6.33 | 9.9 | 20 | 1.8456 |  |  |  | MIN | 0.81 | 13 | 20.7692 | 16.8231 | 6.31 | 13 | 15 | 1.1215 |  |  |  | 1.0317
AVERAGE | 6.52 | 17.5 | 16.8333 | 14.2333 | 94.3333 | 173.5 | 11.55 | 0.38883 | 0.0475 | 6.115 | 10.8333 | 0.06 | 6.15 | 10.8333 |  | 6.1183 | 10.8333 |  | 6.265 | 0.4135 | 3.25 | 0.8025 | 11.475 | 11.5 | 0.79807 | 0.041 | 6.2825 | 0.37375 | 4.5 | 0.765 | 11.075 | 5.875 | 0.49146 | 6.2625 | 0.422 | 3.75 | 0.84 | 12.975 | 12.6 | 0.82 | 0.023333 | 1 | 0.60833 | 0.022 | 0.041667 | 0.013333 | 1 | 0.58667 |  | 0.031167 | 1 | 0.61 |  | 7.4033 | 0.0585 | 1 | 4.3333 | 9.7 | 23.5 | 52.5 | 0.0265 | 7.3667 | 0.060333 | 1.1667 | 4.1333 | 11.9167 | 22.5 | 53 | 0.019 | 4.2833 | 3.85 | 2.8333 |  |  | MAXIMUM | 12 | 8 | 13 | 30.1 | 9 | 9 | 10.5 | 28.5 |  | 11.5747 |  | 13.1976 | 24.107 | 2.9059 | MAXIMUM | 85.7776 | 8977.16 |  | 761.2335 | [6 empty] | 2.102 | 1.7805 | 1.7629 | 0.31693 | 0.30742 | 0.261 | 0.261 | 0.23404 | 0.27659 | 1.5218 | 5 | 0.060965 | 0.060965 | 0.052235 | 1.1239 | 0.54861 | 0.096324 | 3.7029 | 0.66906 | 3.6635 | 1.0509 | 0.57748 | 0.11444 | 3.8823 | 0.63232 | 5.7779
MINIMUM | 6.36 | 16 | 16 | 13.7 | 90 | 169 | 10.9 | 0.365 | 0.035 | 6.05 | 9 | 0.051 | 6.03 | 9 |  | 6 | 9 |  | 6.14 | 0.352 | 3 | 0.73 | 11.1 | 10 | 0.70962 | 0.039 | 6.18 | 0.296 | 3 | 0.61 | 9.9 | 5.1 | 0.4266 | 6.22 | 0.384 | 3 | 0.81 | 12.4 | 11.4 | 0.75333 | 0.02 | 1 | 0.57 | 0.008 | 0.038 | 0.009 | 1 | 0.43 |  | 0.017 | 1 | 0.52 |  | 7.2 | 0.052 | 1 | 4.2 | 9.1 | 20 | 47 | 0.016 | 7.22 | 0.054 | 1 | 4 | 10.8 | 21 | 46 | 0.012 | 4.2 | 3.6 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 58880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2330 | 1670 | 2330 | 5220 | 4830 | 2380 | 2350 | 4280 | 4700 | 4800 | 0 | 6160 | 6170 | 5960 | 510 | 672 | 72 | 7330 | 1502 | 1352 | 280 | 394 | 45 | 4080 | 805 | 1200
MAXIMUM | 6.62 | 20 | 18 | 15 | 103 | 181 | 11.8 | 0.404 | 0.06 | 6.2 | 12 | 0.07 | 6.2 | 12 |  | 6.22 | 12 |  | 6.37 | 0.531 | 4 | 0.95 | 11.9 | 12 | 0.82755 | 0.044 | 6.41 | 0.462 | 7 | 0.99 | 12.7 | 8 | 0.5917 | 6.31 | 0.503 | 4 | 0.9 | 13.3 | 13 | 0.84222 | 0.027 | 1 | 0.65 | 0.036 | 0.045 | 0.016 | 1 | 0.7 |  | 0.04 | 1 | 0.83 |  | 7.61 | 0.064 | 1 | 4.5 | 10 | 27 | 58 | 0.037 | 7.54 | 0.069 | 2 | 4.6 | 13 | 24 | 60 | 0.026 | 4.4 | 4.1 | 3.2 | [17 empty] | AVERAGE | 9813.3333 | [9 empty] | 388.3333 | 278.3333 | 388.3333 | 870 | 805 | 396.6667 | 391.6667 | 713.3333 | 783.3333 | 800 |  | 1026.6667 | 1028.3333 | 993.3333 | 85 | 112 | 12 | 1221.6667 | 250.3333 | 225.3333 | 46.6667 | 65.6667 | 7.5 | 680 | 134.1667 | 200
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1278 |  | TOTAL AVG COAG ALK: |  |  |  | 10.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.531 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.61 | [5 empty] | 6.27 |  |  |  |  | 0.04 |  |  |  |  | 0.61 | [6 empty] | 0.04 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 8940 | [9 empty] | 350 | 170 | 350 | 700 | 640 | 300 | 350 | 640 | 700 | 800 |  | 1020 | 1020 | 960 | 82 | 108 | 12 | 1180 | 230 | 225 | 46 | 62 | 7 | 620 | 125 | 200
[90 empty] | MAXIMUM | 10560 | [9 empty] | 425 | 360 | 400 | 1000 | 970 | 520 | 440 | 800 | 850 | 800 |  | 1040 | 1040 | 1000 | 88 | 114 | 12 | 1250 | 264 | 226 | 48 | 70 | 8 | 740 | 140 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.126 |  | TOTAL MGD: |  | 0.008 |  |  | FINISHED SOUTH 1 |  | START: | 23827202 |  | END: | 23827210 |  |  | Alum | 6411 | 10792 | 10792 | 10904 | 10904 | 0 | [44 empty] | 0.73 | 12 | 21.2 | 15.476 | 6.37 | 11.9 | 15 | 1.0317
[73 empty] | FINISHED 2 | 12.716 |  | TOTAL MGD: |  | 11.118 |  |  | FINISHED SOUTH 2 |  | START: | 44075179 |  | END: | 44086297 |  |  | Caustic | 6575 | 8008 | 8008
[73 empty] | TOTAL RAW | 28.489 |  | TOTAL MGD: |  | 4.622 |  |  | FINISHED CONWAY |  | START: | 10323833 |  | END: | 10328455 |  |  | Hypochlorite | 9 |  | 36
[76 empty] | TOTAL MGD: |  | 8.094 |  |  | FINISHED PERRY |  | START: | 34003725 |  | END: | 34011819 |  |  | Phosphate | 1791
[76 empty] | TOTAL MGD: |  | 10.673 |  |  | RAW PLANT 1 |  | START: | 31166411 |  | END: | 31177084 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 6.022 |  |  | RAW PLANT 2 |  | START: | 31064602 |  | END: | 31070624 |  |  | Cal~Flo | 15.88 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.794 |  |  | RAW PLANT 3 |  | START: | 7720462 |  | END: | 7732256 |  |  | Zinc | 785
[76 empty] | TOTAL MGD: |  | 1.178 |  |  | DECANT |  | START: | 1884134 |  | END: | 1885312 |  |  | Polymer | 15
[76 empty] | TOTAL MGD: |  | 1.6112 |  |  | BLOW DOWN |  | START: | 9164.6206 |  | END: | 9166.2318 |  |  | NH3 | 10.89 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 761
23827210
44086297
10328455
34011819
31177084
31070624
7732256
1885312
9166.2318
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 24
DATE: | 2019-01-24 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-24 | [23 empty] | DATE: | 2019-01-24
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-24 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43489.0056 | 2,3,5 | 50 | 10 | 8 | 11 | 29 | 9 | 9 | 10.5 | 28.5 | ,1,3 | 11.1874 | 1,3 | 13.9162 | 25.1035 | 2.0902 | 43489.0056 | 75.3731 | 7132.538 | 0 | 761.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8794 | 1.7805 | 1.6957 | 0.28904 | 0.2434 | 0.20917 | 0.20917 | 0.22127 | 0.24893 | 1.5218 | 0.5 | 0.060965 | 0.060965 | 0.050246 | 1.0473 | 0.51974 | 0.096324 | 3.6255 | 0.60823 | 3.6635 | 1.0509 | 0.57748 | 0.096324 | 3.5236 | 0.54306 | 5.5577 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.01 | 0.37 | 3 | 0.9 | 11.7 | 9 | 0.65066 |  | 6.11 | 0.346 | 3 | 0.98 | 10.9 | 8 | 0.5917 | 6.16 | 0.401 | 3 | 0.9 | 13.7 | 10.9 | 0.72556 | [13 empty] | 7.22 | 0.052 | 1 | 4.4 | 9.9 |  |  |  | 7.18 | 0.05 | 1 | 4.3 | 12.3 |  |  |  | 3.9 | 4.1 | 2.8 | [18 empty] | 8940 | [6 empty] | 0 | 0 | 0 | 380 | 360 | 400 | 760 | 640 | 440 | 440 | 640 | 720 | 800 |  | 1040 | 1040 | 1000 | 82 | 108 | 12 | 1180 | 240 | 226 | 48 | 70 | 7 | 620 | 125 | 200 |  | 1:00 | 0.9 | 9 | 28.2667 | 25.44 | 6.01 | 11.7 | 15 | 1.696 | 10 | 6.5 | 0.53066 | 1:00 | 0.98 | 8 | 31.8 | 31.164 | 6.11 | 10.9 | 15 | 2.0776 | 10 | 6.5 | 0.4717 | 1:00 | 0.9 | 10.9 | 24.7706 | 22.2936 | 6.16 | 13.7 | 15 | 1.4862 | 10 | 6.5 | 0.60556
2:00 | [72 empty] | 43489.4045 | 2,3,5 | 50 | 9 | 9 | 10 | 28 | 8.5 | 8.5 | 9.5 | 26.5 | ,1,3 | 11.1874 | 1,3 | 13.9162 | 25.1035 | 0.0020304 | 43489.4045 | 74.6594 | 7255.5128 | 0 | 713.6564 | 0 | 0 | 0 | 0 | 0 | 0 | 1.702 | 1.702 | 1.5228 | 0.25354 | 0.24509 | 0.18593 | 0.18593 | 0.22819 | 0.22819 | 1.5218 | 2 | 0.060206 | 0.060206 | 0.051092 | 1.1089 | 0.55031 | 0.10199 | 3.7664 | 0.64938 | 3.8618 | 1.1131 | 0.56533 | 0.091255 | 3.497 | 0.55701 | 6.1428 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.4 | 15 | 17 | 14.2 | 98 | 172 | 12.8 | 0.392 |  | 6.12 | 8 | 0.058 | 6.14 | 9 |  | 6.07 | 9 | [8 empty] | 0.039 | [14 empty] | 0.024 | 2 | 0.55 |  | 0.041 | 0.016 | 2 | 0.65 |  | 0.024 | 2 | 0.76 | [38 empty] | 8550 | [6 empty] | 0 | 0 | 0 | 325 | 325 | 325 | 600 | 580 | 440 | 440 | 600 | 600 | 800 |  | 970 | 970 | 920 | 82 | 108 | 12 | 1180 | 242 | 225 | 46 | 62 | 6 | 570 | 116 | 200 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43489.5806 | 2,3,5 | 50 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 11.1874 | 1,3 | 13.9162 | 25.1035 | 0.0020304 | 43489.5806 | 75.0489 | 6394.6892 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.712 | 1.712 | 1.5175 | 0.27492 | 0.27492 | 0.20161 | 0.20161 | 0.22492 | 0.22492 | 1.5218 | 3 | 0.059522 | 0.059522 | 0.04976 | 1.1052 | 0.54972 | 0.09262 | 3.9921 | 0.68719 | 4.0214 | 1.0972 | 0.54139 | 0.098514 | 3.5074 | 0.57022 | 6.2998 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.23 | 0.055 | 1 | 4.5 | 10.1 |  |  |  | 7.16 | 0.057 | 1 | 4.6 | 12.4 |  |  |  | 4.3 | 4.1 | 3.5 | [18 empty] | 7950 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 600 | 600 | 440 | 440 | 550 | 550 | 800 |  | 880 | 880 | 830 | 75 | 99 | 10 | 1160 | 235 | 215 | 42 | 55 | 6 | 530 | 110 | 190 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43489.8483 | 2,3,5 | 35 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 9.1195 | 1,3 | 15.7234 | 24.8429 | 0.0020304 | 43489.8483 | 75.0489 | 6394.6892 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3696 | 1.5979 | 1.821 | 0.2566 | 0.27492 | 0.21994 | 0.20161 | 0.22901 | 0.22901 | 1.5218 | 5 | 0.059522 | 0.059522 | 0.052758 | 1.061 | 0.54972 | 0.10188 | 3.9845 | 0.74567 | 4.0214 | 1.0449 | 0.59061 | 0.11493 | 3.5011 | 0.57022 | 6.2998 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.5 | 17 | 17 | 14.1 | 96 | 172 | 12.6 | 0.393 |  | 6.15 | 10 | 0.066 | 6.14 | 10 |  | 6.09 | 10 | [8 empty] | 0.044 | [14 empty] | 0.022 | 1 | 0.66 |  | 0.041 | 0.016 | 1 | 0.8 |  | 0.023 | 1 | 0.89 | [38 empty] | 7950 | [6 empty] | 0 | 0 | 0 | 240 | 280 | 360 | 560 | 600 | 480 | 440 | 560 | 560 | 800 |  | 880 | 880 | 880 | 72 | 99 | 11 | 1260 | 255 | 215 | 40 | 60 | 7 | 550 | 110 | 190 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.066 | [9 empty] | 6.18 | 0.32 | 3 | 0.91 | 12.1 | 9 | 0.65066 |  | 6.25 | 0.357 | 3 | 0.98 | 11.2 | 9 | 0.65066 | 6.23 | 0.36 | 3 | 0.97 | 13.1 | 10 | 0.67556 |  |  |  | 0.024 | [9 empty] | 7.15 | 0.057 | 1 | 3.8 | 10.7 | 23 | 49 | 0.031 | 7.19 | 0.054 | 1 | 4.3 | 12.6 | 21 | 53 | 0.029 | 4.2 | 4.1 | 3.3 | [55 empty] | 9:00 | 0.91 | 9 | 28.2667 | 25.7227 | 6.18 | 12.1 | 15 | 1.7148 | 10 | 6.5 | 0.53066 | 9:00 | 0.98 | 9 | 28.2667 | 27.7013 | 6.25 | 11.2 | 15 | 1.8468 | 10 | 6.5 | 0.53066 | 9:00 | 0.97 | 10 | 27 | 26.19 | 6.23 | 13.1 | 15 | 1.746 | 10 | 6.5 | 0.55556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.72 | 18 | 17 | 14.3 | 98 | 172 | 12.7 | 0.394 |  | 6.15 | 10 | 0.062 | 6.2 | 10 |  | 6.12 | 10 | [8 empty] | 0.044 | [14 empty] | 0.036 | 1 | 0.39 |  | 0.043 | 0.023 | 1 | 0.44 |  | 0.022 | 1 | 0.7 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.1 | 0.315 | 3 | 0.8 | 12.2 | 8.3 | 0.60939 |  | 6.12 | 0.327 | 3 | 0.78 | 11.5 | 8.3 | 0.60939 | 6.14 | 0.345 | 3 | 0.82 | 14.5 | 9.3 | 0.63667 | [13 empty] | 7.55 | 0.052 | 1 | 4 | 10.5 |  |  |  | 7.31 | 0.05 | 1 | 4.2 | 13.5 |  |  |  | 4.2 | 4 | 2.6 | [55 empty] | 13:00 | 0.8 | 8.3 | 30.6506 | 24.5205 | 6.1 | 12.2 | 15 | 1.6347 | 10 | 6.5 | 0.48939 | 13:00 | 0.78 | 8.3 | 30.6506 | 23.9075 | 6.12 | 11.5 | 15 | 1.5938 | 10 | 6.5 | 0.48939 | 13:00 | 0.82 | 9.3 | 29.0323 | 23.8065 | 6.14 | 14.5 | 15 | 1.5871 | 10 | 6.5 | 0.51667
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.55 | 19 | 18 | 14.8 | 96 | 176 | 13 | 0.341 |  | 6.12 | 10 | 0.05 | 6.13 | 11 |  | 6.09 | 11 | [8 empty] | 0.037 | [14 empty] | 0.04 | 1 | 0.28 |  | 0.039 | 0.011 | 1 | 0.36 |  | 0.021 | 1 | 0.32 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.35 | 0.053 | 1 | 4 | 10.5 |  |  |  | 7.28 | 0.052 | 1 | 4.2 | 13.5 |  |  |  | 4.2 | 4 | 2.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.6 | 15 | 19 | 14.3 | 97 | 169 | 13.1 | 0.378 |  | 6.18 | 9 | 0.062 | 6.13 | 9 |  | 6.09 | 10 | [8 empty] | 0.038 | [14 empty] | 0.038 | 1 | 0.31 |  | 0.04 | 0.012 | 1 | 0.29 |  | 0.021 | 1 | 0.65 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.038 | [9 empty] | 6.13 | 0.317 | 3 | 0.64 | 12.2 | 8.6 | 0.62708 |  | 6.22 | 0.32 | 4 | 0.67 | 11.6 | 8.6 | 0.62708 | 6.23 | 0.38 | 4 | 0.82 | 14.3 | 9.6 | 0.65333 |  |  |  | 0.014 | [9 empty] | 7.28 | 0.059 | 1 | 3.6 | 10.6 | 21 | 41 | 0.013 | 7.38 | 0.055 | 1 | 3.7 | 12.7 | 20 | 38 | 0.01 | 4.1 | 3.8 | 2.8 | [55 empty] | 21:00 | 0.64 | 8.6 | 29.5814 | 18.9321 | 6.13 | 12.2 | 15 | 1.2621 | 10 | 6.5 | 0.50708 | 21:00 | 0.67 | 8.6 | 29.5814 | 19.8195 | 6.22 | 11.6 | 15 | 1.3213 | 10 | 6.5 | 0.50708 | 21:00 | 0.82 | 9.6 | 28.125 | 23.0625 | 6.23 | 14.3 | 15 | 1.5375 | 10 | 6.5 | 0.53333
22:00 | [72 empty] | DOSE |  | TOTAL | 35.6 | 33.6 | 39.6 | 108.8 | 33.1 | 33.1 | 37.6 | 103.8 | 0 | 42.6816 | 0 | 57.4718 | 100.1534 | 2.0963 | TOTAL | 300.1302 | 27177.4292 | 0 | 2775.3304 | 0 | 0 | 0 | 0 | 0 | 0 | 6.663 | 6.7924 | 6.557 | 1.0741 | 1.0383 | 0.81665 | 0.79833 | 0.90338 | 0.93104 | 6.0872 | 10.5 | 0.24021 | 0.24021 | 0.20386 | 4.3223 | 2.1695 | 0.39282 | 15.3684 | 2.6905 | 15.568 | 4.3061 | 2.2748 | 0.40103 | 14.0291 | 2.2405 | 24.3002 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.59 | 16 | 18 | 14.2 | 90 | 170 | 12.9 | 0.355 |  | 6.1 | 10 | 0.057 | 6.07 | 10 |  | 6.06 | 9 | [8 empty] | 0.037 | [14 empty] | 0.034 | 1 | 0.4 |  | 0.039 | 0.013 | 1 | 0.35 |  | 0.022 | 1 | 0.7 | [22 empty] | AVERAGE | 8.9 | 8.4 | 9.9 | 27.2 | 8.275 | 8.275 | 9.4 | 25.95 |  | 10.6704 |  | 14.368 | 25.0384 | 0.52406 | AVERAGE | 75.0326 | 6794.3573 |  | 693.8326 | 0 | 0 | 0 |  |  |  | 1.6658 | 1.6981 | 1.6392 | 0.26853 | 0.25958 | 0.20416 | 0.19958 | 0.22585 | 0.23276 | 1.5218 | 2.625 | 0.060053 | 0.060053 | 0.050964 | 1.0806 | 0.54237 | 0.098204 | 3.8421 | 0.67262 | 3.892 | 1.0765 | 0.5687 | 0.10026 | 3.5073 | 0.56013 | 6.075 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.36 | 100 | 106 | 85.9 | 575 | 1031 | 77.1 | 2.253 | 0.104 | 36.82 | 57 | 0.355 | 36.81 | 59 | 0 | 36.52 | 59 | 0 | 24.42 | 1.322 | 12 | 3.25 | 48.2 | 34.9 | 2.5378 | 0.239 | 24.7 | 1.35 | 13 | 3.41 | 45.2 | 33.9 | 2.4788 | 24.76 | 1.486 | 13 | 3.51 | 55.6 | 39.8 | 2.6911 | 0.194 | 7 | 2.59 | 0.038 | 0.243 | 0.091 | 7 | 2.89 | 0 |  | 7 | 4.02 | 0 | 43.78 | 0.328 | 6 | 24.3 | 62.3 | 44 | 90 | 0.044 | 43.5 | 0.318 | 6 | 25.3 | 77 | 41 | 91 | 0.039 | 24.9 | 24.1 | 17.6 |  |  | MINIMUM | 8.3 | 8 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 |  | 9.1195 |  | 13.9162 | 24.8429 | 0.0020304 | MINIMUM | 74.6594 | 6394.6892 |  | 650.2203 | [6 empty] | 1.3696 | 1.5979 | 1.5175 | 0.25354 | 0.2434 | 0.18593 | 0.18593 | 0.22127 | 0.22492 | 1.5218 | 0.5 | 0.059522 | 0.059522 | 0.04976 | 1.0473 | 0.51974 | 0.09262 | 3.6255 | 0.60823 | 3.6635 | 1.0449 | 0.54139 | 0.091255 | 3.497 | 0.54306 | 5.5577 |  | MIN | 0.64 | 8.6 | 29.5814 | 18.9321 | 6.13 | 12.2 | 15 | 1.2621 |  |  |  | MIN | 0.67 | 8.6 | 29.5814 | 19.8195 | 6.22 | 11.6 | 15 | 1.3213 |  |  |  | MIN | 0.9 | 10.9 | 24.7706 | 22.2936 | 6.16 | 13.7 | 15 | 1.4862 |  |  |  | 1.2621
AVERAGE | 6.56 | 16.6667 | 17.6667 | 14.3167 | 95.8333 | 171.8333 | 12.85 | 0.3755 | 0.052 | 6.1367 | 9.5 | 0.059167 | 6.135 | 9.8333 |  | 6.0867 | 9.8333 |  | 6.105 | 0.3305 | 3 | 0.8125 | 12.05 | 8.725 | 0.63445 | 0.039833 | 6.175 | 0.3375 | 3.25 | 0.8525 | 11.3 | 8.475 | 0.61971 | 6.19 | 0.3715 | 3.25 | 0.8775 | 13.9 | 9.95 | 0.67278 | 0.032333 | 1.1667 | 0.43167 | 0.019 | 0.0405 | 0.015167 | 1.1667 | 0.48167 |  |  | 1.1667 | 0.67 |  | 7.2967 | 0.054667 | 1 | 4.05 | 10.3833 | 22 | 45 | 0.022 | 7.25 | 0.053 | 1 | 4.2167 | 12.8333 | 20.5 | 45.5 | 0.0195 | 4.15 | 4.0167 | 2.9333 |  |  | MAXIMUM | 10 | 9 | 11 | 29 | 9 | 9 | 10.5 | 28.5 |  | 11.1874 |  | 15.7234 | 25.1035 | 2.0902 | MAXIMUM | 75.3731 | 7255.5128 |  | 761.2335 | [6 empty] | 1.8794 | 1.7805 | 1.821 | 0.28904 | 0.27492 | 0.21994 | 0.20917 | 0.22901 | 0.24893 | 1.5218 | 5 | 0.060965 | 0.060965 | 0.052758 | 1.1089 | 0.55031 | 0.10199 | 3.9921 | 0.74567 | 4.0214 | 1.1131 | 0.59061 | 0.11493 | 3.5236 | 0.57022 | 6.2998
MINIMUM | 6.4 | 15 | 17 | 14.1 | 90 | 169 | 12.6 | 0.341 | 0.038 | 6.1 | 8 | 0.05 | 6.07 | 9 |  | 6.06 | 9 |  | 6.01 | 0.315 | 3 | 0.64 | 11.7 | 8.3 | 0.60939 | 0.037 | 6.11 | 0.32 | 3 | 0.67 | 10.9 | 8 | 0.5917 | 6.14 | 0.345 | 3 | 0.82 | 13.1 | 9.3 | 0.63667 | 0.022 | 1 | 0.28 | 0.014 | 0.039 | 0.011 | 1 | 0.29 |  |  | 1 | 0.32 |  | 7.15 | 0.052 | 1 | 3.6 | 9.9 | 21 | 41 | 0.013 | 7.16 | 0.05 | 1 | 3.7 | 12.3 | 20 | 38 | 0.01 | 3.9 | 3.8 | 2.6 | [15 empty] | MIL/MIN |  | TOTAL | 33390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245 | 1265 | 1385 | 2520 | 2420 | 1800 | 1760 | 2350 | 2430 | 3200 | 0 | 3770 | 3770 | 3630 | 311 | 414 | 45 | 4780 | 972 | 881 | 176 | 247 | 26 | 2270 | 461 | 780
MAXIMUM | 6.72 | 19 | 19 | 14.8 | 98 | 176 | 13.1 | 0.394 | 0.066 | 6.18 | 10 | 0.066 | 6.2 | 11 |  | 6.12 | 11 |  | 6.18 | 0.37 | 3 | 0.91 | 12.2 | 9 | 0.65066 | 0.044 | 6.25 | 0.357 | 4 | 0.98 | 11.6 | 9 | 0.65066 | 6.23 | 0.401 | 4 | 0.97 | 14.5 | 10.9 | 0.72556 | 0.04 | 2 | 0.66 | 0.024 | 0.043 | 0.023 | 2 | 0.8 |  |  | 2 | 0.89 |  | 7.55 | 0.059 | 1 | 4.5 | 10.7 | 23 | 49 | 0.031 | 7.38 | 0.057 | 1 | 4.6 | 13.5 | 21 | 53 | 0.029 | 4.3 | 4.1 | 3.5 | [17 empty] | AVERAGE | 8347.5 | [9 empty] | 311.25 | 316.25 | 346.25 | 630 | 605 | 450 | 440 | 587.5 | 607.5 | 800 |  | 942.5 | 942.5 | 907.5 | 77.75 | 103.5 | 11.25 | 1195 | 243 | 220.25 | 44 | 61.75 | 6.5 | 567.5 | 115.25 | 195
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1194 |  | TOTAL AVG COAG ALK: |  |  |  | 9.7222 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.401 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.64 | [5 empty] | 6.1567 |  |  |  |  | 0.04 |  |  |  |  | 0.64 | [6 empty] | 0.04 | [16 empty] | Pump Station MIN |  | 2.6 | [17 empty] | MINIMUM | 7950 | [9 empty] | 240 | 280 | 300 | 560 | 580 | 440 | 440 | 550 | 550 | 800 |  | 880 | 880 | 830 | 72 | 99 | 10 | 1160 | 235 | 215 | 40 | 55 | 6 | 530 | 110 | 190
[90 empty] | MAXIMUM | 8940 | [9 empty] | 380 | 360 | 400 | 760 | 640 | 480 | 440 | 640 | 720 | 800 |  | 1040 | 1040 | 1000 | 82 | 108 | 12 | 1260 | 255 | 226 | 48 | 70 | 7 | 620 | 125 | 200
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.786 |  | TOTAL MGD: |  | 0.001 |  |  | FINISHED SOUTH 1 |  | START: | 23827210 |  | END: | 23827211 |  |  | Alum | 8892 | 10792 | 10792 | 10303 | 10303 | 0 | [44 empty] | 0.64 | 8.6 | 29.5814 | 18.9321 | 6.13 | 12.2 | 15 | 1.2621
[73 empty] | FINISHED 2 | 13.749 |  | TOTAL MGD: |  | 10.785 |  |  | FINISHED SOUTH 2 |  | START: | 44086297 |  | END: | 44097082 |  |  | Caustic | 6484 | 7952 | 7952
[73 empty] | TOTAL RAW | 27.727 |  | TOTAL MGD: |  | 4.799 |  |  | FINISHED CONWAY |  | START: | 10328455 |  | END: | 10333254 |  |  | Hypochlorite | 8 |  | 33
[76 empty] | TOTAL MGD: |  | 8.95 |  |  | FINISHED PERRY |  | START: | 34011819 |  | END: | 34020769 |  |  | Phosphate | 1747
[76 empty] | TOTAL MGD: |  | 8.971 |  |  | RAW PLANT 1 |  | START: | 31177084 |  | END: | 31186055 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 8.412 |  |  | RAW PLANT 2 |  | START: | 31070624 |  | END: | 31079036 |  |  | Cal~Flo | 12.88 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.344 |  |  | RAW PLANT 3 |  | START: | 7732256 |  | END: | 7742600 |  |  | Zinc | 815
[76 empty] | TOTAL MGD: |  | 1.028 |  |  | DECANT |  | START: | 1885312 |  | END: | 1886340 |  |  | Polymer | 15
[76 empty] | TOTAL MGD: |  | 1.6893 |  |  | BLOW DOWN |  | START: | 9166.2318 |  | END: | 9167.9211 |  |  | NH3 | 10.74 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827211
44097082
10333254
34020769
31186055
31079036
7742600
1886340
9167.9211
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 25
DATE: | 2019-01-25 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-25 | [23 empty] | DATE: | 2019-01-25
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-25 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43490.0081 | 2,3,5 | 35 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 9.1195 | 1,3 | 15.7234 | 24.8429 | 1.7519 | 43490.0081 | 69.8568 | 6394.6892 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3696 | 1.5979 | 1.821 | 0.2566 | 0.27492 | 0.21994 | 0.20161 | 0.22901 | 0.22901 | 1.5218 | 5 | 0.059522 | 0.059522 | 0.052758 | 1.061 | 0.54972 | 0.10188 | 3.9845 | 0.74567 | 4.0214 | 1.0449 | 0.59061 | 0.11493 | 3.5011 | 0.57022 | 6.2998 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.17 | 0.337 | 4 | 0.67 | 12 | 8.6 | 0.62708 |  | 6.24 | 0.335 | 4 | 0.59 | 11.4 | 8.6 | 0.62708 | 6.2 | 0.353 | 4 | 0.92 | 14.5 | 9.6 | 0.65333 | [13 empty] | 7.34 | 0.05 | 1 | 3.9 | 10.6 |  |  |  | 7.33 | 0.053 | 1 | 3.8 | 12.5 |  |  |  | 4 | 3.9 | 2.9 | [18 empty] | 7400 | [6 empty] | 0 | 0 | 0 | 240 | 280 | 360 | 560 | 600 | 480 | 440 | 560 | 560 | 800 |  | 880 | 880 | 880 | 72 | 99 | 11 | 1260 | 255 | 215 | 40 | 60 | 7 | 550 | 110 | 190 |  | 1:00 | 0.67 | 8.6 | 29.5814 | 19.8195 | 6.17 | 12 | 15 | 1.3213 | 10 | 6.5 | 0.50708 | 1:00 | 0.59 | 8.6 | 29.5814 | 17.453 | 6.24 | 11.4 | 15 | 1.1635 | 10 | 6.5 | 0.50708 | 1:00 | 0.92 | 9.6 | 28.125 | 25.875 | 6.2 | 14.5 | 15 | 1.725 | 10 | 6.5 | 0.53333
2:00 | [72 empty] | 43490.3624 | 2,3,5 | 35 | 8.3 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 9.1195 | 1,3 | 15.7234 | 24.8429 | 1.8864 | 43490.3624 | 69.7624 | 5964.2774 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4267 | 1.4267 | 1.5175 | 0.2566 | 0.26576 | 0.20619 | 0.20619 | 0.22492 | 0.22492 | 1.5218 | 0 | 0.059522 | 0.059522 | 0.050959 | 1.0905 | 0.55527 | 0.09262 | 3.9875 | 0.73105 | 4.0214 | 1.0972 | 0.57092 | 0.098514 | 3.5011 | 0.58059 | 6.2998 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.48 | 15 | 16 | 14.4 | 95 | 172 | 13 | 0.378 |  | 6.14 | 8 | 0.064 | 6.13 | 9 |  | 6.09 | 9 | [8 empty] | 0.038 | [14 empty] | 0.031 | 1 | 0.48 |  | 0.039 | 0.011 | 1 | 0.36 |  | 0.021 | 1 | 0.65 | [38 empty] | 7390 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 300 | 560 | 580 | 450 | 450 | 550 | 550 | 800 |  | 880 | 880 | 850 | 74 | 100 | 10 | 1220 | 250 | 215 | 42 | 58 | 6 | 550 | 112 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43490.4751 | 2,3,5 | 35 | 6 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 9.1195 | 1,3 | 15.7234 | 24.8429 | 1.8864 | 43490.4751 | 69.4941 | 5964.2774 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4267 | 1.4267 | 1.5175 | 0.2472 | 0 | 0.20817 | 0.20817 | 0.21732 | 0.21732 | 1.5218 | 0 | 0.059522 | 0.059522 | 0.050959 | 1.0905 | 0.55527 | 0.09262 | 3.9875 | 0.73105 | 4.0214 | 1.0972 | 0.57092 | 0.098514 | 3.5011 | 0.58059 | 6.2998 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.39 | 0.052 | 1 | 3.7 | 10.6 |  |  |  | 7.4 | 0.055 | 1 | 3.8 | 12.3 |  |  |  | 4 | 3.9 | 3.2 | [18 empty] | 7390 | [6 empty] | 0 | 0 | 0 | 250 | 250 | 300 | 780 | 0 | 520 | 520 | 600 | 600 | 800 |  | 880 | 880 | 850 | 74 | 100 | 10 | 1220 | 250 | 215 | 42 | 58 | 6 | 550 | 112 | 190 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43490.8411 | 2,3,5 | 34 | 6 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 12.0182 | 1,3 | 12.8434 | 24.8616 | 1.8864 | 43490.8411 | 70.3404 | 5226.4286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.712 | 1.7198 | 0.24086 | 0 | 0.25621 | 0.25621 | 0.20283 | 0.23181 | 1.4267 | 3 | 0.059522 | 0.059522 | 0.052758 | 1.061 | 0.54972 | 0.10188 | 4.003 | 0.76029 | 4.0214 | 1.0972 | 0.59061 | 0.11493 | 3.4666 | 0.62206 | 6.2998 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.57 | 19 | 17 | 14.3 | 91 | 166 | 12.6 | 0.368 |  | 6.19 | 10 | 0.057 | 6.15 | 10 |  | 6.09 | 10 | [8 empty] | 0.038 | [14 empty] | 0.028 | 1 | 0.44 |  | 0.038 | 0.01 | 1 | 0.4 |  | 0.021 | 1 | 0.62 | [38 empty] | 7480 | [6 empty] | 0 | 0 | 0 | 280 | 300 | 340 | 760 | 0 | 640 | 640 | 560 | 640 | 750 |  | 880 | 880 | 880 | 72 | 99 | 11 | 1280 | 260 | 215 | 42 | 60 | 7 | 580 | 120 | 190 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43490.8753 | 2,3,5 | 34 | 6 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 12.0182 | 1,3 | 12.8434 | 24.8616 | 1.8864 | 43490.8753 | 65.0743 | 5226.4286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.712 | 1.7198 | 0.24086 | 0 | 0.25621 | 0.25621 | 0.20283 | 0.23181 | 1.4267 | 3 | 0.059522 | 0.059522 | 0.052758 | 1.061 | 0.54972 | 0.10188 | 4.003 | 0.76029 | 4.0214 | 1.0972 | 0.59061 | 0.11493 | 3.4666 | 0.62206 | 6.2998 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.057 | [9 empty] | 6.16 | 0.347 | 3 | 0.81 | 11.7 | 8.3 | 0.60939 |  | 6.17 | 0.371 | 4 | 0.81 | 11.2 | 8.3 | 0.60939 | 6.21 | 0.359 | 3 | 0.94 | 14.1 | 9.3 | 0.63667 |  |  |  | 0.043 | [9 empty] | 7.29 | 0.064 | 1 | 3.8 | 11.4 | 25 | 43 | 0.036 | 7.39 | 0.057 | 1 | 4.6 | 12 | 23 | 39 | 0.026 | 4 | 3.9 | 3.1 | [18 empty] | 6920 | [6 empty] | 0 | 0 | 0 | 280 | 300 | 340 | 760 | 0 | 640 | 640 | 560 | 640 | 750 |  | 880 | 880 | 880 | 72 | 99 | 11 | 1280 | 260 | 215 | 42 | 60 | 7 | 580 | 120 | 190 |  | 9:00 | 0.81 | 8.3 | 30.6506 | 24.827 | 6.16 | 11.7 | 15 | 1.6551 | 10 | 6.5 | 0.48939 | 9:00 | 0.81 | 8.3 | 30.6506 | 24.827 | 6.17 | 11.2 | 15 | 1.6551 | 10 | 6.5 | 0.48939 | 9:00 | 0.94 | 9.3 | 29.0323 | 27.2903 | 6.21 | 14.1 | 15 | 1.8194 | 10 | 6.5 | 0.51667
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.42 | 20 | 16 | 14.9 | 96 | 170 | 12.3 | 0.376 |  | 6.19 | 10 | 0.054 | 6.15 | 10 |  | 6.1 | 10 | [8 empty] | 0.041 | [14 empty] | 0.027 | 1 | 0.66 |  | 0.04 | 0.015 | 1 | 0.65 |  | 0.021 | 1 | 0.86 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.29 | 0.255 | 3 | 0.84 | 12.2 | 6 | 0.47377 |  | 6.25 | 0.351 | 4 | 0.8 | 11.6 | 9.5 | 0.68014 | 6.21 | 0.329 | 3 | 0.88 | 14 | 10.5 | 0.70333 | [13 empty] | 7.31 | 0.058 | 1 | 4 | 10.5 |  |  |  | 7.35 | 0.054 | 1 | 4.2 | 13 |  |  |  | 4.1 | 3.9 | 3.3 | [55 empty] | 13:00 | 0.84 | 6 | 42.4 | 35.616 | 6.29 | 12.2 | 15 | 2.3744 | 10 | 6.5 | 0.35377 | 13:00 | 0.8 | 9.5 | 26.7789 | 21.4232 | 6.25 | 11.6 | 15 | 1.4282 | 10 | 6.5 | 0.56014 | 13:00 | 0.88 | 10.5 | 25.7143 | 22.6286 | 6.21 | 14 | 15 | 1.5086 | 10 | 6.5 | 0.58333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.46 | 21 | 17 | 14.6 | 92 | 172 | 13 | 0.335 |  | 6.23 | 11 | 0.034 | 6.19 | 11 |  | 6.11 | 11 | [8 empty] | 0.017 | [14 empty] | 0.025 | 1 | 0.6 |  | 0.017 | 0.01 | 1 | 0.42 |  | 0.022 | 1 | 0.75 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.34 | 0.054 | 1 | 4 | 10.5 |  |  |  | 7.28 | 0.052 | 1 | 4 | 13 |  |  |  | 4.1 | 4 | 3.2 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.5 | 19 | 16 | 14.7 | 95 | 171 | 12.9 | 0.36 |  | 6.25 | 9 | 0.062 | 6.09 | 9 |  | 6.02 | 8 | [8 empty] | 0.036 | [14 empty] | 0.021 | 1 | 0.28 |  | 0.039 | 0.012 | 1 | 0.24 |  | 0.021 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.033 | [9 empty] | 5.92 | 0.393 | 4 | 0.59 | 12.2 | 6 | 0.4266 |  | 6.03 | 0.335 | 5 | 0.65 | 11.6 | 9.6 | 0.68604 | 6.09 | 0.408 | 3 | 0.73 | 14.2 | 10.5 | 0.70333 |  |  |  | 0.011 | [9 empty] | 7.12 | 0.06 | 1 | 3.9 | 10.6 | 21 | 35 | 0.012 | 7.22 | 0.059 | 1 | 3.8 | 12.7 | 22 | 38 | 0.011 | 4 | 3.9 | 3.1 | [55 empty] | 21:00 | 0.59 | 6 | 42.4 | 25.016 | 5.92 | 12.2 | 13 | 1.9243 | 10 | 6 | 0.3066 | 21:00 | 0.65 | 9.6 | 26.5 | 17.225 | 6.03 | 11.6 | 15 | 1.1483 | 10 | 6.5 | 0.56604 | 21:00 | 0.73 | 10.5 | 25.7143 | 18.7714 | 6.09 | 14.2 | 15 | 1.2514 | 10 | 6.5 | 0.58333
22:00 | [72 empty] | DOSE |  | TOTAL | 34.6 | 45.1 | 50.1 | 129.8 | 39 | 39 | 44 | 122 | 0 | 51.395 | 0 | 72.8568 | 124.2518 | 9.2975 | TOTAL | 344.528 | 28776.1012 | 0 | 3251.1013 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4188 | 7.8753 | 8.2955 | 1.2421 | 0.54069 | 1.1467 | 1.1284 | 1.0769 | 1.1349 | 7.4188 | 11 | 0.29761 | 0.29761 | 0.26019 | 5.364 | 2.7597 | 0.49088 | 19.9654 | 3.7283 | 20.1068 | 5.4336 | 2.9137 | 0.54183 | 17.4365 | 2.9755 | 31.4992 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.49 | 18 | 17 | 14.6 | 94 | 169 | 12.8 | 0.379 |  | 6.17 | 8 | 0.062 | 5.97 | 8 |  | 5.95 | 8 | [8 empty] | 0.04 | [14 empty] | 0.023 | 1 | 0.32 |  | 0.04 | 0.011 | 1 | 0.32 |  | 0.019 | 1 | 0.49 | [22 empty] | AVERAGE | 6.92 | 9.02 | 10.02 | 25.96 | 7.8 | 7.8 | 8.8 | 24.4 |  | 10.279 |  | 14.5714 | 24.8504 | 1.8595 | AVERAGE | 68.9056 | 5755.2202 |  | 650.2203 | 0 | 0 | 0 |  |  |  | 1.4838 | 1.5751 | 1.6591 | 0.24843 | 0.10814 | 0.22935 | 0.22568 | 0.21538 | 0.22697 | 1.4838 | 2.2 | 0.059522 | 0.059522 | 0.052038 | 1.0728 | 0.55194 | 0.098177 | 3.9931 | 0.74567 | 4.0214 | 1.0867 | 0.58273 | 0.10837 | 3.4873 | 0.5951 | 6.2998 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 38.92 | 112 | 99 | 87.5 | 563 | 1020 | 76.6 | 2.196 | 0.09 | 37.17 | 56 | 0.333 | 36.68 | 57 | 0 | 36.36 | 56 | 0 | 24.54 | 1.332 | 14 | 2.91 | 48.1 | 28.9 | 2.1368 | 0.21 | 24.69 | 1.392 | 17 | 2.85 | 45.8 | 36 | 2.6026 | 24.71 | 1.449 | 13 | 3.47 | 56.8 | 39.9 | 2.6967 | 0.155 | 6 | 2.78 | 0.054 | 0.213 | 0.069 | 6 | 2.39 | 0 | 0.125 | 6 | 3.83 | 0 | 43.79 | 0.338 | 6 | 23.3 | 64.2 | 46 | 78 | 0.048 | 43.97 | 0.33 | 6 | 24.2 | 75.5 | 45 | 77 | 0.037 | 24.2 | 23.5 | 18.8 |  |  | MINIMUM | 6 | 8.3 | 9.3 | 25.9 | 7.8 | 7.8 | 8.8 | 24.4 |  | 9.1195 |  | 12.8434 | 24.8429 | 1.7519 | MINIMUM | 65.0743 | 5226.4286 |  | 650.2203 | [6 empty] | 1.3696 | 1.4267 | 1.5175 | 0.24086 | 0 | 0.20619 | 0.20161 | 0.20283 | 0.21732 | 1.4267 | 0 | 0.059522 | 0.059522 | 0.050959 | 1.061 | 0.54972 | 0.09262 | 3.9845 | 0.73105 | 4.0214 | 1.0449 | 0.57092 | 0.098514 | 3.4666 | 0.57022 | 6.2998 |  | MIN | 0.67 | 8.6 | 29.5814 | 19.8195 | 6.17 | 12 | 15 | 1.3213 |  |  |  | MIN | 0.65 | 9.6 | 26.5 | 17.225 | 6.03 | 11.6 | 15 | 1.1483 |  |  |  | MIN | 0.73 | 10.5 | 25.7143 | 18.7714 | 6.09 | 14.2 | 15 | 1.2514 |  |  |  | 1.1483
AVERAGE | 6.4867 | 18.6667 | 16.5 | 14.5833 | 93.8333 | 170 | 12.7667 | 0.366 | 0.045 | 6.195 | 9.3333 | 0.0555 | 6.1133 | 9.5 |  | 6.06 | 9.3333 |  | 6.135 | 0.333 | 3.5 | 0.7275 | 12.025 | 7.225 | 0.53421 | 0.035 | 6.1725 | 0.348 | 4.25 | 0.7125 | 11.45 | 9 | 0.65066 | 6.1775 | 0.36225 | 3.25 | 0.8675 | 14.2 | 9.975 | 0.67417 | 0.025833 | 1 | 0.46333 | 0.027 | 0.0355 | 0.0115 | 1 | 0.39833 |  | 0.020833 | 1 | 0.63833 |  | 7.2983 | 0.056333 | 1 | 3.8833 | 10.7 | 23 | 39 | 0.024 | 7.3283 | 0.055 | 1 | 4.0333 | 12.5833 | 22.5 | 38.5 | 0.0185 | 4.0333 | 3.9167 | 3.1333 |  |  | MAXIMUM | 8.3 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 |  | 12.0182 |  | 15.7234 | 24.8616 | 1.8864 | MAXIMUM | 70.3404 | 6394.6892 |  | 650.2203 | [6 empty] | 1.5979 | 1.712 | 1.821 | 0.2566 | 0.27492 | 0.25621 | 0.25621 | 0.22901 | 0.23181 | 1.5218 | 5 | 0.059522 | 0.059522 | 0.052758 | 1.0905 | 0.55527 | 0.10188 | 4.003 | 0.76029 | 4.0214 | 1.0972 | 0.59061 | 0.11493 | 3.5011 | 0.62206 | 6.2998
MINIMUM | 6.42 | 15 | 16 | 14.3 | 91 | 166 | 12.3 | 0.335 | 0.033 | 6.14 | 8 | 0.034 | 5.97 | 8 |  | 5.95 | 8 |  | 5.92 | 0.255 | 3 | 0.59 | 11.7 | 6 | 0.4266 | 0.017 | 6.03 | 0.335 | 4 | 0.59 | 11.2 | 8.3 | 0.60939 | 6.09 | 0.329 | 3 | 0.73 | 14 | 9.3 | 0.63667 | 0.021 | 1 | 0.28 | 0.011 | 0.017 | 0.01 | 1 | 0.24 |  | 0.019 | 1 | 0.46 |  | 7.12 | 0.05 | 1 | 3.7 | 10.5 | 21 | 35 | 0.012 | 7.22 | 0.052 | 1 | 3.8 | 12 | 22 | 38 | 0.011 | 4 | 3.9 | 2.9 | [15 empty] | MIL/MIN |  | TOTAL | 36580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 1380 | 1640 | 3420 | 1180 | 2730 | 2690 | 2830 | 2990 | 3900 | 0 | 4400 | 4400 | 4340 | 364 | 497 | 53 | 6260 | 1275 | 1075 | 208 | 296 | 33 | 2810 | 574 | 950
MAXIMUM | 6.57 | 21 | 17 | 14.9 | 96 | 172 | 13 | 0.379 | 0.057 | 6.25 | 11 | 0.064 | 6.19 | 11 |  | 6.11 | 11 |  | 6.29 | 0.393 | 4 | 0.84 | 12.2 | 8.6 | 0.62708 | 0.041 | 6.25 | 0.371 | 5 | 0.81 | 11.6 | 9.6 | 0.68604 | 6.21 | 0.408 | 4 | 0.94 | 14.5 | 10.5 | 0.70333 | 0.031 | 1 | 0.66 | 0.043 | 0.04 | 0.015 | 1 | 0.65 |  | 0.022 | 1 | 0.86 |  | 7.39 | 0.064 | 1 | 4 | 11.4 | 25 | 43 | 0.036 | 7.4 | 0.059 | 1 | 4.6 | 13 | 23 | 39 | 0.026 | 4.1 | 4 | 3.3 | [17 empty] | AVERAGE | 7316 | [9 empty] | 260 | 276 | 328 | 684 | 236 | 546 | 538 | 566 | 598 | 780 |  | 880 | 880 | 868 | 72.8 | 99.4 | 10.6 | 1252 | 255 | 215 | 41.6 | 59.2 | 6.6 | 562 | 114.8 | 190
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.1228 |  | TOTAL AVG COAG ALK: |  |  |  | 9.3889 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.408 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.59 | [5 empty] | 6.1617 |  |  |  |  | 0.031 |  |  |  |  | 0.59 | [6 empty] | 0.031 | [16 empty] | Pump Station MIN |  | 2.9 | [17 empty] | MINIMUM | 6920 | [9 empty] | 240 | 250 | 300 | 560 | 0 | 450 | 440 | 550 | 550 | 750 |  | 880 | 880 | 850 | 72 | 99 | 10 | 1220 | 250 | 215 | 40 | 58 | 6 | 550 | 110 | 190
[90 empty] | MAXIMUM | 7480 | [9 empty] | 280 | 300 | 360 | 780 | 600 | 640 | 640 | 600 | 640 | 800 |  | 880 | 880 | 880 | 74 | 100 | 11 | 1280 | 260 | 215 | 42 | 60 | 7 | 580 | 120 | 190
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.062 |  | TOTAL MGD: |  | 0.009 |  |  | FINISHED SOUTH 1 |  | START: | 23827211 |  | END: | 23827220 |  |  | Alum | 8891 | 10795 | 10795 | 11101 | 11101 | 0 | [44 empty] | 0.65 | 9.6 | 26.5 | 17.225 | 6.03 | 11.6 | 15 | 1.1483
[73 empty] | FINISHED 2 | 12.989 |  | TOTAL MGD: |  | 10.053 |  |  | FINISHED SOUTH 2 |  | START: | 44097082 |  | END: | 44107135 |  |  | Caustic | 6414 | 7956 | 7956
[73 empty] | TOTAL RAW | 26.321 |  | TOTAL MGD: |  | 4.458 |  |  | FINISHED CONWAY |  | START: | 10333254 |  | END: | 10337712 |  |  | Hypochlorite | 6 |  | 33
[76 empty] | TOTAL MGD: |  | 8.531 |  |  | FINISHED PERRY |  | START: | 34020769 |  | END: | 34029300 |  |  | Phosphate | 1696
[76 empty] | TOTAL MGD: |  | 7.112 |  |  | RAW PLANT 1 |  | START: | 31186055 |  | END: | 31193167 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.188 |  |  | RAW PLANT 2 |  | START: | 31079036 |  | END: | 31088224 |  |  | Cal~Flo | 17.29 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.021 |  |  | RAW PLANT 3 |  | START: | 7742600 |  | END: | 7752621 |  |  | Zinc | 787
[76 empty] | TOTAL MGD: |  | 0.597 |  |  | DECANT |  | START: | 1886340 |  | END: | 1886937 |  |  | Polymer | 31
[76 empty] | TOTAL MGD: |  | 1.2185 |  |  | BLOW DOWN |  | START: | 9167.9211 |  | END: | 9169.1396 |  |  | NH3 | 10.57 |  | BI-SUL | 1050
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827220
44107135
10337712
34029300
31193167
31088224
7752621
1886937
9169.1396
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2BCOperator:
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. BuildingBCOperator:
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1BCOperator:
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 26
DATE: | 2019-01-26 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-26 | [23 empty] | DATE: | 2019-01-26
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-26 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 |  | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43491.0026 | 2,3,5 | 34 | 6 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 12.0182 | 1,3 | 12.8434 | 24.8616 | 1.3791 | 43491.0026 | 65.0743 | 5226.4286 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5979 | 1.712 | 1.7198 | 0.24086 | 0 | 0.25621 | 0.25621 | 0.20283 | 0.23181 | 1.4267 | 3 | 0.059522 | 0.059522 | 0.052758 | 1.061 | 0.54972 | 0.10188 | 4.003 | 0.76029 | 4.0214 | 1.0972 | 0.59061 | 0.11493 | 3.4666 | 0.62206 | 6.2998 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.14 | 0.371 | 4 | 0.61 | 12.1 | 5.8 | 0.46198 |  | 6.12 | 0.322 | 4 | 0.72 | 11.4 | 7.4 | 0.55632 | 6.11 | 0.33 | 3 | 0.91 | 13.4 | 10.7 | 0.71444 | [13 empty] | 7.34 | 0.052 | 1 | 3.6 | 10.6 |  |  |  | 7.22 | 0.055 | 1 | 3.5 | 12.3 |  |  |  | 4.2 | 3.8 | 2.8 | [18 empty] | 6920 | [6 empty] | 0 | 0 | 0 | 280 | 300 | 340 | 760 | 0 | 640 | 640 | 560 | 640 | 750 |  | 880 | 880 | 880 | 72 | 99 | 11 | 1280 | 260 | 215 | 42 | 60 | 7 | 580 | 120 | 190 |  | 1:00 | 0.61 | 5.8 | 43.8621 | 26.7559 | 6.14 | 12.1 | 15 | 1.7837 | 10 | 6.5 | 0.34198 | 1:00 | 0.72 | 7.4 | 34.3784 | 24.7524 | 6.12 | 11.4 | 15 | 1.6502 | 10 | 6.5 | 0.43632 | 1:00 | 0.91 | 10.7 | 25.2336 | 22.9626 | 6.11 | 13.4 | 15 | 1.5308 | 10 | 6.5 | 0.59444
2:00 | [72 empty] | 8:26 | 2,3,5 | 34 | 6 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 | ,1,3 | 12.0182 | 1,3 | 12.8434 | 24.8616 | 1.5134 | 43491.4682 | 64.8862 | 4796.0168 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.712 | 1.712 | 1.5175 | 0.24086 | 0 | 0.22018 | 0.22018 | 0.20283 | 0.20283 | 1.4267 | 3 | 0.059522 | 0.059522 | 0.050959 | 1.0905 | 0.55527 | 0.09262 | 4.018 | 0.76029 | 4.0214 | 1.0972 | 0.57092 | 0.098514 | 3.5166 | 0.61169 | 6.2998 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.45 | 14 | 14 | 14.8 | 94 | 171 | 12.6 | 0.37 |  | 6.21 | 7 | 0.065 | 6 | 7 |  | 5.92 | 7 | [8 empty] | 0.04 | [14 empty] | 0.024 | 1 | 0.23 |  | 0.04 | 0.009 | 1 | 0.32 |  | 0.021 | 1 | 0.51 | [38 empty] | 6900 | [6 empty] | 0 | 0 | 0 | 300 | 300 | 300 | 760 | 0 | 550 | 550 | 560 | 560 | 750 |  | 880 | 880 | 850 | 74 | 100 | 10 | 1280 | 260 | 215 | 42 | 58 | 6 | 580 | 118 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43491.8603 | 2,3,5 | 37 | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 9.9749 | 1,3 | 14.0458 | 24.0206 | 1.5134 | 43491.8603 | 64.8453 | 4796.0168 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6089 | 1.5016 | 1.5316 | 0.27382 | 0 | 0.1972 | 0.1972 | 0.20627 | 0.21916 | 1.4267 | 4 | 0.05975 | 0.05975 | 0.049921 | 1.1079 | 0.54791 | 0.095744 | 3.9973 | 0.76945 | 4.3943 | 1.0876 | 0.55886 | 0.10875 | 3.5093 | 0.63766 | 6.4317 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.06 | 0.047 | 1 | 3.7 | 10.6 |  |  |  | 7.03 | 0.05 | 1 | 3.4 | 12.3 |  |  |  | 4.2 | 3.8 | 3 | [18 empty] | 7320 | [6 empty] | 0 | 0 | 0 | 300 | 280 | 320 | 720 | 0 | 560 | 560 | 640 | 680 | 750 |  | 940 | 940 | 880 | 80 | 105 | 11 | 1380 | 280 | 250 | 44 | 60 | 7 | 640 | 130 | 205 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.46 | 15 | 16 | 14.7 | 89 | 168 | 12.1 | 0.367 |  | 6.23 | 9 | 0.058 | 6.01 | 9 |  | 5.99 | 9 | [8 empty] | 0.038 | [14 empty] | 0.022 | 1 | 0.27 |  | 0.038 | 0.013 | 1 | 0.44 |  | 0.019 | 1 | 0.66 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.056 | [9 empty] | 5.97 | 0.381 | 3 | 0.52 | 11.5 | 6 | 0.4266 |  | 6.02 | 0.342 | 4 | 0.64 | 10.6 | 9.5 | 0.68014 | 6 | 0.376 | 3 | 0.91 | 13 | 10.5 | 0.62556 |  |  |  | 0.02 | [9 empty] | 7.23 | 0.055 | 1 | 4.9 | 10.6 | 21 | 31 | 0.029 | 7.17 | 0.052 | 1 | 3.3 | 11.6 | 22 | 30 | 0.024 | 4.2 | 3.8 | 3 | [55 empty] | 9:00 | 0.52 | 6 | 42.4 | 22.048 | 5.97 | 11.5 | 13 | 1.696 | 10 | 6 | 0.3066 | 9:00 | 0.64 | 9.5 | 26.7789 | 17.1385 | 6.02 | 10.6 | 15 | 1.1426 | 10 | 6.5 | 0.56014 | 9:00 | 0.91 | 10.5 | 25.7143 | 23.4 | 6 | 13 | 13 | 1.8 | 10 | 6 | 0.50556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.51 | 16 | 16 | 14.7 | 90 | 170 | 12.5 | 0.371 |  | 6.16 | 10 | 0.06 | 5.95 | 10 |  | 5.94 | 10 | [8 empty] | 0.038 | [14 empty] | 0.023 | 1 | 0.33 |  | 0.039 | 0.013 | 1 | 0.42 |  | 0.018 | 1 | 0.59 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.04 | 0.327 | 3 | 0.55 | 12.2 | 6 | 0.47377 |  | 6.02 | 0.295 | 3 | 0.65 | 11.5 | 9.5 | 0.68014 | 6 | 0.427 | 3 | 0.79 | 13.4 | 10.5 | 0.62556 | [13 empty] | 7.22 | 0.051 | 1 | 4.4 | 10.5 |  |  |  | 7.09 | 0.05 | 1 | 3.5 | 13 |  |  |  | 4.2 | 3.8 | 2.3 | [55 empty] | 13:00 | 0.55 | 6 | 42.4 | 23.32 | 6.04 | 12.2 | 15 | 1.5547 | 10 | 6.5 | 0.35377 | 13:00 | 0.65 | 9.5 | 26.7789 | 17.4063 | 6.02 | 11.5 | 15 | 1.1604 | 10 | 6.5 | 0.56014 | 13:00 | 0.79 | 10.5 | 25.7143 | 20.3143 | 6 | 13.4 | 13 | 1.5626 | 10 | 6 | 0.50556
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.65 | 18 | 16 | 14.8 | 90 | 166 | 12.5 | 0.345 |  | 6.24 | 10 | 0.05 | 6.17 | 11 |  | 6 | 11 | [8 empty] | 0.035 | [14 empty] | 0.023 | 1 | 0.3 |  | 0.036 | 0.015 | 1 | 0.42 |  | 0.021 | 1 | 0.55 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.14 | 0.05 | 1 | 4.2 | 10.5 |  |  |  | 7.11 | 0.048 | 1 | 3.6 | 13 |  |  |  | 4.2 | 3.8 | 2.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.57 | 15 | 18 | 14.9 | 94 | 168 | 12.5 | 0.355 |  | 6.27 | 9 | 0.057 | 5.99 | 8 |  | 5.95 | 9 | [8 empty] | 0.038 | [14 empty] | 0.022 | 1 | 0.16 |  | 0.042 | 0.012 | 1 | 0.25 |  | 0.019 | 1 | 0.37 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.036 | [9 empty] | 6.08 | 0.388 | 4 | 0.6 | 12.1 | 5.4 | 0.4384 |  | 6.09 | 0.315 | 5 | 0.64 | 11.3 | 10.5 | 0.7391 | 6 | 0.42 | 5 | 0.75 | 13.3 | 11.8 | 0.68815 |  |  |  | 0.013 | [9 empty] | 7.31 | 0.056 | 1 | 3.7 | 10.4 | 22 | 32 | 0.014 | 7.26 | 0.057 | 1 | 3.8 | 12.5 | 23 | 35 | 0.012 | 4.1 | 3.9 | 2.6 | [55 empty] | 21:00 | 0.6 | 5.4 | 47.1111 | 28.2667 | 6.08 | 12.1 | 15 | 1.8844 | 10 | 6.5 | 0.3184 | 21:00 | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.09 | 11.3 | 15 | 1.0338 | 10 | 6.5 | 0.6191 | 21:00 | 0.75 | 11.8 | 22.8814 | 17.161 | 6 | 13.3 | 13 | 1.3201 | 10 | 6 | 0.56815
22:00 | [72 empty] | DOSE |  | TOTAL | 17 | 29.8 | 32.8 | 79.6 | 23.9 | 23.9 | 26.9 | 74.7 | 0 | 34.0114 | 0 | 39.7325 | 73.7438 | 4.406 | TOTAL | 194.8058 | 14818.4622 | 0 | 1950.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9188 | 4.9257 | 4.7689 | 0.75555 | 0 | 0.67359 | 0.67359 | 0.61194 | 0.65381 | 4.2801 | 10 | 0.17879 | 0.17879 | 0.15364 | 3.2594 | 1.6529 | 0.29025 | 12.0182 | 2.29 | 12.437 | 3.282 | 1.7204 | 0.3222 | 10.4925 | 1.8714 | 19.0314 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.5 | 16 | 17 | 14.9 | 92 | 168 | 12.6 | 0.367 |  | 6.24 | 10 | 0.069 | 5.96 | 9 |  | 5.93 | 9 | [8 empty] | 0.04 | [14 empty] | 0.021 | 1 | 0.45 |  | 0.043 | 0.016 | 1 | 0.44 |  | 0.021 | 1 | 0.65 | [22 empty] | AVERAGE | 5.6667 | 9.9333 | 10.9333 | 26.5333 | 7.9667 | 7.9667 | 8.9667 | 24.9 |  | 11.3371 |  | 13.2442 | 24.5813 | 1.4687 | AVERAGE | 64.9353 | 4939.4874 |  | 650.2203 | 0 | 0 | 0 |  |  |  | 1.6396 | 1.6419 | 1.5896 | 0.25185 |  | 0.22453 | 0.22453 | 0.20398 | 0.21794 | 1.4267 | 3.3333 | 0.059598 | 0.059598 | 0.051213 | 1.0865 | 0.55097 | 0.096749 | 4.0061 | 0.76334 | 4.1457 | 1.094 | 0.57346 | 0.1074 | 3.4975 | 0.6238 | 6.3438 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.14 | 94 | 97 | 88.8 | 549 | 1011 | 74.8 | 2.175 | 0.092 | 37.35 | 55 | 0.359 | 36.08 | 54 | 0 | 35.73 | 55 | 0 | 24.23 | 1.467 | 14 | 2.28 | 47.9 | 23.2 | 1.8008 | 0.229 | 24.25 | 1.274 | 16 | 2.65 | 44.8 | 36.9 | 2.6557 | 24.11 | 1.553 | 14 | 3.36 | 53.1 | 43.5 | 2.6537 | 0.135 | 6 | 1.74 | 0.033 | 0.238 | 0.078 | 6 | 2.29 | 0 | 0.119 | 6 | 3.33 | 0 | 43.3 | 0.311 | 6 | 24.5 | 63.2 | 43 | 63 | 0.043 | 42.88 | 0.312 | 6 | 21.1 | 74.7 | 45 | 65 | 0.036 | 25.1 | 22.9 | 16.1 |  |  | MINIMUM | 5 | 9.5 | 10.5 | 26 | 7.8 | 7.8 | 8.8 | 24.4 |  | 9.9749 |  | 12.8434 | 24.0206 | 1.3791 | MINIMUM | 64.8453 | 4796.0168 |  | 650.2203 | [6 empty] | 1.5979 | 1.5016 | 1.5175 | 0.24086 |  | 0.1972 | 0.1972 | 0.20283 | 0.20283 | 1.4267 | 3 | 0.059522 | 0.059522 | 0.049921 | 1.061 | 0.54791 | 0.09262 | 3.9973 | 0.76029 | 4.0214 | 1.0876 | 0.55886 | 0.098514 | 3.4666 | 0.61169 | 6.2998 |  | MIN | 0.55 | 6 | 42.4 | 23.32 | 6.04 | 12.2 | 15 | 1.5547 |  |  |  | MIN | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.09 | 11.3 | 15 | 1.0338 |  |  |  | MIN | 0.75 | 11.8 | 22.8814 | 17.161 | 6 | 13.3 | 13 | 1.3201 |  |  |  | 1.0338
AVERAGE | 6.5233 | 15.6667 | 16.1667 | 14.8 | 91.5 | 168.5 | 12.4667 | 0.3625 | 0.046 | 6.225 | 9.1667 | 0.059833 | 6.0133 | 9 |  | 5.955 | 9.1667 |  | 6.0575 | 0.36675 | 3.5 | 0.57 | 11.975 | 5.8 | 0.45019 | 0.038167 | 6.0625 | 0.3185 | 4 | 0.6625 | 11.2 | 9.225 | 0.66393 | 6.0275 | 0.38825 | 3.5 | 0.84 | 13.275 | 10.875 | 0.66343 | 0.0225 | 1 | 0.29 | 0.0165 | 0.039667 | 0.013 | 1 | 0.38167 |  | 0.019833 | 1 | 0.555 |  | 7.2167 | 0.051833 | 1 | 4.0833 | 10.5333 | 21.5 | 31.5 | 0.0215 | 7.1467 | 0.052 | 1 | 3.5167 | 12.45 | 22.5 | 32.5 | 0.018 | 4.1833 | 3.8167 | 2.6833 |  |  | MAXIMUM | 6 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 |  | 12.0182 |  | 14.0458 | 24.8616 | 1.5134 | MAXIMUM | 65.0743 | 5226.4286 |  | 650.2203 | [6 empty] | 1.712 | 1.712 | 1.7198 | 0.27382 |  | 0.25621 | 0.25621 | 0.20627 | 0.23181 | 1.4267 | 4 | 0.05975 | 0.05975 | 0.052758 | 1.1079 | 0.55527 | 0.10188 | 4.018 | 0.76945 | 4.3943 | 1.0972 | 0.59061 | 0.11493 | 3.5166 | 0.63766 | 6.4317
MINIMUM | 6.45 | 14 | 14 | 14.7 | 89 | 166 | 12.1 | 0.345 | 0.036 | 6.16 | 7 | 0.05 | 5.95 | 7 |  | 5.92 | 7 |  | 5.97 | 0.327 | 3 | 0.52 | 11.5 | 5.4 | 0.4266 | 0.035 | 6.02 | 0.295 | 3 | 0.64 | 10.6 | 7.4 | 0.55632 | 6 | 0.33 | 3 | 0.75 | 13 | 10.5 | 0.62556 | 0.021 | 1 | 0.16 | 0.013 | 0.036 | 0.009 | 1 | 0.25 |  | 0.018 | 1 | 0.37 |  | 7.06 | 0.047 | 1 | 3.6 | 10.4 | 21 | 31 | 0.014 | 7.03 | 0.048 | 1 | 3.3 | 11.6 | 22 | 30 | 0.012 | 4.1 | 3.8 | 2.3 | [15 empty] | MIL/MIN |  | TOTAL | 21140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 880 | 960 | 2240 | 0 | 1750 | 1750 | 1760 | 1880 | 2250 | 0 | 2700 | 2700 | 2610 | 226 | 304 | 32 | 3940 | 800 | 680 | 128 | 178 | 20 | 1800 | 368 | 585
MAXIMUM | 6.65 | 18 | 18 | 14.9 | 94 | 171 | 12.6 | 0.371 | 0.056 | 6.27 | 10 | 0.069 | 6.17 | 11 |  | 6 | 11 |  | 6.14 | 0.388 | 4 | 0.61 | 12.2 | 6 | 0.47377 | 0.04 | 6.12 | 0.342 | 5 | 0.72 | 11.5 | 10.5 | 0.7391 | 6.11 | 0.427 | 5 | 0.91 | 13.4 | 11.8 | 0.71444 | 0.024 | 1 | 0.45 | 0.02 | 0.043 | 0.016 | 1 | 0.44 |  | 0.021 | 1 | 0.66 |  | 7.34 | 0.056 | 1 | 4.9 | 10.6 | 22 | 32 | 0.029 | 7.26 | 0.057 | 1 | 3.8 | 13 | 23 | 35 | 0.024 | 4.2 | 3.9 | 3 | [17 empty] | AVERAGE | 7046.6667 | [9 empty] | 293.3333 | 293.3333 | 320 | 746.6667 |  | 583.3333 | 583.3333 | 586.6667 | 626.6667 | 750 |  | 900 | 900 | 870 | 75.3333 | 101.3333 | 10.6667 | 1313.3333 | 266.6667 | 226.6667 | 42.6667 | 59.3333 | 6.6667 | 600 | 122.6667 | 195
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0644 |  | TOTAL AVG COAG ALK: |  |  |  | 9.1111 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.427 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.52 | [5 empty] | 6.0492 |  |  |  |  | 0.024 |  |  |  |  | 0.52 | [6 empty] | 0.024 | [16 empty] | Pump Station MIN |  | 2.3 | [17 empty] | MINIMUM | 6900 | [9 empty] | 280 | 280 | 300 | 720 |  | 550 | 550 | 560 | 560 | 750 |  | 880 | 880 | 850 | 72 | 99 | 10 | 1280 | 260 | 215 | 42 | 58 | 6 | 580 | 118 | 190
[90 empty] | MAXIMUM | 7320 | [9 empty] | 300 | 300 | 340 | 760 |  | 640 | 640 | 640 | 680 | 750 |  | 940 | 940 | 880 | 80 | 105 | 11 | 1380 | 280 | 250 | 44 | 60 | 7 | 640 | 130 | 205
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.481 |  | TOTAL MGD: |  | 0.012 |  |  | FINISHED SOUTH 1 |  | START: | 23827220 |  | END: | 23827232 |  |  | Alum | 6299 | 10795 | 10795 | 11104 | 11104 | 0 | [44 empty] | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.09 | 11.3 | 15 | 1.0338
[73 empty] | FINISHED 2 | 12.448 |  | TOTAL MGD: |  | 10.469 |  |  | FINISHED SOUTH 2 |  | START: | 44107135 |  | END: | 44117604 |  |  | Caustic | 6332 | 7956 | 7956
[73 empty] | TOTAL RAW | 26.537 |  | TOTAL MGD: |  | 4.712 |  |  | FINISHED CONWAY |  | START: | 10337712 |  | END: | 10342424 |  |  | Hypochlorite | 12 |  | 36
[76 empty] | TOTAL MGD: |  | 7.736 |  |  | FINISHED PERRY |  | START: | 34029300 |  | END: | 34037036 |  |  | Phosphate | 1692
[76 empty] | TOTAL MGD: |  | 5.846 |  |  | RAW PLANT 1 |  | START: | 31193167 |  | END: | 31199013 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 9.877 |  |  | RAW PLANT 2 |  | START: | 31088224 |  | END: | 31098101 |  |  | Cal~Flo | 15.29 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 10.814 |  |  | RAW PLANT 3 |  | START: | 7752621 |  | END: | 7763435 |  |  | Zinc | 794
[76 empty] | TOTAL MGD: |  | 0.936 |  |  | DECANT |  | START: | 1886937 |  | END: | 1887873 |  |  | Polymer | 31
[76 empty] | TOTAL MGD: |  | 1.2694 |  |  | BLOW DOWN |  | START: | 9169.1396 |  | END: | 9170.409 |  |  | NH3 | 10.36 |  | BI-SUL | 1025
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 650
23827232
44117604
10342424
34037036
31199013
31098101
7763435
1887873
9170.409
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 27
DATE: | 2019-01-27 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 | DATE: |  | 2019-01-27 | [23 empty] | DATE: | 2019-01-27
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-27 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43492.0014 | 2,3,5 | 37 | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 9.9749 | 1,3 | 14.0458 | 24.0206 | 2.2702 | 43492.0014 | 64.8453 | 4796.0168 | 0 | 650.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6089 | 1.5016 | 1.5316 | 0.27382 | 0 | 0.1972 | 0.1972 | 0.20627 | 0.21916 | 1.4267 | 4 | 0.05975 | 0.05975 | 0.049921 | 1.1079 | 0.54791 | 0.095744 | 3.9973 | 0.76945 | 4.3943 | 1.0876 | 0.55886 | 0.10875 | 3.5093 | 0.63766 | 6.4317 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.96 | 0.398 | 4 | 0.78 | 11.9 | 5.4 | 0.39594 |  | 6.02 | 0.435 | 5 | 0.64 | 11.1 | 10.5 | 0.7391 | 6.03 | 0.397 | 3 | 0.66 | 13.1 | 10.6 | 0.70889 | [13 empty] | 7.19 | 0.05 | 1 | 3.7 | 10.6 |  |  |  | 7.1 | 0.053 | 1 | 3.6 | 12.2 |  |  |  | 4.4 | 3.8 | 2.5 | [18 empty] | 7320 | [6 empty] | 0 | 0 | 0 | 300 | 280 | 320 | 720 | 0 | 560 | 560 | 640 | 680 | 750 |  | 940 | 940 | 880 | 80 | 105 | 11 | 1380 | 280 | 250 | 44 | 60 | 7 | 640 | 130 | 205 |  | 1:00 | 0.78 | 5.4 | 47.1111 | 36.7467 | 5.96 | 11.9 | 13 | 2.8267 | 10 | 6 | 0.27594 | 1:00 | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.02 | 11.1 | 15 | 1.0338 | 10 | 6.5 | 0.6191 | 1:00 | 0.66 | 10.6 | 25.4717 | 16.8113 | 6.03 | 13.1 | 15 | 1.1208 | 10 | 6.5 | 0.58889
2:00 | [72 empty] | 43492.3654 | 2,3,5 | 37 | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 9.9749 | 1,3 | 14.0458 | 24.0206 | 2.1499 | 43492.3654 | 64.8453 | 4796.0168 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3407 | 1.6089 | 1.5795 | 0.26622 | 0 | 0.1972 | 0.1972 | 0.20949 | 0.20949 | 1.4267 | 4 | 0.060385 | 0.060385 | 0.049921 | 1.1079 | 0.54791 | 0.10445 | 4.0273 | 0.76945 | 4.3943 | 1.09 | 0.55886 | 0.093217 | 3.5221 | 0.61804 | 6.4317 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.51 | 15 | 17 | 14.7 | 93 | 167 | 12.2 | 0.369 |  | 6.31 | 8 | 0.066 | 5.96 | 7 |  | 5.92 | 9 | [8 empty] | 0.043 | [14 empty] | 0.018 | 1 | 0.24 |  | 0.041 | 0.011 | 1 | 0.23 |  | 0.031 | 1 | 0.53 | [38 empty] | 7320 | [6 empty] | 0 | 0 | 0 | 250 | 300 | 330 | 700 | 0 | 560 | 560 | 650 | 650 | 750 |  | 950 | 950 | 880 | 80 | 105 | 12 | 1380 | 280 | 250 | 44 | 60 | 6 | 610 | 126 | 205 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43492.8126 | 2,3,5 | 38 | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 11.4826 | 1,3 | 12.6562 | 24.1387 | 2.1499 | 43492.8126 | 64.8453 | 4796.0168 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5016 | 1.7161 | 1.6273 | 0.30425 | 0 | 0.22537 | 0.23946 | 0.20627 | 0.21916 | 1.4267 | 4 | 0.05975 | 0.05975 | 0.049921 | 1.1079 | 0.54791 | 0.095744 | 4.0148 | 0.76945 | 4.3943 | 1.1371 | 0.55886 | 0.10875 | 3.4612 | 0.61314 | 6.4317 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.49 | 0.051 | 1 | 4.4 | 10.3 |  |  |  | 7.36 | 0.056 | 1 | 3.8 | 11.7 |  |  |  | 4.2 | 3.9 | 3 | [18 empty] | 7320 | [6 empty] | 0 | 0 | 0 | 280 | 320 | 340 | 800 | 0 | 640 | 680 | 640 | 680 | 750 |  | 940 | 940 | 880 | 80 | 105 | 11 | 1370 | 280 | 250 | 46 | 60 | 7 | 620 | 125 | 205 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.55 | 19 | 18 | 14.7 | 86 | 155 | 11.9 | 0.359 |  | 6.3 | 10 | 0.059 | 5.92 | 10 |  | 5.9 | 10 | [8 empty] | 0.038 | [14 empty] | 0.021 | 1 | 0.29 |  | 0.039 | 0.012 | 1 | 0.36 |  | 0.039 | 1 | 0.49 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.062 | [9 empty] | 6.03 | 0.391 | 4 | 0.64 | 11.4 | 5 | 0.41481 |  | 6.02 | 0.405 | 3 | 0.76 | 10.5 | 10.8 | 0.75679 | 6.03 | 0.461 | 4 | 0.85 | 12.8 | 11.8 | 0.77556 |  |  |  | 0.031 | [9 empty] | 7.85 | 0.067 | 1 | 4.9 | 10.2 | 21 | 37 | 0.051 | 7.47 | 0.054 | 1 | 4.1 | 12.1 | 21 | 40 | 0.032 | 4.3 | 3.9 | 3 | [55 empty] | 9:00 | 0.64 | 5 | 50.88 | 32.5632 | 6.03 | 11.4 | 15 | 2.1709 | 10 | 6.5 | 0.29481 | 9:00 | 0.76 | 10.8 | 23.5556 | 17.9022 | 6.02 | 10.5 | 15 | 1.1935 | 10 | 6.5 | 0.63679 | 9:00 | 0.85 | 11.8 | 22.8814 | 19.4492 | 6.03 | 12.8 | 15 | 1.2966 | 10 | 6.5 | 0.65556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.52 | 20 | 17 | 14.7 | 92 | 168 | 11.9 | 0.369 |  | 6.3 | 10 | 0.058 | 5.96 | 10 |  | 5.91 | 10 | [8 empty] | 0.038 | [14 empty] | 0.029 | 1 | 0.28 |  | 0.04 | 0.012 | 1 | 0.37 |  | 0.031 | 1 | 0.56 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 5.95 | 0.355 | 3 | 0.6 | 12 | 5 | 0.3755 |  | 5.97 | 0.385 | 3 | 0.74 | 11 | 10.8 | 0.67189 | 5.96 | 0.474 | 3 | 0.84 | 13 | 11.8 | 0.68815 | [13 empty] | 7.29 | 0.058 | 1 | 4.4 | 10 |  |  |  | 7.33 | 0.052 | 1 | 4 | 12 |  |  |  | 4.6 | 4 | 2.5 | [55 empty] | 13:00 | 0.6 | 5 | 50.88 | 30.528 | 5.95 | 12 | 13 | 2.3483 | 10 | 6 | 0.2555 | 13:00 | 0.74 | 10.8 | 23.5556 | 17.4311 | 5.97 | 11 | 13 | 1.3409 | 10 | 6 | 0.55189 | 13:00 | 0.84 | 11.8 | 22.8814 | 19.2203 | 5.96 | 13 | 13 | 1.4785 | 10 | 6 | 0.56815
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.6 | 21 | 18 | 14.8 | 88 | 164 | 12.5 | 0.341 |  | 6.28 | 12 | 0.05 | 6.08 | 12 |  | 6 | 12 | [8 empty] | 0.036 | [14 empty] | 0.024 | 1 | 0.3 |  | 0.038 | 0.01 | 1 | 0.35 |  | 0.029 | 1 | 0.5 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.31 | 0.054 | 1 | 4.2 | 10 |  |  |  | 7.18 | 0.054 | 1 | 4.2 | 12 |  |  |  | 4.6 | 4 | 2.6 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.55 | 18 | 17 | 14.5 | 90 | 165 | 12.1 | 0.359 |  | 6.21 | 10 | 0.057 | 5.82 | 9 |  | 5.77 | 9 | [8 empty] | 0.036 | [14 empty] | 0.023 | 1 | 0.28 |  | 0.035 | 0.006 | 1 | 0.22 |  | 0.028 | 1 | 0.42 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 5.92 | 0.4 | 3 | 0.6 | 11.5 | 5.4 | 0.39594 |  | 5.88 | 0.444 | 4 | 0.62 | 10.8 | 10.5 | 0.65656 | 5.99 | 0.458 | 3 | 0.65 | 13.8 | 11.5 | 0.6737 |  |  |  | 0.017 | [9 empty] | 7.28 | 0.046 | 1 | 4.3 | 10.1 | 22 | 34 | 0.017 | 7.14 | 0.047 | 1 | 3.6 | 11.1 | 23 | 35 | 0.015 | 4.7 | 3.9 | 2.8 | [55 empty] | 21:00 | 0.6 | 5.4 | 47.1111 | 28.2667 | 5.92 | 11.5 | 13 | 2.1744 | 10 | 6 | 0.27594 | 21:00 | 0.62 | 10.5 | 24.2286 | 15.0217 | 5.88 | 10.8 | 13 | 1.1555 | 10 | 6 | 0.53656 | 21:00 | 0.65 | 11.5 | 23.4783 | 15.2609 | 5.99 | 13.8 | 13 | 1.1739 | 10 | 6 | 0.5537
22:00 | [72 empty] | DOSE |  | TOTAL | 15 | 32.4 | 35.4 | 82.8 | 24.9 | 24.9 | 27.9 | 77.7 | 0 | 31.4323 | 0 | 40.7477 | 72.18 | 6.57 | TOTAL | 194.536 | 14388.0504 | 0 | 2045.815 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4513 | 4.8267 | 4.7384 | 0.84429 | 0 | 0.61977 | 0.63385 | 0.62204 | 0.64782 | 4.2801 | 12 | 0.17989 | 0.17989 | 0.14976 | 3.3236 | 1.6437 | 0.29594 | 12.0394 | 2.3084 | 13.1829 | 3.3147 | 1.6766 | 0.31072 | 10.4925 | 1.8688 | 19.2952 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.54 | 16 | 16 | 14.4 | 85 | 163 | 12.1 | 0.35 |  | 6.22 | 11 | 0.052 | 5.95 | 10 |  | 5.86 | 10 | [8 empty] | 0.042 | [14 empty] | 0.023 | 1 | 0.31 |  | 0.039 | 0.007 | 1 | 0.29 |  | 0.025 | 1 | 0.45 | [22 empty] | AVERAGE | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 |  | 10.4774 |  | 13.5826 | 24.06 | 2.19 | AVERAGE | 64.8453 | 4796.0168 |  | 681.9383 | 0 | 0 | 0 |  |  |  | 1.4838 | 1.6089 | 1.5795 | 0.28143 |  | 0.20659 | 0.21128 | 0.20735 | 0.21594 | 1.4267 | 4 | 0.059962 | 0.059962 | 0.049921 | 1.1079 | 0.54791 | 0.098646 | 4.0131 | 0.76945 | 4.3943 | 1.1049 | 0.55886 | 0.10357 | 3.4975 | 0.62295 | 6.4317 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.27 | 109 | 103 | 87.8 | 534 | 982 | 72.7 | 2.147 | 0.105 | 37.62 | 61 | 0.342 | 35.69 | 58 | 0 | 35.36 | 60 | 0 | 23.86 | 1.544 | 14 | 2.62 | 46.8 | 20.8 | 1.5822 | 0.233 | 23.89 | 1.669 | 15 | 2.76 | 43.4 | 42.6 | 2.8243 | 24.01 | 1.79 | 13 | 3 | 52.7 | 45.7 | 2.8463 | 0.138 | 6 | 1.7 | 0.048 | 0.232 | 0.058 | 6 | 1.82 | 0 | 0.183 | 6 | 2.95 | 0 | 44.41 | 0.326 | 6 | 25.9 | 61.2 | 43 | 71 | 0.068 | 43.58 | 0.316 | 6 | 23.3 | 71.1 | 44 | 75 | 0.047 | 26.8 | 23.5 | 16.4 |  |  | MINIMUM | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 |  | 9.9749 |  | 12.6562 | 24.0206 | 2.1499 | MINIMUM | 64.8453 | 4796.0168 |  | 650.2203 | [6 empty] | 1.3407 | 1.5016 | 1.5316 | 0.26622 |  | 0.1972 | 0.1972 | 0.20627 | 0.20949 | 1.4267 | 4 | 0.05975 | 0.05975 | 0.049921 | 1.1079 | 0.54791 | 0.095744 | 3.9973 | 0.76945 | 4.3943 | 1.0876 | 0.55886 | 0.093217 | 3.4612 | 0.61314 | 6.4317 |  | MIN | 0.64 | 5 | 50.88 | 32.5632 | 6.03 | 11.4 | 15 | 2.1709 |  |  |  | MIN | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.02 | 11.1 | 15 | 1.0338 |  |  |  | MIN | 0.66 | 10.6 | 25.4717 | 16.8113 | 6.03 | 13.1 | 15 | 1.1208 |  |  |  | 1.0338
AVERAGE | 6.545 | 18.1667 | 17.1667 | 14.6333 | 89 | 163.6667 | 12.1167 | 0.35783 | 0.0525 | 6.27 | 10.1667 | 0.057 | 5.9483 | 9.6667 |  | 5.8933 | 10 |  | 5.965 | 0.386 | 3.5 | 0.655 | 11.7 | 5.2 | 0.39555 | 0.038833 | 5.9725 | 0.41725 | 3.75 | 0.69 | 10.85 | 10.65 | 0.70608 | 6.0025 | 0.4475 | 3.25 | 0.75 | 13.175 | 11.425 | 0.71157 | 0.023 | 1 | 0.28333 | 0.024 | 0.038667 | 0.0096667 | 1 | 0.30333 |  | 0.0305 | 1 | 0.49167 |  | 7.4017 | 0.054333 | 1 | 4.3167 | 10.2 | 21.5 | 35.5 | 0.034 | 7.2633 | 0.052667 | 1 | 3.8833 | 11.85 | 22 | 37.5 | 0.0235 | 4.4667 | 3.9167 | 2.7333 |  |  | MAXIMUM | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 |  | 11.4826 |  | 14.0458 | 24.1387 | 2.2702 | MAXIMUM | 64.8453 | 4796.0168 |  | 697.7974 | [6 empty] | 1.6089 | 1.7161 | 1.6273 | 0.30425 |  | 0.22537 | 0.23946 | 0.20949 | 0.21916 | 1.4267 | 4 | 0.060385 | 0.060385 | 0.049921 | 1.1079 | 0.54791 | 0.10445 | 4.0273 | 0.76945 | 4.3943 | 1.1371 | 0.55886 | 0.10875 | 3.5221 | 0.63766 | 6.4317
MINIMUM | 6.51 | 15 | 16 | 14.4 | 85 | 155 | 11.9 | 0.341 | 0.043 | 6.21 | 8 | 0.05 | 5.82 | 7 |  | 5.77 | 9 |  | 5.92 | 0.355 | 3 | 0.6 | 11.4 | 5 | 0.3755 | 0.036 | 5.88 | 0.385 | 3 | 0.62 | 10.5 | 10.5 | 0.65656 | 5.96 | 0.397 | 3 | 0.65 | 12.8 | 10.6 | 0.6737 | 0.018 | 1 | 0.24 | 0.017 | 0.035 | 0.006 | 1 | 0.22 |  | 0.025 | 1 | 0.42 |  | 7.19 | 0.046 | 1 | 3.7 | 10 | 21 | 34 | 0.017 | 7.1 | 0.047 | 1 | 3.6 | 11.1 | 21 | 35 | 0.015 | 4.2 | 3.8 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 21960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 900 | 990 | 2220 | 0 | 1760 | 1800 | 1930 | 2010 | 2250 | 0 | 2830 | 2830 | 2640 | 240 | 315 | 34 | 4130 | 840 | 750 | 134 | 180 | 20 | 1870 | 381 | 615
MAXIMUM | 6.6 | 21 | 18 | 14.8 | 93 | 168 | 12.5 | 0.369 | 0.062 | 6.31 | 12 | 0.066 | 6.08 | 12 |  | 6 | 12 |  | 6.03 | 0.4 | 4 | 0.78 | 12 | 5.4 | 0.41481 | 0.043 | 6.02 | 0.444 | 5 | 0.76 | 11.1 | 10.8 | 0.75679 | 6.03 | 0.474 | 4 | 0.85 | 13.8 | 11.8 | 0.77556 | 0.029 | 1 | 0.31 | 0.031 | 0.041 | 0.012 | 1 | 0.37 |  | 0.039 | 1 | 0.56 |  | 7.85 | 0.067 | 1 | 4.9 | 10.6 | 22 | 37 | 0.051 | 7.47 | 0.056 | 1 | 4.2 | 12.2 | 23 | 40 | 0.032 | 4.7 | 4 | 3 | [17 empty] | AVERAGE | 7320 | [9 empty] | 276.6667 | 300 | 330 | 740 |  | 586.6667 | 600 | 643.3333 | 670 | 750 |  | 943.3333 | 943.3333 | 880 | 80 | 105 | 11.3333 | 1376.6667 | 280 | 250 | 44.6667 | 60 | 6.6667 | 623.3333 | 127 | 205
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0372 |  | TOTAL AVG COAG ALK: |  |  |  | 9.9444 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.474 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.6 | [5 empty] | 5.98 |  |  |  |  | 0.039 |  |  |  |  | 0.6 | [6 empty] | 0.039 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 7320 | [9 empty] | 250 | 280 | 320 | 700 |  | 560 | 560 | 640 | 650 | 750 |  | 940 | 940 | 880 | 80 | 105 | 11 | 1370 | 280 | 250 | 44 | 60 | 6 | 610 | 125 | 205
[90 empty] | MAXIMUM | 7320 | [9 empty] | 300 | 320 | 340 | 800 |  | 640 | 680 | 650 | 680 | 750 |  | 950 | 950 | 880 | 80 | 105 | 12 | 1380 | 280 | 250 | 46 | 60 | 7 | 640 | 130 | 205
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.995 |  | TOTAL MGD: |  | 0.012 |  |  | FINISHED SOUTH 1 |  | START: | 23827232 |  | END: | 23827244 |  |  | Alum | 3623 | 10789 | 10789 | 11104 | 11104 | 0 | [44 empty] | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.02 | 11.1 | 15 | 1.0338
[73 empty] | FINISHED 2 | 12.85 |  | TOTAL MGD: |  | 10.983 |  |  | FINISHED SOUTH 2 |  | START: | 44117604 |  | END: | 44128587 |  |  | Caustic | 6242 | 7911 | 7911
[73 empty] | TOTAL RAW | 27.214 |  | TOTAL MGD: |  | 4.716 |  |  | FINISHED CONWAY |  | START: | 10342424 |  | END: | 10347140 |  |  | Hypochlorite | 12 |  | 33
[76 empty] | TOTAL MGD: |  | 8.134 |  |  | FINISHED PERRY |  | START: | 34037036 |  | END: | 34045170 |  |  | Phosphate | 1613
[76 empty] | TOTAL MGD: |  | 5.266 |  |  | RAW PLANT 1 |  | START: | 31199013 |  | END: | 31204279 |  |  | Fluoride | 2750 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.396 |  |  | RAW PLANT 2 |  | START: | 31098101 |  | END: | 31108497 |  |  | Cal~Flo | 13.3 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.552 |  |  | RAW PLANT 3 |  | START: | 7763435 |  | END: | 7774987 |  |  | Zinc | 793
[76 empty] | TOTAL MGD: |  | 1.03 |  |  | DECANT |  | START: | 1887873 |  | END: | 1888903 |  |  | Polymer | 31
[76 empty] | TOTAL MGD: |  | 1.179 |  |  | BLOW DOWN |  | START: | 9170.409 |  | END: | 9171.588 |  |  | NH3 | 10 |  | BI-SUL | 1025
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 698
23827244
44128587
10347140
34045170
31204279
31108497
7774987
1888903
9171.588
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 28
DATE: | 2019-01-28 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW | 14 | RH | 17 | [20 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE | 16 | JM | 18 |  | DATE: | 2019-01-28 | [23 empty] | DATE: | 2019-01-28
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-28 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43493.0059 | 2,3,5 | 38 | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 11.4826 | 1,3 | 12.6562 | 24.1387 | 1.6134 | 43493.0059 | 64.8453 | 4796.0168 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5016 | 1.7161 | 1.6273 | 0.30425 | 0 | 0.22537 | 0.23946 | 0.20627 | 0.21916 | 1.4267 | 4 | 0.05975 | 0.05975 | 0.049921 | 1.1079 | 0.54791 | 0.095744 | 4.0148 | 0.76945 | 4.3943 | 1.1371 | 0.55886 | 0.10875 | 3.4612 | 0.61314 | 6.4317 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 5.92 | 0.403 | 3 | 0.5 | 11.5 | 5.4 | 0.39594 |  | 6.02 | 0.444 | 4 | 0.68 | 10.9 | 10.5 | 0.7391 | 6.03 | 0.421 | 3 | 0.66 | 12.7 | 11.5 | 0.75889 | [13 empty] | 7.3 | 0.049 | 1 | 4.2 | 10.1 |  |  |  | 7.1 | 0.051 | 1 | 3.6 | 12.1 |  |  |  | 4.7 | 4 | 3.1 | [18 empty] | 7320 | [6 empty] | 0 | 0 | 0 | 280 | 320 | 340 | 800 | 0 | 640 | 680 | 640 | 680 | 750 |  | 940 | 940 | 880 | 80 | 105 | 11 | 1370 | 280 | 250 | 46 | 60 | 7 | 620 | 125 | 205 |  | 1:00 | 0.5 | 5.4 | 47.1111 | 23.5556 | 5.92 | 11.5 | 13 | 1.812 | 10 | 6 | 0.27594 | 1:00 | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.02 | 10.9 | 15 | 1.0984 | 10 | 6.5 | 0.6191 | 1:00 | 0.66 | 11.5 | 23.4783 | 15.4957 | 6.03 | 12.7 | 15 | 1.033 | 10 | 6.5 | 0.63889
2:00 | [72 empty] | 43493.3448 | 2,3,5 | 38 | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 11.4826 | 1,3 | 12.6562 | 24.1387 | 1.8101 | 43493.3448 | 64.8453 | 4857.5042 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6089 | 1.7161 | 1.6752 | 0.27382 | 0 | 0.21128 | 0.21128 | 0.20949 | 0.20949 | 1.4267 | 5 | 0.05975 | 0.05975 | 0.049921 | 1.1079 | 0.5427 | 0.10445 | 4.0173 | 0.75846 | 4.3943 | 1.1371 | 0.55886 | 0.093217 | 3.4912 | 0.62785 | 6.5886 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.56 | 15 | 16 | 14.4 | 90 | 165 | 11.9 | 0.358 |  | 6.24 | 9 | 0.056 | 5.92 | 8 |  | 5.91 | 8 | [8 empty] | 0.037 | [14 empty] | 0.023 | 1.31 | 0.31 |  | 0.035 | 0.01 | 1 | 0.25 |  | 0.023 | 1 | 0.45 | [38 empty] | 7320 | [6 empty] | 0 | 0 | 0 | 300 | 320 | 350 | 720 | 0 | 600 | 600 | 650 | 650 | 750 |  | 940 | 940 | 880 | 80 | 104 | 12 | 1360 | 276 | 250 | 46 | 60 | 6 | 620 | 128 | 210 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43493.8505 | 2,3,5 | 36 | 5 | 9.8 | 10.8 | 25.6 | 7.7 | 7.7 | 8.8 | 24.2 | ,1,3 | 10.597 | 1,3 | 14.2358 | 24.8328 | 1.8101 | 43493.8505 | 65.136 | 5287.916 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0811 | 1.6186 | 1.821 | 0.25861 | 0 | 0.26389 | 0.23284 | 0.21128 | 0.23946 | 1.4267 | 1 | 0.060295 | 0.060295 | 0.05036 | 1.0748 | 0.55124 | 0.1032 | 3.9788 | 0.74054 | 3.8841 | 1.0972 | 0.54139 | 0.098514 | 3.4666 | 0.62206 | 6.2998 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.47 | 0.047 | 1 | 4.5 | 10.1 |  |  |  | 7.18 | 0.05 | 1 | 3.9 | 12.1 |  |  |  | 4.6 | 4 | 3.3 | [18 empty] | 6820 | [6 empty] | 0 | 0 | 0 | 360 | 280 | 360 | 680 | 0 | 680 | 600 | 600 | 680 | 750 |  | 880 | 880 | 840 | 72 | 98 | 11 | 1220 | 250 | 205 | 42 | 55 | 6 | 580 | 120 | 190 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [127 empty] | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.57 | 15 | 16 | 14.9 | 84 | 166 | 11.7 | 0.352 |  | 6.24 | 9 | 0.059 | 5.92 | 9 |  | 5.9 | 8 | [8 empty] | 0.038 | [14 empty] | 0.021 | 1 | 0.29 |  | 0.041 | 0.01 | 1 | 0.41 |  | 0.021 | 1 | 0.68 | [75 empty] | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.063 | [9 empty] | 6.03 | 0.303 | 3 | 0.55 | 12.1 | 5 | 0.41481 |  | 6.07 | 0.347 | 3 | 0.72 | 10.4 | 10.5 | 0.7391 | 6.08 | 0.409 | 3 | 0.9 | 12.6 | 11.5 | 0.75889 |  |  |  | 0.039 | [9 empty] | 7.3 | 0.052 | 1 | 4.7 | 10.6 | 24 | 50 | 0.049 | 7.1 | 0.062 | 2 | 4 | 11.7 | 22 | 45 | 0.039 | 4.5 | 3.9 | 3 | [55 empty] | 9:00 | 0.55 | 5 | 50.88 | 27.984 | 6.03 | 12.1 | 15 | 1.8656 | 10 | 6.5 | 0.29481 | 9:00 | 0.72 | 10.5 | 24.2286 | 17.4446 | 6.07 | 10.4 | 15 | 1.163 | 10 | 6.5 | 0.6191 | 9:00 | 0.9 | 11.5 | 23.4783 | 21.1304 | 6.08 | 12.6 | 15 | 1.4087 | 10 | 6.5 | 0.63889
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.52 | 20 | 17 | 14.7 | 91 | 165 | 11.7 | 0.371 |  | 6.04 | 9 | 0.06 | 6.02 | 9 |  | 5.97 | 9 | [8 empty] | 0.039 | [14 empty] | 0.02 | 1 | 0.31 |  | 0.04 | 0.009 | 1 | 0.39 |  | 0.021 | 1 | 0.65 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.11 | 0.275 | 3 | 0.52 | 13 | 5 | 0.41481 |  | 6.1 | 0.305 | 3 | 0.74 | 11 | 10.5 | 0.7391 | 6.09 | 0.39 | 3 | 0.85 | 13 | 11.5 | 0.75889 | [13 empty] | 7.59 | 0.05 | 1 | 4.4 | 10 |  |  |  | 7.27 | 0.058 | 2 | 4 | 12.5 |  |  |  | 4.6 | 3.8 | 2.6 | [55 empty] | 13:00 | 0.52 | 5 | 50.88 | 26.4576 | 6.11 | 13 | 15 | 1.7638 | 10 | 6.5 | 0.29481 | 13:00 | 0.74 | 10.5 | 24.2286 | 17.9291 | 6.1 | 11 | 15 | 1.1953 | 10 | 6.5 | 0.6191 | 13:00 | 0.85 | 11.5 | 23.4783 | 19.9565 | 6.09 | 13 | 15 | 1.3304 | 10 | 6.5 | 0.63889
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.62 | 22 | 18 | 14.4 | 86 | 164 | 12.2 | 0.34 |  | 6.01 | 10 | 0.054 | 6.05 | 10 |  | 6 | 10 | [8 empty] | 0.039 | [14 empty] | 0.023 | 1 | 0.32 |  | 0.039 | 0.01 | 1 | 0.35 |  | 0.021 | 1 | 0.64 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.45 | 0.048 | 1 | 4.3 | 10 |  |  |  | 7.22 | 0.055 | 1 | 4 | 12.5 |  |  |  | 4.6 | 3.8 | 2.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.61 | 16 | 19 | 14.4 | 93 | 163 | 12.1 | 0.36 |  | 6.11 | 9 | 0.055 | 6.04 | 9 |  | 6.01 | 10 | [8 empty] | 0.037 | [14 empty] | 0.016 | 1 | 0.35 |  | 0.039 | 0.009 | 1 | 0.38 |  | 0.02 | 1 | 0.46 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.034 | [9 empty] | 6.06 | 0.327 | 3 | 0.7 | 11.5 | 5.1 | 0.42071 |  | 6.08 | 0.337 | 4 | 0.69 | 10.7 | 9.9 | 0.70373 | 6.07 | 0.326 | 4 | 0.75 | 12.6 | 11 | 0.73111 |  |  |  | 0.013 | [9 empty] | 7.34 | 0.051 | 1 | 4.6 | 10.1 | 21 | 38 | 0.012 | 7.24 | 0.049 | 1 | 4.3 | 11.7 | 22 | 40 | 0.012 | 4.8 | 3.9 | 2.6 | [55 empty] | 21:00 | 0.7 | 5.1 | 49.8824 | 34.9176 | 6.06 | 11.5 | 15 | 2.3278 | 10 | 6.5 | 0.30071 | 21:00 | 0.69 | 9.9 | 25.697 | 17.7309 | 6.08 | 10.7 | 15 | 1.1821 | 10 | 6.5 | 0.58373 | 21:00 | 0.75 | 11 | 24.5455 | 18.4091 | 6.07 | 12.6 | 15 | 1.2273 | 10 | 6.5 | 0.61111
22:00 | [72 empty] | DOSE |  | TOTAL | 15 | 31.4 | 34.4 | 80.8 | 24.3 | 24.3 | 27.4 | 76 | 0 | 33.5621 | 0 | 39.5482 | 73.1102 | 5.2335 | TOTAL | 194.8267 | 14941.437 | 0 | 2093.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1916 | 5.0509 | 5.1235 | 0.83669 | 0 | 0.70055 | 0.68359 | 0.62705 | 0.66811 | 4.2801 | 10 | 0.17979 | 0.17979 | 0.1502 | 3.2905 | 1.6418 | 0.3034 | 12.011 | 2.2685 | 12.6727 | 3.3713 | 1.6591 | 0.30048 | 10.4189 | 1.863 | 19.3202 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.53 | 18 | 18 | 14.3 | 88 | 162 | 12.4 | 0.35 |  | 6.03 | 8 | 0.048 | 5.98 | 9 |  | 5.96 | 9 | [8 empty] | 0.038 | [14 empty] | 0.017 | 1 | 0.4 |  | 0.041 | 0.01 | 1 | 0.45 |  | 0.019 | 1 | 0.52 | [22 empty] | AVERAGE | 5 | 10.4667 | 11.4667 | 26.9333 | 8.1 | 8.1 | 9.1333 | 25.3333 |  | 11.1874 |  | 13.1827 | 24.3701 | 1.7445 | AVERAGE | 64.9422 | 4980.479 |  | 697.7974 | 0 | 0 | 0 |  |  |  | 1.7305 | 1.6836 | 1.7078 | 0.2789 |  | 0.23352 | 0.22786 | 0.20902 | 0.2227 | 1.4267 | 3.3333 | 0.059931 | 0.059931 | 0.050067 | 1.0968 | 0.54728 | 0.10113 | 4.0037 | 0.75615 | 4.2242 | 1.1238 | 0.55303 | 0.10016 | 3.473 | 0.62102 | 6.4401 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.41 | 106 | 104 | 87.1 | 532 | 985 | 72 | 2.131 | 0.097 | 36.67 | 54 | 0.332 | 35.93 | 54 | 0 | 35.75 | 54 | 0 | 24.12 | 1.308 | 12 | 2.27 | 48.1 | 20.5 | 1.6463 | 0.228 | 24.27 | 1.433 | 14 | 2.83 | 43 | 41.4 | 2.921 | 24.27 | 1.546 | 13 | 3.16 | 50.9 | 45.5 | 3.0078 | 0.12 | 6.31 | 1.98 | 0.052 | 0.235 | 0.058 | 6 | 2.23 | 0 | 0.125 | 6 | 3.4 | 0 | 44.45 | 0.297 | 6 | 26.7 | 60.9 | 45 | 88 | 0.061 | 43.11 | 0.325 | 8 | 23.8 | 72.6 | 44 | 85 | 0.051 | 27.8 | 23.4 | 17.1 |  |  | MINIMUM | 5 | 9.8 | 10.8 | 25.6 | 7.7 | 7.7 | 8.8 | 24.2 |  | 10.597 |  | 12.6562 | 24.1387 | 1.6134 | MINIMUM | 64.8453 | 4796.0168 |  | 697.7974 | [6 empty] | 1.5016 | 1.6186 | 1.6273 | 0.25861 |  | 0.21128 | 0.21128 | 0.20627 | 0.20949 | 1.4267 | 1 | 0.05975 | 0.05975 | 0.049921 | 1.0748 | 0.5427 | 0.095744 | 3.9788 | 0.74054 | 3.8841 | 1.0972 | 0.54139 | 0.093217 | 3.4612 | 0.61314 | 6.2998 |  | MIN | 0.52 | 5 | 50.88 | 26.4576 | 6.11 | 13 | 15 | 1.7638 |  |  |  | MIN | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.02 | 10.9 | 15 | 1.0984 |  |  |  | MIN | 0.66 | 11.5 | 23.4783 | 15.4957 | 6.03 | 12.7 | 15 | 1.033 |  |  |  | 1.033
AVERAGE | 6.5683 | 17.6667 | 17.3333 | 14.5167 | 88.6667 | 164.1667 | 12 | 0.35517 | 0.0485 | 6.1117 | 9 | 0.055333 | 5.9883 | 9 |  | 5.9583 | 9 |  | 6.03 | 0.327 | 3 | 0.5675 | 12.025 | 5.125 | 0.41157 | 0.038 | 6.0675 | 0.35825 | 3.5 | 0.7075 | 10.75 | 10.35 | 0.73026 | 6.0675 | 0.3865 | 3.25 | 0.79 | 12.725 | 11.375 | 0.75194 | 0.02 | 1.0517 | 0.33 | 0.026 | 0.039167 | 0.0096667 | 1 | 0.37167 |  | 0.020833 | 1 | 0.56667 |  | 7.4083 | 0.0495 | 1 | 4.45 | 10.15 | 22.5 | 44 | 0.0305 | 7.185 | 0.054167 | 1.3333 | 3.9667 | 12.1 | 22 | 42.5 | 0.0255 | 4.6333 | 3.9 | 2.85 |  |  | MAXIMUM | 5 | 10.8 | 11.8 | 27.6 | 8.3 | 8.3 | 9.3 | 25.9 |  | 11.4826 |  | 14.2358 | 24.8328 | 1.8101 | MAXIMUM | 65.136 | 5287.916 |  | 697.7974 | [6 empty] | 2.0811 | 1.7161 | 1.821 | 0.30425 |  | 0.26389 | 0.23946 | 0.21128 | 0.23946 | 1.4267 | 5 | 0.060295 | 0.060295 | 0.05036 | 1.1079 | 0.55124 | 0.10445 | 4.0173 | 0.76945 | 4.3943 | 1.1371 | 0.55886 | 0.10875 | 3.4912 | 0.62785 | 6.5886
MINIMUM | 6.52 | 15 | 16 | 14.3 | 84 | 162 | 11.7 | 0.34 | 0.034 | 6.01 | 8 | 0.048 | 5.92 | 8 |  | 5.9 | 8 |  | 5.92 | 0.275 | 3 | 0.5 | 11.5 | 5 | 0.39594 | 0.037 | 6.02 | 0.305 | 3 | 0.68 | 10.4 | 9.9 | 0.70373 | 6.03 | 0.326 | 3 | 0.66 | 12.6 | 11 | 0.73111 | 0.016 | 1 | 0.29 | 0.013 | 0.035 | 0.009 | 1 | 0.25 |  | 0.019 | 1 | 0.45 |  | 7.3 | 0.047 | 1 | 4.2 | 10 | 21 | 38 | 0.012 | 7.1 | 0.049 | 1 | 3.6 | 11.7 | 22 | 40 | 0.012 | 4.5 | 3.8 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 21460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 920 | 1050 | 2200 | 0 | 1920 | 1880 | 1890 | 2010 | 2250 | 0 | 2760 | 2760 | 2600 | 232 | 307 | 34 | 3950 | 806 | 705 | 134 | 175 | 19 | 1820 | 373 | 605
MAXIMUM | 6.62 | 22 | 19 | 14.9 | 93 | 166 | 12.4 | 0.371 | 0.063 | 6.24 | 10 | 0.06 | 6.05 | 10 |  | 6.01 | 10 |  | 6.11 | 0.403 | 3 | 0.7 | 13 | 5.4 | 0.42071 | 0.039 | 6.1 | 0.444 | 4 | 0.74 | 11 | 10.5 | 0.7391 | 6.09 | 0.421 | 4 | 0.9 | 13 | 11.5 | 0.75889 | 0.023 | 1.31 | 0.4 | 0.039 | 0.041 | 0.01 | 1 | 0.45 |  | 0.023 | 1 | 0.68 |  | 7.59 | 0.052 | 1 | 4.7 | 10.6 | 24 | 50 | 0.049 | 7.27 | 0.062 | 2 | 4.3 | 12.5 | 22 | 45 | 0.039 | 4.8 | 4 | 3.3 | [17 empty] | AVERAGE | 7153.3333 | [9 empty] | 313.3333 | 306.6667 | 350 | 733.3333 |  | 640 | 626.6667 | 630 | 670 | 750 |  | 920 | 920 | 866.6667 | 77.3333 | 102.3333 | 11.3333 | 1316.6667 | 268.6667 | 235 | 44.6667 | 58.3333 | 6.3333 | 606.6667 | 124.3333 | 201.6667
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0194 |  | TOTAL AVG COAG ALK: |  |  |  | 9 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.444 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.5 | [5 empty] | 6.055 |  |  |  |  | 0.023 |  |  |  |  | 0.5 | [6 empty] | 0.023 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 6820 | [9 empty] | 280 | 280 | 340 | 680 |  | 600 | 600 | 600 | 650 | 750 |  | 880 | 880 | 840 | 72 | 98 | 11 | 1220 | 250 | 205 | 42 | 55 | 6 | 580 | 120 | 190
[90 empty] | MAXIMUM | 7320 | [9 empty] | 360 | 320 | 360 | 800 |  | 680 | 680 | 650 | 680 | 750 |  | 940 | 940 | 880 | 80 | 105 | 12 | 1370 | 280 | 250 | 46 | 60 | 7 | 620 | 128 | 210
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 11.145 |  | TOTAL MGD: |  | 0.011 |  |  | FINISHED SOUTH 1 |  | START: | 23827244 |  | END: | 23827255 |  |  | Alum | 5524 | 10792 | 10792 | 11104 | 11104 | 0 | [44 empty] | 0.66 | 11.5 | 23.4783 | 15.4957 | 6.03 | 12.7 | 15 | 1.033
[73 empty] | FINISHED 2 | 12.948 |  | TOTAL MGD: |  | 11.134 |  |  | FINISHED SOUTH 2 |  | START: | 44128587 |  | END: | 44139721 |  |  | Caustic | 6145 | 7906 | 7906
[73 empty] | TOTAL RAW | 27.708 |  | TOTAL MGD: |  | 4.206 |  |  | FINISHED CONWAY |  | START: | 10347140 |  | END: | 10351346 |  |  | Hypochlorite | 11 |  | 31
[76 empty] | TOTAL MGD: |  | 8.742 |  |  | FINISHED PERRY |  | START: | 34045170 |  | END: | 34053912 |  |  | Phosphate | 1550
[76 empty] | TOTAL MGD: |  | 5.383 |  |  | RAW PLANT 1 |  | START: | 31204279 |  | END: | 31209662 |  |  | Fluoride | 2250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.565 |  |  | RAW PLANT 2 |  | START: | 31108497 |  | END: | 31119062 |  |  | Cal~Flo | 11.25 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.76 |  |  | RAW PLANT 3 |  | START: | 7774987 |  | END: | 7786747 |  |  | Zinc | 785
[76 empty] | TOTAL MGD: |  | 0.742 |  |  | DECANT |  | START: | 1888903 |  | END: | 1889645 |  |  | Polymer | 31
[76 empty] | TOTAL MGD: |  | 0.82915 |  |  | BLOW DOWN |  | START: | 9171.588 |  | END: | 9172.4171 |  |  | NH3 | 9.94 |  | BI-SUL | 1025
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 698
23827255
44139721
10351346
34053912
31209662
31119062
7786747
1889645
9172.4171
Note on AP36: MAX OF ALL 3 PLANTS
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 29
DATE: | 2019-01-29 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 4 |  | 5 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 20 |  | 16 | [23 empty] | 6:00 - 18:00 |  | 4 |  | 5 | [37 empty] | 6:00 - 18:00 |  | 4 |  | 5
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 20 |  | 16 | [37 empty] | 18:00 - 6:00 |  | 20 |  | 16
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2019-01-29 | [23 empty] | DATE: | 2019-01-29
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-29 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43494.0032 | 2,3,5 | 36 | 5 | 9.8 | 10.8 | 25.6 | 7.7 | 7.7 | 8.8 | 24.2 | ,1,3 | 10.597 | 1,3 | 14.2358 | 24.8328 | 1.5993 | 43494.0032 | 65.136 | 5287.916 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0811 | 1.6186 | 1.821 | 0.25861 | 0 | 0.26389 | 0.23284 | 0.21128 | 0.23946 | 1.4267 | 1 | 0.060295 | 0.060295 | 0.05036 | 1.0748 | 0.55124 | 0.1032 | 3.9788 | 0.74054 | 3.8841 | 1.0972 | 0.54139 | 0.098514 | 3.4666 | 0.62206 | 6.2998 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.03 | 0.325 | 3 | 0.61 | 11.4 | 5.1 | 0.42071 |  | 6.06 | 0.337 | 3 | 0.75 | 10.9 | 10.1 | 0.71552 | 6.07 | 0.332 | 4 | 0.85 | 12.8 | 11 | 0.73111 | [13 empty] | 7.34 | 0.05 | 1 | 4.5 | 10.1 |  |  |  | 7.15 | 0.048 | 1 | 4.1 | 11.9 |  |  |  | 4.6 | 3.9 | 2.7 | [18 empty] | 6820 | [6 empty] | 0 | 0 | 0 | 360 | 280 | 360 | 680 | 0 | 680 | 600 | 600 | 680 | 750 |  | 880 | 880 | 840 | 72 | 98 | 11 | 1220 | 250 | 205 | 42 | 55 | 6 | 580 | 120 | 190 |  | 1:00 | 0.61 | 5.1 | 49.8824 | 30.4282 | 6.03 | 11.4 | 15 | 2.0285 | 10 | 6.5 | 0.30071 | 1:00 | 0.75 | 10.1 | 25.1881 | 18.8911 | 6.06 | 10.9 | 15 | 1.2594 | 10 | 6.5 | 0.59552 | 1:00 | 0.85 | 11 | 24.5455 | 20.8636 | 6.07 | 12.8 | 15 | 1.3909 | 10 | 6.5 | 0.61111
2:00 | [72 empty] | 43494.3418 | 2,3,5 | 36 | 5 | 9.8 | 10.8 | 25.6 | 7.7 | 7.7 | 8.8 | 24.2 | ,1,3 | 10.597 | 1,3 | 14.2358 | 24.8328 | 1.512 | 43494.3418 | 64.6585 | 5041.9664 | 0 | 634.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8499 | 1.8499 | 1.7704 | 0.50962 | 0.25861 | 0.21344 | 0.21344 | 0.21128 | 0.21128 | 1.4267 | 1 | 0.060295 | 0.060295 | 0.050959 | 1.0748 | 0.55124 | 0.093823 | 3.8846 | 0.75239 | 3.8841 | 1.0972 | 0.55124 | 0.098514 | 3.4566 | 0.62206 | 6.2998 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.58 | 15 | 16 | 14.5 | 87 | 163 | 12.4 | 0.357 |  | 6.01 | 9 | 0.06 | 6.09 | 9 |  | 5.99 | 8 | [8 empty] | 0.042 | [14 empty] | 0.021 | 1 | 0.3 |  | 0.04 | 0.006 | 1 | 0.36 |  | 0.019 | 2 | 0.45 | [38 empty] | 6770 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 350 | 670 | 340 | 550 | 550 | 600 | 600 | 750 |  | 880 | 880 | 850 | 72 | 98 | 10 | 1200 | 254 | 205 | 42 | 56 | 6 | 580 | 120 | 190 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43494.5636 | 2,3,5 | 36 | 5.8 | 10.3 | 11.4 | 27.5 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 10.597 | 1,3 | 14.2358 | 24.8328 | 1.512 | 43494.5636 | 65.2589 | 5164.9412 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7161 | 1.7161 | 1.6752 | 0.459 | 0.24589 | 0.22154 | 0.22154 | 0.20016 | 0.20016 | 1.4267 | 0 | 0.05975 | 0.05975 | 0.051056 | 1.1079 | 0.54791 | 0.10445 | 3.9024 | 0.75571 | 3.867 | 1.1123 | 0.55886 | 0.077681 | 3.4912 | 0.62295 | 6.2749 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.09 | 0.047 | 1 | 4.8 | 10.1 |  |  |  | 7.16 | 0.049 | 1 | 4.3 | 11.9 |  |  |  | 4.8 | 3.9 | 3.4 | [18 empty] | 7340 | [6 empty] | 0 | 0 | 0 | 320 | 320 | 350 | 700 | 375 | 600 | 600 | 600 | 600 | 750 |  | 940 | 940 | 900 | 80 | 105 | 12 | 1300 | 275 | 220 | 45 | 60 | 5 | 620 | 127 | 200 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43494.8381 | 2,3,5 | 44 | 5.8 | 10.3 | 11.4 | 27.5 | 8.3 | 8.3 | 9.3 | 25.9 | ,1,3 | 12.6835 | 1,3 | 14.2978 | 26.9813 | 1.512 | 43494.8381 | 65.4368 | 5472.3782 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8234 | 1.5016 | 1.8188 | 0.24917 | 0.10491 | 0.23631 | 0.23631 | 0.21351 | 0.22685 | 1.4267 | 1.5 | 0.058479 | 0.058479 | 0.049921 | 1.0802 | 0.54791 | 0.095744 | 4.0049 | 0.74197 | 3.867 | 1.0876 | 0.55886 | 0.093217 | 3.4774 | 0.66219 | 6.2749 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.59 | 17 | 17 | 14.6 | 86 | 166 | 12 | 0.353 |  | 6 | 10 | 0.058 | 6.06 | 10 |  | 5.97 | 10 | [8 empty] | 0.039 | [14 empty] | 0.016 | 1 | 0.35 |  | 0.043 | 0.009 | 1 | 0.44 |  | 0.018 | 1 | 0.7 | [38 empty] | 7360 | [6 empty] | 0 | 0 | 0 | 340 | 280 | 380 | 760 | 320 | 640 | 640 | 640 | 680 | 750 |  | 920 | 920 | 880 | 78 | 105 | 11 | 1330 | 270 | 220 | 44 | 60 | 6 | 660 | 135 | 200 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [72 empty] | 43494.9243 | 2,3,5 | 45 | 5.8 | 11.1 | 12.1 | 29 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 12.6835 | 1,3 | 14.2978 | 26.9813 | 1.512 | 43494.9243 | 64.9186 | 5472.3782 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8419 | 1.8419 | 1.6747 | 0.24917 | 0.10491 | 0.21928 | 0.21928 | 0.2263 | 0.2263 | 1.4267 | 1.5 | 0.060641 | 0.060641 | 0.049101 | 1.0834 | 0.54761 | 0.099646 | 3.9941 | 0.74718 | 3.9407 | 1.0925 | 0.55747 | 0.10014 | 3.4919 | 0.6549 | 6.2112 |  | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.061 | [9 empty] | 6.02 | 0.369 | 4 | 0.69 | 10.8 | 5 | 0.41481 |  | 6.11 | 0.374 | 4 | 0.77 | 10.2 | 9.5 | 0.68014 | 6.1 | 0.481 | 4 | 0.91 | 12.3 | 10.5 | 0.70333 |  |  |  | 0.03 | [9 empty] | 7.46 | 0.049 | 2 | 4.6 | 10.6 | 28 | 57 | 0.034 | 7.29 | 0.048 | 2 | 4 | 11.3 | 24 | 47 | 0.031 | 4.6 | 3.8 | 3 | [18 empty] | 7700 | [6 empty] | 0 | 0 | 0 | 360 | 360 | 380 | 760 | 320 | 640 | 640 | 720 | 720 | 750 |  | 1000 | 1000 | 940 | 82 | 110 | 12 | 1390 | 285 | 235 | 48 | 65 | 7 | 720 | 145 | 215 |  | 9:00 | 0.69 | 5 | 50.88 | 35.1072 | 6.02 | 10.8 | 15 | 2.3405 | 10 | 6.5 | 0.29481 | 9:00 | 0.77 | 9.5 | 26.7789 | 20.6198 | 6.11 | 10.2 | 15 | 1.3747 | 10 | 6.5 | 0.56014 | 9:00 | 0.91 | 10.5 | 25.7143 | 23.4 | 6.1 | 12.3 | 15 | 1.56 | 10 | 6.5 | 0.58333
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.61 | 19 | 17 | 14.7 | 89 | 169 | 11.7 | 0.355 |  | 6.24 | 10 | 0.059 | 6.13 | 10 |  | 6.06 | 10 | [8 empty] | 0.039 | [14 empty] | 0.022 | 1 | 0.42 |  | 0.04 | 0.012 | 1 | 0.47 |  | 0.018 | 1 | 0.69 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.15 | 0.305 | 3 | 0.7 | 11.5 | 5.8 | 0.46198 |  | 6.17 | 0.324 | 3 | 0.78 | 11 | 10.3 | 0.72731 | 6.15 | 0.476 | 3 | 0.85 | 12.5 | 11.4 | 0.75333 | [13 empty] | 7.24 | 0.047 | 1 | 4.2 | 10 |  |  |  | 7.1 | 0.05 | 1 | 3.9 | 12 |  |  |  | 4.6 | 3.9 | 2.5 | [55 empty] | 13:00 | 0.7 | 5.8 | 43.8621 | 30.7034 | 6.15 | 11.5 | 15 | 2.0469 | 10 | 6.5 | 0.34198 | 13:00 | 0.78 | 10.3 | 24.699 | 19.2652 | 6.17 | 11 | 15 | 1.2843 | 10 | 6.5 | 0.60731 | 13:00 | 0.85 | 11.4 | 23.6842 | 20.1316 | 6.15 | 12.5 | 15 | 1.3421 | 10 | 6.5 | 0.63333
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.69 | 21 | 18 | 14.6 | 84 | 162 | 12.2 | 0.328 |  | 6.22 | 11 | 0.047 | 6.18 | 12 |  | 6.1 | 11 | [8 empty] | 0.032 | [14 empty] | 0.044 | 1 | 0.4 |  | 0.035 | 0.011 | 1 | 0.45 |  | 0.019 | 1 | 0.65 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.24 | 0.048 | 1 | 4.2 | 10 |  |  |  | 7.18 | 0.05 | 1 | 4 | 12 |  |  |  | 4.6 | 3.9 | 2.5 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.65 | 19 | 20 | 15.2 | 90 | 163 | 12.1 | 0.348 |  | 6.24 | 9 | 0.061 | 6.12 | 9 |  | 6.11 | 10 | [8 empty] | 0.039 | [14 empty] | 0.037 | 1 | 0.38 |  | 0.037 | 0.011 | 1 | 0.32 |  | 0.019 | 1 | 0.24 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.038 | [9 empty] | 6.2 | 0.356 | 4 | 0.66 | 11.3 | 5.6 | 0.45019 |  | 6.23 | 0.425 | 4 | 0.73 | 10.9 | 11.1 | 0.77448 | 6.21 | 0.405 | 3 | 0.79 | 12.4 | 12.2 | 0.79778 |  |  |  | 0.013 | [9 empty] | 7.35 | 0.052 | 1 | 4.4 | 10.2 | 21 | 41 | 0.016 | 7.29 | 0.051 | 1 | 3.9 | 11.7 | 22 | 44 | 0.013 | 4.3 | 3.9 | 3.1 | [55 empty] | 21:00 | 0.66 | 5.6 | 45.4286 | 29.9829 | 6.2 | 11.3 | 15 | 1.9989 | 10 | 6.5 | 0.33019 | 21:00 | 0.73 | 11.1 | 22.9189 | 16.7308 | 6.23 | 10.9 | 15 | 1.1154 | 10 | 6.5 | 0.65448 | 21:00 | 0.79 | 12.2 | 22.1311 | 17.4836 | 6.21 | 12.4 | 15 | 1.1656 | 10 | 6.5 | 0.67778
22:00 | [72 empty] | DOSE |  | TOTAL | 27.4 | 51.3 | 56.5 | 135.2 | 40.7 | 40.7 | 46.3 | 127.7 | 0 | 57.1579 | 0 | 71.303 | 128.461 | 7.6473 | TOTAL | 325.4088 | 26439.58 | 0 | 3425.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3124 | 8.5282 | 8.7601 | 1.7256 | 0.71433 | 1.1545 | 1.1234 | 1.0625 | 1.1041 | 7.1334 | 5 | 0.29946 | 0.29946 | 0.2514 | 5.421 | 2.7459 | 0.49687 | 19.7649 | 3.7378 | 19.4429 | 5.4869 | 2.7678 | 0.46806 | 17.3837 | 3.1841 | 31.3606 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.64 | 20 | 19 | 15.7 | 82 | 166 | 12 | 0.356 |  | 6.23 | 9 | 0.051 | 6.17 | 10 |  | 6.15 | 10 | [8 empty] | 0.044 | [14 empty] | 0.033 | 1 | 0.46 |  | 0.046 | 0.01 | 1 | 0.4 |  | 0.018 | 1 | 0.31 | [22 empty] | AVERAGE | 5.48 | 10.26 | 11.3 | 27.04 | 8.14 | 8.14 | 9.26 | 25.54 |  | 11.4316 |  | 14.2606 | 25.6922 | 1.5295 | AVERAGE | 65.0818 | 5287.916 |  | 685.1101 | 0 | 0 | 0 |  |  |  | 1.8625 | 1.7056 | 1.752 | 0.34511 | 0.14287 | 0.23089 | 0.22468 | 0.21251 | 0.22081 | 1.4267 | 1 | 0.059892 | 0.059892 | 0.05028 | 1.0842 | 0.54918 | 0.099373 | 3.953 | 0.74756 | 3.8886 | 1.0974 | 0.55356 | 0.093613 | 3.4767 | 0.63683 | 6.2721 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.76 | 111 | 107 | 89.3 | 518 | 989 | 72.4 | 2.097 | 0.099 | 36.94 | 58 | 0.336 | 36.75 | 60 | 0 | 36.38 | 59 | 0 | 24.4 | 1.355 | 14 | 2.66 | 45 | 21.5 | 1.7477 | 0.235 | 24.57 | 1.46 | 14 | 3.03 | 43 | 41 | 2.8975 | 24.53 | 1.694 | 14 | 3.4 | 50 | 45.1 | 2.9856 |  | 6 | 2.31 | 0.043 | 0.241 | 0.059 | 6 | 2.44 | 0 | 0.111 | 7 | 3.04 | 0 | 43.72 | 0.293 | 7 | 26.7 | 61 | 49 | 98 | 0.05 | 43.17 | 0.296 | 7 | 24.2 | 70.8 | 46 | 91 | 0.044 | 27.5 | 23.3 | 17.2 |  |  | MINIMUM | 5 | 9.8 | 10.8 | 25.6 | 7.7 | 7.7 | 8.8 | 24.2 |  | 10.597 |  | 14.2358 | 24.8328 | 1.512 | MINIMUM | 64.6585 | 5041.9664 |  | 634.3612 | [6 empty] | 1.7161 | 1.5016 | 1.6747 | 0.24917 | 0 | 0.21344 | 0.21344 | 0.20016 | 0.20016 | 1.4267 | 0 | 0.058479 | 0.058479 | 0.049101 | 1.0748 | 0.54761 | 0.093823 | 3.8846 | 0.74054 | 3.867 | 1.0876 | 0.54139 | 0.077681 | 3.4566 | 0.62206 | 6.2112 |  | MIN | 0.66 | 5.6 | 45.4286 | 29.9829 | 6.2 | 11.3 | 15 | 1.9989 |  |  |  | MIN | 0.73 | 11.1 | 22.9189 | 16.7308 | 6.23 | 10.9 | 15 | 1.1154 |  |  |  | MIN | 0.79 | 12.2 | 22.1311 | 17.4836 | 6.21 | 12.4 | 15 | 1.1656 |  |  |  | 1.1154
AVERAGE | 6.6267 | 18.5 | 17.8333 | 14.8833 | 86.3333 | 164.8333 | 12.0667 | 0.3495 | 0.0495 | 6.1567 | 9.6667 | 0.056 | 6.125 | 10 |  | 6.0633 | 9.8333 |  | 6.1 | 0.33875 | 3.5 | 0.665 | 11.25 | 5.375 | 0.43692 | 0.039167 | 6.1425 | 0.365 | 3.5 | 0.7575 | 10.75 | 10.25 | 0.72436 | 6.1325 | 0.4235 | 3.5 | 0.85 | 12.5 | 11.275 | 0.74639 |  | 1 | 0.385 | 0.0215 | 0.040167 | 0.0098333 | 1 | 0.40667 |  | 0.0185 | 1.1667 | 0.50667 |  | 7.2867 | 0.048833 | 1.1667 | 4.45 | 10.1667 | 24.5 | 49 | 0.025 | 7.195 | 0.049333 | 1.1667 | 4.0333 | 11.8 | 23 | 45.5 | 0.022 | 4.5833 | 3.8833 | 2.8667 |  |  | MAXIMUM | 5.8 | 11.1 | 12.1 | 29 | 8.7 | 8.7 | 10.1 | 27.5 |  | 12.6835 |  | 14.2978 | 26.9813 | 1.5993 | MAXIMUM | 65.4368 | 5472.3782 |  | 697.7974 | [6 empty] | 2.0811 | 1.8499 | 1.821 | 0.50962 | 0.25861 | 0.26389 | 0.23631 | 0.2263 | 0.23946 | 1.4267 | 1.5 | 0.060641 | 0.060641 | 0.051056 | 1.1079 | 0.55124 | 0.10445 | 4.0049 | 0.75571 | 3.9407 | 1.1123 | 0.55886 | 0.10014 | 3.4919 | 0.66219 | 6.2998
MINIMUM | 6.58 | 15 | 16 | 14.5 | 82 | 162 | 11.7 | 0.328 | 0.038 | 6 | 9 | 0.047 | 6.06 | 9 |  | 5.97 | 8 |  | 6.02 | 0.305 | 3 | 0.61 | 10.8 | 5 | 0.41481 | 0.032 | 6.06 | 0.324 | 3 | 0.73 | 10.2 | 9.5 | 0.68014 | 6.07 | 0.332 | 3 | 0.79 | 12.3 | 10.5 | 0.70333 |  | 1 | 0.3 | 0.013 | 0.035 | 0.006 | 1 | 0.32 |  | 0.018 | 1 | 0.24 |  | 7.09 | 0.047 | 1 | 4.2 | 10 | 21 | 41 | 0.016 | 7.1 | 0.048 | 1 | 3.9 | 11.3 | 22 | 44 | 0.013 | 4.3 | 3.8 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 35990 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1700 | 1560 | 1820 | 3570 | 1355 | 3110 | 3030 | 3160 | 3280 | 3750 | 0 | 4620 | 4620 | 4410 | 384 | 516 | 56 | 6440 | 1334 | 1085 | 221 | 296 | 30 | 3160 | 647 | 995
MAXIMUM | 6.69 | 21 | 20 | 15.7 | 90 | 169 | 12.4 | 0.357 | 0.061 | 6.24 | 11 | 0.061 | 6.18 | 12 |  | 6.15 | 11 |  | 6.2 | 0.369 | 4 | 0.7 | 11.5 | 5.8 | 0.46198 | 0.044 | 6.23 | 0.425 | 4 | 0.78 | 11 | 11.1 | 0.77448 | 6.21 | 0.481 | 4 | 0.91 | 12.8 | 12.2 | 0.79778 |  | 1 | 0.46 | 0.03 | 0.046 | 0.012 | 1 | 0.47 |  | 0.019 | 2 | 0.7 |  | 7.46 | 0.052 | 2 | 4.8 | 10.6 | 28 | 57 | 0.034 | 7.29 | 0.051 | 2 | 4.3 | 12 | 24 | 47 | 0.031 | 4.8 | 3.9 | 3.4 | [17 empty] | AVERAGE | 7198 | [9 empty] | 340 | 312 | 364 | 714 | 271 | 622 | 606 | 632 | 656 | 750 |  | 924 | 924 | 882 | 76.8 | 103.2 | 11.2 | 1288 | 266.8 | 217 | 44.2 | 59.2 | 6 | 632 | 129.4 | 199
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.115 |  | TOTAL AVG COAG ALK: |  |  |  | 9.8333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.481 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.61 | [5 empty] | 6.125 |  |  |  |  | 0.019 |  |  |  |  | 0.61 | [23 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 6770 | [9 empty] | 320 | 280 | 350 | 670 | 0 | 550 | 550 | 600 | 600 | 750 |  | 880 | 880 | 840 | 72 | 98 | 10 | 1200 | 250 | 205 | 42 | 55 | 5 | 580 | 120 | 190
[63 empty] | 0 | [26 empty] | MAXIMUM | 7700 | [9 empty] | 360 | 360 | 380 | 760 | 375 | 680 | 640 | 720 | 720 | 750 |  | 1000 | 1000 | 940 | 82 | 110 | 12 | 1390 | 285 | 235 | 48 | 65 | 7 | 720 | 145 | 215
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 10.4 |  | TOTAL MGD: |  | 0.01 |  |  | FINISHED SOUTH 1 |  | START: | 23827255 |  | END: | 23827265 |  |  | Alum | 2934 | 10795 | 10795 | 11104 | 11104 | 0 | [44 empty] | 0.73 | 11.1 | 22.9189 | 16.7308 | 6.23 | 10.9 | 15 | 1.1154
[73 empty] | FINISHED 2 | 12.267 |  | TOTAL MGD: |  | 10.39 |  |  | FINISHED SOUTH 2 |  | START: | 44139721 |  | END: | 44150111 |  |  | Caustic | 6073 | 7861 | 7861
[73 empty] | TOTAL RAW | 26.75 |  | TOTAL MGD: |  | 4.264 |  |  | FINISHED CONWAY |  | START: | 10351346 |  | END: | 10355610 |  |  | Hypochlorite | 14 |  | 34
[76 empty] | TOTAL MGD: |  | 8.003 |  |  | FINISHED PERRY |  | START: | 34053912 |  | END: | 34061915 |  |  | Phosphate | 1523
[76 empty] | TOTAL MGD: |  | 5.354 |  |  | RAW PLANT 1 |  | START: | 31209662 |  | END: | 31215016 |  |  | Fluoride | 2250 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.134 |  |  | RAW PLANT 2 |  | START: | 31119062 |  | END: | 31129196 |  |  | Cal~Flo | 9.13 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.262 |  |  | RAW PLANT 3 |  | START: | 7786747 |  | END: | 7798009 |  |  | Zinc | 818
[76 empty] | TOTAL MGD: |  | 1.038 |  |  | DECANT |  | START: | 1889645 |  | END: | 1890683 |  |  | Polymer | 30
[76 empty] | TOTAL MGD: |  | 1.7428 |  |  | BLOW DOWN |  | START: | 9172.4171 |  | END: | 9174.1599 |  |  | NH3 | 10 |  | BI-SUL | 1000
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 698
23827265
44150111
10355610
34061915
31215016
31129196
7798009
1890683
9174.1599
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 30
DATE: | 2019-01-30 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 14 |  | 18 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 14 |  | 18 | [37 empty] | 18:00 - 6:00 |  | 14 |  | 18
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2019-01-30 | [23 empty] | DATE: | 2019-01-30
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-30 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43495.0024 | 2,3,5 | 45 | 5.8 | 11.1 | 12.1 | 29 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 12.6835 | 1,3 | 14.2978 | 26.9813 | 2.2736 | 43495.0024 | 64.9186 | 5472.3782 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8419 | 1.8419 | 1.6747 | 0.24917 | 0.10491 | 0.21928 | 0.21928 | 0.2263 | 0.2263 | 1.4267 | 1.5 | 0.060641 | 0.060641 | 0.049101 | 1.0834 | 0.54761 | 0.099646 | 3.9941 | 0.74718 | 3.9407 | 1.0925 | 0.55747 | 0.10014 | 3.4919 | 0.6549 | 6.2112 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.12 | 0.403 | 3 | 0.47 | 11.4 | 5.6 | 0.45019 |  | 6.22 | 0.454 | 4 | 0.68 | 10.6 | 11.1 | 0.77448 | 6.24 | 0.432 | 4 | 0.74 | 12.5 | 12.2 | 0.79778 | [13 empty] | 7.57 | 0.047 | 1 | 4 | 10.2 |  |  |  | 7.75 | 0.049 | 1 | 3.9 | 11.1 |  |  |  | 4.3 | 3.8 | 3.3 | [18 empty] | 7700 | [6 empty] | 0 | 0 | 0 | 360 | 360 | 380 | 760 | 320 | 640 | 640 | 720 | 720 | 750 |  | 1000 | 1000 | 940 | 82 | 110 | 12 | 1390 | 285 | 235 | 48 | 65 | 7 | 720 | 145 | 215 |  | 1:00 | 0.47 | 5.6 | 45.4286 | 21.3514 | 6.12 | 11.4 | 15 | 1.4234 | 10 | 6.5 | 0.33019 | 1:00 | 0.68 | 11.1 | 22.9189 | 15.5849 | 6.22 | 10.6 | 15 | 1.039 | 10 | 6.5 | 0.65448 | 1:00 | 0.74 | 12.2 | 22.1311 | 16.377 | 6.24 | 12.5 | 15 | 1.0918 | 10 | 6.5 | 0.67778
2:00 | [72 empty] | 43495.3335 | 2,3,5 | 45 | 5.9 | 11.3 | 12.7 | 29.9 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 10.3694 | 1,3 | 12.8952 | 23.2646 | 2.2736 | 43495.3335 | 61.9833 | 5349.4034 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76746 | 1.8419 | 1.5866 | 0.25139 | 0.09669 | 0.24232 | 0.23559 | 0.20363 | 0.20962 | 1.4267 | 3.5 | 0.060641 | 0.059428 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.8632 | 0.64231 | 3.9407 | 1.0925 | 0.53174 | 0.085834 | 3.5206 | 0.49682 | 6.2112 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.62 | 17 | 19 | 15.8 | 89 | 156 | 12.1 | 0.354 |  | 6.01 | 8 | 0.058 | 6.08 | 8 |  | 6.02 | 9 | [8 empty] | 0.039 | [14 empty] | 0.031 | 1 | 0.45 |  | 0.041 | 0.01 | 1 | 0.41 |  | 0.066 | 1 | 0.58 | [38 empty] | 7580 | [6 empty] | 0 | 0 | 0 | 150 | 360 | 360 | 780 | 300 | 720 | 700 | 680 | 700 | 750 |  | 1000 | 980 | 960 | 84 | 110 | 12 | 1300 | 245 | 235 | 48 | 62 | 6 | 640 | 110 | 215 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43495.8623 | 2,3,5 | 45 | 5.9 | 11.3 | 12.5 | 29.7 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 10.9786 | 1,3 | 15.9955 | 26.9741 | 2.7288 | 43495.8623 | 62.5653 | 4918.9916 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76746 | 1.8419 | 1.5866 | 0.25139 | 0.09669 | 0.24232 | 0.23559 | 0.20689 | 0.21297 | 1.4267 | 4 | 0.060641 | 0.060035 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.8932 | 0.64231 | 4.2761 | 1.0925 | 0.53174 | 0.085834 | 3.5306 | 0.49682 | 7.3668 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.3 | 0.048 | 1 | 4.7 | 10.2 |  |  |  | 7.29 | 0.05 | 1 | 4.2 | 11.1 |  |  |  | 4.4 | 3.8 | 4.1 | [18 empty] | 7600 | [6 empty] | 0 | 0 | 0 | 150 | 360 | 360 | 780 | 300 | 720 | 700 | 680 | 700 | 750 |  | 1000 | 990 | 960 | 84 | 110 | 12 | 1300 | 245 | 255 | 48 | 62 | 6 | 640 | 110 | 255 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43495.9533 | 2,3,5 | 45 | 5.9 | 11.3 | 12.5 | 29.7 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 10.9786 | 1,3 | 15.9955 | 26.9741 | 2.7288 | 43495.9533 | 62.5653 | 4918.9916 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76746 | 1.8419 | 1.5866 | 0.25139 | 0.09669 | 0.24232 | 0.23559 | 0.20689 | 0.21297 | 1.4267 | 4 | 0.060641 | 0.060035 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.8932 | 0.64231 | 4.2761 | 1.0925 | 0.53174 | 0.085834 | 3.5306 | 0.49682 | 7.3668 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.67 | 17 | 18 | 15.9 | 94 | 174 | 11.5 | 0.372 |  | 6.09 | 7 | 0.048 | 6.09 | 8 |  | 6.09 | 8 | [8 empty] | 0.046 | [14 empty] | 0.026 | 1 | 0.48 |  | 0.044 | 0.011 | 1 | 0.43 |  | 0.041 | 1 | 0.63 | [38 empty] | 7600 | [6 empty] | 0 | 0 | 0 | 150 | 360 | 360 | 780 | 300 | 720 | 700 | 680 | 700 | 750 |  | 1000 | 990 | 960 | 84 | 110 | 12 | 1300 | 245 | 255 | 48 | 62 | 6 | 640 | 110 | 255 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.041 | [9 empty] | 6.09 | 0.349 | 4 | 0.46 | 11 | 5.9 | 0.46788 |  | 6.2 | 0.497 | 4 | 0.69 | 10.3 | 11.4 | 0.79217 | 6.15 | 0.503 | 4 | 0.79 | 12.4 | 12.6 | 0.82 |  |  |  | 0.019 | [9 empty] | 7.26 | 0.057 | 1 | 4.5 | 10 | 20 | 42 | 0.014 | 7.17 | 0.055 | 1 | 3.9 | 11.4 | 21 | 43 | 0.012 | 4.4 | 4 | 4.2 | [55 empty] | 9:00 | 0.46 | 5.9 | 43.1186 | 19.8346 | 6.09 | 11 | 15 | 1.3223 | 10 | 6.5 | 0.34788 | 9:00 | 0.69 | 11.4 | 22.3158 | 15.3979 | 6.2 | 10.3 | 15 | 1.0265 | 10 | 6.5 | 0.67217 | 9:00 | 0.79 | 12.6 | 21.4286 | 16.9286 | 6.15 | 12.4 | 15 | 1.1286 | 10 | 6.5 | 0.7
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.66 | 17 | 18 | 16.1 | 87 | 174 | 11.3 | 0.355 |  | 6.05 | 7 | 0.047 | 6.04 | 7 |  | 6.04 | 8 | [8 empty] | 0.041 | [14 empty] | 0.026 | 1 | 0.43 |  | 0.044 | 0.009 | 1 | 0.46 |  | 0.034 | 1 | 0.65 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | . | [126 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.11 | 0.408 | 4 | 0.63 | 11.5 | 5.8 | 0.46198 |  | 6.13 | 0.515 | 4 | 0.7 | 10.6 | 11.3 | 0.78627 | 6.11 | 0.55 | 4 | 0.73 | 12.5 | 12.6 | 0.82 | [13 empty] | 7.21 | 0.065 | 1 | 4.4 | 9.8 |  |  |  | 7.11 | 0.067 | 1 | 3.9 | 11.2 |  |  |  | 4.4 | 4 | 4.2 | [55 empty] | 13:00 | 0.63 | 5.8 | 43.8621 | 27.6331 | 6.11 | 11.5 | 15 | 1.8422 | 10 | 6.5 | 0.34198 | 13:00 | 0.7 | 11.3 | 22.5133 | 15.7593 | 6.13 | 10.6 | 15 | 1.0506 | 10 | 6.5 | 0.66627 | 13:00 | 0.73 | 12.6 | 21.4286 | 15.6429 | 6.11 | 12.5 | 15 | 1.0429 | 10 | 6.5 | 0.7
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.64 | 17 | 18 | 15.9 | 86 | 177 | 11.4 | 0.354 |  | 5.9 | 7 | 0.054 | 5.91 | 7 |  | 5.89 | 7 | [8 empty] | 0.042 | [14 empty] | 0.021 | 1 | 0.48 |  | 0.044 | 0.044 | 1 | 0.49 |  | 0.027 | 1 | 0.64 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.11 | 0.062 | 1 | 4.3 | 10.3 |  |  |  | 7.06 | 0.06 | 1 | 3.9 | 11 |  |  |  | 4.4 | 3.9 | 4.4 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.61 | 17 | 18 | 15.9 | 97 | 174 | 11.5 | 0.374 |  | 6.01 | 8 | 0.044 | 6.1 | 7 |  | 6.07 | 8 | [8 empty] | 0.034 | [14 empty] | 0.026 | 1 | 0.53 |  | 0.035 | 0.018 | 1 | 0.58 |  | 0.023 | 1 | 0.78 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.046 | [9 empty] | 6.03 | 0.315 | 3 | 0.74 | 10.9 | 5.9 | 0.46788 |  | 6.02 | 0.254 | 4 | 0.74 | 10.4 | 11.3 | 0.78627 | 6 | 0.692 | 4 | 0.8 | 12.5 | 12.7 | 0.73148 |  |  |  | 0.017 | [9 empty] | 7.22 | 0.062 | 1 | 4.5 | 9.6 | 20 | 42 | 0.019 | 7.19 | 0.067 | 1 | 4.1 | 11 | 20 | 42 | 0.014 | 4.3 | 3.8 | 4.2 | [55 empty] | 21:00 | 0.74 | 5.9 | 43.1186 | 31.9078 | 6.03 | 10.9 | 15 | 2.1272 | 10 | 6.5 | 0.34788 | 21:00 | 0.74 | 11.3 | 22.5133 | 16.6598 | 6.02 | 10.4 | 15 | 1.1107 | 10 | 6.5 | 0.66627 | 21:00 | 0.8 | 12.7 | 21.2598 | 17.0079 | 6 | 12.5 | 13 | 1.3083 | 10 | 6 | 0.61148
22:00 | [72 empty] | DOSE |  | TOTAL | 23.5 | 45 | 49.8 | 118.3 | 34.8 | 34.8 | 40.4 | 110 | 0 | 45.0101 | 0 | 59.184 | 104.1941 | 10.0048 | TOTAL | 252.0326 | 20659.7648 | 0 | 2791.1894 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1443 | 7.3676 | 6.4345 | 1.0033 | 0.39498 | 0.94625 | 0.92605 | 0.84371 | 0.86187 | 5.7067 | 13 | 0.24256 | 0.24014 | 0.19954 | 4.4127 | 2.1905 | 0.39858 | 15.6437 | 2.6741 | 16.4337 | 4.3701 | 2.1527 | 0.35764 | 14.0738 | 2.1454 | 27.1559 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.69 | 17 | 17 | 16.4 | 97 | 173 | 11.4 | 0.382 |  | 6.09 | 8 | 0.047 | 6 | 8 |  | 6.01 | 8 | [8 empty] | 0.036 | [14 empty] | 0.022 | 1 | 0.51 |  | 0.037 | 0.016 | 1 | 0.48 |  | 0.022 | 1 | 0.67 | [22 empty] | AVERAGE | 5.875 | 11.25 | 12.45 | 29.575 | 8.7 | 8.7 | 10.1 | 27.5 |  | 11.2525 |  | 14.796 | 26.0485 | 2.5012 | AVERAGE | 63.0082 | 5164.9412 |  | 697.7974 | 0 | 0 | 0 |  |  |  | 1.0361 | 1.8419 | 1.6086 | 0.25084 | 0.098746 | 0.23656 | 0.23151 | 0.21093 | 0.21547 | 1.4267 | 3.25 | 0.060641 | 0.060035 | 0.049885 | 1.1032 | 0.54761 | 0.099646 | 3.9109 | 0.66853 | 4.1084 | 1.0925 | 0.53818 | 0.08941 | 3.5184 | 0.53634 | 6.789 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.89 | 102 | 108 | 96 | 550 | 1028 | 69.2 | 2.191 | 0.087 | 36.15 | 45 | 0.298 | 36.22 | 45 | 0 | 36.12 | 48 | 0 | 24.35 | 1.475 | 14 | 2.3 | 44.8 | 23.2 | 1.8479 | 0.238 | 24.57 | 1.72 | 16 | 2.81 | 41.9 | 45.1 | 3.1392 | 24.5 | 2.177 | 16 | 3.06 | 49.9 | 50.1 | 3.1693 | 0.152 | 6 | 2.88 | 0.036 | 0.245 | 0.108 | 6 | 2.85 | 0 | 0.213 | 6 | 3.95 | 0 | 43.67 | 0.341 | 6 | 26.4 | 60.1 | 40 | 84 | 0.033 | 43.57 | 0.348 | 6 | 23.9 | 66.8 | 41 | 85 | 0.026 | 26.2 | 23.3 | 24.4 |  |  | MINIMUM | 5.8 | 11.1 | 12.1 | 29 | 8.7 | 8.7 | 10.1 | 27.5 |  | 10.3694 |  | 12.8952 | 23.2646 | 2.2736 | MINIMUM | 61.9833 | 4918.9916 |  | 697.7974 | [6 empty] | 0.76746 | 1.8419 | 1.5866 | 0.24917 | 0.09669 | 0.21928 | 0.21928 | 0.20363 | 0.20962 | 1.4267 | 1.5 | 0.060641 | 0.059428 | 0.049101 | 1.0834 | 0.54761 | 0.099646 | 3.8632 | 0.64231 | 3.9407 | 1.0925 | 0.53174 | 0.085834 | 3.4919 | 0.49682 | 6.2112 |  | MIN | 0.46 | 5.9 | 43.1186 | 19.8346 | 6.09 | 11 | 15 | 1.3223 |  |  |  | MIN | 0.69 | 11.4 | 22.3158 | 15.3979 | 6.2 | 10.3 | 15 | 1.0265 |  |  |  | MIN | 0.73 | 12.6 | 21.4286 | 15.6429 | 6.11 | 12.5 | 15 | 1.0429 |  |  |  | 1.0265
AVERAGE | 6.6483 | 17 | 18 | 16 | 91.6667 | 171.3333 | 11.5333 | 0.36517 | 0.0435 | 6.025 | 7.5 | 0.049667 | 6.0367 | 7.5 |  | 6.02 | 8 |  | 6.0875 | 0.36875 | 3.5 | 0.575 | 11.2 | 5.8 | 0.46198 | 0.039667 | 6.1425 | 0.43 | 4 | 0.7025 | 10.475 | 11.275 | 0.7848 | 6.125 | 0.54425 | 4 | 0.765 | 12.475 | 12.525 | 0.79231 | 0.025333 | 1 | 0.48 | 0.018 | 0.040833 | 0.018 | 1 | 0.475 |  | 0.0355 | 1 | 0.65833 |  | 7.2783 | 0.056833 | 1 | 4.4 | 10.0167 | 20 | 42 | 0.0165 | 7.2617 | 0.058 | 1 | 3.9833 | 11.1333 | 20.5 | 42.5 | 0.013 | 4.3667 | 3.8833 | 4.0667 |  |  | MAXIMUM | 5.9 | 11.3 | 12.7 | 29.9 | 8.7 | 8.7 | 10.1 | 27.5 |  | 12.6835 |  | 15.9955 | 26.9813 | 2.7288 | MAXIMUM | 64.9186 | 5472.3782 |  | 697.7974 | [6 empty] | 1.8419 | 1.8419 | 1.6747 | 0.25139 | 0.10491 | 0.24232 | 0.23559 | 0.2263 | 0.2263 | 1.4267 | 4 | 0.060641 | 0.060641 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.9941 | 0.74718 | 4.2761 | 1.0925 | 0.55747 | 0.10014 | 3.5306 | 0.6549 | 7.3668
MINIMUM | 6.61 | 17 | 17 | 15.8 | 86 | 156 | 11.3 | 0.354 | 0.041 | 5.9 | 7 | 0.044 | 5.91 | 7 |  | 5.89 | 7 |  | 6.03 | 0.315 | 3 | 0.46 | 10.9 | 5.6 | 0.45019 | 0.034 | 6.02 | 0.254 | 4 | 0.68 | 10.3 | 11.1 | 0.77448 | 6 | 0.432 | 4 | 0.73 | 12.4 | 12.2 | 0.73148 | 0.021 | 1 | 0.43 | 0.017 | 0.035 | 0.009 | 1 | 0.41 |  | 0.022 | 1 | 0.58 |  | 7.11 | 0.047 | 1 | 4 | 9.6 | 20 | 42 | 0.014 | 7.06 | 0.049 | 1 | 3.9 | 11 | 20 | 42 | 0.012 | 4.3 | 3.8 | 3.3 | [15 empty] | MIL/MIN |  | TOTAL | 30480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 1440 | 1460 | 3100 | 1220 | 2800 | 2740 | 2760 | 2820 | 3000 | 0 | 4000 | 3960 | 3820 | 334 | 440 | 48 | 5290 | 1020 | 980 | 192 | 251 | 25 | 2640 | 475 | 940
MAXIMUM | 6.69 | 17 | 19 | 16.4 | 97 | 177 | 12.1 | 0.382 | 0.046 | 6.09 | 8 | 0.058 | 6.1 | 8 |  | 6.09 | 9 |  | 6.12 | 0.408 | 4 | 0.74 | 11.5 | 5.9 | 0.46788 | 0.046 | 6.22 | 0.515 | 4 | 0.74 | 10.6 | 11.4 | 0.79217 | 6.24 | 0.692 | 4 | 0.8 | 12.5 | 12.7 | 0.82 | 0.031 | 1 | 0.53 | 0.019 | 0.044 | 0.044 | 1 | 0.58 |  | 0.066 | 1 | 0.78 |  | 7.57 | 0.065 | 1 | 4.7 | 10.3 | 20 | 42 | 0.019 | 7.75 | 0.067 | 1 | 4.2 | 11.4 | 21 | 43 | 0.014 | 4.4 | 4 | 4.4 | [17 empty] | AVERAGE | 7620 | [9 empty] | 202.5 | 360 | 365 | 775 | 305 | 700 | 685 | 690 | 705 | 750 |  | 1000 | 990 | 955 | 83.5 | 110 | 12 | 1322.5 | 255 | 245 | 48 | 62.75 | 6.25 | 660 | 118.75 | 235
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0272 |  | TOTAL AVG COAG ALK: |  |  |  | 7.6667 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.692 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.46 | [5 empty] | 6.1183 |  |  |  |  | 0.066 |  |  |  |  | 0.46 | [6 empty] | 0.066 | [16 empty] | Pump Station MIN |  | 3.3 | [17 empty] | MINIMUM | 7580 | [9 empty] | 150 | 360 | 360 | 760 | 300 | 640 | 640 | 680 | 700 | 750 |  | 1000 | 980 | 940 | 82 | 110 | 12 | 1300 | 245 | 235 | 48 | 62 | 6 | 640 | 110 | 215
[90 empty] | MAXIMUM | 7700 | [9 empty] | 360 | 360 | 380 | 780 | 320 | 720 | 700 | 720 | 720 | 750 |  | 1000 | 1000 | 960 | 84 | 110 | 12 | 1390 | 285 | 255 | 48 | 65 | 7 | 720 | 145 | 255
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 7.668 |  | TOTAL MGD: |  | 0.01 |  |  | FINISHED SOUTH 1 |  | START: | 23827265 |  | END: | 23827275 |  |  | Alum | 9134 | 10792 | 10792 | 11101 | 11101 | 0 | [44 empty] | 0.69 | 11.4 | 22.3158 | 15.3979 | 6.2 | 10.3 | 15 | 1.0265
[73 empty] | FINISHED 2 | 13.812 |  | TOTAL MGD: |  | 7.658 |  |  | FINISHED SOUTH 2 |  | START: | 44150111 |  | END: | 44157769 |  |  | Caustic | 5985 | 7819 | 7819
[73 empty] | TOTAL RAW | 29.625 |  | TOTAL MGD: |  | 4.834 |  |  | FINISHED CONWAY |  | START: | 10355610 |  | END: | 10360444 |  |  | Hypochlorite | 19 |  | 46
[76 empty] | TOTAL MGD: |  | 8.978 |  |  | FINISHED PERRY |  | START: | 34061915 |  | END: | 34070893 |  |  | Phosphate | 1468
[76 empty] | TOTAL MGD: |  | 5.733 |  |  | RAW PLANT 1 |  | START: | 31215016 |  | END: | 31220749 |  |  | Fluoride | 2100 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 11.197 |  |  | RAW PLANT 2 |  | START: | 31129196 |  | END: | 31140393 |  |  | Cal~Flo | 6.96 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 12.695 |  |  | RAW PLANT 3 |  | START: | 7798009 |  | END: | 7810704 |  |  | Zinc | 788
[76 empty] | TOTAL MGD: |  | 0.925 |  |  | DECANT |  | START: | 1890683 |  | END: | 1891608 |  |  | Polymer | 30
[76 empty] | TOTAL MGD: |  | 1.3423 |  |  | BLOW DOWN |  | START: | 9174.1599 |  | END: | 9175.5022 |  |  | NH3 | 9.56 |  | BI-SUL | 900
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 0
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 678
23827275
44157769
10360444
34070893
31220749
31140393
7810704
1891608
9175.5022
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## 31
DATE: | 2019-01-31 | [11 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [30 empty] | 6:00 - 18:00 |  |  | 17 |  | 21 | [5 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY | [27 empty] | BULL CREEK SURFACE WATER TREATMENT FACILITY
HOURS IN OPERATION | [5 empty] | 24 | [37 empty] | 18:00 - 6:00 |  |  | 18 |  | 14 | [23 empty] | 6:00 - 18:00 |  | 17 |  | 21 | [37 empty] | 6:00 - 18:00 |  | 17 |  | 21
AVERAGE WIND SPEED | [41 empty] | SN | 21 | DH |  | 4 | HE | 12 | CW 14 | RH | 17 | [21 empty] | 18:00 - 6:00 |  | 18 |  | 14 | [37 empty] | 18:00 - 6:00 |  | 18 |  | 14
OUTSIDE TEMP | [41 empty] | WL | 3 | MN |  | 5 | DB | 20 | GE 16 | JM | 18 |  |  | DATE: | 2019-01-31 | [23 empty] | DATE: | 2019-01-31
RAIN: | Y |  |  |  | N |  |  |  |  | PLT 1 |  |  | PLT 2 |  |  | PLT 3 |  |  | PLANT 1 | [7 empty] | PLANT 2 | [6 empty] | PLANT 3 | [6 empty] | PLANT 1 |  |  |  |  | PLANT 2 |  |  |  | PLANT 3 | [23 empty] | RAW | [5 empty] | FILTER |  |  |  | FINISHED 1 |  | FINISHED 2 |  | FIN 1 + 2 |  |  | RAW | [9 empty] | SETTLED | [10 empty] | FILTER |  |  | FINISHED 1 | [5 empty] | FINISHED 2
2019-01-31 | RAW | [8 empty] | TREATED |  |  | TREATED |  |  | TREATED |  |  | SETTLED | [7 empty] | SETTLED | [6 empty] | SETTLED | [6 empty] | FILTER |  |  |  |  | FILTER |  |  |  | FILTER |  |  |  | FINISHED 1 | [7 empty] | FINISHED 2 | [8 empty] | PUMP STATIONS |  |  |  |  | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 | PLT 2 | PLT 3 | FLOW | PLT 1 |  | PLT 2 |  | FLOW | FLOW |  | DOSE |  | LBS |  | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 | PLT 2 | PLT 3 | PLT 1 |  | PLT 2 |  | PLT 3 |  | THINCKENER |  | PLT 1 | PLT 2 | PLT 3 | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | POST | [6 empty] | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
TIME | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | MN | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | ALKALINITY | Treated UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | SETTLED UV | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | PH | NTU | COLOR | FREE CL2 | Temp | FLOW | MIN CT | NTU | COLOR | FREE CL2 | MN | FILTER UV | NTU | COLOR | FREE CL2 | MN | NTU | COLOR | FREE CL2 | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | PH | NTU | COLOR | TOTAL CL2 | TEMP | ALK | HARDNESS | MN | South Pump station | Conway Pump station | Perry Road station | TIME | PUMPS | VALVE SET | FLOW | FLOW | FLOW | TOTAL | FLOW | FLOW | FLOW | TOTAL | PUMPS | FLOW | PUMPS | FLOW | TOTAL | DECANT | TIME | ALUM | CAL-FLOW RAW | Hydrated | CARBON | Cal~Flo Slurry | Cal~Flo Slurry | Cal~Flo Slurry | CAUSTIC TO COAG | CAUSTIC TO COAG | CAUSTIC TO COAG | FREE CHLORINE | FREE CHLORINE | FREE CHLORINE | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | POLYMER | Sludge Judge | FILTER AID | FILTER AID | FILTER AID | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC | PHOSPHATE | FLUORIDE | ZINC | CHLORINE | AMMONIA | CAUSTIC |  |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | min CT |  | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table) | use Temp | use PH | DAILY CT
0:00 | [72 empty] | 43496.0055 | 2,3,5 | 45 | 5.9 | 11.3 | 12.5 | 29.7 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 10.9786 | 1,3 | 15.9955 | 26.9741 | 2.7288 | 43496.0055 | 62.5653 | 4918.9916 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76746 | 1.8419 | 1.5866 | 0.25139 | 0.09669 | 0.24232 | 0.23559 | 0.20689 | 0.21297 | 1.4267 | 4 | 0.060641 | 0.060035 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.8932 | 0.64231 | 4.2761 | 1.0925 | 0.53174 | 0.085834 | 3.5306 | 0.49682 | 7.3668 |  | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 0:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
1:00 | [18 empty] | 6.19 | 0.308 | 3 | 0.67 | 11 | 5.9 | 0.46788 |  | 6.1 | 0.244 | 4 | 0.71 | 10.8 | 11.3 | 0.78627 | 6.12 | 0.698 | 4 | 0.72 | 12.7 | 12.5 | 0.81444 | [13 empty] | 7.6 | 0.064 | 1 | 4.6 | 9.8 |  |  |  | 7.26 | 0.067 | 1 | 3.8 | 11 |  |  |  | 4.3 | 3.6 | 2.8 | [18 empty] | 7600 | [6 empty] | 0 | 0 | 0 | 150 | 360 | 360 | 780 | 300 | 720 | 700 | 680 | 700 | 750 |  | 1000 | 990 | 960 | 84 | 110 | 12 | 1300 | 245 | 255 | 48 | 62 | 6 | 640 | 110 | 255 |  | 1:00 | 0.67 | 5.9 | 43.1186 | 28.8895 | 6.19 | 11 | 15 | 1.926 | 10 | 6.5 | 0.34788 | 1:00 | 0.71 | 11.3 | 22.5133 | 15.9844 | 6.1 | 10.8 | 15 | 1.0656 | 10 | 6.5 | 0.66627 | 1:00 | 0.72 | 12.5 | 21.6 | 15.552 | 6.12 | 12.7 | 15 | 1.0368 | 10 | 6.5 | 0.69444
2:00 | [72 empty] | 43496.1362 | 2,3,5 | 45 | 5.9 | 11.3 | 12.5 | 29.7 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 12.5352 | 1,3 | 11.7806 | 24.3158 | 2.7288 | 43496.1362 | 62.5653 | 4918.9916 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76746 | 1.8419 | 1.5866 | 0.25139 | 0.09669 | 0.24232 | 0.23559 | 0.20689 | 0.21297 | 1.4267 | 4 | 0.060641 | 0.060035 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.8932 | 0.64231 | 4.2761 | 1.0925 | 0.53174 | 0.085834 | 3.5306 | 0.49682 | 7.3668 |  | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 2:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
3:00 | 6.69 | 18 | 17 | 16.3 | 103 | 174 | 11.3 | 0.385 |  | 6.04 | 7 | 0.045 | 6 | 7 |  | 6.03 | 8 | [8 empty] | 0.038 | [14 empty] | 0.024 | 1 | 0.51 |  | 0.037 | 0.015 | 1 | 0.56 |  | 0.026 | 1 | 0.85 | [38 empty] | 7600 | [6 empty] | 0 | 0 | 0 | 150 | 360 | 360 | 780 | 300 | 720 | 700 | 680 | 700 | 750 |  | 1000 | 990 | 960 | 84 | 110 | 12 | 1300 | 245 | 255 | 48 | 62 | 6 | 640 | 110 | 255 |  | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 3:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
4:00 | [72 empty] | 43496.426 | 2,3,5 | 40 | 5.4 | 10.8 | 11.8 | 28 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 12.6835 | 1,3 | 10.8058 | 23.4893 | 2.7288 | 43496.426 | 63.5784 | 6640.6388 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97211 | 1.7907 | 1.5866 | 0.26763 | 0.11269 | 0.23946 | 0.23946 | 0.20627 | 0.21272 | 1.5218 | 1 | 0.059428 | 0.058822 | 0.041788 | 1.0834 | 0.54761 | 0.099646 | 3.701 | 0.57677 | 4.36 | 1.0925 | 0.53174 | 0.10014 | 3.4099 | 0.54199 | 6.6445 |  | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 4:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
5:00 | [53 empty] | 7.29 | 0.06 | 1 | 4.5 | 9.8 |  |  |  | 7.5 | 0.055 | 1 | 4.8 | 10.8 |  |  |  | 4.3 | 3.7 | 2.7 | [18 empty] | 7281 | [6 empty] | 0 | 0 | 0 | 190 | 350 | 360 | 760 | 320 | 680 | 680 | 640 | 660 | 800 |  | 980 | 970 | 800 | 82 | 110 | 12 | 1200 | 220 | 260 | 48 | 62 | 7 | 600 | 120 | 230 |  | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 5:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
6:00 | [72 empty] | 43496.8282 | 2,3,5 | 40 | 5.4 | 10.8 | 11.8 | 28 | 8.7 | 8.7 | 10.1 | 27.5 | ,1,3 | 10.849 | 1,3 | 13.7822 | 24.6312 | 0 | 43496.8282 | 62.8711 | 6148.7396 | 0 | 697.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4838 | 1.5349 | 1.5866 | 0.23241 | 0.21128 | 0.23946 | 0.23946 | 0.20627 | 0.21272 | 1.5218 | 0 | 0.059428 | 0.059428 | 0.044922 | 1.0834 | 0.54761 | 0.099646 | 3.7747 | 0.65542 | 4.863 | 1.0925 | 0.53174 | 0.10014 | 3.3503 | 0.58715 | 7.2223 |  | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 6:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
7:00 | 6.61 | 16 | 17 | 16.4 | 89 | 176 | 11.5 | 0.361 |  | 5.91 | 7 | 0.043 | 5.91 | 7 |  | 5.89 | 7 | [8 empty] | 0.039 | [14 empty] | 0.018 | 1 | 0.54 |  | 0.036 | 0.016 | 1 | 0.56 |  | 0.023 | 1 | 0.7 | [38 empty] | 7200 | [6 empty] | 0 | 0 | 0 | 290 | 300 | 360 | 660 | 600 | 680 | 680 | 640 | 660 | 800 |  | 980 | 980 | 860 | 82 | 110 | 12 | 1230 | 250 | 290 | 48 | 62 | 7 | 620 | 130 | 250 |  | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 7:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
8:00 | [127 empty] | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 8:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
9:00 | [8 empty] | 0.042 | [9 empty] | 6.1 | 0.418 | 4 | 0.72 | 10.5 | 5.4 | 0.4384 |  | 6.05 | 0.447 | 4 | 0.83 | 10 | 10.8 | 0.75679 | 6.03 | 0.716 | 6 | 0.68 | 12.3 | 11.8 | 0.77556 |  |  |  | 0.018 |  |  |  |  | 0.013 |  |  |  | 0.017 | 7.22 | 0.05 | 1 | 4.5 | 10.2 | 21 | 40 | 0.017 | 7.17 | 0.054 | 1 | 4.1 | 10.7 | 20 | 41 | 0.018 | 4.3 | 3.5 | 4.3 | [55 empty] | 9:00 | 0.72 | 5.4 | 47.1111 | 33.92 | 6.1 | 10.5 | 15 | 2.2613 | 10 | 6.5 | 0.3184 | 9:00 | 0.83 | 10.8 | 23.5556 | 19.5511 | 6.05 | 10 | 15 | 1.3034 | 10 | 6.5 | 0.63679 | 9:00 | 0.68 | 11.8 | 22.8814 | 15.5593 | 6.03 | 12.3 | 15 | 1.0373 | 10 | 6.5 | 0.65556
10:00 | [127 empty] | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 10:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
11:00 | 6.66 | 17 | 17 | 16.2 | 88 | 175 | 10.9 | 0.348 |  | 6.03 | 7 | 0.042 | 6.01 | 8 |  | 6.01 | 8 | [8 empty] | 0.034 | [14 empty] | 0.027 | 1 | 0.59 |  | 0.033 | 0.016 | 1 | 0.51 |  | 0.019 | 1 | 0.55 | [75 empty] | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 11:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
12:00 | [127 empty] | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 12:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
13:00 | [18 empty] | 6.08 | 0.408 | 4 | 0.84 | 11.4 | 5.5 | 0.44429 |  | 6.09 | 0.578 | 5 | 0.75 | 10.3 | 10.6 | 0.745 | 6.09 | 0.602 | 5 | 0.69 | 12.3 | 11.8 | 0.77556 | [13 empty] | 7.23 | 0.061 | 1 | 4.4 | 9.9 |  |  |  | 7.12 | 0.059 | 1 | 3.7 | 11.5 |  |  |  | 4.3 | 3.4 | 2.5 | [55 empty] | 13:00 | 0.84 | 5.5 | 46.2545 | 38.8538 | 6.08 | 11.4 | 15 | 2.5903 | 10 | 6.5 | 0.32429 | 13:00 | 0.75 | 10.6 | 24 | 18 | 6.09 | 10.3 | 15 | 1.2 | 10 | 6.5 | 0.625 | 13:00 | 0.69 | 11.8 | 22.8814 | 15.7881 | 6.09 | 12.3 | 15 | 1.0525 | 10 | 6.5 | 0.65556
14:00 | [126 empty] | #REF! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 14:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
15:00 | 6.68 | 16 | 17 | 15.9 | 92 | 173 | 11.9 | 0.37 |  | 6.13 | 10 | 0.048 | 6.2 | 10 |  | 6.15 | 11 | [8 empty] | 0.044 | [14 empty] | 0.023 | 1 | 0.49 |  | 0.042 | 0.015 | 1 | 0.39 |  | 0.02 | 1 | 0.57 | [75 empty] | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 15:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
16:00 | [127 empty] | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 16:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
17:00 | [53 empty] | 7.64 | 0.057 | 1 | 4.1 | 9.6 |  |  |  | 7.57 | 0.065 | 1 | 3.8 | 10.9 |  |  |  | 4.2 | 3.5 | 2.8 | [55 empty] | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 17:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
18:00 | [127 empty] | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 18:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
19:00 | 6.65 | 17 | 17 | 15.3 | 94 | 171 | 11.8 | 0.378 |  | 6.19 | 9 | 0.049 | 6.22 | 8 |  | 6.17 | 9 | [8 empty] | 0.038 | [14 empty] | 0.023 | 1 | 0.5 |  | 0.41 | 0.01 | 1 | 0.51 |  | 0.019 | 1 | 0.63 | [75 empty] | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 19:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
20:00 | [127 empty] | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 20:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
21:00 | [8 empty] | 0.043 | [9 empty] | 6.24 | 0.339 | 4 | 0.72 | 10.7 | 5.4 | 0.4384 |  | 6.28 | 0.215 | 5 | 0.76 | 10.1 | 10.8 | 0.75679 | 6.23 | 0.565 | 5 | 0.69 | 12.4 | 11.8 | 0.77556 |  |  |  | 0.014 | [9 empty] | 7.81 | 0.064 | 1 | 4.2 | 10.3 | 20 | 41 | 0.011 | 7.68 | 0.059 | 1 | 4 | 10.9 | 20 | 42 | 0.01 | 4.3 | 3.5 | 2.9 | [55 empty] | 21:00 | 0.72 | 5.4 | 47.1111 | 33.92 | 6.24 | 10.7 | 15 | 2.2613 | 10 | 6.5 | 0.3184 | 21:00 | 0.76 | 10.8 | 23.5556 | 17.9022 | 6.28 | 10.1 | 15 | 1.1935 | 10 | 6.5 | 0.63679 | 21:00 | 0.69 | 11.8 | 22.8814 | 15.7881 | 6.23 | 12.4 | 15 | 1.0525 | 10 | 6.5 | 0.65556
22:00 | [72 empty] | DOSE |  | TOTAL | 22.6 | 44.2 | 48.6 | 115.4 | 34.8 | 34.8 | 40.4 | 110 | 0 | 47.0462 | 0 | 52.3642 | 99.4104 | 8.1864 | TOTAL | 251.5802 | 22627.3616 | 0 | 2791.1894 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9908 | 7.0094 | 6.3463 | 1.0028 | 0.51735 | 0.96356 | 0.9501 | 0.82632 | 0.85138 | 5.897 | 9 | 0.24014 | 0.23832 | 0.187 | 4.3863 | 2.1905 | 0.39858 | 15.2621 | 2.5168 | 17.7752 | 4.3701 | 2.127 | 0.37195 | 13.8214 | 2.1228 | 28.6004 |  | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 22:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE!
23:00 | 6.61 | 17 | 17 | 15.6 | 96 | 172 | 11 | 0.43 |  | 6.2 | 9 | 0.046 | 6.15 | 9 |  | 6.12 | 9 | [8 empty] | 0.037 | [14 empty] | 0.022 | 1 | 0.51 |  | 0.035 | 0.007 | 1 | 0.54 |  | 0.018 | 1 | 0.65 | [22 empty] | AVERAGE | 5.65 | 11.05 | 12.15 | 28.85 | 8.7 | 8.7 | 10.1 | 27.5 |  | 11.7616 |  | 13.091 | 24.8526 | 2.0466 | AVERAGE | 62.8951 | 5656.8404 |  | 697.7974 | 0 | 0 | 0 |  |  |  | 0.9977 | 1.7524 | 1.5866 | 0.25071 | 0.12934 | 0.24089 | 0.23752 | 0.20658 | 0.21285 | 1.4742 | 2.25 | 0.060035 | 0.05958 | 0.046751 | 1.0966 | 0.54761 | 0.099646 | 3.8155 | 0.62921 | 4.4438 | 1.0925 | 0.53174 | 0.092986 | 3.4554 | 0.5307 | 7.1501 |  | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | 23:00 |  |  | #VALUE! | #VALUE! |  |  | 0 |  | 25 | 7 | #VALUE! | MIN CT OF THE DAY
TOTAL | 39.9 | 101 | 102 | 95.7 | 562 | 1041 | 68.4 | 2.272 | 0.085 | 36.5 | 49 | 0.273 | 36.49 | 49 | 0 | 36.37 | 52 | 0 | 24.61 | 1.473 | 15 | 2.95 | 43.6 | 22.2 | 1.789 | 0.23 | 24.52 | 1.484 | 18 | 3.05 | 41.2 | 43.5 | 3.0449 | 24.47 | 2.581 | 20 | 2.78 | 49.7 | 47.9 | 3.1411 | 0.137 | 6 | 3.14 | 0.032 | 0.593 | 0.079 | 6 | 3.07 | 0.013 | 0.125 | 6 | 3.95 | 0.017 | 44.79 | 0.356 | 6 | 26.3 | 59.6 | 41 | 81 | 0.028 | 44.3 | 0.359 | 6 | 24.2 | 65.8 | 40 | 83 | 0.028 | 25.7 | 21.2 | 18 |  |  | MINIMUM | 5.4 | 10.8 | 11.8 | 28 | 8.7 | 8.7 | 10.1 | 27.5 |  | 10.849 |  | 10.8058 | 23.4893 | 0 | MINIMUM | 62.5653 | 4918.9916 |  | 697.7974 | [6 empty] | 0.76746 | 1.5349 | 1.5866 | 0.23241 | 0.09669 | 0.23946 | 0.23559 | 0.20627 | 0.21272 | 1.4267 | 0 | 0.059428 | 0.058822 | 0.041788 | 1.0834 | 0.54761 | 0.099646 | 3.701 | 0.57677 | 4.2761 | 1.0925 | 0.53174 | 0.085834 | 3.3503 | 0.49682 | 6.6445 |  | MIN | 0.67 | 5.9 | 43.1186 | 28.8895 | 6.19 | 11 | 15 | 1.926 |  |  |  | MIN | 0.71 | 11.3 | 22.5133 | 15.9844 | 6.1 | 10.8 | 15 | 1.0656 |  |  |  | MIN | 0.72 | 12.5 | 21.6 | 15.552 | 6.12 | 12.7 | 15 | 1.0368 |  |  |  | 1.0368
AVERAGE | 6.65 | 16.8333 | 17 | 15.95 | 93.6667 | 173.5 | 11.4 | 0.37867 | 0.0425 | 6.0833 | 8.1667 | 0.0455 | 6.0817 | 8.1667 |  | 6.0617 | 8.6667 |  | 6.1525 | 0.36825 | 3.75 | 0.7375 | 10.9 | 5.55 | 0.44724 | 0.038333 | 6.13 | 0.371 | 4.5 | 0.7625 | 10.3 | 10.875 | 0.76121 | 6.1175 | 0.64525 | 5 | 0.695 | 12.425 | 11.975 | 0.78528 | 0.022833 | 1 | 0.52333 | 0.016 | 0.098833 | 0.013167 | 1 | 0.51167 | 0.013 | 0.020833 | 1 | 0.65833 | 0.017 | 7.465 | 0.059333 | 1 | 4.3833 | 9.9333 | 20.5 | 40.5 | 0.014 | 7.3833 | 0.059833 | 1 | 4.0333 | 10.9667 | 20 | 41.5 | 0.014 | 4.2833 | 3.5333 | 3 |  |  | MAXIMUM | 5.9 | 11.3 | 12.5 | 29.7 | 8.7 | 8.7 | 10.1 | 27.5 |  | 12.6835 |  | 15.9955 | 26.9741 | 2.7288 | MAXIMUM | 63.5784 | 6640.6388 |  | 697.7974 | [6 empty] | 1.4838 | 1.8419 | 1.5866 | 0.26763 | 0.21128 | 0.24232 | 0.23946 | 0.20689 | 0.21297 | 1.5218 | 4 | 0.060641 | 0.060035 | 0.050146 | 1.1098 | 0.54761 | 0.099646 | 3.8932 | 0.65542 | 4.863 | 1.0925 | 0.53174 | 0.10014 | 3.5306 | 0.58715 | 7.3668
MINIMUM | 6.61 | 16 | 17 | 15.3 | 88 | 171 | 10.9 | 0.348 | 0.042 | 5.91 | 7 | 0.042 | 5.91 | 7 |  | 5.89 | 7 |  | 6.08 | 0.308 | 3 | 0.67 | 10.5 | 5.4 | 0.4384 | 0.034 | 6.05 | 0.215 | 4 | 0.71 | 10 | 10.6 | 0.745 | 6.03 | 0.565 | 4 | 0.68 | 12.3 | 11.8 | 0.77556 | 0.018 | 1 | 0.49 | 0.014 | 0.033 | 0.007 | 1 | 0.39 | 0.013 | 0.018 | 1 | 0.55 | 0.017 | 7.22 | 0.05 | 1 | 4.1 | 9.6 | 20 | 40 | 0.011 | 7.12 | 0.054 | 1 | 3.7 | 10.7 | 20 | 41 | 0.01 | 4.2 | 3.4 | 2.5 | [15 empty] | MIL/MIN |  | TOTAL | 29681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 1370 | 1440 | 2980 | 1520 | 2800 | 2760 | 2640 | 2720 | 3100 | 0 | 3960 | 3930 | 3580 | 332 | 440 | 48 | 5030 | 960 | 1060 | 192 | 248 | 26 | 2500 | 470 | 990
MAXIMUM | 6.69 | 18 | 17 | 16.4 | 103 | 176 | 11.9 | 0.43 | 0.043 | 6.2 | 10 | 0.049 | 6.22 | 10 |  | 6.17 | 11 |  | 6.24 | 0.418 | 4 | 0.84 | 11.4 | 5.9 | 0.46788 | 0.044 | 6.28 | 0.578 | 5 | 0.83 | 10.8 | 11.3 | 0.78627 | 6.23 | 0.716 | 6 | 0.72 | 12.7 | 12.5 | 0.81444 | 0.027 | 1 | 0.59 | 0.018 | 0.41 | 0.016 | 1 | 0.56 | 0.013 | 0.026 | 1 | 0.85 | 0.017 | 7.81 | 0.064 | 1 | 4.6 | 10.3 | 21 | 41 | 0.017 | 7.68 | 0.067 | 1 | 4.8 | 11.5 | 20 | 42 | 0.018 | 4.3 | 3.7 | 4.3 | [17 empty] | AVERAGE | 7420.25 | [9 empty] | 195 | 342.5 | 360 | 745 | 380 | 700 | 690 | 660 | 680 | 775 |  | 990 | 982.5 | 895 | 83 | 110 | 12 | 1257.5 | 240 | 265 | 48 | 62 | 6.5 | 625 | 117.5 | 247.5
# 0F DAYS IN THE MONTH |  | 31 |  |  |  | TOTAL AVG COAG PH: | [5 empty] | 6.0756 |  | TOTAL AVG COAG ALK: |  |  |  | 8.3333 |  | TOTAL MAX SETTLED NTU: |  |  |  | 0.716 |  |  | TOTAL MIN SETTLED DISEN.: |  |  | 0.67 | [5 empty] | 6.1333 |  |  |  |  | 0.027 |  |  |  |  | 0.67 | [6 empty] | 0.027 | [16 empty] | Pump Station MIN |  | 2.5 | [17 empty] | MINIMUM | 7200 | [9 empty] | 150 | 300 | 360 | 660 | 300 | 680 | 680 | 640 | 660 | 750 |  | 980 | 970 | 800 | 82 | 110 | 12 | 1200 | 220 | 255 | 48 | 62 | 6 | 600 | 110 | 230
[90 empty] | MAXIMUM | 7600 | [9 empty] | 290 | 360 | 360 | 780 | 600 | 720 | 700 | 680 | 700 | 800 |  | 1000 | 990 | 960 | 84 | 110 | 12 | 1300 | 250 | 290 | 48 | 62 | 7 | 640 | 130 | 255
MIN OF THE DAY OF ALL THREE PLANTS
[90 empty] | BULK TANK Chemical Inventory | [50 empty] | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
[73 empty] | FINISHED 1 | 13.382 |  | TOTAL MGD: |  | 0.015 |  |  | FINISHED SOUTH 1 |  | START: | 23827275 |  | END: | 23827290 |  |  | Alum | 6100 | 10792 | 10792 | 11101 | 11101 | 0 | [44 empty] | 0.72 | 12.5 | 21.6 | 15.552 | 6.12 | 12.7 | 15 | 1.0368
[73 empty] | FINISHED 2 | 13.299 |  | TOTAL MGD: |  | 13.367 |  |  | FINISHED SOUTH 2 |  | START: | 44157769 |  | END: | 44171136 |  |  | Caustic | 5850 | 7793 | 7793
[73 empty] | TOTAL RAW | 28.127 |  | TOTAL MGD: |  | 4.846 |  |  | FINISHED CONWAY |  | START: | 10360444 |  | END: | 10365290 |  |  | Hypochlorite | 19 |  | 45
[76 empty] | TOTAL MGD: |  | 8.453 |  |  | FINISHED PERRY |  | START: | 34070893 |  | END: | 34079346 |  |  | Phosphate | 1305
[76 empty] | TOTAL MGD: |  | 5.562 |  |  | RAW PLANT 1 |  | START: | 31220749 |  | END: | 31226311 |  |  | Fluoride | 2000 |  |  |  |  | cal %
[76 empty] | TOTAL MGD: |  | 10.8 |  |  | RAW PLANT 2 |  | START: | 31140393 |  | END: | 31151193 |  |  | Cal~Flo | 13.4 |  |  |  | 0 | 25
[76 empty] | TOTAL MGD: |  | 11.765 |  |  | RAW PLANT 3 |  | START: | 7810704 |  | END: | 7822469 |  |  | Zinc | 775
[76 empty] | TOTAL MGD: |  | 1.125 |  |  | DECANT |  | START: | 1891608 |  | END: | 1892733 |  |  | Polymer | 30
[76 empty] | TOTAL MGD: |  | 1.5822 |  |  | BLOW DOWN |  | START: | 9175.5022 |  | END: | 9177.0844 |  |  | NH3 | 9.35 |  | BI-SUL | 900
[87 empty] | 0 |  |  | Lime | 0 |  | FILTER AIDE | 1
[82 empty] | BACKWASH WATER USED : | [7 empty] | Cabon | 670
23827290
44171136
10365290
34079346
31226311
31151193
7822469
1892733
9177.0844
Note on AP36: MAX OF ALL 3 PLANTS
Note on CJ40: IF THIS IS THE LAST DAY OF THE MONTH TYPE THESE NUMBERS TO NEW MONTH AT THE START COLUMN MONTH
Note on CM40: GEO PO# 150517 Phone: 1-800-453-2586
Note on CN40: Alum Bulk Tank 1 / 2
Note on CP40: Alum Bulk Tank 3 / 4
Note on CR40: TOWER
Note on CM41: Colonial PO# 150524 1-800-285-8593
Note on CN41: Caustic Bulk Tank in chem. Building
Note on CP41: Caustic Bulk Tank in Plant 3 biulding
Note on CM42: Oltrin PO#150518 Phone:1-910-410-1180 e-Mail: oltrincs@trinitymfg.com
Note on CN42: PREcl2 plant 1
Note on CP42: post Fin 1 cl2 building
Note on CM43: Shannon PO# 150527 1-843-744-7421
Note on CM44: Key Chemical PO# 150529 1-704-843-9873
Note on CM45: Burnett Lime PO# 150522 Phone:1-800-726-4187
Note on CN45: from day before
Note on CP45: Truck out
Note on CQ45: 12:00
Note on CM46: Shannon PO#150528 1-610-363-9090 E-Mail: h2odoc@shannonchem.com
Note on CM47: Lori Brenntag PO#150573 1-800-763-5056
Note on CM48: Brenntag PO#150521 Phone:1-843-744-7421
Note on CM49: Lhoist PO#150523 Phone:1-855-865-5719
Note on CN49: From computer lime / Carbon System
Note on CM50: Standard Purfication PO# 150575 1-888-616-5959
Note on CN50: From computer lime / Carbon System

## BULK TANK LEVEL
cal-flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday
| 2019-01-01 | 2019-01-02 | 2019-01-03 | 2019-01-04 | 2019-01-05 | 2019-01-06 | 2019-01-07 | 2019-01-08 | 2019-01-09 | 2019-01-10 | 2019-01-11 | 2019-01-12 | 2019-01-13 | 2019-01-14 | 2019-01-15 | 2019-01-16 | 2019-01-17 | 2019-01-18 | 2019-01-19 | 2019-01-20 | 2019-01-21 | 2019-01-22 | 2019-01-23 | 2019-01-24 | 2019-01-25 | 2019-01-26 | 2019-01-27 | 2019-01-28 | 2019-01-29 | 2019-01-30 | 2019-01-31
Alum1 | 360 | 4970 | 7269 | 4308 | 588 | 5085 | 3223 | 4034 | 6957 | 5233 | 5830 | 3060 | 7279 | 5692 | 7660 | 7350 | 8195 | 8827 | 4043 | 366 | 4011 | 5879 | 6411 | 8892 | 8891 | 6299 | 3623 | 5524 | 2934 | 9134 | 6100
Alum2 | 9791 | 11531 | 11142 | 11148 | 11151 | 9617 | 11163 | 11163 | 10934 | 10937 | 10934 | 10937 | 10392 | 10392 | 10174 | 10200 | 10200 | 10200 | 10200 | 10200 | 8976 | 11000 | 10792 | 10792 | 10795 | 10795 | 10789 | 10792 | 10795 | 10792 | 10792
Alum Tower | 877300% | 1188500% | 1162400% | 1161800% | 1161500% | 1100600% | 1024800% | 1024800% | 974700% | 1115100% | 1114500% | 1091600% | 960400% | 846000% | 1029500% | 1120000% | 1120000% | 1150000% | 1170000% | 1170000% | 1150000% | 1100000% | 1090400% | 1030300% | 1110100% | 1110400% | 1110400% | 1110400% | 1110400% | 1110100% | 1110100%
Caustic | 4980 | 4884 | 4821 | 4715 | 4642 | 4548 | 4496 | 4446 | 8015 | 7982 | 7805 | 7645 | 7460 | 7318 | 7283 | 7182 | 7138 | 7051 | 6940 | 6854 | 6785 | 6647 | 6575 | 6484 | 6414 | 6332 | 6242 | 6145 | 6073 | 5985 | 5850
Caustic | 6570 | 6517 | 6492 | 6470 | 6460 | 6427 | 6407 | 6372 | 6367 | 6372 | 8267 | 8262 | 8213 | 8200 | 8200 | 8147 | 8132 | 8104 | 8075 | 8080 | 8036 | 8014 | 8008 | 7952 | 7956 | 7956 | 7911 | 7906 | 7861 | 7819 | 7793
Hypochlorite | 14 | 22 | 21 | 20 | 20 | 17 | 16 | 19 | 18 | 17 | 15 | 21 | 20 | 18 | 17 | 14.5 | 19 | 18 | 16 | 14 | 17 | 16 | 9 | 8 | 6 | 12 | 12 | 11 | 14 | 19 | 19
Hypochlorite | 19 | 42 | 38 | 48 | 48 | 45 | 44 | 38 | 48 | 47 | 45 | 49 | 48 | 47 | 39 | 43.5 | 35.5 | 46.5 | 45 | 43.5 | 46 | 48 | 36 | 33 | 33 | 36 | 33 | 31 | 34 | 46 | 45
Phosphate | 2732 | 2643 | 2641 | 2537 | 2488 | 2451 | 2398 | 2373 | 2382 | 2354 | 2345 | 2242 | 2210 | 2168 | 2156 | 2055 | 1993 | 1999 | 1957 | 1946 | 1902 | 1843 | 1791 | 1747 | 1696 | 1692 | 1613 | 1550 | 1523 | 1468 | 1305
Fluoride | 3750 | 4000 | 3800 | 3800 | 3800 | 3800 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3100 | 3100 | 3000 | 2950 | 2950 | 2950 | 2950 | 2950 | 2900 | 2900 | 2750 | 2750 | 2750 | 2750 | 2750 | 2250 | 2250 | 2100 | 2000
Cal~Flo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zinc | 967 | 929 | 940 | 942 | 935 | 941 | 923 | 985 | 1005 | 962 | 946 | 786 | 786 | 791 | 781 | 786 | 781 | 786 | 805 | 804 | 809 | 801 | 785 | 815 | 787 | 794 | 793 | 785 | 818 | 788 | 775
Polymer | 19 | 19 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 15 | 15 | 15 | 15 | 15 | 31 | 31 | 31 | 31 | 30 | 30 | 30
NH3 | 7.71 | 7.63 | 7.39 | 7.23 | 7.19 | 7 | 6.22 | 13.7 | 13.53 | 13 | 13 | 13 | 13 | 12.5 | 12 | 12.06 | 11.92 | 11.76 | 11.59 | 11.45 | 11.29 | 11.11 | 10.89 | 10.74 | 10.57 | 10.36 | 10 | 9.94 | 10 | 9.56 | 9.35
Lime | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cabon | 650 | 650 | 600 | 666 | 602 | 628 | 630 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 587 | 585 | 760 | 720 | 650 | 737 | 717 | 761 | 650 | 650 | 650 | 698 | 698 | 698 | 678 | 670
filter aid | 2019-01-01: 3.0758

## AWOP 2018
2019-08-12 | Raw | Settled | Filter
Average | 12.9497 | 0.46757 | 0.037767
Max | 16.4 | 0.692 | 0.081
Count |  | 0 | 0 | Average Raw
AWOP Count |  | 0 | 0 | Per day
2019-01-01 | 9 | 0.286 | 0.032
2019-01-02 | 9.52 | 0.364 | 0.027
2019-01-03 | 8.96 | 0.352 | 0.026
2019-01-04 | 9.71 | 0.36 | 0.081
2019-01-05 | 10.7 | 0.447 | 0.038
2019-01-06 | 10.4 | 0.49 | 0.028
2019-01-07 | 11.7 | 0.464 | 0.024
2019-01-08 | 11.4 | 0.438 | 0.057
2019-01-09 | 12.8 | 0.466 | 0.034
2019-01-10 | 11.1 | 0.488 | 0.033
2019-01-11 | 10.3 | 0.393 | 0.028
2019-01-12 | 11.8 | 0.44 | 0.052
2019-01-13 | 12.2 | 0.437 | 0.029
2019-01-14 | 12.2 | 0.44 | 0.029
2019-01-15 | 12.2 | 0.494 | 0.06
2019-01-16 | 12.3 | 0.525 | 0.027
2019-01-17 | 13.1 | 0.487 | 0.046
2019-01-18 | 15.5 | 0.54 | 0.053
2019-01-19 | 16.1 | 0.58 | 0.033
2019-01-20 | 15.9 | 0.53 | 0.043
2019-01-21 | 15.2 | 0.518 | 0.04
2019-01-22 | 15 | 0.63 | 0.031
2019-01-23 | 15 | 0.531 | 0.04
2019-01-24 | 14.8 | 0.401 | 0.04
2019-01-25 | 14.9 | 0.408 | 0.031
2019-01-26 | 14.9 | 0.427 | 0.024
2019-01-27 | 14.8 | 0.474 | 0.039
2019-01-28 | 14.9 | 0.444 | 0.023
2019-01-29 | 15.7 | 0.481 | 0.019
2019-01-30 | 16.4 | 0.692 | 0.066
2019-01-31

## REMOVAL
PLT1
2019-08-12 08:45 |  | DAILY AVG | RAW | RAW | RAW | RAW | RAW | RAW | RAW | RAW | avg last 12 | RAW | TREATED | TREATED | TREATED | Percent | Calculated Raw | Alum Dose: | Alum Dose | Treated pH | Settled UV | FILTER UV
Date | Time | ALUM DOSE | PH | ALK | HARDNESS | NTU | TRUE | APPARENT | TEMP | UV | raw uv | MN | PH | ALKALINITY | Treated UV | Removal | TOC, mg/L | TOC Ratio | Divided By 100 | Divided By 10
2019-01-01 | 0:00 | 90.2474
| 1:00 | 90.2474 | [8 empty] | #DIV/0!
| 2:00 | 90.2474 | [8 empty] | #DIV/0!
| 3:00 | 90.2474 | 6.25 | 12 | 14 | 8.99 | 115 | 158 | 15.5 | 0.485 | 0.485 |  | 6.07 | 8 | 0.075 | 84.54% | 12.7632 | 7.0709 | 0.90247 | 0.607 | 0.053 | 0.051
| 4:00 | 90.2474 | [8 empty] | 0.485
| 5:00 | 90.2474 | [8 empty] | 0.485
| 6:00 | 90.2474 | [8 empty] | 0.485
| 7:00 | 90.2474 | 6.27 | 11 | 14 | 8.66 | 116 | 159 | 15.1 | 0.498 | 0.4915 |  | 6 | 10 | 0.072 | 85.54% | 13.1053 | 6.8863 | 0.90247 | 0.6 | 0.051 | 0.05
| 8:00 | 90.2474 | [8 empty] | 0.4915
| 9:00 | 90.2474 | [8 empty] | 0.4915 | 0.056
| 10:00 | 90.2474 | [8 empty] | 0.4915
| 11:00 | 90.2474 | 6.28 | 16 | 15 | 8.72 | 116 | 156 | 15.6 | 0.497 | 0.49333 |  | 6.02 | 10 | 0.074 | 85.11% | 13.0789 | 6.9002 | 0.90247 | 0.602 | 0.05 | 0.053
| 12:00 | 90.2474 | [8 empty] | 0.49333
| 13:00 | 90.2474 | [8 empty] | 0.49333
| 14:00 | 90.2474 | [8 empty] | 0.49333
| 15:00 | 90.2474 | 6.44 | 18 | 14 | 8.75 | 112 | 158 | 16 | 0.458 | 0.4845 |  | 6.05 | 12 | 0.056 | 87.77% | 12.0526 | 7.4878 | 0.90247 | 0.605 | 0.039 | 0.039
| 16:00 | 90.2474 | [8 empty] | 0.48433
| 17:00 | 90.2474 | [8 empty] | 0.48433
| 18:00 | 90.2474 | [8 empty] | 0.48433
| 19:00 | 90.2474 | 6.23 | 14 | 18 | 8.25 | 115 | 156 | 15.9 | 0.491 | 0.486 |  | 5.96 | 8 | 0.076 | 84.52% | 12.9211 | 6.9845 | 0.90247 | 0.596 | 0.051 | 0.049
| 20:00 | 90.2474 | [8 empty] | 0.486
| 21:00 | 90.2474 | [8 empty] | 0.482 | 0.032
| 22:00 | 90.2474 | [8 empty] | 0.482
| 23:00 | 90.2474 | 6.29 | 16 | 17 | 9 | 116 | 159 | 16.2 | 0.489 | 0.48375 |  | 5.92 | 9 | 0.06 | 87.73% | 12.8684 | 7.0131 | 0.90247 | 0.592 | 0.047 | 0.049
2019-01-02 | 0:00 | 90.3794 | [8 empty] | 0.48375
| 1:00 | 90.3794 | [8 empty] | 0.47933
| 2:00 | 90.3794 | [8 empty] | 0.47933
| 3:00 | 90.3794 | 6.29 | 12 | 14 | 9.52 | 118 | 162 | 16.2 | 0.489 | 0.48175 |  | 5.99 | 7 | 0.075 | 84.66% | 12.8684 | 7.0233 | 0.90379 | 0.599 | 0.05 | 0.05
| 4:00 | 90.3794 | [8 empty] | 0.48175
| 5:00 | 90.3794 | [8 empty] | 0.48967
| 6:00 | 90.3794 | [8 empty] | 0.48967
| 7:00 | 90.3794 | 6.27 | 12 | 13 | 8.89 | 119 | 160 | 15.8 | 0.512 | 0.49525 |  | 5.89 | 7 | 0.06 | 88.28% | 13.4737 | 6.7078 | 0.90379 | 0.589 | 0.051 | 0.057
| 8:00 | 90.3794 | [8 empty] | 0.49525
| 9:00 | 90.3794 | [8 empty] | 0.49667 | 0.044
| 10:00 | 90.3794 | [8 empty] | 0.49667
| 11:00 | 90.3794 | 6.28 | 12 | 14 | 8.95 | 110 | 163 | 16.1 | 0.487 | 0.49425 |  | 5.89 | 7 | 0.059 | 87.89% | 12.8158 | 7.0522 | 0.90379 | 0.589 | 0.055 | 0.057
| 12:00 | 90.3794 | [8 empty] | 0.49425
| 13:00 | 90.3794 | [8 empty] | 0.496
| 14:00 | 90.3794 | [8 empty] | 0.496
| 15:00 | 90.3794 | 6.29 | 13 | 14 | 8.61 | 115 | 159 | 16.2 | 0.5 | 0.497 |  | 5.98 | 8 | 0.06 | 88% | 13.1579 | 6.8688 | 0.90379 | 0.598 | 0.06 | 0.056
| 16:00 | 90.3794 | [8 empty] | 0.497
| 17:00 | 90.3794 | [8 empty] | 0.49967
| 18:00 | 90.3794 | [8 empty] | 0.49967
| 19:00 | 90.3794 | 6.32 | 11 | 13 | 8 | 120 | 161 | 16 | 0.517 | 0.504 |  | 6.07 | 7 | 0.062 | 88.01% | 13.6053 | 6.643 | 0.90379 | 0.607 | 0.05 | 0.05
| 20:00 | 90.3794 | [8 empty] | 0.504
| 21:00 | 90.3794 | [8 empty] | 0.50133 | 0.031
| 22:00 | 90.3794 | [8 empty] | 0.50133
| 23:00 | 90.3794 | 6.28 | 11 | 14 | 8.65 | 120 | 158 | 16.1 | 0.516 | 0.505 |  | 6.12 | 7 | 0.061 | 88.18% | 13.5789 | 6.6558 | 0.90379 | 0.612 | 0.049 | 0.048
2019-01-03 | 24:00 | 90.5974 | [8 empty] | 0.505
| 25:00 | 90.5974 | [8 empty] | 0.511
| 26:00 | 90.5974 | [8 empty] | 0.511
| 27:00 | 90.5974 | 6.33 | 11 | 13 | 8.47 | 122 | 164 | 15.9 | 0.523 | 0.514 |  | 6.1 | 7 | 0.072 | 86.23% | 13.7632 | 6.5826 | 0.90597 | 0.61 | 0.055 | 0.051
| 28:00 | 90.5974 | [8 empty] | 0.514
| 29:00 | 90.5974 | [8 empty] | 0.51867
| 30:00 | 90.5974 | [8 empty] | 0.51867
| 31:00 | 90.5974 | 6.27 | 12 | 13 | 8.71 | 114 | 160 | 15.9 | 0.502 | 0.5145 |  | 6.03 | 7 | 0.061 | 87.85% | 13.2105 | 6.858 | 0.90597 | 0.603 | 0.055 | 0.057
| 32:00 | 90.5974 | [8 empty] | 0.5145
| 33:00 | 90.5974 | [8 empty] | 0.51367 | 0.037
| 34:00 | 90.5974 | [8 empty] | 0.51367
| 35:00 | 90.5974 | 6.24 | 12 | 12 | 8.65 | 111 | 156 | 16.1 | 0.486 | 0.50675 |  | 5.97 | 7 | 0.087 | 82.1% | 12.7895 | 7.0837 | 0.90597 | 0.597 | 0.057 | 0.053
| 36:00 | 90.5974 | [8 empty] | 0.50675
| 37:00 | 90.5974 | [8 empty] | 0.50367
| 38:00 | 90.5974 | [8 empty] | 0.50367
| 39:00 | 90.5974 | 6.25 | 12 | 13 | 8.96 | 110 | 155 | 16.5 | 0.479 | 0.4975 |  | 6.06 | 8 | 0.062 | 87.06% | 12.6053 | 7.1873 | 0.90597 | 0.606 | 0.06 | 0.054
| 40:00 | 90.5974 | [8 empty] | 0.4975
| 41:00 | 90.5974 | [8 empty] | 0.489
| 42:00 | 90.5974 | [8 empty] | 0.489
| 43:00 | 90.5974 | 6.31 | 12 | 12 | 8.2 | 113 | 158 | 16.5 | 0.506 | 0.49325 |  | 6.1 | 8 | 0.056 | 88.93% | 13.3158 | 6.8038 | 0.90597 | 0.61 | 0.052 | 0.05
| 44:00 | 90.5974 | [8 empty] | 0.49325
| 45:00 | 90.5974 | [8 empty] | 0.49033 | 0.032
| 46:00 | 90.5974 | [8 empty] | 0.49033
| 47:00 | 90.5974 | 6.35 | 12 | 12 | 8.4 | 120 | 157 | 16.4 | 0.518 | 0.49725 |  | 6.02 | 8 | 0.067 | 87.07% | 13.6316 | 6.6461 | 0.90597 | 0.602 | 0.054 | 0.052
2019-01-04 | 48:00 | 90.4659 | [8 empty] | 0.49725
| 49:00 | 90.4659 | [8 empty] | 0.501
| 50:00 | 90.4659 | [8 empty] | 0.501
| 51:00 | 90.4659 | 6.21 | 12 | 12 | 8.47 | 122 | 160 | 15.4 | 0.527 | 0.5075 |  | 6.1 | 7 | 0.068 | 87.1% | 13.8684 | 6.5232 | 0.90466 | 0.61 | 0.058 | 0.053
| 52:00 | 90.4659 | [8 empty] | 0.5075
| 53:00 | 90.4659 | [8 empty] | 0.517
| 54:00 | 90.4659 | [8 empty] | 0.517
| 55:00 | 90.4659 | 6.27 | 13 | 13 | 9.28 | 122 | 162 | 16.5 | 0.506 | 0.51425 |  | 6.03 | 8 | 0.058 | 88.54% | 13.3158 | 6.7939 | 0.90466 | 0.603 | 0.049 | 0.043
| 56:00 | 90.4659 | [8 empty] | 0.51425
| 57:00 | 90.4659 | [8 empty] | 0.517 | 0.043
| 58:00 | 90.4659 | [8 empty] | 0.517
| 59:00 | 90.4659 | 6.28 | 13 | 13 | 9.39 | 106 | 166 | 17 | 0.459 | 0.5025 |  | 6.11 | 9 | 0.067 | 85.4% | 12.0789 | 7.4895 | 0.90466 | 0.611 | 0.056 | 0.058
| 60:00 | 90.4659 | [8 empty] | 0.5025
| 61:00 | 90.4659 | [8 empty] | 0.49733
| 62:00 | 90.4659 | [8 empty] | 0.49733
| 63:00 | 90.4659 | 6.29 | 13 | 13 | 9.61 | 118 | 167 | 16.3 | 0.484 | 0.494 |  | 6.03 | 9 | 0.056 | 88.43% | 12.7368 | 7.1027 | 0.90466 | 0.603 | 0.056 | 0.052
| 64:00 | 90.4659 | [8 empty] | 0.494
| 65:00 | 90.4659 | [8 empty] | 0.483
| 66:00 | 90.4659 | [8 empty] | 0.483
| 67:00 | 90.4659 | 6.21 | 12 | 14 | 9.71 | 123 | 163 | 16.4 | 0.516 | 0.49125 |  | 6.14 | 8 | 0.064 | 87.6% | 13.5789 | 6.6622 | 0.90466 | 0.614 | 0.057 | 0.055
| 68:00 | 90.4659 | [8 empty] | 0.49125
| 69:00 | 90.4659 | [8 empty] | 0.48633 | 0.038
| 70:00 | 90.4659 | [8 empty] | 0.48633
| 71:00 | 90.4659 | 6.33 | 12 | 13 | 9.45 | 121 | 166 | 16.6 | 0.514 | 0.49325 |  | 6.15 | 8 | 0.055 | 89.3% | 13.5263 | 6.6881 | 0.90466 | 0.615 | 0.049 | 0.045
2019-01-05 | 72:00 | 90.8464 | [8 empty] | 0.49325
| 73:00 | 90.8464 | [8 empty] | 0.50467
| 74:00 | 90.8464 | [8 empty] | 0.50467
| 75:00 | 90.8464 | 6.29 | 13 | 13 | 9.15 | 123 | 161 | 16.6 | 0.523 | 0.50925 |  | 6.13 | 9 | 0.062 | 88.15% | 13.7632 | 6.6007 | 0.90846 | 0.613 | 0.054 | 0.052
| 76:00 | 90.8464 | [8 empty] | 0.50925
| 77:00 | 90.8464 | [8 empty] | 0.51767
| 78:00 | 90.8464 | [8 empty] | 0.51767
| 79:00 | 90.8464 | 6.25 | 13 | 13 | 9.27 | 119 | 166 | 16.4 | 0.505 | 0.5145 |  | 6.14 | 10 | 0.063 | 87.52% | 13.2895 | 6.836 | 0.90846 | 0.614 | 0.056 | 0.054
| 80:00 | 90.8464 | [8 empty] | 0.5145
| 81:00 | 90.8464 | [8 empty] | 0.514 | 0.037
| 82:00 | 90.8464 | [8 empty] | 0.514
| 83:00 | 90.8464 | 6.28 | 12 | 13 | 9.42 | 117 | 163 | 16.6 | 0.492 | 0.5085 |  | 6.07 | 9 | 0.056 | 88.62% | 12.9474 | 7.0166 | 0.90846 | 0.607 | 0.046 | 0.052
| 84:00 | 90.8464 | [8 empty] | 0.5085
| 85:00 | 90.8464 | [8 empty] | 0.50667
| 86:00 | 90.8464 | [8 empty] | 0.50667
| 87:00 | 90.8464 | 6.36 | 13 | 13 | 10.7 | 121 | 170 | 17.1 | 0.499 | 0.50475 |  | 6.17 | 10 | 0.057 | 88.58% | 13.1316 | 6.9182 | 0.90846 | 0.617 | 0.053 | 0.055
| 88:00 | 90.8464 | [8 empty] | 0.50475
| 89:00 | 90.8464 | [8 empty] | 0.49867
| 90:00 | 90.8464 | [8 empty] | 0.49867
| 91:00 | 90.8464 | 6.32 | 13 | 13 | 9.78 | 124 | 161 | 16.7 | 0.508 | 0.501 |  | 6.04 | 9 | 0.05 | 90.16% | 13.3684 | 6.7956 | 0.90846 | 0.604 | 0.045 | 0.04
| 92:00 | 90.8464 | [8 empty] | 0.501
| 93:00 | 90.8464 | [8 empty] | 0.49967 | 0.041
| 94:00 | 90.8464 | [8 empty] | 0.49967
| 95:00 | 90.8464 | 6.28 | 12 | 12 | 9.83 | 123 | 167 | 16.4 | 0.514 | 0.50325 |  | 6.06 | 9 | 0.06 | 88.33% | 13.5263 | 6.7163 | 0.90846 | 0.606 | 0.049 | 0.051
2019-01-06 | 96:00 | 90.8464 | [8 empty] | 0.50325
| 97:00 | 90.8464 | [8 empty] | 0.507
| 98:00 | 90.8464 | [8 empty] | 0.507
| 99:00 | 90.8464 | 6.32 | 13 | 13 | 10.1 | 124 | 169 | 16.1 | 0.521 | 0.5105 |  | 6.04 | 9 | 0.07 | 86.56% | 13.7105 | 6.626 | 0.90846 | 0.604 | 0.049 | 0.044
| 100:00 | 90.8464 | [8 empty] | 0.5105
| 101:00 | 90.8464 | [8 empty] | 0.51433
| 102:00 | 90.8464 | [8 empty] | 0.51433
| 103:00 | 90.8464 | 6.3 | 14 | 14 | 10.4 | 118 | 172 | 16.2 | 0.505 | 0.512 |  | 5.97 | 9 | 0.059 | 88.32% | 13.2895 | 6.836 | 0.90846 | 0.597 | 0.052 | 0.056
| 104:00 | 90.8464 | [8 empty] | 0.512
| 105:00 | 90.8464 | [8 empty] | 0.51333 | 0.037
| 106:00 | 90.8464 | [8 empty] | 0.51333
| 107:00 | 90.8464 | 6.31 | 14 | 13 | 10.3 | 120 | 172 | 16.1 | 0.504 | 0.511 |  | 5.98 | 9 | 0.06 | 88.1% | 13.2632 | 6.8495 | 0.90846 | 0.598 | 0.056 | 0.048
| 108:00 | 90.8464 | [8 empty] | 0.511
| 109:00 | 90.8464 | [8 empty] | 0.51
| 110:00 | 90.8464 | [8 empty] | 0.51
| 111:00 | 90.8464 | 6.34 | 14 | 13 | 10.4 | 122 | 174 | 16.1 | 0.496 | 0.5065 |  | 6.03 | 10 | 0.061 | 87.7% | 13.0526 | 6.96 | 0.90846 | 0.603 | 0.054 | 0.049
| 112:00 | 90.8464 | [8 empty] | 0.5065
| 113:00 | 90.8464 | [8 empty] | 0.50167
| 114:00 | 90.8464 | [8 empty] | 0.50167
| 115:00 | 90.8464 | 6.35 | 13 | 13 | 9.86 | 124 | 173 | 16.3 | 0.515 | 0.505 |  | 6 | 9 | 0.061 | 88.16% | 13.5526 | 6.7032 | 0.90846 | 0.6 | 0.055 | 0.052
| 116:00 | 90.8464 | [8 empty] | 0.505
| 117:00 | 90.8464 | [8 empty] | 0.505 | 0.036
| 118:00 | 90.8464 | [8 empty] | 0.505
| 119:00 | 90.8464 | 6.34 | 14 | 13 | 10.2 | 130 | 171 | 16.1 | 0.52 | 0.50875 |  | 6.14 | 10 | 0.055 | 89.42% | 13.6842 | 6.6388 | 0.90846 | 0.614 | 0.044 | 0.046
2019-01-07 | 120:00 | 90.4643 | [8 empty] | 0.50875
| 121:00 | 90.4643 | [8 empty] | 0.51033
| 122:00 | 90.4643 | [8 empty] | 0.51033
| 123:00 | 90.4643 | 6.37 | 11 | 14 | 10.4 | 125 | 174 | 16.1 | 0.524 | 0.51375 |  | 6.15 | 8 | 0.053 | 89.89% | 13.7895 | 6.5604 | 0.90464 | 0.615 | 0.049 | 0.049
| 124:00 | 90.4643 | [8 empty] | 0.51375
| 125:00 | 90.4643 | [8 empty] | 0.51967
| 126:00 | 90.4643 | [8 empty] | 0.51967
| 127:00 | 90.4643 | 6.38 | 15 | 12 | 11 | 120 | 175 | 16.1 | 0.494 | 0.51325 |  | 6.03 | 9 | 0.053 | 89.27% | 13 | 6.9588 | 0.90464 | 0.603 | 0.054 | 0.049
| 128:00 | 90.4643 | [8 empty] | 0.51325
| 129:00 | 90.4643 | [8 empty] | 0.51267 | 0.05
| 130:00 | 90.4643 | [8 empty] | 0.51267
| 131:00 | 90.4643 | 6.34 | 12 | 14 | 11.5 | 120 | 173 | 16.2 | 0.499 | 0.50925 |  | 5.88 | 7 | 0.054 | 89.18% | 13.1316 | 6.8891 | 0.90464 | 0.588 | 0.048 | 0.045
| 132:00 | 90.4643 | [8 empty] | 0.50925
| 133:00 | 90.4643 | [8 empty] | 0.50567
| 134:00 | 90.4643 | [8 empty] | 0.50567
| 135:00 | 90.4643 | 6.36 | 12 | 13 | 11.7 | 119 | 188 | 16.7 | 0.503 | 0.505 |  | 6 | 8 | 0.057 | 88.67% | 13.2368 | 6.8343 | 0.90464 | 0.6 | 0.051 | 0.049
| 136:00 | 90.4643 | [8 empty] | 0.505
| 137:00 | 90.4643 | [8 empty] | 0.49867
| 138:00 | 90.4643 | [8 empty] | 0.49867
| 139:00 | 90.4643 | 6.35 | 12 | 12 | 11.3 | 126 | 180 | 15.9 | 0.521 | 0.50425 |  | 6.1 | 8 | 0.06 | 88.48% | 13.7105 | 6.5982 | 0.90464 | 0.61 | 0.05 | 0.048
| 140:00 | 90.4643 | [8 empty] | 0.50425
| 141:00 | 90.4643 | [8 empty] | 0.50767 | 0.033
| 142:00 | 90.4643 | [8 empty] | 0.50767
| 143:00 | 90.4643 | 6.39 | 12 | 12 | 11.3 | 125 | 174 | 16.1 | 0.527 | 0.5125 |  | 6.12 | 8 | 0.059 | 88.8% | 13.8684 | 6.523 | 0.90464 | 0.612 | 0.051 | 0.051
2019-01-08 | 144:00 | 90.6455 | [8 empty] | 0.5125
| 145:00 | 90.6455 | [8 empty] | 0.517
| 146:00 | 90.6455 | [8 empty] | 0.517
| 147:00 | 90.6455 | 6.38 | 11 | 12 | 10.5 | 126 | 174 | 16.1 | 0.526 | 0.51925 |  | 6.16 | 9 | 0.064 | 87.83% | 13.8421 | 6.5485 | 0.90645 | 0.616 | 0.05 | 0.05
| 148:00 | 90.6455 | [8 empty] | 0.51925
| 149:00 | 90.6455 | [8 empty] | 0.52467
| 150:00 | 90.6455 | [8 empty] | 0.52467
| 151:00 | 90.6455 | 6.47 | 14 | 13 | 10.9 | 124 | 175 | 16.1 | 0.498 | 0.518 |  | 6.04 | 8 | 0.058 | 88.35% | 13.1053 | 6.9167 | 0.90645 | 0.604 | 0.054 | 0.049
| 152:00 | 90.6455 | [8 empty] | 0.518
| 153:00 | 90.6455 | [8 empty] | 0.517 | 0.051
| 154:00 | 90.6455 | [8 empty] | 0.517
| 155:00 | 90.6455 | 6.33 | 13 | 13 | 11.4 | 117 | 174 | 15.9 | 0.48 | 0.50775 |  | 6.02 | 7 | 0.06 | 87.5% | 12.6316 | 7.1761 | 0.90645 | 0.602 | 0.057 | 0.053
| 156:00 | 90.6455 | [8 empty] | 0.50775
| 157:00 | 90.6455 | [8 empty] | 0.50133
| 158:00 | 90.6455 | [8 empty] | 0.50133
| 159:00 | 90.6455 | 6.33 | 14 | 13 | 11.2 | 122 | 175 | 16 | 0.507 | 0.50275 |  | 6.08 | 8 | 0.06 | 88.17% | 13.3421 | 6.7939 | 0.90645 | 0.608 | 0.056 | 0.054
| 160:00 | 90.6455 | [8 empty] | 0.50275
| 161:00 | 90.6455 | [8 empty] | 0.495
| 162:00 | 90.6455 | [8 empty] | 0.495
| 163:00 | 90.6455 | 6.35 | 13 | 15 | 10.1 | 116 | 171 | 16.1 | 0.524 | 0.50225 |  | 6.15 | 8 | 0.059 | 88.74% | 13.7895 | 6.5735 | 0.90645 | 0.615 | 0.052 | 0.052
| 164:00 | 90.6455 | [8 empty] | 0.50225
| 165:00 | 90.6455 | [8 empty] | 0.50367 | 0.037
| 166:00 | 90.6455 | [8 empty] | 0.50367
| 167:00 | 90.6455 | 6.34 | 13 | 15 | 10.4 | 126 | 176 | 16.1 | 0.526 | 0.50925 |  | 6.17 | 8 | 0.057 | 89.16% | 13.8421 | 6.5485 | 0.90645 | 0.617 | 0.046 | 0.05
2019-01-09 | 168:00 | 90.1733 | [8 empty] | 0.50925
| 169:00 | 90.1733 | [8 empty] | 0.519
| 170:00 | 90.1733 | [8 empty] | 0.519
| 171:00 | 90.1733 | 6.38 | 14 | 15 | 11.8 | 130 | 179 | 16.2 | 0.539 | 0.524 |  | 6.22 | 9 | 0.063 | 88.31% | 14.1842 | 6.3573 | 0.90173 | 0.622 | 0.048 | 0.047
| 172:00 | 90.1733 | [8 empty] | 0.524
| 173:00 | 90.1733 | [8 empty] | 0.52967
| 174:00 | 90.1733 | [8 empty] | 0.52967
| 175:00 | 90.1733 | 6.36 | 12 | 14 | 11.7 | 120 | 177 | 166 | 0.491 | 0.52 |  | 6.06 | 10 | 0.172 | 64.97% | 12.9211 | 6.9788 | 0.90173 | 0.606 | 0.049 | 0.049
| 176:00 | 90.1733 | [8 empty] | 0.52
| 177:00 | 90.1733 | [8 empty] | 0.51867 | 0.046
| 178:00 | 90.1733 | [8 empty] | 0.51867
| 179:00 | 90.1733 | 6.4 | 13 | 14 | 12.8 | 128 | 190 | 16.4 | 0.513 | 0.51725 |  | 6.05 | 10 | 0.115 | 77.58% | 13.5 | 6.6795 | 0.90173 | 0.605 | 0.05 | 0.049
| 180:00 | 90.1733 | [8 empty] | 0.51725
| 181:00 | 90.1733 | [8 empty] | 0.51433
| 182:00 | 90.1733 | [8 empty] | 0.51433
| 183:00 | 90.1733 | 6.36 | 14 | 13 | 10.4 | 123 | 173 | 16.4 | 0.499 | 0.5105 |  | 6.09 | 8 | 0.078 | 84.37% | 13.1316 | 6.8669 | 0.90173 | 0.609 | 0.051 | 0.052
| 184:00 | 90.1733 | [8 empty] | 0.5105
| 185:00 | 90.1733 | [8 empty] | 0.501
| 186:00 | 90.1733 | [8 empty] | 0.501
| 187:00 | 90.1733 | 6.42 | 16 | 14 | 10.3 | 123 | 170 | 16.1 | 0.509 | 0.503 |  | 6.01 | 10 | 0.078 | 84.68% | 13.3947 | 6.732 | 0.90173 | 0.601 | 0.051 | 0.05
| 188:00 | 90.1733 | [8 empty] | 0.503
| 189:00 | 90.1733 | [8 empty] | 0.507 | 0.044
| 190:00 | 90.1733 | [8 empty] | 0.507
| 191:00 | 90.1733 | 6.41 | 18 | 14 | 10.5 | 127 | 172 | 15.8 | 0.51 | 0.50775 |  | 5.99 | 10 | 0.08 | 84.31% | 13.4211 | 6.7188 | 0.90173 | 0.599 | 0.049 | 0.051
2019-01-10 | 192:00 | 89.9461 | [8 empty] | 0.50775
| 193:00 | 89.9461 | [8 empty] | 0.506
| 194:00 | 89.9461 | [8 empty] | 0.506
| 195:00 | 89.9461 | 6.35 | 16 | 14 | 9.7 | 125 | 170 | 16.5 | 0.484 | 0.5005 |  | 6.06 | 10 | 0.065 | 86.57% | 12.7368 | 7.0619 | 0.89946 | 0.606 | 0.046 | 0.049
| 196:00 | 89.9461 | [8 empty] | 0.5005
| 197:00 | 89.9461 | [8 empty] | 0.501
| 198:00 | 89.9461 | [8 empty] | 0.501
| 199:00 | 89.9461 | 6.38 | 12 | 14 | 11.1 | 125 | 174 | 15.4 | 0.502 | 0.50125 |  | 6.08 | 10 | 0.077 | 84.66% | 13.2105 | 6.8087 | 0.89946 | 0.608 | 0.05 | 0.05
| 200:00 | 89.9461 | [8 empty] | 0.50125
| 201:00 | 89.9461 | [8 empty] | 0.49867 | 0.031
| 202:00 | 89.9461 | [8 empty] | 0.49867
| 203:00 | 89.9461 | 6.44 | 12 | 13 | 10.1 | 123 | 173 | 15.7 | 0.497 | 0.49825 |  | 6.03 | 9 | 0.069 | 86.12% | 13.0789 | 6.8772 | 0.89946 | 0.603 | 0.051 | 0.044
| 204:00 | 89.9461 | [8 empty] | 0.49825
| 205:00 | 89.9461 | [8 empty] | 0.49433
| 206:00 | 89.9461 | [8 empty] | 0.49433
| 207:00 | 89.9461 | 6.43 | 14 | 14 | 9.68 | 124 | 170 | 15.6 | 0.516 | 0.49975 |  | 6.1 | 10 | 0.083 | 83.91% | 13.5789 | 6.6239 | 0.89946 | 0.61 | 0.052 | 0.044
| 208:00 | 89.9461 | [8 empty] | 0.49975
| 209:00 | 89.9461 | [8 empty] | 0.505
| 210:00 | 89.9461 | [8 empty] | 0.505
| 211:00 | 89.9461 | 6.43 | 20 | 14 | 10.1 | 122 | 171 | 15.2 | 0.504 | 0.50475 |  | 6.05 | 10 | 0.078 | 84.52% | 13.2632 | 6.7817 | 0.89946 | 0.605 | 0.052 | 0.051
| 212:00 | 89.9461 | [8 empty] | 0.50475
| 213:00 | 89.9461 | [8 empty] | 0.50567 | 0.036
| 214:00 | 89.9461 | [8 empty] | 0.50567
| 215:00 | 89.9461 | 6.43 | 16 | 14 | 9.94 | 125 | 173 | 14.9 | 0.512 | 0.50725 |  | 6.06 | 10 | 0.074 | 85.55% | 13.4737 | 6.6757 | 0.89946 | 0.606 | 0.05 | 0.05
2019-01-11 | 216:00 | 90.1697 | [8 empty] | 0.50725
| 217:00 | 90.1697 | [8 empty] | 0.51067
| 218:00 | 90.1697 | [8 empty] | 0.51067
| 219:00 | 90.1697 | 6.43 | 22 | 16 | 9.71 | 122 | 172 | 15.5 | 0.48 | 0.503 |  | 6.05 | 10 | 0.061 | 87.29% | 12.6316 | 7.1384 | 0.9017 | 0.605 | 0.042 | 0.042
| 220:00 | 90.1697 | [8 empty] | 0.503
| 221:00 | 90.1697 | [8 empty] | 0.49867
| 222:00 | 90.1697 | [8 empty] | 0.49867
| 223:00 | 90.1697 | 6.51 | 14 | 15 | 9.99 | 127 | 171 | 15.1 | 0.495 | 0.49775 |  | 6.08 | 9 | 0.07 | 85.86% | 13.0263 | 6.9221 | 0.9017 | 0.608 | 0.052 | 0.052
| 224:00 | 90.1697 | [8 empty] | 0.49775
| 225:00 | 90.1697 | [8 empty] | 0.49567 | 0.03
| 226:00 | 90.1697 | [8 empty] | 0.49567
| 227:00 | 90.1697 | 6.45 | 13 | 14 | 10 | 128 | 172 | 14.5 | 0.515 | 0.5005 |  | 6.15 | 10 | 0.086 | 83.3% | 13.5526 | 6.6533 | 0.9017 | 0.615 | 0.051 | 0.052
| 228:00 | 90.1697 | [8 empty] | 0.5005
| 229:00 | 90.1697 | [8 empty] | 0.49667
| 230:00 | 90.1697 | [8 empty] | 0.49667
| 231:00 | 90.1697 | 6.42 | 12 | 15 | 10.2 | 128 | 176 | 14.7 | 0.514 | 0.501 |  | 5.88 | 7 | 0.079 | 84.63% | 13.5263 | 6.6662 | 0.9017 | 0.588 | 0.047 | 0.046
| 232:00 | 90.1697 | [8 empty] | 0.501
| 233:00 | 90.1697 | [8 empty] | 0.508
| 234:00 | 90.1697 | [8 empty] | 0.508
| 235:00 | 90.1697 | 6.35 | 15 | 15 | 10.2 | 123 | 170 | 14.3 | 0.509 | 0.50825 |  | 5.93 | 9 | 0.073 | 85.66% | 13.3947 | 6.7317 | 0.9017 | 0.593 | 0.054 | 0.048
| 236:00 | 90.1697 | [8 empty] | 0.50825
| 237:00 | 90.1697 | [8 empty] | 0.51267 | 0.034
| 238:00 | 90.1697 | [8 empty] | 0.51267
| 239:00 | 90.1697 | 6.38 | 16 | 15 | 10.3 | 127 | 177 | 13.9 | 0.52 | 0.5145 |  | 6.09 | 10 | 0.08 | 84.62% | 13.6842 | 6.5893 | 0.9017 | 0.609 | 0.055 | 0.05
2019-01-12 | 240:00 | 89.6722 | [8 empty] | 0.5145
| 241:00 | 89.6722 | [8 empty] | 0.51433
| 242:00 | 89.6722 | [8 empty] | 0.51433
| 243:00 | 89.6722 | 6.44 | 18 | 15 | 10 | 127 | 176 | 14.5 | 0.484 | 0.50675 |  | 6.11 | 10 | 0.051 | 89.46% | 12.7368 | 7.0404 | 0.89672 | 0.611 | 0.032 | 0.029
| 244:00 | 89.6722 | [8 empty] | 0.50675
| 245:00 | 89.6722 | [8 empty] | 0.50433
| 246:00 | 89.6722 | [8 empty] | 0.50433
| 247:00 | 89.6722 | 6.47 | 14 | 18 | 10.7 | 129 | 180 | 14.2 | 0.514 | 0.50675 |  | 6.03 | 9 | 0.071 | 86.19% | 13.5263 | 6.6295 | 0.89672 | 0.603 | 0.047 | 0.045
| 248:00 | 89.6722 | [8 empty] | 0.50675
| 249:00 | 89.6722 | [8 empty] | 0.506 | 0.035
| 250:00 | 89.6722 | [8 empty] | 0.506
| 251:00 | 89.6722 | 6.45 | 14 | 14 | 10.9 | 128 | 182 | 13.8 | 0.51 | 0.507 |  | 6.07 | 8 | 0.072 | 85.88% | 13.4211 | 6.6815 | 0.89672 | 0.607 | 0.047 | 0.044
| 252:00 | 89.6722 | [8 empty] | 0.507
| 253:00 | 89.6722 | [8 empty] | 0.50267
| 254:00 | 89.6722 | [8 empty] | 0.50267
| 255:00 | 89.6722 | 6.42 | 15 | 17 | 10.9 | 129 | 181 | 13.9 | 0.518 | 0.5065 |  | 6.01 | 8 | 0.077 | 85.14% | 13.6316 | 6.5783 | 0.89672 | 0.601 | 0.05 | 0.049
| 256:00 | 89.6722 | [8 empty] | 0.5065
| 257:00 | 89.6722 | [8 empty] | 0.514
| 258:00 | 89.6722 | [8 empty] | 0.514
| 259:00 | 89.6722 | 6.41 | 15 | 15 | 11.1 | 129 | 184 | 13.4 | 0.522 | 0.516 |  | 6.12 | 12 | 0.079 | 84.87% | 13.7368 | 6.5279 | 0.89672 | 0.612 | 0.05 | 0.05
| 260:00 | 89.6722 | [8 empty] | 0.516
| 261:00 | 89.6722 | [8 empty] | 0.51667 | 0.034
| 262:00 | 89.6722 | [8 empty] | 0.51667
| 263:00 | 89.6722 | 6.44 | 16 | 17 | 11.8 | 130 | 188 | 13.1 | 0.525 | 0.51875 |  | 6.01 | 12 | 0.081 | 84.57% | 13.8158 | 6.4906 | 0.89672 | 0.601 | 0.051 | 0.057
2019-01-13 | 264:00 | 90.1325 | [8 empty] | 0.51875
| 265:00 | 90.1325 | [8 empty] | 0.52167
| 266:00 | 90.1325 | [8 empty] | 0.52167
| 267:00 | 90.1325 | 6.42 | 18 | 15 | 11.2 | 120 | 184 | 13.8 | 0.478 | 0.51075 |  | 6 | 12 | 0.049 | 89.75% | 12.5789 | 7.1653 | 0.90133 | 0.6 | 0.033 | 0.038
| 268:00 | 90.1325 | [8 empty] | 0.51075
| 269:00 | 90.1325 | [8 empty] | 0.50833
| 270:00 | 90.1325 | [8 empty] | 0.50833
| 271:00 | 90.1325 | 6.58 | 14 | 18 | 11.7 | 129 | 181 | 13.5 | 0.513 | 0.5095 |  | 5.86 | 9 | 0.074 | 85.58% | 13.5 | 6.6765 | 0.90133 | 0.586 | 0.051 | 0.041
| 272:00 | 90.1325 | [8 empty] | 0.5095
| 273:00 | 90.1325 | [8 empty] | 0.50533 | 0.035
| 274:00 | 90.1325 | [8 empty] | 0.50533
| 275:00 | 90.1325 | 6.46 | 17 | 17 | 11.6 | 124 | 186 | 13.4 | 0.492 | 0.502 |  | 5.96 | 10 | 0.063 | 87.2% | 12.9474 | 6.9615 | 0.90133 | 0.596 | 0.049 | 0.05
| 276:00 | 90.1325 | [8 empty] | 0.502
| 277:00 | 90.1325 | [8 empty] | 0.49433
| 278:00 | 90.1325 | [8 empty] | 0.49433
| 279:00 | 90.1325 | 6.63 | 16 | 18 | 11.7 | 129 | 185 | 13.4 | 0.512 | 0.49875 |  | 6.04 | 10 | 0.064 | 87.5% | 13.4737 | 6.6895 | 0.90133 | 0.604 | 0.044 | 0.043
| 280:00 | 90.1325 | [8 empty] | 0.49875
| 281:00 | 90.1325 | [8 empty] | 0.50567
| 282:00 | 90.1325 | [8 empty] | 0.50567
| 283:00 | 90.1325 | 6.44 | 19 | 17 | 12.1 | 123 | 193 | 12.9 | 0.505 | 0.5055 |  | 6.09 | 10 | 0.083 | 83.56% | 13.2895 | 6.7822 | 0.90133 | 0.609 | 0.048 | 0.049
| 284:00 | 90.1325 | [8 empty] | 0.5055
| 285:00 | 90.1325 | [8 empty] | 0.503 | 0.044
| 286:00 | 90.1325 | [8 empty] | 0.503
| 287:00 | 90.1325 | 6.5 | 17 | 17 | 12.2 | 129 | 189 | 12.6 | 0.524 | 0.50825 |  | 6.02 | 10 | 0.08 | 84.73% | 13.7895 | 6.5363 | 0.90133 | 0.602 | 0.05 | 0.051
2019-01-14 | 288:00 | 89.891 | [8 empty] | 0.50825
| 289:00 | 89.891 | [8 empty] | 0.51367
| 290:00 | 89.891 | [8 empty] | 0.51367
| 291:00 | 89.891 | 6.44 | 20 | 17 | 11.6 | 122 | 186 | 13.2 | 0.466 | 0.50175 |  | 6.05 | 10 | 0.052 | 88.84% | 12.2632 | 7.3302 | 0.89891 | 0.605 | 0.038 | 0.039
| 292:00 | 89.891 | [8 empty] | 0.50175
| 293:00 | 89.891 | [8 empty] | 0.49833
| 294:00 | 89.891 | [8 empty] | 0.49833
| 295:00 | 89.891 | 6.51 | 15 | 16 | 11.6 | 127 | 188 | 12.8 | 0.512 | 0.50175 |  | 6 | 11 | 0.07 | 86.33% | 13.4737 | 6.6716 | 0.89891 | 0.6 | 0.05 | 0.053
| 296:00 | 89.891 | [8 empty] | 0.50175
| 297:00 | 89.891 | [8 empty] | 0.50067 | 0.041
| 298:00 | 89.891 | [8 empty] | 0.50067
| 299:00 | 89.891 | 6.53 | 16 | 15 | 12.2 | 129 | 190 | 12.8 | 0.499 | 0.50025 |  | 6.08 | 10 | 0.073 | 85.37% | 13.1316 | 6.8454 | 0.89891 | 0.608 | 0.052 | 0.05
| 300:00 | 89.891 | [8 empty] | 0.50025
| 301:00 | 89.891 | [8 empty] | 0.49233
| 302:00 | 89.891 | [8 empty] | 0.49233
| 303:00 | 89.891 | 6.48 | 14 | 15 | 11.7 | 128 | 187 | 12.9 | 0.509 | 0.4965 |  | 6.11 | 8 | 0.068 | 86.64% | 13.3947 | 6.7109 | 0.89891 | 0.611 | 0.05 | 0.056
| 304:00 | 89.891 | [8 empty] | 0.4965
| 305:00 | 89.891 | [8 empty] | 0.50667
| 306:00 | 89.891 | [8 empty] | 0.50667
| 307:00 | 89.891 | 6.43 | 16 | 15 | 12 | 126 | 190 | 12.4 | 0.519 | 0.50975 |  | 6.02 | 10 | 0.076 | 85.36% | 13.6579 | 6.5816 | 0.89891 | 0.602 | 0.052 | 0.057
| 308:00 | 89.891 | [8 empty] | 0.50975
| 309:00 | 89.891 | [8 empty] | 0.509 | 0.042
| 310:00 | 89.891 | [8 empty] | 0.509
| 311:00 | 89.891 | 6.49 | 15 | 15 | 12.1 | 132 | 191 | 12.4 | 0.52 | 0.51175 |  | 6 | 10 | 0.079 | 84.81% | 13.6842 | 6.569 | 0.89891 | 0.6 | 0.05 | 0.054
2019-01-15 | 312:00 | 89.7836 | [8 empty] | 0.51175
| 313:00 | 89.7836 | [8 empty] | 0.516
| 314:00 | 89.7836 | [8 empty] | 0.516
| 315:00 | 89.7836 | 6.46 | 18 | 15 | 11.8 | 120 | 188 | 13 | 0.467 | 0.50375 |  | 6.07 | 10 | 0.053 | 88.65% | 12.2895 | 7.3057 | 0.89784 | 0.607 | 0.038 | 0.041
| 316:00 | 89.7836 | [8 empty] | 0.50375
| 317:00 | 89.7836 | [8 empty] | 0.502
| 318:00 | 89.7836 | [8 empty] | 0.502
| 319:00 | 89.7836 | 6.5 | 17 | 16 | 12 | 127 | 189 | 12.5 | 0.511 | 0.50425 |  | 5.97 | 8 | 0.07 | 86.3% | 13.4474 | 6.6767 | 0.89784 | 0.597 | 0.049 | 0.05
| 320:00 | 89.7836 | [8 empty] | 0.50425
| 321:00 | 89.7836 | [8 empty] | 0.49933 | 0.035
| 322:00 | 89.7836 | [8 empty] | 0.49933
| 323:00 | 89.7836 | 6.51 | 18 | 16 | 12.2 | 125 | 190 | 12.6 | 0.489 | 0.49675 |  | 6.08 | 9 | 0.062 | 87.32% | 12.8684 | 6.977 | 0.89784 | 0.608 | 0.047 | 0.042
| 324:00 | 89.7836 | [8 empty] | 0.49675
| 325:00 | 89.7836 | [8 empty] | 0.489
| 326:00 | 89.7836 | [8 empty] | 0.489
| 327:00 | 89.7836 | 6.47 | 15 | 17 | 12.1 | 129 | 190 | 12.3 | 0.504 | 0.49275 |  | 6.12 | 8 | 0.07 | 86.11% | 13.2632 | 6.7694 | 0.89784 | 0.612 | 0.044 | 0.046
| 328:00 | 89.7836 | [8 empty] | 0.49275
| 329:00 | 89.7836 | [8 empty] | 0.50133
| 330:00 | 89.7836 | [8 empty] | 0.50133
| 331:00 | 89.7836 | 6.5 | 15 | 16 | 11.5 | 131 | 191 | 11.9 | 0.52 | 0.506 |  | 6.09 | 10 | 0.071 | 86.35% | 13.6842 | 6.5611 | 0.89784 | 0.609 | 0.048 | 0.05
| 332:00 | 89.7836 | [8 empty] | 0.506
| 333:00 | 89.7836 | [8 empty] | 0.50433 | 0.034
| 334:00 | 89.7836 | [8 empty] | 0.50433
| 335:00 | 89.7836 | 6.53 | 18 | 15 | 11.9 | 130 | 190 | 11.8 | 0.52 | 0.50825 |  | 6 | 10 | 0.082 | 84.23% | 13.6842 | 6.5611 | 0.89784 | 0.6 | 0.054 | 0.054
2019-01-16 | 336:00 | 89.4686 | [8 empty] | 0.50825
| 337:00 | 89.4686 | [8 empty] | 0.51467
| 338:00 | 89.4686 | [8 empty] | 0.51467
| 339:00 | 89.4686 | 6.48 | 18 | 16 | 12.2 | 122 | 190 | 12.2 | 0.474 | 0.5045 |  | 6.03 | 10 | 0.056 | 88.19% | 12.4737 | 7.1726 | 0.89469 | 0.603 | 0.039 | 0.043
| 340:00 | 89.4686 | [8 empty] | 0.5045
| 341:00 | 89.4686 | [8 empty] | 0.50467
| 342:00 | 89.4686 | [8 empty] | 0.50467
| 343:00 | 89.4686 | 6.54 | 16 | 17 | 12 | 134 | 191 | 11.7 | 0.541 | 0.51375 |  | 6 | 8 | 0.056 | 89.65% | 14.2368 | 6.2843 | 0.89469 | 0.6 | 0.046 | 0.047
| 344:00 | 89.4686 | [8 empty] | 0.51375
| 345:00 | 89.4686 | [8 empty] | 0.51167 | 0.068
| 346:00 | 89.4686 | [8 empty] | 0.51167
| 347:00 | 89.4686 | 6.56 | 16 | 19 | 12.1 | 134 | 190 | 12.2 | 0.539 | 0.5185 |  | 6.08 | 8 | 0.055 | 89.8% | 14.1842 | 6.3076 | 0.89469 | 0.608 | 0.048 | 0.047
| 348:00 | 89.4686 | [8 empty] | 0.5185
| 349:00 | 89.4686 | [8 empty] | 0.518
| 350:00 | 89.4686 | [8 empty] | 0.518
| 351:00 | 89.4686 | 6.56 | 16 | 18 | 12 | 135 | 195 | 12.2 | 0.537 | 0.52275 |  | 6.13 | 8 | 0.053 | 90.13% | 14.1316 | 6.3311 | 0.89469 | 0.613 | 0.044 | 0.043
| 352:00 | 89.4686 | [8 empty] | 0.52275
| 353:00 | 89.4686 | [8 empty] | 0.539
| 354:00 | 89.4686 | [8 empty] | 0.539
| 355:00 | 89.4686 | 6.48 | 15 | 15 | 12 | 129 | 191 | 12.1 | 0.52 | 0.53425 |  | 6.09 | 10 | 0.057 | 89.04% | 13.6842 | 6.5381 | 0.89469 | 0.609 | 0.052 | 0.051
| 356:00 | 89.4686 | [8 empty] | 0.53425
| 357:00 | 89.4686 | [8 empty] | 0.532 | 0.037
| 358:00 | 89.4686 | [8 empty] | 0.532
| 359:00 | 89.4686 | 6.48 | 16 | 15 | 12.3 | 123 | 183 | 12.2 | 0.498 | 0.5235 |  | 6.12 | 10 | 0.054 | 89.16% | 13.1053 | 6.8269 | 0.89469 | 0.612 | 0.047 | 0.045
2019-01-17 | 360:00 | 90.6668 | [8 empty] | 0.5235
| 361:00 | 90.6668 | [8 empty] | 0.51833
| 362:00 | 90.6668 | [8 empty] | 0.51833
| 363:00 | 90.6668 | 6.51 | 15 | 15 | 12.1 | 126 | 190 | 11.9 | 0.495 | 0.5125 |  | 6.13 | 10 | 0.051 | 89.7% | 13.0263 | 6.9603 | 0.90667 | 0.613 | 0.045 | 0.049
| 364:00 | 90.6668 | [8 empty] | 0.5125
| 365:00 | 90.6668 | [8 empty] | 0.50433
| 366:00 | 90.6668 | [8 empty] | 0.50433
| 367:00 | 90.6668 | 6.52 | 14 | 15 | 12.6 | 119 | 190 | 11.8 | 0.528 | 0.51025 |  | 6.18 | 7 | 0.058 | 89.02% | 13.8947 | 6.5253 | 0.90667 | 0.618 | 0.051 | 0.048
| 368:00 | 90.6668 | [8 empty] | 0.51025
| 369:00 | 90.6668 | [8 empty] | 0.507 | 0.042
| 370:00 | 90.6668 | [8 empty] | 0.507
| 371:00 | 90.6668 | 6.54 | 15 | 15 | 12.7 | 131 | 191 | 11.8 | 0.537 | 0.5145 |  | 6.03 | 8 | 0.057 | 89.39% | 14.1316 | 6.4159 | 0.90667 | 0.603 | 0.048 | 0.046
| 372:00 | 90.6668 | [8 empty] | 0.5145
| 373:00 | 90.6668 | [8 empty] | 0.52
| 374:00 | 90.6668 | [8 empty] | 0.52
| 375:00 | 90.6668 | 6.54 | 15 | 15 | 12.3 | 131 | 188 | 11.9 | 0.527 | 0.52175 |  | 6.32 | 9 | 0.06 | 88.61% | 13.8684 | 6.5376 | 0.90667 | 0.632 | 0.049 | 0.048
| 376:00 | 90.6668 | [8 empty] | 0.52175
| 377:00 | 90.6668 | [8 empty] | 0.53067
| 378:00 | 90.6668 | [8 empty] | 0.53067
| 379:00 | 90.6668 | 6.55 | 16 | 15 | 12.5 | 129 | 190 | 12 | 0.502 | 0.5235 |  | 6.18 | 8 | 0.049 | 90.24% | 13.2105 | 6.8632 | 0.90667 | 0.618 | 0.044 | 0.045
| 380:00 | 90.6668 | [8 empty] | 0.5235
| 381:00 | 90.6668 | [8 empty] | 0.522 | 0.038
| 382:00 | 90.6668 | [8 empty] | 0.522
| 383:00 | 90.6668 | 6.45 | 15 | 16 | 13.1 | 119 | 192 | 12.1 | 0.501 | 0.51675 |  | 6.14 | 8 | 0.06 | 88.02% | 13.1842 | 6.8769 | 0.90667 | 0.614 | 0.051 | 0.048
2019-01-18 | 384:00 | 90.0808 | [8 empty] | 0.51675
| 385:00 | 90.0808 | [8 empty] | 0.51
| 386:00 | 90.0808 | [8 empty] | 0.51
| 387:00 | 90.0808 | 6.49 | 16 | 16 | 13.4 | 129 | 191 | 11.8 | 0.481 | 0.50275 |  | 6.09 | 8 | 0.054 | 88.77% | 12.6579 | 7.1166 | 0.90081 | 0.609 | 0.047 | 0.046
| 388:00 | 90.0808 | [8 empty] | 0.50275
| 389:00 | 90.0808 | [8 empty] | 0.49467
| 390:00 | 90.0808 | [8 empty] | 0.49467
| 391:00 | 90.0808 | 6.52 | 16 | 16 | 13.7 | 129 | 192 | 11.8 | 0.499 | 0.49575 |  | 6.09 | 8 | 0.05 | 89.98% | 13.1316 | 6.8599 | 0.90081 | 0.609 | 0.046 | 0.047
| 392:00 | 90.0808 | [8 empty] | 0.49575
| 393:00 | 90.0808 | [8 empty] | 0.49367 | 0.044
| 394:00 | 90.0808 | [8 empty] | 0.49367
| 395:00 | 90.0808 | 6.5 | 16 | 16 | 13.6 | 128 | 191 | 11.8 | 0.498 | 0.49475 |  | 6.2 | 8 | 0.055 | 88.96% | 13.1053 | 6.8736 | 0.90081 | 0.62 | 0.046 | 0.049
| 396:00 | 90.0808 | [8 empty] | 0.49475
| 397:00 | 90.0808 | [8 empty] | 0.49267
| 398:00 | 90.0808 | [8 empty] | 0.49267
| 399:00 | 90.0808 | 6.5 | 16 | 16 | 15.2 | 129 | 203 | 11.9 | 0.469 | 0.48675 |  | 6.08 | 9 | 0.052 | 88.91% | 12.3421 | 7.2987 | 0.90081 | 0.608 | 0.04 | 0.041
| 400:00 | 90.0808 | [8 empty] | 0.48675
| 401:00 | 90.0808 | [8 empty] | 0.48867
| 402:00 | 90.0808 | [8 empty] | 0.48867
| 403:00 | 90.0808 | 6.44 | 15 | 16 | 15.1 | 114 | 204 | 11.8 | 0.473 | 0.48475 |  | 5.96 | 8 | 0.058 | 87.74% | 12.4474 | 7.2369 | 0.90081 | 0.596 | 0.045 | 0.047
| 404:00 | 90.0808 | [8 empty] | 0.48475
| 405:00 | 90.0808 | [8 empty] | 0.48 | 0.039
| 406:00 | 90.0808 | [8 empty] | 0.48
| 407:00 | 90.0808 | 6.4 | 16 | 15 | 15.5 | 114 | 206 | 11.8 | 0.464 | 0.476 |  | 6.04 | 8 | 0.051 | 89.01% | 12.2105 | 7.3773 | 0.90081 | 0.604 | 0.045 | 0.044
2019-01-19 | 408:00 | 90.6388 | [8 empty] | 0.476
| 409:00 | 90.6388 | [8 empty] | 0.46867
| 410:00 | 90.6388 | [8 empty] | 0.46867
| 411:00 | 90.6388 | 6.61 | 16 | 16 | 15.7 | 115 | 205 | 11.8 | 0.462 | 0.467 |  | 5.95 | 8 | 0.055 | 88.1% | 12.1579 | 7.4551 | 0.90639 | 0.595 | 0.048 | 0.046
| 412:00 | 90.6388 | [8 empty] | 0.467
| 413:00 | 90.6388 | [8 empty] | 0.46633
| 414:00 | 90.6388 | [8 empty] | 0.46633
| 415:00 | 90.6388 | 6.6 | 16 | 16 | 15.5 | 124 | 205 | 12 | 0.487 | 0.4715 |  | 6.09 | 8 | 0.052 | 89.32% | 12.8158 | 7.0724 | 0.90639 | 0.609 | 0.045 | 0.044
| 416:00 | 90.6388 | [8 empty] | 0.4715
| 417:00 | 90.6388 | [8 empty] | 0.471 | 0.045
| 418:00 | 90.6388 | [8 empty] | 0.471
| 419:00 | 90.6388 | 6.6 | 16 | 16 | 15.8 | 122 | 200 | 12 | 0.475 | 0.472 |  | 6 | 8 | 0.053 | 88.84% | 12.5 | 7.2511 | 0.90639 | 0.6 | 0.043 | 0.043
| 420:00 | 90.6388 | [8 empty] | 0.472
| 421:00 | 90.6388 | [8 empty] | 0.47467
| 422:00 | 90.6388 | [8 empty] | 0.47467
| 423:00 | 90.6388 | 6.58 | 16 | 17 | 16.1 | 125 | 203 | 12.3 | 0.483 | 0.47675 |  | 6 | 9 | 0.056 | 88.41% | 12.7105 | 7.131 | 0.90639 | 0.6 | 0.048 | 0.049
| 424:00 | 90.6388 | [8 empty] | 0.47675
| 425:00 | 90.6388 | [8 empty] | 0.48167
| 426:00 | 90.6388 | [8 empty] | 0.48167
| 427:00 | 90.6388 | 6.62 | 17 | 17 | 15.7 | 114 | 203 | 12.4 | 0.467 | 0.478 |  | 5.94 | 10 | 0.049 | 89.51% | 12.2895 | 7.3753 | 0.90639 | 0.594 | 0.046 | 0.045
| 428:00 | 90.6388 | [8 empty] | 0.478
| 429:00 | 90.6388 | [8 empty] | 0.475 | 0.048
| 430:00 | 90.6388 | [8 empty] | 0.475
| 431:00 | 90.6388 | 6.63 | 18 | 17 | 15.6 | 109 | 200 | 13.1 | 0.455 | 0.47 |  | 6.14 | 10 | 0.049 | 89.23% | 11.9737 | 7.5698 | 0.90639 | 0.614 | 0.044 | 0.046
2019-01-20 | 432:00 | 90.1666 | [8 empty] | 0.47
| 433:00 | 90.1666 | [8 empty] | 0.46833
| 434:00 | 90.1666 | [8 empty] | 0.46833
| 435:00 | 90.1666 | 6.55 | 18 | 17 | 15.5 | 115 | 201 | 12.5 | 0.443 | 0.462 |  | 5.98 | 10 | 0.047 | 89.39% | 11.6579 | 7.7344 | 0.90167 | 0.598 | 0.046 | 0.045
| 436:00 | 90.1666 | [8 empty] | 0.462
| 437:00 | 90.1666 | [8 empty] | 0.455
| 438:00 | 90.1666 | [8 empty] | 0.455
| 439:00 | 90.1666 | 6.6 | 18 | 17 | 15.3 | 117 | 198 | 12.7 | 0.453 | 0.4545 |  | 6 | 8 | 0.046 | 89.85% | 11.9211 | 7.5636 | 0.90167 | 0.6 | 0.041 | 0.044
| 440:00 | 90.1666 | [8 empty] | 0.4545
| 441:00 | 90.1666 | [8 empty] | 0.45033 | 0.047
| 442:00 | 90.1666 | [8 empty] | 0.45033
| 443:00 | 90.1666 | 6.62 | 18 | 17 | 15.8 | 119 | 194 | 12.8 | 0.466 | 0.45425 |  | 6.09 | 10 | 0.054 | 88.41% | 12.2632 | 7.3526 | 0.90167 | 0.609 | 0.04 | 0.043
| 444:00 | 90.1666 | [8 empty] | 0.45425
| 445:00 | 90.1666 | [8 empty] | 0.454
| 446:00 | 90.1666 | [8 empty] | 0.454
| 447:00 | 90.1666 | 6.6 | 17 | 17 | 15.9 | 118 | 194 | 12.7 | 0.46 | 0.4555 |  | 6.19 | 8 | 0.05 | 89.13% | 12.1053 | 7.4485 | 0.90167 | 0.619 | 0.043 | 0.045
| 448:00 | 90.1666 | [8 empty] | 0.4555
| 449:00 | 90.1666 | [8 empty] | 0.45967
| 450:00 | 90.1666 | [8 empty] | 0.45967
| 451:00 | 90.1666 | 6.57 | 17 | 17 | 15.4 | 106 | 198 | 12.8 | 0.427 | 0.4515 |  | 6.1 | 10 | 0.048 | 88.76% | 11.2368 | 8.0242 | 0.90167 | 0.61 | 0.044 | 0.046
| 452:00 | 90.1666 | [8 empty] | 0.4515
| 453:00 | 90.1666 | [8 empty] | 0.451 | 0.041
| 454:00 | 90.1666 | [8 empty] | 0.451
| 455:00 | 90.1666 | 6.53 | 17 | 17 | 15.2 | 111 | 195 | 12.8 | 0.441 | 0.4485 |  | 6.12 | 9 | 0.05 | 88.66% | 11.6053 | 7.7695 | 0.90167 | 0.612 | 0.046 | 0.046
2019-01-21 | 456:00 | 89.6621 | [8 empty] | 0.4485
| 457:00 | 89.6621 | [8 empty] | 0.44267
| 458:00 | 89.6621 | [8 empty] | 0.44267
| 459:00 | 89.6621 | 6.61 | 16 | 17 | 15 | 115 | 192 | 12.4 | 0.449 | 0.44425 |  | 6.02 | 9 | 0.054 | 87.97% | 11.8158 | 7.5883 | 0.89662 | 0.602 | 0.042 | 0.049
| 460:00 | 89.6621 | [8 empty] | 0.44425
| 461:00 | 89.6621 | [8 empty] | 0.439
| 462:00 | 89.6621 | [8 empty] | 0.439
| 463:00 | 89.6621 | 6.53 | 16 | 17 | 15.1 | 115 | 191 | 12.2 | 0.448 | 0.44125 |  | 6.08 | 9 | 0.052 | 88.39% | 11.7895 | 7.6053 | 0.89662 | 0.608 | 0.04 | 0.044
| 464:00 | 89.6621 | [8 empty] | 0.44125
| 465:00 | 89.6621 | [8 empty] | 0.446 | 0.034
| 466:00 | 89.6621 | [8 empty] | 0.446
| 467:00 | 89.6621 | 6.58 | 17 | 17 | 15.2 | 116 | 190 | 12 | 0.445 | 0.44575 |  | 6.1 | 9 | 0.054 | 87.87% | 11.7105 | 7.6565 | 0.89662 | 0.61 | 0.046 | 0.05
| 468:00 | 89.6621 | [8 empty] | 0.44575
| 469:00 | 89.6621 | [8 empty] | 0.44733
| 470:00 | 89.6621 | [8 empty] | 0.44733
| 471:00 | 89.6621 | 6.53 | 16 | 17 | 15 | 114 | 187 | 12 | 0.45 | 0.448 |  | 6.13 | 8 | 0.054 | 88% | 11.8421 | 7.5715 | 0.89662 | 0.613 | 0.045 | 0.043
| 472:00 | 89.6621 | [8 empty] | 0.448
| 473:00 | 89.6621 | [8 empty] | 0.44767
| 474:00 | 89.6621 | [8 empty] | 0.44767
| 475:00 | 89.6621 | 6.58 | 16 | 17 | 15 | 113 | 187 | 11.8 | 0.449 | 0.448 |  | 6.05 | 9 | 0.049 | 89.09% | 11.8158 | 7.5883 | 0.89662 | 0.605 | 0.047 | 0.048
| 476:00 | 89.6621 | [8 empty] | 0.448
| 477:00 | 89.6621 | [8 empty] | 0.448 | 0.041
| 478:00 | 89.6621 | [8 empty] | 0.448
| 479:00 | 89.6621 | 6.47 | 17 | 17 | 15.1 | 113 | 189 | 11.6 | 0.447 | 0.44775 |  | 6.12 | 9 | 0.051 | 88.59% | 11.7632 | 7.6223 | 0.89662 | 0.612 | 0.046 | 0.044
2019-01-22 | 480:00 | 88.0196 | [8 empty] | 0.44775
| 481:00 | 88.0196 | [8 empty] | 0.44867
| 482:00 | 88.0196 | [8 empty] | 0.44867
| 483:00 | 88.0196 | 6.44 | 16 | 17 | 15 | 106 | 189 | 11.2 | 0.401 | 0.43675 |  | 6.23 | 10 | 0.047 | 88.28% | 10.5526 | 8.341 | 0.8802 | 0.623 | 0.045 | 0.043
| 484:00 | 88.0196 | [8 empty] | 0.43675
| 485:00 | 88.0196 | [8 empty] | 0.43233
| 486:00 | 88.0196 | [8 empty] | 0.43233
| 487:00 | 88.0196 | 6.57 | 16 | 16 | 15 | 107 | 189 | 11 | 0.425 | 0.4305 |  | 6.2 | 8 | 0.052 | 87.76% | 11.1842 | 7.87 | 0.8802 | 0.62 | 0.043 | 0.044
| 488:00 | 88.0196 | [8 empty] | 0.4305
| 489:00 | 88.0196 | [8 empty] | 0.42433 | 0.037
| 490:00 | 88.0196 | [8 empty] | 0.42433
| 491:00 | 88.0196 | 6.56 | 16 | 17 | 15 | 105 | 189 | 11 | 0.435 | 0.427 |  | 6.07 | 8 | 0.053 | 87.82% | 11.4474 | 7.6891 | 0.8802 | 0.607 | 0.042 | 0.043
| 492:00 | 88.0196 | [8 empty] | 0.427
| 493:00 | 88.0196 | [8 empty] | 0.42033
| 494:00 | 88.0196 | [8 empty] | 0.42033
| 495:00 | 88.0196 | 6.57 | 16 | 17 | 14.9 | 106 | 188 | 11 | 0.441 | 0.4255 |  | 6.17 | 8 | 0.058 | 86.85% | 11.6053 | 7.5845 | 0.8802 | 0.617 | 0.046 | 0.044
| 496:00 | 88.0196 | [8 empty] | 0.4255
| 497:00 | 88.0196 | [8 empty] | 0.43367
| 498:00 | 88.0196 | [8 empty] | 0.43367
| 499:00 | 88.0196 | 6.58 | 17 | 17 | 14.5 | 106 | 185 | 10.9 | 0.428 | 0.43225 |  | 6.25 | 10 | 0.054 | 87.38% | 11.2632 | 7.8148 | 0.8802 | 0.625 | 0.047 | 0.046
| 500:00 | 88.0196 | [8 empty] | 0.43225
| 501:00 | 88.0196 | [8 empty] | 0.43467 | 0.031
| 502:00 | 88.0196 | [8 empty] | 0.43467
| 503:00 | 88.0196 | 6.48 | 17 | 17 | 14.6 | 104 | 185 | 11.1 | 0.417 | 0.43025 |  | 6.24 | 9 | 0.052 | 87.53% | 10.9737 | 8.021 | 0.8802 | 0.624 | 0.046 | 0.047
2019-01-23 | 504:00 | 80.7007 | [8 empty] | 0.43025
| 505:00 | 80.7007 | [8 empty] | 0.42867
| 506:00 | 80.7007 | [8 empty] | 0.42867
| 507:00 | 80.7007 | 6.36 | 16 | 17 | 15 | 103 | 181 | 10.9 | 0.404 | 0.4225 |  | 6.05 | 9 | 0.051 | 87.38% | 10.6316 | 7.5907 | 0.80701 | 0.605 | 0.044 | 0.043
| 508:00 | 80.7007 | [8 empty] | 0.4225
| 509:00 | 80.7007 | [8 empty] | 0.41633
| 510:00 | 80.7007 | [8 empty] | 0.41633
| 511:00 | 80.7007 | 6.59 | 18 | 17 | 14.2 | 91 | 169 | 11.6 | 0.384 | 0.40825 |  | 6.2 | 12 | 0.061 | 84.11% | 10.1053 | 7.986 | 0.80701 | 0.62 | 0.04 | 0.045
| 512:00 | 80.7007 | [8 empty] | 0.40825
| 513:00 | 80.7007 | [8 empty] | 0.40167 | 0.06
| 514:00 | 80.7007 | [8 empty] | 0.40167
| 515:00 | 80.7007 | 6.47 | 18 | 17 | 13.7 | 90 | 171 | 11.5 | 0.389 | 0.3985 |  | 6.19 | 11 | 0.06 | 84.58% | 10.2368 | 7.8834 | 0.80701 | 0.619 | 0.042 | 0.044
| 516:00 | 80.7007 | [8 empty] | 0.3985
| 517:00 | 80.7007 | [8 empty] | 0.39233
| 518:00 | 80.7007 | [8 empty] | 0.39233
| 519:00 | 80.7007 | 6.55 | 20 | 18 | 14.2 | 90 | 175 | 11.8 | 0.365 | 0.3855 |  | 6.05 | 12 | 0.053 | 85.48% | 9.6053 | 8.4017 | 0.80701 | 0.605 | 0.039 | 0.039
| 520:00 | 80.7007 | [8 empty] | 0.3855
| 521:00 | 80.7007 | [8 empty] | 0.37933
| 522:00 | 80.7007 | [8 empty] | 0.37933
| 523:00 | 80.7007 | 6.62 | 16 | 16 | 14.1 | 100 | 173 | 11.8 | 0.395 | 0.38325 |  | 6.12 | 11 | 0.07 | 82.28% | 10.3947 | 7.7636 | 0.80701 | 0.612 | 0.042 | 0.038
| 524:00 | 80.7007 | [8 empty] | 0.38325
| 525:00 | 80.7007 | [8 empty] | 0.383 | 0.035
| 526:00 | 80.7007 | [8 empty] | 0.383
| 527:00 | 80.7007 | 6.53 | 17 | 16 | 14.2 | 92 | 172 | 11.7 | 0.396 | 0.38625 |  | 6.08 | 10 | 0.065 | 83.59% | 10.4211 | 7.744 | 0.80701 | 0.608 | 0.039 | 0.041
2019-01-24 | 528:00 | 75.0326 | [8 empty] | 0.38625
| 529:00 | 75.0326 | [8 empty] | 0.38533
| 530:00 | 75.0326 | [8 empty] | 0.38533
| 531:00 | 75.0326 | 6.4 | 15 | 17 | 14.2 | 98 | 172 | 12.8 | 0.392 | 0.387 |  | 6.12 | 8 | 0.058 | 85.2% | 10.3158 | 7.2736 | 0.75033 | 0.612 | 0.039 | 0.041
| 532:00 | 75.0326 | [8 empty] | 0.387
| 533:00 | 75.0326 | [8 empty] | 0.39433
| 534:00 | 75.0326 | [8 empty] | 0.39433
| 535:00 | 75.0326 | 6.5 | 17 | 17 | 14.1 | 96 | 172 | 12.6 | 0.393 | 0.394 |  | 6.15 | 10 | 0.066 | 83.21% | 10.3421 | 7.2551 | 0.75033 | 0.615 | 0.044 | 0.041
| 536:00 | 75.0326 | [8 empty] | 0.394
| 537:00 | 75.0326 | [8 empty] | 0.39367 | 0.066
| 538:00 | 75.0326 | [8 empty] | 0.39367
| 539:00 | 75.0326 | 6.72 | 18 | 17 | 14.3 | 98 | 172 | 12.7 | 0.394 | 0.39375 |  | 6.15 | 10 | 0.062 | 84.26% | 10.3684 | 7.2366 | 0.75033 | 0.615 | 0.044 | 0.043
| 540:00 | 75.0326 | [8 empty] | 0.39375
| 541:00 | 75.0326 | [8 empty] | 0.393
| 542:00 | 75.0326 | [8 empty] | 0.393
| 543:00 | 75.0326 | 6.55 | 19 | 18 | 14.8 | 96 | 176 | 13 | 0.341 | 0.38 |  | 6.12 | 10 | 0.05 | 85.34% | 8.9737 | 8.3614 | 0.75033 | 0.612 | 0.037 | 0.039
| 544:00 | 75.0326 | [8 empty] | 0.38
| 545:00 | 75.0326 | [8 empty] | 0.376
| 546:00 | 75.0326 | [8 empty] | 0.376
| 547:00 | 75.0326 | 6.6 | 15 | 19 | 14.3 | 97 | 169 | 13.1 | 0.378 | 0.3765 |  | 6.18 | 9 | 0.062 | 83.6% | 9.9474 | 7.543 | 0.75033 | 0.618 | 0.038 | 0.04
| 548:00 | 75.0326 | [8 empty] | 0.3765
| 549:00 | 75.0326 | [8 empty] | 0.371 | 0.038
| 550:00 | 75.0326 | [8 empty] | 0.371
| 551:00 | 75.0326 | 6.59 | 16 | 18 | 14.2 | 90 | 170 | 12.9 | 0.355 | 0.367 |  | 6.1 | 10 | 0.057 | 83.94% | 9.3421 | 8.0317 | 0.75033 | 0.61 | 0.037 | 0.039
2019-01-25 | 552:00 | 68.9056 | [8 empty] | 0.367
| 553:00 | 68.9056 | [8 empty] | 0.358
| 554:00 | 68.9056 | [8 empty] | 0.358
| 555:00 | 68.9056 | 6.48 | 15 | 16 | 14.4 | 95 | 172 | 13 | 0.378 | 0.363 |  | 6.14 | 8 | 0.064 | 83.07% | 9.9474 | 6.927 | 0.68906 | 0.614 | 0.038 | 0.039
| 556:00 | 68.9056 | [8 empty] | 0.363
| 557:00 | 68.9056 | [8 empty] | 0.37033
| 558:00 | 68.9056 | [8 empty] | 0.37033
| 559:00 | 68.9056 | 6.57 | 19 | 17 | 14.3 | 91 | 166 | 12.6 | 0.368 | 0.36975 |  | 6.19 | 10 | 0.057 | 84.51% | 9.6842 | 7.1153 | 0.68906 | 0.619 | 0.038 | 0.038
| 560:00 | 68.9056 | [8 empty] | 0.36975
| 561:00 | 68.9056 | [8 empty] | 0.367 | 0.057
| 562:00 | 68.9056 | [8 empty] | 0.367
| 563:00 | 68.9056 | 6.42 | 20 | 16 | 14.9 | 96 | 170 | 12.3 | 0.376 | 0.36925 |  | 6.19 | 10 | 0.054 | 85.64% | 9.8947 | 6.9639 | 0.68906 | 0.619 | 0.041 | 0.04
| 564:00 | 68.9056 | [8 empty] | 0.36925
| 565:00 | 68.9056 | [8 empty] | 0.374
| 566:00 | 68.9056 | [8 empty] | 0.374
| 567:00 | 68.9056 | 6.46 | 21 | 17 | 14.6 | 92 | 172 | 13 | 0.335 | 0.36425 |  | 6.23 | 11 | 0.034 | 89.85% | 8.8158 | 7.8162 | 0.68906 | 0.623 | 0.017 | 0.017
| 568:00 | 68.9056 | [8 empty] | 0.36425
| 569:00 | 68.9056 | [8 empty] | 0.35967
| 570:00 | 68.9056 | [8 empty] | 0.35967
| 571:00 | 68.9056 | 6.5 | 19 | 16 | 14.7 | 95 | 171 | 12.9 | 0.36 | 0.35975 |  | 6.25 | 9 | 0.062 | 82.78% | 9.4737 | 7.2734 | 0.68906 | 0.625 | 0.036 | 0.039
| 572:00 | 68.9056 | [8 empty] | 0.35975
| 573:00 | 68.9056 | [8 empty] | 0.357 | 0.033
| 574:00 | 68.9056 | [8 empty] | 0.357
| 575:00 | 68.9056 | 6.49 | 18 | 17 | 14.6 | 94 | 169 | 12.8 | 0.379 | 0.3625 |  | 6.17 | 8 | 0.062 | 83.64% | 9.9737 | 6.9087 | 0.68906 | 0.617 | 0.04 | 0.04
2019-01-26 | 576:00 | 64.9353 | [8 empty] | 0.3625
| 577:00 | 64.9353 | [8 empty] | 0.358
| 578:00 | 64.9353 | [8 empty] | 0.358
| 579:00 | 64.9353 | 6.45 | 14 | 14 | 14.8 | 94 | 171 | 12.6 | 0.37 | 0.361 |  | 6.21 | 7 | 0.065 | 82.43% | 9.7368 | 6.669 | 0.64935 | 0.621 | 0.04 | 0.04
| 580:00 | 64.9353 | [8 empty] | 0.361
| 581:00 | 64.9353 | [8 empty] | 0.36967
| 582:00 | 64.9353 | [8 empty] | 0.36967
| 583:00 | 64.9353 | 6.46 | 15 | 16 | 14.7 | 89 | 168 | 12.1 | 0.367 | 0.369 |  | 6.23 | 9 | 0.058 | 84.2% | 9.6579 | 6.7235 | 0.64935 | 0.623 | 0.038 | 0.038
| 584:00 | 64.9353 | [8 empty] | 0.369
| 585:00 | 64.9353 | [8 empty] | 0.372 | 0.056
| 586:00 | 64.9353 | [8 empty] | 0.372
| 587:00 | 64.9353 | 6.51 | 16 | 16 | 14.7 | 90 | 170 | 12.5 | 0.371 | 0.37175 |  | 6.16 | 10 | 0.06 | 83.83% | 9.7632 | 6.6511 | 0.64935 | 0.616 | 0.038 | 0.039
| 588:00 | 64.9353 | [8 empty] | 0.37175
| 589:00 | 64.9353 | [8 empty] | 0.36933
| 590:00 | 64.9353 | [8 empty] | 0.36933
| 591:00 | 64.9353 | 6.65 | 18 | 16 | 14.8 | 90 | 166 | 12.5 | 0.345 | 0.36325 |  | 6.24 | 10 | 0.05 | 85.51% | 9.0789 | 7.1523 | 0.64935 | 0.624 | 0.035 | 0.036
| 592:00 | 64.9353 | [8 empty] | 0.36325
| 593:00 | 64.9353 | [8 empty] | 0.361
| 594:00 | 64.9353 | [8 empty] | 0.361
| 595:00 | 64.9353 | 6.57 | 15 | 18 | 14.9 | 94 | 168 | 12.5 | 0.355 | 0.3595 |  | 6.27 | 9 | 0.057 | 83.94% | 9.3421 | 6.9508 | 0.64935 | 0.627 | 0.038 | 0.042
| 596:00 | 64.9353 | [8 empty] | 0.3595
| 597:00 | 64.9353 | [8 empty] | 0.357 | 0.036
| 598:00 | 64.9353 | [8 empty] | 0.357
| 599:00 | 64.9353 | 6.5 | 16 | 17 | 14.9 | 92 | 168 | 12.6 | 0.367 | 0.3595 |  | 6.24 | 10 | 0.069 | 81.2% | 9.6579 | 6.7235 | 0.64935 | 0.624 | 0.04 | 0.043
2019-01-27 | 600:00 | 64.8453 | [8 empty] | 0.3595
| 601:00 | 64.8453 | [8 empty] | 0.35567
| 602:00 | 64.8453 | [8 empty] | 0.35567
| 603:00 | 64.8453 | 6.51 | 15 | 17 | 14.7 | 93 | 167 | 12.2 | 0.369 | 0.359 |  | 6.31 | 8 | 0.066 | 82.11% | 9.7105 | 6.6778 | 0.64845 | 0.631 | 0.043 | 0.041
| 604:00 | 64.8453 | [8 empty] | 0.359
| 605:00 | 64.8453 | [8 empty] | 0.36367
| 606:00 | 64.8453 | [8 empty] | 0.36367
| 607:00 | 64.8453 | 6.55 | 19 | 18 | 14.7 | 86 | 155 | 11.9 | 0.359 | 0.3625 |  | 6.3 | 10 | 0.059 | 83.57% | 9.4474 | 6.8639 | 0.64845 | 0.63 | 0.038 | 0.039
| 608:00 | 64.8453 | [8 empty] | 0.3625
| 609:00 | 64.8453 | [8 empty] | 0.365 | 0.062
| 610:00 | 64.8453 | [8 empty] | 0.365
| 611:00 | 64.8453 | 6.52 | 20 | 17 | 14.7 | 92 | 168 | 11.9 | 0.369 | 0.366 |  | 6.3 | 10 | 0.058 | 84.28% | 9.7105 | 6.6778 | 0.64845 | 0.63 | 0.038 | 0.04
| 612:00 | 64.8453 | [8 empty] | 0.366
| 613:00 | 64.8453 | [8 empty] | 0.36567
| 614:00 | 64.8453 | [8 empty] | 0.36567
| 615:00 | 64.8453 | 6.6 | 21 | 18 | 14.8 | 88 | 164 | 12.5 | 0.341 | 0.3595 |  | 6.28 | 12 | 0.05 | 85.34% | 8.9737 | 7.2262 | 0.64845 | 0.628 | 0.036 | 0.038
| 616:00 | 64.8453 | [8 empty] | 0.3595
| 617:00 | 64.8453 | [8 empty] | 0.35633
| 618:00 | 64.8453 | [8 empty] | 0.35633
| 619:00 | 64.8453 | 6.55 | 18 | 17 | 14.5 | 90 | 165 | 12.1 | 0.359 | 0.357 |  | 6.21 | 10 | 0.057 | 84.12% | 9.4474 | 6.8639 | 0.64845 | 0.621 | 0.036 | 0.035
| 620:00 | 64.8453 | [8 empty] | 0.357
| 621:00 | 64.8453 | [8 empty] | 0.35633 | 0.043
| 622:00 | 64.8453 | [8 empty] | 0.35633
| 623:00 | 64.8453 | 6.54 | 16 | 16 | 14.4 | 85 | 163 | 12.1 | 0.35 | 0.35475 |  | 6.22 | 11 | 0.052 | 85.14% | 9.2105 | 7.0403 | 0.64845 | 0.622 | 0.042 | 0.039
2019-01-28 | 624:00 | 64.9422 | [8 empty] | 0.35475
| 625:00 | 64.9422 | [8 empty] | 0.35
| 626:00 | 64.9422 | [8 empty] | 0.35
| 627:00 | 64.9422 | 6.56 | 15 | 16 | 14.4 | 90 | 165 | 11.9 | 0.358 | 0.352 |  | 6.24 | 9 | 0.056 | 84.36% | 9.4211 | 6.8933 | 0.64942 | 0.624 | 0.037 | 0.035
| 628:00 | 64.9422 | [8 empty] | 0.352
| 629:00 | 64.9422 | [8 empty] | 0.35567
| 630:00 | 64.9422 | [8 empty] | 0.35567
| 631:00 | 64.9422 | 6.57 | 15 | 16 | 14.9 | 84 | 166 | 11.7 | 0.352 | 0.35475 |  | 6.24 | 9 | 0.059 | 83.24% | 9.2632 | 7.0108 | 0.64942 | 0.624 | 0.038 | 0.041
| 632:00 | 64.9422 | [8 empty] | 0.35475
| 633:00 | 64.9422 | [8 empty] | 0.35333 | 0.063
| 634:00 | 64.9422 | [8 empty] | 0.35333
| 635:00 | 64.9422 | 6.52 | 20 | 17 | 14.7 | 91 | 165 | 11.7 | 0.371 | 0.35775 |  | 6.04 | 9 | 0.06 | 83.83% | 9.7632 | 6.6518 | 0.64942 | 0.604 | 0.039 | 0.04
| 636:00 | 64.9422 | [8 empty] | 0.35775
| 637:00 | 64.9422 | [8 empty] | 0.36033
| 638:00 | 64.9422 | [8 empty] | 0.36033
| 639:00 | 64.9422 | 6.62 | 22 | 18 | 14.4 | 86 | 164 | 12.2 | 0.34 | 0.35525 |  | 6.01 | 10 | 0.054 | 84.12% | 8.9474 | 7.2582 | 0.64942 | 0.601 | 0.039 | 0.039
| 640:00 | 64.9422 | [8 empty] | 0.35525
| 641:00 | 64.9422 | [8 empty] | 0.35433
| 642:00 | 64.9422 | [8 empty] | 0.35433
| 643:00 | 64.9422 | 6.61 | 16 | 19 | 14.4 | 93 | 163 | 12.1 | 0.36 | 0.35575 |  | 6.11 | 9 | 0.055 | 84.72% | 9.4737 | 6.855 | 0.64942 | 0.611 | 0.037 | 0.039
| 644:00 | 64.9422 | [8 empty] | 0.35575
| 645:00 | 64.9422 | [8 empty] | 0.357 | 0.034
| 646:00 | 64.9422 | [8 empty] | 0.357
| 647:00 | 64.9422 | 6.53 | 18 | 18 | 14.3 | 88 | 162 | 12.4 | 0.35 | 0.35525 |  | 6.03 | 8 | 0.048 | 86.29% | 9.2105 | 7.0509 | 0.64942 | 0.603 | 0.038 | 0.041
2019-01-29 | 648:00 | 65.0818 | [8 empty] | 0.35525
| 649:00 | 65.0818 | [8 empty] | 0.35
| 650:00 | 65.0818 | [8 empty] | 0.35
| 651:00 | 65.0818 | 6.58 | 15 | 16 | 14.5 | 87 | 163 | 12.4 | 0.357 | 0.35175 |  | 6.01 | 9 | 0.06 | 83.19% | 9.3947 | 6.9275 | 0.65082 | 0.601 | 0.042 | 0.04
| 652:00 | 65.0818 | [8 empty] | 0.35175
| 653:00 | 65.0818 | [8 empty] | 0.35567
| 654:00 | 65.0818 | [8 empty] | 0.35567
| 655:00 | 65.0818 | 6.59 | 17 | 17 | 14.6 | 86 | 166 | 12 | 0.353 | 0.355 |  | 6 | 10 | 0.058 | 83.57% | 9.2895 | 7.006 | 0.65082 | 0.6 | 0.039 | 0.043
| 656:00 | 65.0818 | [8 empty] | 0.355
| 657:00 | 65.0818 | [8 empty] | 0.35333 | 0.061
| 658:00 | 65.0818 | [8 empty] | 0.35333
| 659:00 | 65.0818 | 6.61 | 19 | 17 | 14.7 | 89 | 169 | 11.7 | 0.355 | 0.35375 |  | 6.24 | 10 | 0.059 | 83.38% | 9.3421 | 6.9665 | 0.65082 | 0.624 | 0.039 | 0.04
| 660:00 | 65.0818 | [8 empty] | 0.35375
| 661:00 | 65.0818 | [8 empty] | 0.355
| 662:00 | 65.0818 | [8 empty] | 0.355
| 663:00 | 65.0818 | 6.69 | 21 | 18 | 14.6 | 84 | 162 | 12.2 | 0.328 | 0.34825 |  | 6.22 | 11 | 0.047 | 85.67% | 8.6316 | 7.54 | 0.65082 | 0.622 | 0.032 | 0.035
| 664:00 | 65.0818 | [8 empty] | 0.34825
| 665:00 | 65.0818 | [8 empty] | 0.34533
| 666:00 | 65.0818 | [8 empty] | 0.34533
| 667:00 | 65.0818 | 6.65 | 19 | 20 | 15.2 | 90 | 163 | 12.1 | 0.348 | 0.346 |  | 6.24 | 9 | 0.061 | 82.47% | 9.1579 | 7.1066 | 0.65082 | 0.624 | 0.039 | 0.037
| 668:00 | 65.0818 | [8 empty] | 0.346
| 669:00 | 65.0818 | [8 empty] | 0.34367 | 0.038
| 670:00 | 65.0818 | [8 empty] | 0.34367
| 671:00 | 65.0818 | 6.64 | 20 | 19 | 15.7 | 82 | 166 | 12 | 0.356 | 0.34675 |  | 6.23 | 9 | 0.051 | 85.67% | 9.3684 | 6.9469 | 0.65082 | 0.623 | 0.044 | 0.046
2019-01-30 | 672:00 | 63.0082 | [8 empty] | 0.34675
| 673:00 | 63.0082 | [8 empty] | 0.344
| 674:00 | 63.0082 | [8 empty] | 0.344
| 675:00 | 63.0082 | 6.62 | 17 | 19 | 15.8 | 89 | 156 | 12.1 | 0.354 | 0.3465 |  | 6.01 | 8 | 0.058 | 83.62% | 9.3158 | 6.7636 | 0.63008 | 0.601 | 0.039 | 0.041
| 676:00 | 63.0082 | [8 empty] | 0.3465
| 677:00 | 63.0082 | [8 empty] | 0.35267
| 678:00 | 63.0082 | [8 empty] | 0.35267
| 679:00 | 63.0082 | 6.67 | 17 | 18 | 15.9 | 94 | 174 | 11.5 | 0.372 | 0.3575 |  | 6.09 | 7 | 0.048 | 87.1% | 9.7895 | 6.4363 | 0.63008 | 0.609 | 0.046 | 0.044
| 680:00 | 63.0082 | [8 empty] | 0.3575
| 681:00 | 63.0082 | [8 empty] | 0.36067 | 0.041
| 682:00 | 63.0082 | [8 empty] | 0.36067
| 683:00 | 63.0082 | 6.66 | 17 | 18 | 16.1 | 87 | 174 | 11.3 | 0.355 | 0.35925 |  | 6.05 | 7 | 0.047 | 86.76% | 9.3421 | 6.7445 | 0.63008 | 0.605 | 0.041 | 0.044
| 684:00 | 63.0082 | . | [7 empty] | 0.35925 | [5 empty] | #VALUE! | #VALUE! | 0.63008
| 685:00 | 63.0082 | [8 empty] | 0.36033
| 686:00 | 63.0082 | [8 empty] | 0.36033
| 687:00 | 63.0082 | 6.64 | 17 | 18 | 15.9 | 86 | 177 | 11.4 | 0.354 | 0.35875 |  | 5.9 | 7 | 0.054 | 84.75% | 9.3158 | 6.7636 | 0.63008 | 0.59 | 0.042 | 0.044
| 688:00 | 63.0082 | [8 empty] | 0.35875
| 689:00 | 63.0082 | [8 empty] | 0.36033
| 690:00 | 63.0082 | [8 empty] | 0.36033
| 691:00 | 63.0082 | 6.61 | 17 | 18 | 15.9 | 97 | 174 | 11.5 | 0.374 | 0.36375 |  | 6.01 | 8 | 0.044 | 88.24% | 9.8421 | 6.4019 | 0.63008 | 0.601 | 0.034 | 0.035
| 692:00 | 63.0082 | [8 empty] | 0.36375
| 693:00 | 63.0082 | [8 empty] | 0.361 | 0.046
| 694:00 | 63.0082 | [8 empty] | 0.361
| 695:00 | 63.0082 | 6.69 | 17 | 17 | 16.4 | 97 | 173 | 11.4 | 0.382 | 0.36625 |  | 6.09 | 8 | 0.047 | 87.7% | 10.0526 | 6.2678 | 0.63008 | 0.609 | 0.036 | 0.037
2019-01-31 | 696:00 | 62.8951 | [8 empty] | 0.36625
. | 697:00 | 62.8951 | [8 empty] | 0.37
| 698:00 | 62.8951 | [8 empty] | 0.37
| 699:00 | 62.8951 | 6.69 | 18 | 17 | 16.3 | 103 | 174 | 11.3 | 0.385 | 0.37375 |  | 6.04 | 7 | 0.045 | 88.31% | 10.1316 | 6.2078 | 0.62895 | 0.604 | 0.038 | 0.037
| 700:00 | 62.8951 | [8 empty] | 0.37375
| 701:00 | 62.8951 | [8 empty] | 0.38033
| 702:00 | 62.8951 | [8 empty] | 0.38033
| 703:00 | 62.8951 | 6.61 | 16 | 17 | 16.4 | 89 | 176 | 11.5 | 0.361 | 0.3755 |  | 5.91 | 7 | 0.043 | 88.09% | 9.5 | 6.6205 | 0.62895 | 0.591 | 0.039 | 0.036
| 704:00 | 62.8951 | [8 empty] | 0.3755
| 705:00 | 62.8951 | [8 empty] | 0.376 | 0.042
| 706:00 | 62.8951 | [8 empty] | 0.376
| 707:00 | 62.8951 | 6.66 | 17 | 17 | 16.2 | 88 | 175 | 10.9 | 0.348 | 0.369 |  | 6.03 | 7 | 0.042 | 87.93% | 9.1579 | 6.8679 | 0.62895 | 0.603 | 0.034 | 0.033
| 708:00 | 62.8951 | [8 empty] | 0.369
| 709:00 | 62.8951 | [8 empty] | 0.36467
| 710:00 | 62.8951 | [8 empty] | 0.36467
| 711:00 | 62.8951 | 6.68 | 16 | 17 | 15.9 | 92 | 173 | 11.9 | 0.37 | 0.366 |  | 6.13 | 10 | 0.048 | 87.03% | 9.7368 | 6.4595 | 0.62895 | 0.613 | 0.044 | 0.042
| 712:00 | 62.8951 | [8 empty] | 0.366
| 713:00 | 62.8951 | [8 empty] | 0.35967
| 714:00 | 62.8951 | [8 empty] | 0.35967
| 715:00 | 62.8951 | 6.65 | 17 | 17 | 15.3 | 94 | 171 | 11.8 | 0.378 | 0.36425 |  | 6.19 | 9 | 0.049 | 87.04% | #VALUE! | #VALUE! | #VALUE! | 0.619 | 0.038 | 0.41
| 716:00 | 62.8951 | [8 empty] | 0.36425
| 717:00 | 62.8951 | [8 empty] | 0.36533 | 0.043
| 718:00 | 62.8951 | [8 empty] | 0.36533
| 719:00 | 62.8951 | 6.61 | 17 | 17 | 15.6 | 96 | 172 | 11 | 0.43 | 0.3815 |  | 6.2 | 9 | 0.046 | 89.3% | #VALUE! | #VALUE! | #VALUE! | 0.62 | 0.037 | 0.035
TOTAL |  | 62239.4608 | 1203.24 | 2895 | 2901 | 2335.32 | 20966 | 32833 | 2673.2 | 85.064 |  | 2.602 | 1132.42 | 1674 | 11.335 | 160.9903 | #VALUE! | #VALUE! | #VALUE! | 113.242 | 8.509 | 8.855
AVERAGE |  | 83.6463 | 6.469 | 15.5645 | 15.5968 | 12.5555 | 112.7204 | 176.5215 | 14.372 | 0.45733 |  | 0.041968 | 6.0883 | 9 | 0.060941 | 0.86554 | #VALUE! | #VALUE! | #VALUE! | 0.60883 | 0.045747 | 0.047608
MINIMUM |  | 62.8951 | 6.21 | 11 | 12 | 8 | 82 | 155 | 10.9 | 0.328 |  | 0.03 | 5.86 | 7 | 0.034 | 0.64969 | #VALUE! | #VALUE! | #VALUE! | 0.586 | 0.017 | 0.017
MAXIMUM |  | 90.8464 | 6.72 | 22 | 20 | 16.4 | 135 | 206 | 166 | 0.541 |  | 0.068 | 6.32 | 12 | 0.172 | 0.90239 | #VALUE! | #VALUE! | #VALUE! | 0.632 | 0.06 | 0.41
08:44 |  | 08:44 | [13 empty] | HIGHLIGHT BETWEEN LIME |  | 5
08/12/19 |  | 08/13/19 | [12 empty] | TOTAL # IN THIS RANGE |  | 0 | 5.5
| 08:44 |  | TRUE | [11 empty] | TOTAL SAMPLES |  | 184
FALSE
WHAT
2019-08-12 08:45
1901-12-21
Formulas:
Date = MATCH([Date, row above],A4:A747,1)

## BW 1
|  | Surface Water System Monthly Operation Report | [10 empty] | DATE | TIME
|  | Operation of Filters | [9 empty] | LAST WASH | 1900-01-12 | 8:30 | 1900-01-12 08:30
|  | Bureau of Water | [9 empty] | THIS WASH | 1900-01-16 | 11:00 | 1900-01-16 11:00
TOTAL HOURS
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 1 |  |  |  |  | 2019-01-01 | [8 empty] | 98.5
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED
2019-01-01
2019-01-02
2019-01-03
2019-01-04 | 9:00 | 20 | 30 | 81 | 117200 | 44270.8333 | 8.5 | 15684.8004 | SN | TIME | 161470.8333
2019-01-05
2019-01-06
2019-01-07
2019-01-08 | 2:00 | 20 | 30 | 89 | 117200 | 42708.3333 | 8.2 | 16625.6607 | CBW |  | 159908.3333
2019-01-09
2019-01-10
2019-01-11
2019-01-12
2019-01-13 | 8:30 | 20 | 30 | 126.5 | 117200 | 52083.3333 | 10 | 28818.1155 | GE |  | 169283.3333
2019-01-14
2019-01-15
2019-01-16
2019-01-17 | 11:00 | 20 | 30 | 98.5 | 117200 | 44270.8333 | 8.5 | 19073.4919 | JMM |  | 161470.8333
2019-01-18
2019-01-19
2019-01-20 | 12:00 | 20 | 30 | 73 | 117200 | 39062.5 | 7.5 | 12472.6627 | CBW |  | 156262.5
2019-01-21
2019-01-22
2019-01-23
2019-01-24 | 10:00 | 20 | 30 | 94 | 117200 | 44270.8333 | 8.5 | 18202.1141 | MN |  | 161470.8333
2019-01-25
2019-01-26
2019-01-27
2019-01-28
2019-01-29 | 10:00 | 20 | 30 | 120 | 117200 | 49479.1667 | 9.5 | 25970.4757 | DH |  | 166679.1667
2019-01-30
2019-01-31
Total |  | 140 | 210 | 682 | 820400
Average |  | 20 | 30 | 97.4286 | 117200
Maximum |  | 20 | 30 | 126.5 | 117200
Minimum |  | 20 | 30 | 73 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Formulas:
Day = [Day, row above]+1
Note on F8: BCOperator: 5860 = water wash / min

## BW 2
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 2 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1899-12-31 | 0:00 | 1899-12-31
2 | [11 empty] | THIS WASH | 1900-01-04 | 0:30 | 1900-01-04 00:30
3 | [12 empty] | TOTAL HOURS
4
5 | 0:30 | 20 | 30 | 96.5 | 117200 | 46875 | 9 | 16531.5212 | CBW |  | 164075 |  |  | 96.5
6
7
8
9 | 10:00 | 20 | 30 | 105 | 117200 | 46354.1667 | 8.9 | 17787.8026 | GHE | TIME | 163554.1667
10
11
12
13
14 | 3:00 | 20 | 30 | 113 | 117200 | 52083.3333 | 10 | 21509.0605 | DH |  | 169283.3333
15
16
17
18 | 10:30 | 20 | 30 | 103.5 | 117200 | 44270.8333 | 8.5 | 16745.6601 | CBW |  | 161470.8333
19
20
21
22 | 9:00 | 20 | 30 | 94.5 | 117200 | 44270.8333 | 8.5 | 15289.5158 | JMM |  | 161470.8333
23
24
25
26
27 | 7:00 | 20 | 30 | 118 | 117200 | 26041.6667 | 5 | 11230.3944 | MN |  | 143241.6667
28
29
30
31 | 14:00 | 20 | 30 | 104 | 117200 | 28125 | 5.4 | 10689.8127 | R.H. |  | 145325
Total |  | 140 | 210 | 734.5 | 820400
Average |  | 20 | 30 | 104.9286 | 117200
Maximum |  | 20 | 30 | 118 | 117200
Minimum |  | 20 | 30 | 94.5 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash /min

## BW 3
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 3 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1899-12-31 | 0:00 | 1899-12-31
2 | [11 empty] | THIS WASH | 1900-01-04 | 4:00 | 1900-01-04 04:00
3 | [12 empty] | TOTAL HOURS
4
5 | 4:00 | 20 | 30 | 100 | 117200 | 43229.1667 | 8.3 | 18908.3288 | CBW |  | 160429.1667 |  |  | 100
6
7
8
9
10 | 9:30 | 20 | 30 | 125.5 | 117200 | 46875 | 9 | 25731.2739 | GHE | TIME | 164075
11
12
13
14 | 13:00 | 20 | 30 | 99.5 | 117200 | 52083.3333 | 10 | 22667.2134 | DB | LOH | 169283.3333
15
16
17
18 | 14:00 | 20 | 30 | 97 | 117200 | 44270.8333 | 8.5 | 18783.0326 | CBW |  | 161470.8333
19
20
21
22 | 4:00 | 20 | 30 | 86 | 117200 | 63020.8333 | 12.1 | 23706.0324 | R.H. |  | 180220.8333
23
24
25
26 | 10:00 | 20 | 30 | 102 | 117200 | 31250 | 6 | 13942.0448 | MN |  | 148450
27
28
29
30 | 11:00 | 20 | 35 | 97 | 117200 | 52256.9444 | 8.6 | 19004.0095 | SN | AUTO | 169456.9444
31
Total |  | 140 | 215 | 707 | 820400
Average |  | 20 | 30.7143 | 101 | 117200
Maximum |  | 20 | 35 | 125.5 | 117200
Minimum |  | 20 | 30 | 86 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 4
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 4 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-18 | 10:00 | 1900-01-18 10:00
2 | [11 empty] | THIS WASH | 1900-01-21 | 15:00 | 1900-01-21 15:00
3 | [12 empty] | TOTAL HOURS
4
5 | 14:00 | 20 | 30 | 110 | 117200 | 39583.3333 | 7.6 | 19045.0155 | SN |  | 156783.3333 |  |  | 77
6
7
8
9
10 | 15:00 | 20 | 30 | 121 | 117200 | 44270.8333 | 8.5 | 23430.3809 | GE | TIME | 161470.8333
11
12
13
14
15 | 11:30 | 20 | 30 | 116.5 | 117200 | 46875 | 9 | 23886.0033 | GE |  | 164075
16
17
18
19 | 10:00 | 20 | 30 | 94.5 | 117200 | 44270.8333 | 8.5 | 18298.9338 | JMM |  | 161470.8333
20
21
22
23 | 4:00 | 20 | 30 | 76 | 117200 | 62500 | 12 | 20776.3805 | R.H. |  | 179700
24
25
26
27 | 9:00 | 20 | 30 | 101 | 117200 | 26041.6667 | 5 | 11504.4651 | MN |  | 143241.6667
28
29
30
31 | 8:00 | 20 | 30 | 95 | 117200 | 29166.6667 | 5.6 | 12119.5553 | R.H. |  | 146366.6667
Total |  | 140 | 210 | 714 | 820400
Average |  | 20 | 30 | 102 | 117200
Maximum |  | 20 | 30 | 121 | 117200
Minimum |  | 20 | 30 | 76 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 5
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 5 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-25 | 8:00 | 1900-01-25 08:00
2 | [11 empty] | THIS WASH | 1900-01-29 | 13:30 | 1900-01-29 13:30
3 | [12 empty] | TOTAL HOURS
4 | 14:30 | 20 | 30 | 86.5 | 117200 | 48958.3333 | 9.4 | 18523.3279 | SN | TIME | 166158.3333
5 | [13 empty] | 101.5
6
7
8 | 14:00 | 20 | 30 | 95.5 | 117200 | 42708.3333 | 8.2 | 17839.8943 | SN |  | 159908.3333
9
10
11
12
13 | 10:00 | 20 | 30 | 116 | 117200 | 52083.3333 | 10 | 26426.098 | DB |  | 169283.3333
14
15
16
17 | 15:00 | 20 | 30 | 101 | 117200 | 39062.5 | 7.5 | 17256.6976 | WL |  | 156262.5
18
19
20
21 | 16:00 | 20 | 30 | 97 | 117200 | 44270.8333 | 8.5 | 18783.0326 | JMM |  | 161470.8333
22
23
24
25
26 | 8:00 | 20 | 30 | 112 | 117200 | 49479.1667 | 9.5 | 24239.1106 | MN |  | 166679.1667
27
28
29
30 | 13:30 | 20 | 35 | 101.5 | 117200 | 52256.9444 | 8.6 | 19885.6388 | RH | HEAD | 169456.9444
31
Total |  | 140 | 215 | 709.5 | 820400
Average |  | 20 | 30.7143 | 101.3571 | 117200
Maximum |  | 20 | 35 | 116 | 117200
Minimum |  | 20 | 30 | 86.5 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 6
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 6 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-18 | 11:30 | 1900-01-18 11:30
2 | [11 empty] | THIS WASH | 1900-01-22 | 14:30 | 1900-01-22 14:30
3 | [12 empty] | TOTAL HOURS
4
5 | 9:00 | 20 | 30 | 105 | 117200 | 38020.8333 | 7.3 | 17461.7277 | SN |  | 155220.8333 |  |  | 99
6
7
8
9
10 | 12:00 | 20 | 30 | 123 | 117200 | 46875 | 9 | 25218.6987 | GE | TIME | 164075
11
12
13
14 | 15:30 | 20 | 30 | 99.5 | 117200 | 52083.3333 | 10 | 22667.2134 | GE |  | 169283.3333
15
16
17
18
19 | 11:30 | 20 | 30 | 116 | 117200 | 44270.8333 | 8.5 | 22462.1833 | CBW |  | 161470.8333
20
21
22
23 | 14:30 | 20 | 30 | 99 | 117200 | 31250 | 6 | 13531.9847 | DH |  | 148450
24
25
26
27
28 | 9:30 | 20 | 30 | 115 | 117200 | 54687.5 | 10.5 | 27508.2012 | DH |  | 171887.5
29
30
31
Total |  | 120 | 180 | 657.5 | 703200
Average |  | 20 | 30 | 109.5833 | 117200
Maximum |  | 20 | 30 | 123 | 117200
Minimum |  | 20 | 30 | 99 | 117200
|  | 6 | 6 | 6 | 6
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 7
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 7 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1899-12-31 | 0:00 | 1899-12-31
2 | [11 empty] | THIS WASH | 1900-01-04 | 2:30 | 1900-01-04 02:30
3 | [12 empty] | TOTAL HOURS
4
5 | 2:30 | 20 | 30 | 98.5 | 117200 | 46875 | 9 | 20195.462 | CBW |  | 164075 |  |  | 98.5
6
7
8
9 | 13:30 | 20 | 30 | 107 | 117200 | 46354.1667 | 8.9 | 21694.4596 | GHE | TIME | 163554.1667
10
11
12
13 | 16:00 | 20 | 30 | 98.5 | 117200 | 52083.3333 | 10 | 22439.4022 | GE |  | 169283.3333
14
15
16
17
18 | 7:00 | 20 | 30 | 111 | 117200 | 41666.6667 | 8 | 20229.6337 | CBW |  | 158866.6667
19
20
21 | 11:00 | 20 | 30 | 76 | 117200 | 39062.5 | 7.5 | 12985.2378 | JMM |  | 156262.5
22
23
24 | 12:00 | 20 | 30 | 73 | 117200 | 44270.8333 | 8.5 | 14135.6843 | MN |  | 161470.8333
25
26
27
28 | 11:00 | 20 | 30 | 95 | 117200 | 54687.5 | 10.5 | 22724.1662 | MN | HEAD | 171887.5
29
30
31
Total |  | 140 | 210 | 659 | 820400
Average |  | 20 | 30 | 94.1429 | 117200
Maximum |  | 20 | 30 | 111 | 117200
Minimum |  | 20 | 30 | 73 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 8
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 8 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-19 | 10:00 | 1900-01-19 10:00
2 | [11 empty] | THIS WASH | 1900-01-22 | 23:00 | 1900-01-22 23:00
3 | 9:30 | 20 | 30 | 33.5 | 117200 | 43229.1667 | 8.3 | 6334.2901 | SN | HEAD | 160429.1667 |  | TOTAL HOURS
4
5 | [13 empty] | 85
6
7 | 16:30 | 20 | 30 | 103 | 117200 | 44791.6667 | 8.6 | 20179.5152 | SN |  | 161991.6667
8
9
10
11
12
13 | 2:30 | 20 | 30 | 130 | 117200 | 31250 | 6 | 17769.2728 | DH |  | 148450
14
15
16 | 14:30 | 20 | 30 | 84 | 117200 | 31250 | 6 | 11481.684 | JMM |  | 148450
17
18
19
20 | 10:00 | 20 | 30 | 91 | 117200 | 39062.5 | 7.5 | 15548.1137 | JMM |  | 156262.5
21
22
23
24 | 8:00 | 20 | 30 | 94 | 117200 | 44270.8333 | 8.5 | 18202.1141 | MN |  | 161470.8333
25
26
27
28
29 | 8:00 | 20 | 30 | 120 | 117200 | 49479.1667 | 9.5 | 25970.4757 | DH |  | 166679.1667
30
31
Total |  | 140 | 210 | 655.5 | 820400
Average |  | 20 | 30 | 93.6429 | 117200
Maximum |  | 20 | 30 | 130 | 117200
Minimum |  | 20 | 30 | 33.5 | 117200
|  | 7 | 7 | 7 | 7
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 5860 water wash / min

## BW 9
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 9 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-26 | 14:30 | 1900-01-26 14:30
2 | [11 empty] | THIS WASH | 1900-01-30 | 2:00 | 1900-01-30 02:00
3 | [12 empty] | TOTAL HOURS
4
5 | 8:30 | 20 | 30 | 104.5 | 125000 | 44791.6667 | 8.6 | 17763.6781 | RH | TIME | 169791.6667 |  |  | 83.5
6
7
8
9
10 | 8:00 | 20 | 30 | 119.5 | 125000 | 52083.3333 | 10 | 23620.3352 | WL | TIME | 177083.3333
11
12
13
14 | 6:30 | 20 | 30 | 94.5 | 125000 | 57291.6667 | 11 | 20546.7268 | GE |  | 182291.6667
15
16
17
18 | 8:30 | 20 | 30 | 98 | 125000 | 59895.8333 | 11.5 | 22276.2492 | CBW |  | 184895.8333
19
20 | 14:30 | 20 | 30 | 54 | 125000 | 57291.6667 | 11 | 11740.9867 | JMM |  | 182291.6667
21
22
23 | 12:30 | 25 | 45 | 70 | 156250 | 101562.5 | 13 | 17987.0335 | DH |  | 257812.5
24
25
26
27 | 14:30 | 20 | 30 | 98 | 125000 | 61458.3333 | 11.8 | 22857.3688 | DH |  | 186458.3333
28
29
30
31 | 2:00 | 20 | 30 | 83.5 | 125000 | 66145.8333 | 12.7 | 20960.8238 | CBW |  | 191145.8333
Total |  | 165 | 255 | 722 | 1031250
Average |  | 20.625 | 31.875 | 90.25 | 128906.25
Maximum |  | 25 | 45 | 119.5 | 156250
Minimum |  | 20 | 30 | 54 | 125000
|  | 8 | 8 | 8 | 8
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 10
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 10 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-25 | 19:00 | 1900-01-25 19:00
2 | [11 empty] | THIS WASH | 1900-01-29 | 10:00 | 1900-01-29 10:00
3 | 9:00 | 20 | 30 | 33 | 125000 | 42708.3333 | 8.2 | 5348.6717 | RH |  | 167708.3333 |  | TOTAL HOURS
4
5 | [13 empty] | 87
6
7 | 14:00 | 20 | 30 | 101 | 125000 | 50520.8333 | 9.7 | 19364.7217 | RH |  | 175520.8333
8
9
10
11
12
13 | 1:00 | 20 | 30 | 131 | 125000 | 57291.6667 | 11 | 28482.7641 | DH |  | 182291.6667
14
15
16 | 13:00 | 20 | 30 | 84 | 125000 | 54687.5 | 10.5 | 17433.5863 | WL |  | 179687.5
17
18
19 | 14:00 | 20 | 30 | 73 | 125000 | 67708.3333 | 13 | 18757.9064 | CBW |  | 192708.3333
20
21
22 | 10:00 | 20 | 30 | 68 | 125000 | 67708.3333 | 13 | 17473.1183 | CBW |  | 192708.3333
23
24
25
26 | 19:00 | 20 | 30 | 105 | 125000 | 61458.3333 | 11.8 | 24490.038 | GHE | HIT PROB | 186458.3333
27
28
29
30 | 10:00 | 20 | 60 | 87 | 125000 | 131250 | 12.6 | 21667.4573 | sn | head | 256250
31
Total |  | 160 | 270 | 682 | 1000000
Average |  | 20 | 33.75 | 85.25 | 125000
Maximum |  | 20 | 60 | 131 | 125000
Minimum |  | 20 | 30 | 33 | 125000
|  | 8 | 8 | 8 | 8
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 11
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 11 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1899-12-31 | 0:00 | 1899-12-31
2 | [11 empty] | THIS WASH | 1900-01-03 | 3:00 | 1900-01-03 03:00
3 | [12 empty] | TOTAL HOURS
4 | 3:00 | 20 | 30 | 75 | 125000 | 48958.3333 | 9.4 | 13935.0095 | CBW |  | 173958.3333
5 | [13 empty] | 75
6
7
8 | 0:30 | 20 | 30 | 93.5 | 125000 | 47916.6667 | 9.2 | 17002.6882 | CBW |  | 172916.6667
9
10
11
12 | 6:30 | 20 | 30 | 102 | 125000 | 52083.3333 | 10 | 20161.2903 | GE |  | 177083.3333
13
14
15 | 2:30 | 20 | 30 | 68 | 125000 | 57291.6667 | 11 | 14784.9462 | DH |  | 182291.6667
16
17
18 | 13:00 | 20 | 30 | 82.5 | 125000 | 65104.1667 | 12.5 | 20383.6575 | JMM |  | 190104.1667
19
20 | 15:30 | 20 | 30 | 50.5 | 125000 | 57291.6667 | 11 | 10979.9968 | JMM |  | 182291.6667
21
22 | 19:30 | 20 | 30 | 52 | 125000 | 67708.3333 | 13 | 13361.7963 | RH | HEAD | 192708.3333
23
24
25
26 | 14:30 | 20 | 30 | 91 | 125000 | 54687.5 | 10.5 | 18886.3852 | DH | HEAD | 179687.5
27
28
29 | 14:30 | 20 | 30 | 72 | 125000 | 54687.5 | 10.5 | 14943.074 | DH |  | 179687.5
30
31
Total |  | 180 | 270 | 686.5 | 1125000
Average |  | 20 | 30 | 76.2778 | 125000
Maximum |  | 20 | 30 | 102 | 125000
Minimum |  | 20 | 30 | 50.5 | 125000
|  | 9 | 9 | 9 | 9
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## BW 12
Surface Water System Monthly Operation Report
Operation of Filters
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Filter Number: 12 |  |  |  |  | 2019-01-01
Day | Time Backwash Initiated (military) | Time Backwashed (minutes) | Time Rewashed (minutes) | Time in Service (hours) | Wash Water Used (gallons) | Rewash Water (gallons) | Flow At Time of Backwash | UFRV | Oper Init | Comments | BACKWASH WATER USED |  | DATE | TIME
1 | [11 empty] | LAST WASH | 1900-01-26 | 2:00 | 1900-01-26 02:00
2 | [11 empty] | THIS WASH | 1900-01-29 | 0:00 | 1900-01-29
3 | [12 empty] | TOTAL HOURS
4 | 10:30 | 20 | 30 | 82.5 | 125000 | 50520.8333 | 9.7 | 15817.7182 | RH | TIME | 175520.8333
5 | [13 empty] | 70
6
7
8 | 11:00 | 20 | 30 | 95.5 | 125000 | 49479.1667 | 9.5 | 17932.6771 | SN |  | 174479.1667
9
10
11
12 | 10:00 | 20 | 30 | 95 | 125000 | 52083.3333 | 10 | 18777.6724 | GE |  | 177083.3333
13
14
15 | 8:00 | 20 | 30 | 70 | 125000 | 49479.1667 | 9.5 | 13144.3707 | GHE | HIT PROB | 174479.1667
16
17
18 | 21:30 | 20 | 30 | 85.5 | 125000 | 70312.5 | 13.5 | 22814.8719 | SN | HEAD | 195312.5
19
20
21 | 3:00 | 20 | 30 | 53.5 | 125000 | 59895.8333 | 11.5 | 12161.0136 | R.H. |  | 184895.8333
22
23 | 8:00 | 20 | 30 | 53 | 125000 | 66666.6667 | 12.8 | 13409.2347 | MN | HEAD | 191666.6667
24
25
26
27 | 2:00 | 20 | 30 | 90 | 125000 | 61458.3333 | 11.8 | 20991.4611 | GE | HIT PROBE | 186458.3333
28
29
30 | 0:00 | 20 | 30 | 70 | 125000 | 63020.8333 | 12.1 | 16741.7774 | GE | HIT PROBE | 188020.8333
31
Total |  | 180 | 270 | 695 | 1125000
Average |  | 20 | 30 | 77.2222 | 125000
Maximum |  | 20 | 30 | 95.5 | 125000
Minimum |  | 20 | 30 | 53 | 125000
|  | 9 | 9 | 9 | 9
Prepared by: _________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent
Note on F8: BCOperator: 6250 water wash / min

## FILTER PERFORMANCE (hidden)
Filter Performance Test
[18 empty] | Filter 1 |  | Filter 2 |  | Filter 3 |  | Filter 4 |  | Filter 5 |  | Filter 6 |  | Filter 7 |  | Filter 8 |  | Filter 9 |  | Filter 10 |  | Filter 11 |  | Filter 12
Date | OPER | Time | Filter # washed | Flow to Filter Cluster, MGD | Raw Uv 254 | Calculated Alum Dose, mg/L | Alum Dose, mg/L | Filter Washed headloss, ft | Filter washed Time in service, hrs | Filter # Affected with turbidity spike | Filter affected by turbidity spike Headloss, ft | Filter affected by turbidity spike time in service, hrs | Reason for filter washed (time or Headloss) | Settled water turbidity avg. for plant that filter was washed on. 24 hr avg., ntu | Filter affected max turbidity, ntu | Filtration rate, gpm'sq.ft | Solids Loading onto Filters, lbs/day/filter | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs | Filter Head at the time the filter in Column C in the same cluster was washed, ft | Filter in service time when filter in Column C in the same cluster was washed, hrs |  | DATE | TIME
[42 empty] | LAST WASH | 2015-05-29 | 1:00
2015-05-28 | CBW | 1800 | 9 | 11.4 | 0.294 | 38.6842 | 40 | 4.25 | 92 | 10 | 3.91 | 82 | TIME | 0.5 | 0.19 | 5.492 | 35.6535 | [18 empty] | 1.59 | 82 | 2.3 | 5 | 5.29 | 73.5 | THIS WASH | 2015-05-31 | 0:00
2015-05-28 | JM | 2100 | 7 | 10.6 | 0.357 | 46.9737 | 40 | 3.91 | 65 | NONE |  |  | HEAD | 0.47 |  | 5.1066 | 31.1624 | [8 empty] | 5.87 | 106 | 3.61 | 11 |  |  | 3.33 | 25 | [9 empty] | TOTAL HOURS
2015-05-29 | CBW | 100 | 10 | 11.3 | 0.292 | 38.4211 | 40 | 1.9 | 89 | 12 | 6.35 | 101.5 | TURB | 0.5 | 0.11 | 5.4438 | 35.3407 | [16 empty] | 2.45 | 7 |  |  | 2.8 | 12 | 6.35 | 102.5 |  | 2015-05-29 | 48
2015-05-29 | GE | 600 | 3 | 10.4 | 0.276 | 36.3158 | 40 | 4.11 | 87 | NONE |  |  | HEAD | 0.45 |  | 5.0102 | 29.2734 | 5.21 | 86 | 4.23 | 22 |  |  | 4.22 | 89 | [17 empty] | 2015-05-31
2015-05-29 | MN | 700 | 5 | 10.5 | 0.276 | 36.3158 | 40 | 4.74 | 116 | NONE |  |  | TIME/HEAD | 0.29 |  | 5.0584 | 19.0465 | [10 empty] | 3.47 | 21 | 2.29 | 10 | 2.66 | 35
[16 empty] | 0 | 0
2015-05-29 | CBW | 2300 | 12 | 11.2 | 0.312 | 41.0526 | 44 | 5.28 | 123.5 | NONE |  |  | NTU/TIME | 0.591 |  | 5.3956 | 41.4031 | [16 empty] | 1.91 | 29 | 2.4 | 22 | 2.76 | 34 | 5.28 | 132.5
2015-05-30 | GE | 600 | 4 | 10.4 | 0.229 | 30.1316 | 40 | 3.66 | 120 | NONE |  |  | TIME/HEAD | 0.46 |  | 5.0102 | 29.9239 | 4.1 | 110.5 | 3.69 | 75 | 1.98 | 24
2015-05-30 | GE | 1030 | 1 | 10.4 | 0.235 | 30.9211 | 40 | 3.54 | 115 | NONE |  |  | TIME/HEAD | 0.52 |  | 5.0102 | 33.827 |  |  | 3.13 | 79.5 | 1.86 | 29 | 1.01 | 4.5
2015-05-31 | MN | 1000 | 2 | 11.2 | 0.226 | 29.7368 | 40 | 3.25 | 103 | NONE |  |  | TIME/HEAD | 0.41 |  | 5.3956 | 28.723 | 0.083 | 23.5 |  |  | 1.25 | 52.5 | 0.47 | 28
NEW MONTH | [15 empty] | 0 | 0
2015-06-02 | CBW | 4:30 | 8 | 34.1 | 0.241 | 31.7105 | 35 | 4.57 | 127.5/28.5 | NONE |  |  | HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 4.93 | 66/28.5 | 5.78 | 28.5 | 4.24 | 105/28.5
2015-06-02 | MN | 600 | 6 | 34.1 | 0.176 | 23.1579 | 35 | 3.71 | 115 / 30 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.33 | 94 / 30 |  |  | 2.43 | 104 / 30 | 1.03 | 129/30
2015-06-02 | GE | 1000 | 7 | 34.1 | 0.195 | 25.6579 | 32 | 2.42 | 104/34 | NONE |  |  | TIME/HEAD | 0.268 |  | 4.4803 | 57.1632 | [8 empty] | 3.86 | 99/34 | 0.09 | 4 |  |  | 0.45 | 5.5
2015-06-02 | GE | 1330 | 11 | 34.1 | 0.217 | 28.5526 | 32 | 5.37 | 120.5/37.5 | NONE |  |  | TIME/HEAD | 0.272 |  | 4.4803 | 58.0164 | [16 empty] | 5.45 | 115.5 | 1.9 | 67.5 |  |  | 3.83 | 86.5
2015-06-02 | CBW | 1930 | 3 | 34.1 | 0.181 | 23.8158 | 35 | 2.57 | 65.5/43.5 | NONE |  |  | TIME/HEAD | 0.281 |  | 4.4803 | 59.936 | 1.07 | 43.5 | 1.23 | 43.5 | 1.55 | 43.5 | 0.77 | 43.5
2015-06-03 | HE | 700 | 10 | 26.1 | 0.247 | 32.5 | 35 | 1.4 | 55 | NONE |  |  | TIME/HEAD | 0.25 |  | 3.4292 | 40.8139 | [16 empty] | 4.9 | 55 | 1.4 | 55 | 1.49 | 17 | 3.82 | 55
2015-06-10 | CBW | 1130 | 2 | 33.2 | 0.251 | 33.0263 | 35 | 0.19 | 116.5 | NONE |  |  | TIME/HEAD | 0.3 |  | 4.362 | 62.2998 | 0.01 | 29.5 | 0.91 | 116.5 | 0.48 | 26 | 0.27 | 92.5
2015-06-10 | CBW | 1330 | 5 | 33.2 | 0.251 | 33.0263 | 35 | 1.77 | 117.5 | NONE |  |  | TIME/HEAD | 0.21 |  | 4.362 | 43.6099 | [8 empty] | 1.77 | 117.5 | 0.49 | 69 | 0.06 | 45 | 0.05 | 48
2015-06-10 | GHE | 1900 | 12 | 33.2 | 0.239 | 31.4474 | 35 | 4.72 | 156 | NONE |  |  | TIME/HEAD | 0.2 |  | 4.362 | 41.5332 | [16 empty] | 0.05 | 32.5 | 0.06 | 35 | 0.05 | 36
2015-06-11 | GHE | 2:00 | 4 | 33.1 | 0.239 | 31.4474 | 35 | 3.81 | 107 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.3489 | 64.1826 | 3.54 | 44 | 3.48 | 14.5 | 3.51 | 40.5
2015-06-11 | CBW | 6:00 | 7 | 33.1 | 0.283 | 37.2368 | 35 | 3.75 | 67 | NONE |  |  | HEAD/CLEAR | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 3.99 | 16.5 | 5.53 | 85.5 | 3.75 | 61.5 | 0.05 | 64.5
2015-06-11 | CBW | 8:00 | 6 | 33.1 | 0.283 | 37.2368 | 35 | 3.41 | 87.5 | NONE |  |  | TIME/HEAD | 0.323 |  | 4.3489 | 66.8741 | [8 empty] | 2.92 | 18.5 |  |  | 1.56 | 62.5 | 2.1 | 66.5
2015-06-12 | CBW | 9:00 | 11 | 35.7 | 0.291 | 38.2895 | 35 | 3.91 | 98 | NONE |  |  | TIME/HEAD | 0.228 |  | 4.6905 | 50.9132
2015-06-12 | CBW | 14:00 | 8 | 35.7 | 0.232 | 30.5263 | 35 | 1.53 | 96.5 | NONE |  |  | TIME/HEAD | 0.278 |  | 4.6905 | 62.0784 | [8 empty] | 2.67 | 48.5 | 2.35 | 30 | 2.66 | 32 | 1.53 | 96.5 | 2.98 | 70.5 | 2.21 | 75 | 3.91 | 98 | 2.28 | 38
2015-06-13 | CBW | 600 | 1 | 38.6 | 0.224 | 29.4737 | 35 | 3.91 | 96 | NONE |  |  | TIME/HEAD | 0.3 |  | 5.0715 | 72.4329 |  |  | 3.82 | 75.5 | 3.62 | 69.5 | 2.49 | 52
2015-06-13 | CBW | 800 | 10 | 38.6 | 0.224 | 29.4737 | 35 | 3.02 | 98 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [16 empty] | 4.78 | 94.5 |  |  | 2.36 | 23 | 3.36 | 61
2015-06-13 | CBW | 900 | 3 | 38.6 | 0.224 | 29.4737 | 35 | 3.54 | 95.5 | NONE |  |  | TIME/HEAD | 0.35 |  | 5.0715 | 84.505 | 1.91 | 3 | 3.66 | 78.5 |  |  | 2.4 | 55
2015-06-13 | CBW | 1100 | 9 | 38.6 | 0.224 | 29.4737 | 35 | 4.78 | 96.5 | NONE |  |  | TIME/HEAD | 0.27 |  | 5.0715 | 65.1896 | [18 empty] | 2.49 | 3 | 2.36 | 26 | 3.36 | 64
2015-06-14 | CBW | 600 | 7 | 42 | 0.26 | 34.2105 | 35 | 3.27 | 72 | NONE |  |  | HEAD/CLEAR WELL | 0.208 |  | 5.5182 | 54.6437 | [8 empty] | 5.21 | 88.5 | 4.31 | 70 |  |  | 2.97 | 40
2015-06-14 | CBW | 800 | 2 | 42 | 0.26 | 34.2105 | 35 | 3.59 | 92.5 | NONE |  |  | TIME | 0.257 |  | 5.5182 | 67.5165 | 3.37 | 26 |  |  | 2.96 | 23 | 3.74 | 78
2015-06-14 | CBW | 900 | 5 | 42 | 0.26 | 34.2105 | 35 | 5.09 | 91.5 | NONE |  |  | TIME | 0.208 |  | 5.5182 | 54.6437 | [10 empty] | 3.86 | 73 | 2.16 | 3 | 2.4 | 43
2015-06-14 | CBW | 1430 | 4 | 42 | 0.24 | 31.5789 | 35 | 4.68 | 84.5 | NONE |  |  | HEAD/CLEAR WELL | 0.257 |  | 5.5182 | 67.5165 | 4.04 | 32.5 | 3.96 | 6.5 | 3.54 | 29.5 | [10 empty] | 2.47 |  | 2.49 |  | 3.36 |  | 4.67
2015-06-14 | GE | 1800 | 8 | 42 | 0.218 | 28.6842 | 35 | 3.61 | 22 | NONE |  |  | HEAD | 0.31 |  | 5.5182 | 81.4401 | [8 empty] | 4.08 | 9 | 5.65 | 82 | 3.52 | 12
2015-06-15 | GE | 500 | 6 | 41.4 | 0.22 | 28.9474 | 35 | 3.88 | 23 | NONE |  |  | HEAD | 0.32 |  | 5.4394 | 82.8662 | [8 empty] | 4.52 | 20 |  |  | 3.88 | 23 | 3.15 | 11
2015-06-15 | CBW | 10:00 | 12 | 41.4 | 0.254 | 33.4211 | 35 | 5.15 | 111 | NONE |  |  | TIME | 0.202 |  | 5.4394 | 52.3093
2015-06-16 | CBW | 13:30 | 11 | 40.4 | 0.229 | 30.1316 | 35 | 5.36 | 100.5 | NONE |  |  | TIME | 0.216 |  | 5.308 | 54.5836
2015-06-17 | DMH | 1500 | 10 | 40.2 | 0.251 | 33.0263 | 40 | 1.49 | 103 | None |  |  | TIME | 0.225 |  | 5.2817 | 56.5765 | [16 empty] | 5.1 | 100 |  |  | 2.8 | 25.5 | 3.6 | 53
2015-06-18 | WL | 6:00 | 1 | 36.8 | 0.262 | 34.4737 | 40 | 2.2 | 120 | None |  |  | Time | 0.316 |  | 4.835 | 72.7381 |  |  | 1.54 | 93.4 | 2.23 | 84 | 0.79 | 81.5
2015-06-18 | WL | 9:00 | 3 | 36.8 | 0.262 | 34.4737 | 40 | 1.55 | 120 | NONE |  |  | Time | 0.316 |  | 4.835 | 72.7381 | 0.23 | 0.75 | 1.55 | 95.4 |  |  | 1.31 | 83.5
2015-06-18 | DMH | 1300 | 4 | 36.8 | 0.262 | 34.4737 | 40 | 1.31 | 94.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 5.79 | 1.56 | 100.45 | 0 | 3.78
2015-06-18 | DMH | 1530 | 2 | 36.8 | 0.262 | 34.4737 | 40 | 1.57 | 103.5 | NONE |  |  | TIME | 0.316 |  | 4.835 | 72.7381 | 0.23 | 8.17 |  |  | 0 | 6.16 | 0.31 | 0.64
2015-06-19 | WL | 9:00 | 7 | 33.7 | 0.274 | 36.0526 | 40 | 3.5 | 123 | NONE |  |  | Time/HEAD | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 3.7 | 118.54 | 2.4 | 98.21 |  |  | 2.7 | 109.62
2015-06-19 | DMH | 11:00 | 5 | 33.7 | 0.274 | 36.0526 | 40 | 3.88 | 122 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [10 empty] | 2.33 | 100.25 | 0.33 | 0.072 | 2.73 | 111.65
2015-06-19 | DMH | 13:00 | 6 | 33.7 | 0.274 | 36.0526 | 40 | 2.32 | 104 | NONE |  |  | TIME | 0.38 |  | 4.4277 | 80.1015 | [8 empty] | 0.36 | 1.03 |  |  | 0.33 | 3.01 | 2.72 | 113.94
2015-06-20 | WL | 8:30 | 8 | 31.4 | 0.289 | 38.0263 | 45 | 2.72 | 134.5 | NONE |  |  | TIME | 0.243 |  | 4.1255 | 47.7269 | [8 empty] | 0.36 | 20.71 | 0.02 | 18.65 | 0.33 | 22.68
2015-06-20 | WL | 12:00 | 12 | 31.4 | 0.31 | 40.7895 | 45 | 5.32 | 122 | NONE | 9,11 |  | TIME | 0.374 | 0.06 | 4.1255 | 73.4562 | [16 empty] | 2.23 |  | 2.25 |  | 4.41
2015-06-22 | DMH | 13:30 | 11 | 33.5 | 0.327 | 43.0263 | 50 | 6.42 | 144 | 9,10 | 9 |  | TIME/HEAD | 0.466 | .09,.5 | 4.4015 | 97.6468 | [16 empty] | 4.28 | 114.5 | 1.75 | 118.5 |  |  | 2.4 | 49.5
2015-06-23 | WL | 6:00 | 10 | 42.1 | 0.305 | 40.1316 | 50 | 1.25 | 135 | 9 |  |  | TIME | 0.419 | 0.13 | 5.5314 | 110.3376 | [16 empty] | 5.28 |  |  |  | 2.21 |  | 3.47
2015-06-23 | WL | 9:00 | 9 | 42.1 | 0.305 | 40.1316 | 50 | 5.28 | 134 | None | 11,12 |  | TIME | 0.419 |  | 5.5314 | 110.3376 | [18 empty] | 2.26 |  | 2.72 |  | 3.98
2015-06-24 | MN | 1200 | 3 | 42.1 | 0.294 | 38.6842 | 40 | 3.54 | 147 | NONE |  |  | TIME/HEAD | 0.335 |  | 5.5314 | 88.2174 | 2.75 | 150 | 2.2 | 139 |  |  | 2.34 | 142
2015-06-24 | MN | 1600 | 7 | 37.1 | 0.297 | 39.0789 | 40 | 3.87 | 127 | NONE |  |  | TIME/HEAD | 0.31 |  | 4.8744 | 71.9388 | [8 empty] | 3.89 | 125 | 3.05 | 119 |  |  | 2.9 | 104.5
2015-06-25 | GHE | 2:00 | 4 | 37.1 | 0.372 | 48.9474 | 50 | 3.83 | 157 | None |  |  | Time | 0.4 |  | 4.8744 | 92.8242 | 4.76 | 164 | 4.26 | 154.5 | 0.46 | 161
2015-06-25 | MN | 830 | 8 | 37.1 | 0.306 | 40.2632 | 40 | 3.96 | 120 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 | [8 empty] | 5.83 | 141.5 | 4.63 | 138.5 | 0.44 | 18.5
2015-06-25 | MN | 1000 | 1 | 37.1 | 0.306 | 40.2632 | 40 | 4.78 | 172 | NONE |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906 |  |  | 4.21 | 162.5 | 0.46 | 22 | 0.26 | 3 |  |  | 4.61 | 142.5 | 0.97 | 23 | 0.47 | 4.5
2015-06-25 | MN | 1300 | 5 | 37.1 | 0.306 | 40.2632 | 40 | 5.73 | 148 |  |  |  | TIME/HEAD | 0.374 |  | 4.8744 | 86.7906
2015-06-25 | CBW | 1900 | 12 | 37.1 | 0.304 | 40 | 40 | 6.62 | 127 | NONE |  |  | TIME | 0.46 |  | 4.8744 | 106.7478 | [16 empty] | 4.39 | 58 | 1.26 | 61 | 5.75 | 77.5
2015-06-25 | CBW | 2300 | 11 | 37.1 | 0.304 | 40 | 40 | 5.75 | 81.5 | NONE |  |  | TIME | 0.68 |  | 4.8744 | 157.8011 | [16 empty] | 4.39 | 62 | 1.25 | 65 |  |  | 0.76 | 6
2015-06-26 | CBW | 1300 | 2 | 37.1 | 0.304 | 40 | 40 | 4.17 | 178.5 | NONE |  |  | TIME | 0.58 |  | 4.8744 | 134.5951 | 0.27 | 15 |  |  | 0.97 | 37 | 0.05 | 18 | 0.44 | 18 |  |  | 0.97 | 41 | 0.47 | 24.5
2015-06-26 | MN | 900 | 6 | 37.1 | 0.304 | 40 | 40 | 4.55 | 164 | NONE |  |  | TIME/HEAD | 0.52 |  | 4.8744 | 120.6715
2015-06-27 | CBW | 4:30 | 10 | 37.1 | 0.311 | 40.9211 | 40 | 2.81 | 94.5 | 9 | 6.4 | 91.5 | Turb. | 0.48 |  | 4.8744 | 111.389 | [16 empty] | 6.4 | 91.5 |  |  | 2.32 | 29.5 | 2.97 | 33.5
2015-06-27 | CBW | 19:00 | 9 | 37.1 | 0.338 | 44.4737 | 40 | 5.89 | 106 | NONE |  |  | TIME | 0.54 |  | 4.8744 | 125.3127 | [18 empty] | 2.89 | 14.5 | 3.4 | 44 | 3.37 | 48
2015-06-28 | GHE | 19:00 | 7 | 38.3 | 0.226 | 29.7368 | 35 | 2.94 | 101 | NONE |  |  | TIME/AUTO | 0.38 |  | 5.0321 | 91.0353 | [8 empty] | 2.46 | 78 | 1.4 | 58 |  |  | 1.81 | 82.5
2015-06-29 | CBW | 600 | 3 | 38.3 | 0.226 | 29.7368 | 35 | 4 | 114 | NONE |  |  | HEAD | 0.62 |  | 5.0321 | 148.5312 | 2.29 | 102 | 1.01 | 76 |  |  | 2.03 | 100
2015-06-29 | MN | 1030 | 8 | 42 | 0.226 | 29.7368 | 35 | 3.01 | 98 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [8 empty] | 3.47 | 93 | 2.42 | 73.5 | 0.18 | 15.5
2015-06-29 | MN | 1400 | 4 | 42 | 0.232 | 30.5263 | 35 | 2.03 | 103 | NONE |  |  | TIME | 0.31 |  | 5.5182 | 81.4401 | 3.31 | 100 | 2.06 | 61 | 0.11 | 8
2015-06-29 | CBW | 2000 | 12 | 42 | 0.251 | 33.0263 | 35 | 5.39 | 97 | NONE |  |  | TIME | 0.42 |  | 5.5182 | 110.3382 | [16 empty] | 3.31 | 49 | 2.31 | 63.5 | 5.42 | 93
2015-06-29 | CBW | 2200 | 1 | 42 | 0.251 | 33.0263 | 35 | 4.37 | 118 | NONE |  |  | TIME | 0.51 |  | 5.5182 | 133.9821 |  |  | 3.06 | 92 | 0.11 | 16 | 0.11 | 8
2015-06-30 | MN | 700 | 5 | 42 | 0.244 | 32.1053 | 35 | 4.47 | 114 | NONE |  |  | TIME | 0.45 |  | 5.5182 | 118.2195 | [10 empty] | 3.95 | 94 | 1.98 | 36 | 0.85 | 21.5
2015-07-01 | CBW | 1:30 | 6 | 40 | 0.252 | 33.1579 | 35 | 4.97 | 111 | NONE |  |  | TIME | 0.4 |  | 5.2555 | 100.08 | [8 empty] | 0.11 | 18.5 |  |  | 2.74 | 54.5 | 1.87 | 27
2015-07-02 | wl | 1:30 | 8 | 13.3 | 0.226 | 29.7368 | 45 | 3.3 | 63 | none |  |  | head | 0.327 |  | 1.7474 | 27.2036 | [8 empty] | 1.8 | 41.5 | 0.6 | 22.5 | 0 | 15.5
2015-07-02 | wl | 4:00 | 3 | 13.6 | 0.239 | 31.4474 | 45 | 2.8 | 70 | none |  |  | head | 0.306 |  | 1.7869 | 26.0308 | 1.7 | 54 | 0.7 | 38 |  |  | 2 | 61
2015-07-07 | wl | 18:00 | 1 | 11.6 | 0.217 | 28.5526 | 45 | 1.2 | 103 | none |  |  | time | 0.262 |  | 1.5241 | 19.0102 |  |  | 0.2 | 54 | 0 | 30.5 | 1.7 | 128
2015-07-07 | DMH | 20:00 | 4 | 11.6 | 0.217 | 28.5526 | 45 | 1.51 | 131 |  |  |  | time | 0.275 |  | 1.5241 | 19.9535 | 0.35 | 0.79 | 0.25 | 56.12 | 0.03 | 0.06
2015-07-09 | JM | 900 | 12 | 13.7 | 0.253 | 33.2895 | 40 | 6.27 | 147 | NONE |  |  | TIME | 0.372 |  | 1.8 | 31.878 | [16 empty] | 4.09 | 93 | 2.18 | 74 | 5.95 | 123
2015-07-09 | MN | 1100 | 5 | 13.2 | 0.253 | 33.2895 | 40 | 2.86 | 98 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | [10 empty] | 2.27 | 93.5 | 1.61 | 69.5 | 0.54 | 49
2015-07-09 | MN | 1530 | 2 | 13.2 | 0.253 | 33.2895 | 40 | 1.78 | 96 | NONE |  |  | TIME | 0.358 |  | 1.7343 | 29.5586 | 0.3 | 44.5 |  |  | 1.05 | 67 | 0 | 43.5
2015-07-10 | JM | 800 | 11 | 13.8 | 0.252 | 33.1579 | 40 | 6.96 | 146 | NONE |  |  | TIME/TURB | 0.39 |  | 1.8131 | 33.6644 | [16 empty] | 5.09 | 116 | 1.68 | 97 |  |  | 2.17 | 23
2015-07-10 | MN | 1030 | 3 | 13.2 | 0.252 | 33.1579 | 40 | 2.05 | 96 | NONE |  |  | TIME | 0.42 |  | 1.7343 | 34.6777 | 0.86 | 66 | 0.07 | 19 |  |  | 1.01 | 62
2015-07-10 | MN | 1330 | 6 | 13.2 | 0.252 | 33.1579 | 40 | 3.29 | 120 | NONE |  |  | TIME | 0.38 |  | 1.7343 | 31.3751 | [8 empty] | 0.7 | 26.5 |  |  | 3.12 | 102 | 2.07 | 76
2015-07-10 | CBW | 2230 | 9 | 14.4 | 0.272 | 35.7895 | 40 | 6.1 | 130.5 | NONE |  |  | TIME/TURB | 0.52 |  | 1.892 | 46.8374 | [18 empty] | 1.68 | 111.5 | 2.18 | 14.5 | 3.26 | 37.5
2015-07-11 | CBW | 3:30 | 10 | 14.7 | 0.272 | 35.7895 | 40 | 3.01 | 116 | NONE |  |  | TIME/TURB | 0.56 |  | 1.9314 | 51.4912 | [16 empty] | 1.67 | 5 |  |  | 2.68 | 19.5 | 3.26 | 42.5
2015-07-11 | MN | 630 | 7 | 14.5 | 0.281 | 36.9737 | 40 | 4.61 | 118 | NONE |  |  | TIME/HEAD | 0.42 |  | 1.9051 | 38.093 | [8 empty] | 2.21 | 19.5 | 0.15 | 17 |  |  | 3.59 | 92.5
2015-07-11 | MN | 1100 | 4 | 14.4 | 0.281 | 36.9737 | 45 | 2.53 | 86 | NONE |  |  | TIME | 0.28 |  | 1.892 | 25.2202 | 2.4 | 89 | 1.07 | 44 | 0.5 | 24.5
2015-07-11 | MN | 1400 | 8 | 14.5 | 0.281 | 36.9737 | 45 | 4.12 | 100 | NONE |  |  | HEAD | 0.35 |  | 1.9051 | 31.7441 | [8 empty] | 2.71 | 27 | 0.7 | 24.5 | 0.06 | 7.5
2015-07-12 | MN | 900 | 1 | 13.4 | 0.305 | 40.1316 | 45 | 3.4 | 111 | NONE |  |  | TIME | 0.34 |  | 1.7606 | 28.4978 |  |  | 2.08 | 66.5 | 1.5 | 22.5 | 0.46 | 22
2015-07-13 | CBW | 4:00 | 12 | 12.7 | 0.319 | 41.9737 | 45 | 5.75 | 91 | NONE |  |  | TIME | 0.355 |  | 1.6686 | 28.2007 | [16 empty] | 3.68 | 53.5 | 2 | 48.5 | 5.19 | 67.5
2015-07-14 | MN | 600 | 5 | 12 | 0.345 | 45.3947 | 50 | 5.82 | 115 | NONE |  |  | TIME/HEAD | 0.25 |  | 1.5766 | 18.765 | [10 empty] | 3.25 | 91.5 | 2.6 | 71.5 | 2.51 | 62
2015-07-14 | MN | 830 | 2 | 12 | 0.345 | 45.3947 | 50 | 3.55 | 113 | NONE |  |  | TIME | 0.29 |  | 1.5766 | 21.7674 | 0.41 | 23.5 |  |  | 3.3 | 97 | 1 | 69.5
2015-07-15 | DMH | 830 | 3 | 12.1 | 0.388 | 51.0526 | 50 | 4 | 118 | NONE |  |  | TIME/HEAD | 0.23 |  | 1.5898 | 17.4077 | 0.91 | 70.02 | 0.26 | 0.079 |  |  | 1.5 | 91.16
2015-07-15 | DMH | 1130 | 11 | 13.7 | 0.388 | 51.0526 | 50 | 7.25 | 123.5 | 9,10 | 6.03,1.29 | 109104 | TIME/HEAD | 0.369 | 0.215 | 1.8 | 31.6209 | [16 empty] | 6.03 | 109 | 1.29 | 104 |  |  | 3.02 | 55.5
2015-07-15 | DMH | 1300 | 7 | 13.4 | 0.388 | 51.0526 | 50 | 4.14 | 102.5 | NONE |  |  | HEAD | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.26 | 29.63 | 4.25 | 118.24 |  |  | 3.52 | 93.34
2015-07-15 | DMH | 1430 | 6 | 13.4 | 0.388 | 51.0526 | 50 | 4.26 | 121 | NONE |  |  | TIME | 0.369 |  | 1.7606 | 30.9285 | [8 empty] | 0.77 | 30.97 |  |  | 0.49 | 0.27 | 3.52 | 94.69
2015-07-15 | DMH | 1630 | 9 | 13.7 | 0.346 | 45.5263 | 50 | 6.03 | 114 | NONE |  |  | TIME | 0.417 |  | 1.8 | 35.7342 | [18 empty] | 1.29 | 109 | 1.98 | 5 | 3.04 | 60.5
2015-07-16 | DMH | 1000 | 4 | 13 | 0.381 | 50.1316 | 55 | 3.02 | 119 | NONE |  |  | TIME/HEAD | 0.239 |  | 1.708 | 19.4343 | 2.47 | 95.77 | 0.76 | 48.68 | 0.49 | 24.61
2015-07-16 | DMH | 1130 | 1 | 10.8 | 0.381 | 50.1316 | 55 | 1.96 | 107.5 | NONE |  |  | TIME | 0.419 |  | 1.419 | 28.3051 |  |  | 0.76 | 50.32 | 0.49 | 26.25 | 0.47 | 0.86
2015-07-18 | DMH | 1300 | 12 | 10.3 | 0.391 | 51.4474 | 60 | 4.98 | 129 | NONE |  |  | TIME | 0.359 |  | 1.3533 | 23.1291 | [16 empty] | 3.24 | 69 | 1.99 | 65.5 | 4.01 | 74
2015-07-19 | R.H. | 400 | 8 | 10.8 | 0.365 | 48.0263 | 60 | 2.31 | 82 | NONE |  |  | TIME/HEAD | 0.22 |  | 1.419 | 14.8619 | [14 empty] | 2.33 | 82
2015-07-19 | DMH | 900 | 2 | 11.1 | 0.378 | 49.7368 | 60 | 1.77 | 120.5 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 67.03 |  |  | 2.02 | 95.23 | 0.47 | 69.84
2015-07-19 | DMH | 1030 | 7 | 11.2 | 0.378 | 49.7368 | 60 | 3.06 | 93.5 | NONE |  |  | TIME/HEAD | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 12.43 | 2.41 | 91.16 |  |  | 1.62 | 92.45
2015-07-19 | DMH | 1430 | 3 | 11.1 | 0.378 | 49.7368 | 60 | 2.02 | 102 | NONE |  |  | TIME | 0.256 |  | 1.4584 | 17.7742 | 0.51 | 72.28 | 0 | 4 |  |  | 0.47 | 75.1
2015-07-19 | DMH | 1600 | 6 | 11.2 | 0.331 | 43.5526 | 60 | 2.39 | 97.5 | NONE |  |  | TIME | 0.307 |  | 1.4715 | 21.5072 | [8 empty] | 0.02 | 18.01 |  |  | 0.48 | 4.33 | 0.01 | 10.56
2015-07-20 | DMH | 1300 | 10 | 13 | 0.341 | 44.8684 | 55 | 3.24 | 113 | NONE |  |  | TIME | 0.398 |  | 1.708 | 32.3634 | [16 empty] | 2.12 | 43 |  |  | 6.05 | 98 | 2.76 | 48
2015-07-21 | DMH | 1130 | 4 | 11 | 0.358 | 47.1053 | 55 | 1.47 | 121.5 | NONE |  |  | TIME | 0.204 |  | 1.4453 | 14.0362 | 1.02 | 117.42 | 0 | 49.14 | 0.33 | 43.89
2015-07-21 | DMH | 1400 | 1 | 10.7 | 0.358 | 47.1053 | 55 | 1.02 | 122.5 |  |  |  | TIME | 0.204 |  | 1.4058 | 13.6534 |  |  | 0 | 51.75 | 0.33 | 46.5 | 0.46 | 1.31
2015-07-23 | GE | 900 | 2 | 10.9 | 0.267 | 35.1316 | 45 | 0.53 | 96 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | 0.11 | 19 |  |  | 0.85 | 92.5 | 0.46 | 21.5
2015-07-23 | MN | 1200 | 5 | 10.9 | 0.267 | 35.1316 | 40 | 3.07 | 111 | NONE |  |  | TIME | 0.28 |  | 1.4321 | 19.0903 | [10 empty] | 1.52 | 92 | 1.48 | 97.5 | 2.03 | 102
2015-07-24 | GE | 900 | 12 | 10.1 | 0.214 | 28.1579 | 40 | 4.78 | 140 | NONE |  |  | TIME | 0.35 |  | 1.327 | 22.1114 | [16 empty] | 4.16 | 110.5 | 2.21 | 86 | 3.37 | 92
2015-07-24 | MN | 1230 | 4 | 9.6 | 0.214 | 28.1579 | 35 | 0.46 | 73 | NONE |  |  | TIME | 0.3 |  | 1.2613 | 18.0144 | 0.12 | 68.5 | 0.24 | 51.5 | 0.84 | 118
2015-07-25 | GHE | 730 | 7 | 9.1 | 0.188 | 24.7368 | 35 | 2.01 | 141 | NONE |  |  | TIME | 0.24 |  | 1.1956 | 13.6609 | [8 empty] | 0.44 | 19.5 | 2.03 | 111.5 |  |  | 2.52 | 123.5
2015-07-25 | GE | 930 | 9 | 9.4 | 0.181 | 23.8158 | 35 | 4.64 | 160 | NONE |  |  | TIME | 0.31 |  | 1.235 | 18.2271 | [18 empty] | 2.21 | 116.5 | 3.36 | 110.5 | 1.3 | 11.5
2015-07-26 | CBW | 5:00 | 8 | 9.1 | 0.181 | 23.8158 | 35 | 3.75 | 169 | NONE |  |  | HEAD | 0.27 |  | 1.1956 | 15.3685 | [8 empty] | 1.45 | 65 | 3.57 | 157 | 0.02 | 21.5
2015-07-26 | MN | 730 | 3 | 9.1 | 0.163 | 21.4474 | 32 | 2.37 | 157 | NONE |  |  | TIME | 0.28 |  | 1.1956 | 15.9377 | 1.29 | 113 | 0.24 | 69.5 |  |  | 0.46 | 43
2015-07-26 | MN | 900 | 6 | 9.1 | 0.163 | 21.4474 | 32 | 3.05 | 161 | NONE |  |  | TIME | 0.26 |  | 1.1956 | 14.7993 | [8 empty] | 1.45 | 69 |  |  | 0.02 | 25.5 | 0.46 | 4
2015-07-27 | GE | 800 | 10 | 10.9 | 0.169 | 22.2368 | 30 | 1.71 | 163 | NONE |  |  | TIME | 0.29 |  | 1.4321 | 19.7721 | [16 empty] | 4.68 | 23.5 |  |  | 4.93 | 157 | 2.67 | 71
2015-07-27 | MN | 1500 | 1 | 11 | 0.172 | 22.6316 | 30 | 2.82 | 145 | NONE |  |  | TIME | 0.28 |  | 1.4453 | 19.2654 |  |  | 1.79 | 102 | 0 | 31.5 | 0.96 | 74.5
2015-07-28 | GE | 800 | 11 | 9.9 | 0.19 | 25 | 30 | 5.48 | 161 | NONE |  |  | TIME | 0.29 |  | 1.3007 | 17.9581 | [16 empty] | 3.2 | 47 | 2.14 | 24 |  |  | 4.39 | 95
2015-07-28 | MN | 1400 | 5 | 9.9 | 0.19 | 25 | 30 | 4.47 | 122 | NONE |  |  | TIME | 0.25 |  | 1.3007 | 15.4811 | [10 empty] | 0.72 | 52 | 2.06 | 78.5 | 1.47 | 57
2015-08-02 | dh | 2000 | 8 | 10.4 | 0.186 | 24.4737 | 38 | 1.84 | 44 | none |  |  | head | 0.228 |  | 1.3664 | 14.8319 | [8 empty] | 0.26 | 11.21 | 0.01 | 36.7 | 3.06 | 106.11
2015-08-04 | wl | 1800 | 2 | 7.2 | 0.156 | 20.5263 | 38 | 2.07 | 140 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 59 |  |  | 0.04 | 106 | 0 | 31.5
2015-08-04 | dh | 2000 | 3 | 7.2 | 0.156 | 20.5263 | 38 | 1.48 | 92 | none |  |  | time | 0.271 |  | 0.94598 | 12.2048 | 0 | 60.89 | 0 | 0.76 |  |  | 0 | 33.23
2015-08-05 | CBW | 13:30 | 9 | 9.1 | 0.151 | 19.8684 | 30 | 4.84 | 109.5 | NONE |  |  | TIME | 0.19 |  | 1.1956 | 10.8149 | [16 empty] | 4.84 | 109.5 | 109.5 | 1.65 | 4.14 | 102 | 2.18 | 53.5
2015-08-06 | CBW | 7:00 | 10 | 9.6 | 0.163 | 21.4474 | 30 | 2.83 | 127 | NONE |  |  | TIME | 0.391 |  | 1.2613 | 23.4788 | [16 empty] | 1.29 | 17.5 | 2.83 | 127 | 5.68 | 119 | 3.24 | 71
2015-08-06 | CBW | 1400 | 6 | 9.2 | 0.171 | 22.5 | 30 | 1.52 | 134 | NONE |  |  | TIME | 0.39 |  | 1.2088 | 22.4429 | [8 empty] | 1.27 | 102.5 | 1.52 | 134 | 0 | 78.5 | 0.81 | 90
2015-08-06 | CBW | 1600 | 11 | 9.6 | 0.174 | 22.8947 | 30 | 5.69 | 128.5 | NONE |  |  | TIME | 0.31 |  | 1.2613 | 18.6149 | [16 empty] | 1.29 | 26.5 | 2.32 | 9 |  |  | 3.24 | 80
2015-08-07 | CBW | 8:00 | 1 | 8.6 | 0.178 | 23.4211 | 37 | 1.02 | 128 | NONE |  |  | TIME | 0.5 |  | 1.1299 | 26.8965 | 1.02 | 128 | 0.39 | 62 | 0 | 60 | 0.5 | 95.5
2015-08-07 | CBW | 13:00 | 5 | 8.6 | 0.178 | 23.4211 | 37 | 2.27 | 125.5 | NONE |  |  | TIME | 0.32 |  | 1.1299 | 17.2138 | [8 empty] | 2.27 | 125.5 | 0 | 23 | 1.01 | 101.5 | 1.81 | 113
2015-08-08 | CBW | 6:00 | 8 | 8.5 | 0.235 | 30.9211 | 35 | 2.8 | 130 | NONE |  |  | TIME | 0.47 |  | 1.1168 | 24.9887 | [8 empty] | 0 | 17 | 0.5 | 40 | 2.52 | 118.5 | 2.8 | 130
2015-08-08 | CBW | 8:00 | 7 | 8.5 | 0.165 | 21.7105 | 35 | 2.52 | 120 | NONE |  |  | TIME | 0.46 |  | 1.1168 | 24.4571 | [8 empty] | 0 | 19 | 0.5 | 42 | 2.52 | 120 | 0 | 2
2015-08-09 | CBW | 6:30 | 12 | 9.2 | 0.169 | 22.2368 | 35 | 6.05 | 142.5 | NONE |  |  | TIME | 0.58 |  | 1.2088 | 33.3767 | [16 empty] | 3.81 | 89 | 2.34 | 71.5 | 3.42 | 62.5 | 6.05 | 142.5
2015-08-09 | CBW | 9:00 | 4 | 8.9 | 0.169 | 22.2368 | 35 | 2.18 | 144.5 | NONE |  |  | TIME | 0.43 |  | 1.1693 | 23.9379 | 0.46 | 49 | 0.78 | 111 | 2 | 109 | 2.18 | 144.5
2015-08-10 | CBW | 6:00 | 2 | 9.3 | 0.181 | 23.8158 | 35 | 2.37 | 132 | NONE |  |  | TIME | 0.66 |  | 1.2219 | 38.3932 | 0.46 | 70 | 2.37 | 132 | 3.52 | 130 | 0 | 21
2015-08-10 | CBW | 10:00 | 3 | 10 | 0.181 | 23.8158 | 35 | 3.52 | 134 | NONE |  |  | TIME | 0.33 |  | 1.3139 | 20.6415 | 0.96 | 74 | 0.06 | 136 | 3.52 | 134 | 0 | 25
2015-08-11 | CBW | 6:30 | 9 | 9.8 | 0.177 | 23.2895 | 34 | 6.84 | 137 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [18 empty] | 1.32 | 119.5 | 6.97 | 110.5 | 3.74 | 48
2015-08-11 | CBW | 8:00 | 10 | 9.8 | 0.177 | 23.2895 | 34 | 0.8 | 121 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 1.5 |  |  | 6.97 | 112 | 3.76 | 49.5
2015-08-11 | CBW | 13:30 | 11 | 9.8 | 0.177 | 23.2895 | 34 | 6.47 | 117.5 | NONE |  |  | TIME | 0.287 |  | 1.2876 | 17.5928 | [16 empty] | 1.46 | 7 | 2.58 | 5.5 |  |  | 3.74 | 55
2015-08-11 | CBW | 1500 | 6 | 9.4 | 0.177 | 23.2895 | 34 | 5.01 | 121 | NONE |  |  | TIME | 0.27 |  | 1.235 | 15.8752 | [8 empty] | 4.56 | 98 | 5.01 | 121 | 0 | 79 | 3.53 | 81
2015-08-11 | GHE | 18:00 | 1 | 7.4 | 0.138 | 18.1579 | 35 | 1.45 | 106 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 |  |  | 0.06 | 37 | 0 | 32 | 0.51 | 57
2015-08-11 | GHE | 20:00 | 5 | 7.4 | 0.138 | 18.1579 | 35 | 2.5 | 103 | NONE |  |  | TIME | 0.27 |  | 0.97226 | 12.4975 | [10 empty] | 0 | 5 | 0 | 84 | 3.03 | 86
2015-08-12 | MN | 600 | 8 | 7.5 | 0.152 | 20 | 35 | 2.54 | 96 | NONE |  |  | TIME | 0.42 |  | 0.9854 | 19.7032 | [8 empty] | 0.12 | 9 | 0 | 14 | 0.2 | 93
2015-08-12 | DMH | 11:30 | 7 | 7.8 | 0.133 | 17.5 | 35 | 0.02 | 99.5 | NONE |  |  | TIME | 0.282 |  | 1.0248 | 13.7585 | [8 empty] | 0.09 | 14.45 | 0.06 | 19.07 |  |  | 0 | 4.64
2015-08-13 | wl | 10:00 | 12 | 9.3 | 0.149 | 19.6053 | 40 | 4.94 | 99.5 | none |  |  | time | 0.39 |  | 1.2219 | 22.6869 | [16 empty] | 1.37 | 51.5 | 2.57 | 50 | 2.05 | 44.5
2015-08-13 | wl | 16:00 | 4 | 8.8 | 0.15 | 19.7368 | 40 | 1.1 | 103 | none |  |  | time | 0.267 |  | 1.1562 | 14.6967 | 0 | 44.6 | 0.2 | 80.6 | 0.2 | 76
2015-08-14 | dmh | 11:00 | 2 | 10.4 | 0.15 | 19.7368 | 40 | 0.51 | 101 | none |  |  | time | 0.289 |  | 1.3664 | 18.8 | 0 | 63.34 |  |  | 1 | 95.12 | 0 | 17.27
2015-08-14 | dmh | 15:30 | 3 | 10.6 | 0.15 | 19.7368 | 40 | 0.1 | 99.5 | none |  |  | time | 0.289 |  | 1.3927 | 19.1616 | 0 | 3.56 | 0.45 | 68.11 |  |  | 0.06 | 22.04
2015-08-15 | wl | 9:30 | 1 | 9.9 | 0.149 | 19.6053 | 40 | 0 | 84 | none |  |  | time | 0.399 |  | 1.3007 | 24.7079 |  |  | 0 | 22 | 0 | 17 | 0 | 40.5
2015-08-15 | CBW | 11:30 | 9 | 10.4 | 0.149 | 19.6053 | 40 | 3.2 | 101 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [18 empty] | 2 | 99.5 | 3.5 | 94.5 | 2.6 | 49.5
2015-08-15 | CBW | 1400 | 10 | 10.4 | 0.149 | 19.6053 | 40 | 2.9 | 102 | none |  |  | time | 0.487 |  | 1.3664 | 31.6803 | [16 empty] | 1.1 |  |  |  | 3.6 |  | 2.8
2015-08-15 | wl | 1600 | 6 | 9.2 | 0.149 | 19.6053 | 40 | 0.5 | 96 | none |  |  | time | 0.448 |  | 1.2088 | 25.7806 | [8 empty] | 0.5 | 91 |  |  | 0.4 | 75 | 0.2 | 80
2015-08-15 | he | 1800 | 11 |  |  | 0 | 45 | 3.62 | 99.5 | none |  |  | time | 0.487 |  | 0 | 0
2015-08-16 | wl | 8:30 | 5 | 9.4 | 0.147 | 19.3421 | 45 | 1 | 110.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [10 empty] | 0 | 15.5 | 0.8 | 92 | 0.7 | 97
2015-08-16 | wl | 10:30 | 8 | 9.4 | 0.147 | 19.3421 | 45 | 0.7 | 100.5 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 1 | 0 | 17.5 | 0.8 | 94
2015-08-16 | wl | 13:30 | 7 | 9.4 | 0.147 | 19.3421 | 45 | 0.8 | 98 | none |  |  | time | 0.413 |  | 1.235 | 24.2832 | [8 empty] | 0 | 4 | 0 | 20.5 |  |  | 0 | 2
2015-08-17 | wl | 11:00 | 12 | 10.3 | 0.149 | 19.6053 | 45 | 3.63 | 97 | none |  |  | time | 0.348 |  | 1.3533 | 22.4204 | [16 empty] | 1.7 | 47.5 | 2.82 | 45 | 1.89 | 41
2015-08-17 | wl | 1600 | 4 | 9.7 | 0.149 | 19.6053 | 45 | 0.1 | 96 | none |  |  | time | 0.367 |  | 1.2745 | 22.2672 | 0 | 52.5 | 0 | 76 | 0 | 71.5
2015-08-18 | wl | 7:30 | 2 | 9.6 | 0.149 | 19.6053 | 45 | 0.3 | 91.6 | none |  |  | time | 0.354 |  | 1.2613 | 21.257 | 0 | 68.3 |  |  | 0.2 | 86.8 | 0 | 14.1
2015-08-18 | dh | 10:00 | 3 | 9.6 | 0.149 | 19.6053 | 45 | 0.04 | 89 | none |  |  | time | 0.403 |  | 1.2613 | 24.1993 | 0 | 70.53 | 0 | 1.01 |  |  | 0 | 16.39
2015-08-19 | GE | 9:30 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0.45 | 10 | 0.05 | 11.5 | 0 | 17.5
2015-08-19 | GE | 13:30 | 9 | 8.9 |  | 0 | 40 | 2.21 | 98 | NONE |  |  | TIME | 0.32 |  | 1.1693 | 17.8142 | [18 empty] | 2.32 | 93.5 | 2.43 | 91.5 | 1.59 | 51.5
2015-08-19 | GE | 16:00 | 6 | 8.3 |  | 0 | 40 | 0.22 | 96 | NONE |  |  | TIME | 0.3 |  | 1.0905 | 15.575 | [8 empty] | 0.31 | 79.5 |  |  | 0.34 | 74.5 | 0.23 | 77.5
2015-08-19 | CBW | 19:00 | 10 | 8.8 |  | 0 | 39 | 2.91 | 101 | NONE |  |  | TIME | 0.231 |  | 1.1562 | 12.7152 | [16 empty] | 1.26 | 5.5 |  |  | 2.43 | 99 | 1.6 | 56
2015-08-19 | CBW | 23:00 | 11 | 8.8 |  | 0 | 39 | 2.43 | 100.5 | NONE |  |  | TIME | 0.227 |  | 1.1562 | 12.495 | [16 empty] | 1.26 | 9.5 | 2.91 | 4 |  |  | 2.1 | 60
2015-08-20 | MN | 830 | 5 | 8.3 |  | 0 | 38 | 0.81 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [10 empty] | 0.21 | 16 | 0.34 | 91 | 0.23 | 94
2015-08-20 | MN | 1030 | 8 | 8.3 |  | 0 | 38 | 0.21 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | [8 empty] | 0 | 2 | 0.21 | 18 | 0.34 | 93
2015-08-20 | MN | 1330 | 7 | 8.3 |  | 0 | 38 | 0.34 | 96 | NONE |  |  | TIME | 0.2 |  | 1.0905 | 10.3833 | [8 empty] | 0 | 5 | 0.21 | 21 |  |  | 0.13 | 3 | 1.29 | 45.5 | 2.51 | 28 | 1.36 | 38
2015-08-21 | MN | 1100 | 12 | 8.8 |  | 0 | 35 | 2.1 | 96 | NONE |  |  | TIME | 0.22 |  | 1.1562 | 12.1097
2015-08-21 | MN | 1600 | 4 | 8.3 | 0.176 | 23.1579 | 35 | 0 | 96 | NONE |  |  | TIME | 0.22 |  | 1.0905 | 11.4216 | 0 | 54.5 | 0 | 80.5 | 0 | 78
2015-08-22 | CBW | 4:00 | 2 | 8.3 | 0.176 | 23.1579 | 35 | N/A | 92.5 | NONE |  |  | TIME | 0.34 |  | 1.0905 | 17.6516 | N/A | 66.5 |  |  | N/A | 90 | N/A | 12
2015-08-22 | MN | 1000 | 3 | 8.3 |  | 0 | 35 | 0 | 96 | NONE |  |  | TIME | 0.25 |  | 1.0905 | 12.9791 | 0 | 72.5 | 0 | 6 |  |  | 0 | 18
2015-08-23 | MN | 930 | 1 | 8.3 |  | 0 | 40 | 0 | 96 | NONE |  |  | TIME | 0.35 |  | 1.0905 | 18.1708 |  |  | 0 | 29.5 | 0.44 | 23.5 | 0 | 42.5
2015-08-23 | MN | 1600 | 6 | 8.3 |  | 0 | 45 | 0 | 96 | NONE |  |  | TIME | 0.28 |  | 1.0905 | 14.5366 | [8 empty] | 0 | 78 |  |  | 0 | 73 | 0 | 76 |  |  | 2.51 | 110.5 | 1.86 | 105.5 | 1.47 | 69.5
2015-08-24 | MN | 830 | 9 | 9.5 |  | 0 | 45 | 2.3 | 115 | NONE |  |  | TIME | 0.25 |  | 1.2482 | 14.8556
2015-08-24 | MN | 1030 | 5 | 9 |  | 0 | 45 | 1.02 | 98 | NONE |  |  | TIME | 0.23 |  | 1.1825 | 12.9478 | [10 empty] | 0 | 16 | 0 | 92 | 0.52 | 95
2015-08-24 | CBW | 21:00 | 10 | 10.3 | 0.14 | 18.4211 | 35 | 3.03 | 124 | NONE |  |  | TIME | 0.25 |  | 1.3533 | 16.1066 | [16 empty] | 1.19 | 12.5 |  |  | 2.87 | 118 | 2.5 | 82
2015-08-25 | CBW | 2:00 | 11 | 10.2 | 0.14 | 18.4211 | 35 | 2.36 | 123 | NONE |  |  | TIME | 0.2 |  | 1.3401 | 12.7602 | [16 empty] | 1.19 | 17.5 | 2.5 | 5 |  |  | 1.99 | 87
2015-09-02 | CBW | 13:00 | 3 | 7.3 | 0.263 | 34.6053 | 45 | N/A | 37 | NONE |  |  | TIME | 0.26 |  | 0.95912 | 11.872 | N/A | 28 | N/A | 29 |  |  | N/A | 37
2015-09-02 | CBW | 15:00 | 1 | 7.7 | 0.263 | 34.6053 | 45 | N/A | 39 | NONE |  |  | TIME | 0.21 |  | 1.0117 | 10.1143 |  |  | N/A | 31 | N/A | 2 | N/A | 39
2015-09-03 | CBW | 6:00 | 6 | 8.5 | 0.256 | 33.6842 | 45 | 1 | 54 | NONE |  |  | TIME | 0.3 |  | 1.1168 | 15.9503 | [8 empty] | 0.5 | 54 | 1.01 | 54 | 0 | 54 | 0.01 | 54
2015-09-03 | CBW | 9:00 | 9 | 9.2 | 0.256 | 33.6842 | 45 | 2.24 | 57 | NONE |  |  | TIME | 0.276 |  | 1.2088 | 15.8827 | [18 empty] | 2.58 | 57 | 1.92 | 57 | 1.67 | 48
2015-09-03 | CBW | 12:00 | 5 | 7.3 | 0.256 | 33.6842 | 45 | 1 | 60 | NONE |  |  | TIME | 0.22 |  | 0.95912 | 10.0455 | [10 empty] | 0.29 | 6 | 0 | 60 | 0.01 | 60
2015-09-04 | CBW | 7:00 | 10 | 7 | 0.256 | 33.6842 | 45 | 2.08 | 79 | NONE |  |  | TIME | 0.58 |  | 0.91971 | 25.3953 | [16 empty] | 0.67 | 22 |  |  | 1.91 | 79 | 0.67 | 79
2015-09-04 | CBW | 9:30 | 11 | 8.5 | 0.256 | 33.6842 | 45 | 1.92 | 81.5 | NONE |  |  | TIME | 0.4 |  | 1.1168 | 21.267 | [16 empty] | 0.67 | 24.5 | 2.71 | 2.5 |  |  | 1.68 | 81.5
2015-09-04 | CBW | 13:00 | 8 | 8.5 | 0.256 | 33.6842 | 45 | N/A | 85 | NONE |  |  | TIME | 0.32 |  | 1.1168 | 17.0136 | [8 empty] | 4.7 | 25 | 0.29 | 31 | 0 | 85
2015-09-05 | CBW | 7:00 | 12 | 9.1 | 0.256 | 33.6842 | 45 | 1.38 | 103 | NONE |  |  | TIME | 0.6 |  | 1.1956 | 34.1523 | [16 empty] | 1.22 | 46 | 2.62 | 24 | 1.16 | 21.5
2015-09-05 | CBW | 9:00 | 7 | 8.3 | 0.304 | 40 | 45 | 0.31 | 105 | NONE |  |  | TIME | 0.27 |  | 1.0905 | 14.0175 | [8 empty] | N/A | 45 | N/A | 51 |  |  | N/A | 20
2015-09-05 | CBW | 1500 | 4 | 7.1 | 0.304 | 40 | 45 | N/A | 111 | NONE |  |  | TIME | 0.25 |  | 0.93285 | 11.1026 | N/A | 72 | N/A | 103 | N/A | 74
2015-09-06 | CBW | 7:00 | 2 | 7.1 | 0.295 | 38.8158 | 40 | N/A | 119 | NONE |  |  | TIME | 0.56 |  | 0.93285 | 24.8699 | N/A | 88 |  |  | N/A | 90 | N/A | 16
2015-09-07 | CBW | 9:00 | 3 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 116 | NONE |  |  | TIME | 0.49 |  | 1.0117 | 23.6001 | N/A | 114 | N/A | 26 |  |  | N/A | 4
2015-09-07 | CBW | 14:00 | 1 | 7.7 | 0.312 | 41.0526 | 40 | 1 | 119 | NONE |  |  | TIME | 0.38 |  | 1.0117 | 18.3021 |  |  | N/A | 31 | N/A | 5 | N/A | 47
2015-09-08 | CBW | 6:00 | 6 | 8.1 | 0.233 | 30.6579 | 45 | 2.51 | 120 | NONE |  |  | TIME | 0.4 |  | 1.0642 | 20.2662 | [8 empty] | 2.02 | 114 |  |  | 1.72 | 69 | 2.53 | 89
2015-09-08 | CBW | 8:00 | 9 | 8.9 | 0.233 | 30.6579 | 45 | 3.74 | 119 | NONE |  |  | TIME | 0.5 |  | 1.1693 | 27.8347 | [18 empty] | 2.11 | 97 | 3.24 | 94 | 2.43 | 73
2015-09-08 | CBW | 12:00 | 5 | 0.31 | 0.233 | 30.6579 | 45 | 2.56 | 120 | NONE |  |  | TIME | 0.32 |  | 0.04073 | 0.6205 | [10 empty] | 0 | 6 | 2.24 | 7.5 | 3.05 | 95
2015-09-09 | wl | 8:00 | 8 | 7.2 | 0.335 | 44.0789 | 45 | 3.8 | 115 | NONE |  |  | time | 0.367 |  | 0.94598 | 16.5282 | [8 empty] | 0 | 18 | 0 | 25.5 | 2.9 | 93.5
2015-09-10 | wl | 8:30 | 4 | 6.6 | 0.345 | 45.3947 | 50 | 1.3 | 113.5 | NONE |  |  | time | 0.317 |  | 0.86715 | 13.0867 | 0 | 66 | 0.4 | 96 | 0 | 71
2015-09-10 | dh | 10:30 | 12 | 7.5 | 0.345 | 45.3947 | 50 | 3.05 | 123.5 | NONE |  |  | time | 0.381 |  | 0.9854 | 17.8737 | [16 empty] | 1.04 |  | 0.06 |  | 1.06
2015-09-11 | wl | 14:30 | 2 | 7.2 | 0.309 | 40.6579 | 50 | 0.8 | 127.5 | NONE |  |  | time | 0.301 |  | 0.94598 | 13.5558 | 0 | 95.5 |  |  | 0.3 | 101 | 7.4 | 28.5
2015-09-12 | DH | 10:00 | 1 | 7.2 | 0.31 | 40.7895 | 50 | 0.035 | 116 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 |  |  | 0.059 | 18.02 | 0.04 | 120.31 | 0.06 | 47.81
2015-09-12 | DH | 14:00 | 3 | 7.2 | 0.31 | 40.7895 | 50 | 0.04 | 125 | NONE |  |  | TIME | 0.424 |  | 0.94598 | 19.0953 | 0.069 | 2.97 | 0.063 | 22.42 |  |  | 0.06 | 52.21
2015-09-13 | wl | 10:00 | 6 | 6.6 | 0.31 | 40.7895 | 50 | 0.9 | 124 | none |  |  | Time | 0.285 |  | 0.86715 | 11.7657 | [8 empty] | 0.8 | 115.5 |  |  | 0 | 96 | 0 | 98
2015-09-13 | DH | 12:00 | 5 | 6.5 | 0.31 | 40.7895 | 50 | 0.06 | 120 | NONE |  |  | TIME | 0.285 |  | 0.85401 | 11.5874 | [10 empty] | 0.08 | 0.71 | 0.06 | 97.48 | 0.04 | 99.49
2015-09-14 | DH | 9:00 | 10 | 8.5 | 0.306 | 40.2632 | 60 | 2 | 115 | NONE |  |  | TIME | 0.438 |  | 1.1168 | 23.2874 | [16 empty] | 1 | 18 |  |  | 2.3 | 114.5 | 2 | 90.5
2015-09-15 | wl | 8:00 | 7 | 7.3 | 0.31 | 40.7895 | 60 | 1.4 | 142 | none |  |  | time | 0.461 |  | 0.95912 | 21.05 | [8 empty] | 0.2 | 43 | 0.1 | 45 |  |  | 0 | 16
2015-09-15 | wl | 10:00 | 4 | 7.3 | 0.31 | 40.7895 | 60 | 0 | 121.5 | none |  |  | time | 0.422 |  | 0.95912 | 19.2692 | 0 | 70.5 | 0 | 90 | 0 | 66.5
2015-09-15 | DH | 13:00 | 12 | 7.8 | 0.312 | 41.0526 | 60 | 2.4 | 122.5 | NONE |  |  | TIME | 0.426 |  | 1.0248 | 20.7841 | [16 empty] | 1.4 | 46 | 2.5 | 28 | 1.2 | 26.5
2015-09-18 | CBW | 22:00 | 9 | 7.9 | 0.283 | 37.2368 | 45 | 4.58 | 127 | NONE |  |  | TIME | 0.423 |  | 1.038 | 20.9023 | [18 empty] | 1.71 | 109 | 3.78 | 107.5 | 3.01 | 81

## FILTER STUDY
Hour
| DATE | 2019-01-01 | 2019-01-02 | 2019-01-03 | 2019-01-04 | 2019-01-05 | 2019-01-06 | 2019-01-07 | 2019-01-08 | 2019-01-09 | 2019-01-10 | 2019-01-11 | 2019-01-12 | 2019-01-13 | 2019-01-14 | 2019-01-15 | 2019-01-16 | 2019-01-17 | 2019-01-18 | 2019-01-19 | 2019-01-20 | 2019-01-21 | 2019-01-22 | 2019-01-23 | 2019-01-24 | 2019-01-25 | 2019-01-26 | 2019-01-27 | 2019-01-28 | 2019-01-29 | 2019-01-30 | 2019-01-31
| DOSE | 9560 | 9612 | 8953.2 | 9905.6667 | 9735 | 9985 | 9760 | 9579.6 | 10105 | 10116.6667 | 9170 | 9170 | 9953.3333 | 9926.6667 | 9822.5 | 9732 | 9115 | 10461.6 | 10935.75 | 9958.3333 | 10343.5 | 10836 | 9813.3333 | 8347.5 | 7316 | 7046.6667 | 7320 | 7153.3333 | 7198 | 7620 | 7420.25 |  | NUMBER OF WASHS
| Alum Dose:TOC Ratio | 746.9774 | 725.434 | 677.2825 | 751.328 | 729.8849 | 743.7373 | 725.3194 | 713.5409 | 752.6756 | 765.0415 | 689.3373 | 680.3645 | 750.4497 | 748.1917 | 743.7828 | 713.7009 | 672.5631 | 827.0613 | 881.3542 | 844.052 | 877.3504 | 970.0071 | 959.0399 | 844.7537 | 759.5847 | 738.6851 | 777.3451 | 765.3496 | 782.6152 | 792.953 | 744.6378
| UV 254 | 0.48633 | 0.5035 | 0.50233 | 0.501 | 0.50683 | 0.51017 | 0.51133 | 0.51017 | 0.51017 | 0.5025 | 0.5055 | 0.51217 | 0.504 | 0.50417 | 0.50183 | 0.51817 | 0.515 | 0.48067 | 0.4715 | 0.44833 | 0.448 | 0.4245 | 0.38883 | 0.3755 | 0.366 | 0.3625 | 0.35783 | 0.35517 | 0.3495 | 0.36517 | 0.37867
RAW | FLOWS | 26.6 | 25.555 | 25.359 | 27.356 | 25.813 | 26.647 | 25.963 | 26.242 | 29.769 | 25.72 | 25.395 | 25.569 | 27.833 | 26.612 | 26.769 | 27.294 | 25.273 | 27.372 | 29.545 | 27.113 | 28.606 | 30.02 | 28.489 | 27.727 | 26.321 | 26.537 | 27.214 | 27.708 | 26.75 | 29.625 | 28.127
FILTERS | [34 empty] | Days | GAL USED
| FILT 1 |  |  |  | 81 |  |  |  | 89 |  |  |  |  | 126.5 |  |  |  | 98.5 |  |  | 73 |  |  |  | 94 |  |  |  |  | 120 |  |  |  | 7 | 1 | [12 empty] | 0
| FILT 2 |  |  |  |  | 96.5 |  |  |  | 105 |  |  |  |  | 113 |  |  |  | 103.5 |  |  |  | 94.5 |  |  |  |  | 118 |  |  |  | 104 |  | 7 | 2 | [12 empty] | 0
| FILT 3 |  |  |  |  | 100 |  |  |  |  | 125.5 |  |  |  | 99.5 |  |  |  | 97 |  |  |  | 86 |  |  |  | 102 |  |  |  | 97 |  |  | 7 | 3 | [7 empty] | 160429.1667 |  | 167708.3333 |  |  | 328137.5
| FILT 4 |  |  |  |  | 110 |  |  |  |  | 121 |  |  |  |  | 116.5 |  |  |  | 94.5 |  |  |  | 76 |  |  |  | 101 |  |  |  | 95 |  | 7 | 4 | 161470.8333 |  |  |  | 166158.3333 | [5 empty] | 173958.3333 | 175520.8333 | 677108.3333
| FILT 5 |  |  |  | 86.5 |  |  |  | 95.5 |  |  |  |  | 116 |  |  |  | 101 |  |  |  | 97 |  |  |  |  | 112 |  |  |  | 101.5 |  |  | 7 | 5 |  | 164075 | 160429.1667 | 156783.3333 |  | 155220.8333 | 164075 |  | 169791.6667 |  |  |  | 970375
| FILT 6 |  |  |  |  | 105 |  |  |  |  | 123 |  |  |  | 99.5 |  |  |  |  | 116 |  |  |  | 99 |  |  |  |  | 115 |  |  |  |  | 6 | 6 | [12 empty] | 0
| FILT 7 |  |  |  |  | 98.5 |  |  |  | 107 |  |  |  | 98.5 |  |  |  |  | 111 |  |  | 76 |  |  | 73 |  |  |  | 95 |  |  |  |  | 7 | 7 | [7 empty] | 161991.6667 |  | 175520.8333 |  |  | 337512.5
| FILT 8 |  |  | 33.5 |  |  |  | 103 | [5 empty] | 130 |  |  | 84 |  |  |  | 91 |  |  |  | 94 |  |  |  |  | 120 |  |  |  | 7 | 8 | 159908.3333 |  |  |  | 159908.3333 | [5 empty] | 172916.6667 | 174479.1667 | 667212.5
| FILT 9 |  |  |  |  | 104.5 |  |  |  |  | 119.5 |  |  |  | 94.5 |  |  |  | 98 |  | 54 |  |  | 70 |  |  |  | 98 |  |  |  | 83.5 |  | 8 | 9 |  | 163554.1667 |  |  |  |  | 163554.1667 | [5 empty] | 327108.3333
| FILT 10 |  |  | 33 |  |  |  | 101 | [5 empty] | 131 |  |  | 84 |  |  | 73 |  |  | 68 |  |  |  | 105 |  |  |  | 87 |  |  | 8 | 10 |  |  | 164075 | 161470.8333 |  | 164075 |  |  | 177083.3333 |  |  |  | 666704.1667
| FILT 11 |  |  |  | 75 |  |  |  | 93.5 |  |  |  | 102 |  |  | 68 |  |  | 82.5 |  | 50.5 |  | 52 |  |  |  | 91 |  |  | 72 |  |  |  | 9 | 11 | [12 empty] | 0
| FILT 12 |  |  |  | 82.5 |  |  |  | 95.5 |  |  |  | 95 |  |  | 70 |  |  | 85.5 |  |  | 53.5 |  | 53 |  |  |  | 90 |  |  | 70 |  |  | 9 | 12 | [10 empty] | 177083.3333 | 177083.3333 | 354166.6667
NUMBER WASHED |  | 0 | 0 | 2 | 4 | 6 | 0 | 2 | 4 | 2 | 4 | 0 | 2 | 5 | 4 | 3 | 2 | 2 | 6 | 3 | 4 | 3 | 4 | 4 | 3 | 0 | 4 | 4 | 2 | 3 | 4 | 3 | 0 |  | 13 | 169283.3333 |  |  |  | 169283.3333 |  | 169283.3333 | 148450 |  | 182291.6667 |  |  | 838591.6667
GAL USED |  | 0 | 0 | 328137.5 | 677108.3333 | 970375 | 0 | 337512.5 | 667212.5 | 327108.3333 | 666704.1667 | 0 | 354166.6667 | 838591.6667 | 690141.6667 | 520845.8333 | 328137.5 | 317733.3333 | 1052120.8333 | 515650 | 677108.3333 | 502629.1667 | 727108.3333 | 777629.1667 | 484412.5 | 0 | 681275 | 659400 | 343775 | 513045.8333 | 783184.7222 | 482837.5 | 15223951.3889 |  | 14 |  | 169283.3333 | 169283.3333 |  |  | 169283.3333 |  |  | 182291.6667 |  |  |  | 690141.6667
| UV TIMES 100 | 48.6333 | 50.35 | 50.2333 | 50.1 | 50.6833 | 51.0167 | 51.1333 | 51.0167 | 51.0167 | 50.25 | 50.55 | 51.2167 | 50.4 | 50.4167 | 50.1833 | 51.8167 | 51.5 | 48.0667 | 47.15 | 44.8333 | 44.8 | 42.45 | 38.8833 | 37.55 | 36.6 | 36.25 | 35.7833 | 35.5167 | 34.95 | 36.5167 | 37.8667 |  |  | 15 |  |  |  | 164075 | [6 empty] | 182291.6667 | 174479.1667 | 520845.8333
[35 empty] | 16 | [7 empty] | 148450 |  | 179687.5 |  |  | 328137.5
[35 empty] | 17 | 161470.8333 |  |  |  | 156262.5 | [7 empty] | 317733.3333
[35 empty] | 18 |  | 161470.8333 | 161470.8333 |  |  |  | 158866.6667 |  | 184895.8333 |  | 190104.1667 | 195312.5 | 1052120.8333
[35 empty] | 19 |  |  |  | 161470.8333 |  | 161470.8333 |  |  |  | 192708.3333 |  |  | 515650
[35 empty] | 20 | 156262.5 | [6 empty] | 156262.5 | 182291.6667 |  | 182291.6667 |  | 677108.3333
[35 empty] | 21 |  |  |  |  | 161470.8333 |  | 156262.5 |  |  |  |  | 184895.8333 | 502629.1667
[35 empty] | 22 |  | 161470.8333 | 180220.8333 | [6 empty] | 192708.3333 | 192708.3333 |  | 727108.3333
[35 empty] | 23 |  |  |  | 179700 |  | 148450 |  |  | 257812.5 |  |  | 191666.6667 | 777629.1667
[35 empty] | 24 | 161470.8333 | [5 empty] | 161470.8333 | 161470.8333 |  |  |  |  | 484412.5
[35 empty] | 25 | [12 empty] | 0
[35 empty] | 26 |  |  | 148450 |  | 166679.1667 |  |  |  |  | 186458.3333 | 179687.5 |  | 681275
[35 empty] | 27 |  | 143241.6667 |  | 143241.6667 |  |  |  |  | 186458.3333 |  |  | 186458.3333 | 659400
[35 empty] | 28 | [5 empty] | 171887.5 | 171887.5 | [5 empty] | 343775
[35 empty] | 29 | 166679.1667 | [6 empty] | 166679.1667 |  |  | 179687.5 |  | 513045.8333
[35 empty] | 30 |  |  | 169456.9444 |  | 169456.9444 |  |  |  |  | 256250 |  | 188020.8333 | 783184.7222
[35 empty] | 31 |  | 145325 |  | 146366.6667 |  |  |  |  | 191145.8333 |  |  |  | 482837.5

## Total Flows
Water Production and Waste (MGD) | [7 empty] | 2019-01-01
Day | Raw Flow | Finished 1 Flow | Finished 2 Flow | Combined Finished | Finished South Meter 1 | Finished South Meter 2 | Finished Conway #66 | Finished Perry #67 | Blowdown | Backwash | Decant Flow | Decant Actual Flow | Plant 1 Raw Flow, MGD | Plant 2 Raw Flow, MGD | Plant 3 Raw Flow, MGD | Plant 1 Polymer Dose, mg/L | Plant 2 Polymer Dose, mg/L | Plant 3 Polymer Dose, mg/L | Plant 1 Settled Turb. | Plant 2 Settled Turb. | Plant 3 Settled Turb.
1 | 26.6 | 12.487 | 11.194 | 23.681 | 0 | 12.487 | 4.712 | 6.482 | 1.8797 | 0 | 0.877 | 2.0681 | 8.3 | 8.3 | 9.3 | 765 | 765 | 720 | 0.27325 | 0.237 | 0.2285
2 | 25.555 | 11.864 | 10.654 | 22.518 | 0 | 11.864 | 4.572 | 6.082 | 1.6365 | 0 | 0.705 | 1.8261 | 8.34 | 8.34 | 9.34 | 692 | 680 | 650 | 0.296 | 0.29225 | 0.259
3 | 25.359 | 10.666 | 11.353 | 22.019 | 0 | 10.666 | 4.864 | 6.489 | 1.7438 | 0.32814 | 0.825 | 1.8158 | 7.72 | 7.72 | 8.72 | 641 | 619 | 650 | 0.29975 | 0.287 | 0.27375
4 | 27.356 | 11.175 | 12.091 | 23.266 | 0 | 11.175 | 5.066 | 7.025 | 1.6864 | 0.67711 | 0.867 | 1.8475 | 8.7167 | 8.35 | 9.7 | 666.6667 | 600 | 706.75 | 0.32475 | 0.28325 | 0.26425
5 | 25.813 | 11.059 | 11.159 | 22.218 | 0 | 11.059 | 4.338 | 6.821 | 1.6915 | 0.97037 | 1.093 | 1.9339 | 8.5 | 8.2 | 9.5 | 609.125 | 552.375 | 660.5 | 0.37375 | 0.3825 | 0.302
6 | 26.647 | 12.146 | 11.353 | 23.499 | 0.001 | 12.145 | 4.464 | 6.889 | 1.406 | 0 | 0.651 | 2.0131 | 8.625 | 8.325 | 9.9 | 611 | 546.125 | 663.625 | 0.41675 | 0.38775 | 0.3075
7 | 25.963 | 10.396 | 11.462 | 21.858 | 0.001 | 10.395 | 4.692 | 6.77 | 1.8297 | 0.33751 | 0.869 | 1.8158 | 8.38 | 8.38 | 9.62 | 566 | 533 | 643.8 | 0.39 | 0.3695 | 0.311
8 | 26.242 | 9.413 | 11.817 | 21.23 | 0 | 9.413 | 4.625 | 7.192 | 1.6758 | 0.66721 | 0.9 | 1.8158 | 8.28 | 8.28 | 9.28 | 540.6 | 508 | 618.2 | 0.38575 | 0.3835 | 0.2895
9 | 29.769 | 13.904 | 13.861 | 27.765 | 0.001 | 13.903 | 5.796 | 8.065 | 2.175 | 0.32711 | 0.96 | 1.9944 | 8.8 | 8.8 | 9.8 | 581.5 | 535 | 620 | 0.3735 | 0.3415 | 0.32875
10 | 25.72 | 11.073 | 10.9 | 21.973 | 0.006 | 11.067 | 4.67 | 6.23 | 1.3944 | 0.6667 | 0.884 | 1.9094 | 8.8333 | 8.8333 | 9.8333 | 595 | 535 | 600 | 0.353 | 0.34725 | 0.38175
11 | 25.395 | 10.614 | 11.591 | 22.205 | 0.013 | 10.601 | 4.317 | 7.274 | 1.6023 | 0 | 0.821 | 2.3659 | 8.4 | 7.0667 | 9.4 | 588.3333 | 530 | 585 | 0.3135 | 0.28725 | 0.31525
12 | 25.569 | 11.083 | 11.115 | 22.198 | 0.009 | 11.074 | 4.629 | 6.486 | 1.4688 | 0.35417 | 0.914 | 2.2435 | 9.3333 | 5.3333 | 10.3333 | 656.6667 | 696.6667 | 651.6667 | 0.40282 | 0.31625 | 0.36925
13 | 27.833 | 10.821 | 12.1 | 22.921 | 0.011 | 10.81 | 4.58 | 7.52 | 1.4847 | 0.83859 | 1.065 | 2.1528 | 10 | 6 | 11 | 710 | 756.6667 | 661.6667 | 0.3455 | 0.27375 | 0.38475
14 | 26.612 | 11.155 | 11.758 | 22.913 | 0.01 | 11.145 | 4.681 | 7.077 | 1.5426 | 0.69014 | 0.895 | 2.1744 | 10 | 6 | 11 | 786.6667 | 520 | 668.3333 | 0.324 | 0.27575 | 0.356
15 | 26.769 | 10.652 | 11.421 | 22.073 | 0.012 | 10.64 | 4.573 | 6.848 | 1.1015 | 0.52085 | 1.079 | 2.2392 | 9.875 | 6 | 10.875 | 797.5 | 532.5 | 722.5 | 0.31325 | 0.28325 | 0.38
16 | 27.294 | 11.009 | 11.89 | 22.899 | 0.009 | 11 | 4.856 | 7.034 | 1.5335 | 0.32814 | 0.836 | 2.196 | 9.7 | 6 | 10.9 | 768.5 | 400 | 782 | 0.367 | 0.27725 | 0.4725
17 | 25.273 | 9.813 | 11.417 | 21.23 | 0.01 | 9.803 | 4.236 | 7.181 | 1.5069 | 0.31773 | 0.922 | 1.8795 | 8.5833 | 6 | 10 | 668.75 | 439.8333 | 729.1667 | 0.40075 | 0.35 | 0.45775
18 | 27.372 | 10.084 | 12.273 | 22.357 | 0.008 | 10.076 | 4.547 | 7.726 | 1.4839 | 1.0521 | 1.115 | 1.9519 | 11.1 | 5.2 | 12.1 | 802.5 | 437 | 816 | 0.47175 | 0.275 | 0.51825
19 | 29.545 | 11.115 | 13.438 | 24.553 | 0.005 | 11.11 | 4.795 | 8.643 | 1.8357 | 0.51565 | 1.298 | 3.3003 | 11.75 | 5 | 12.75 | 860 | 787.5 | 788.75 | 0.501 | 0.28625 | 0.53675
20 | 27.113 | 10.628 | 12.282 | 22.91 | 0.002 | 10.626 | 4.471 | 7.811 | 1.6616 | 0.67711 | 1.106 | 2.5907 | 10.6667 | 5 | 11.3333 | 841.6667 | 966.6667 | 770 | 0.45925 | 0.314 | 0.515
21 | 28.606 | 11.194 | 12.897 | 24.091 | 0.012 | 11.182 | 4.472 | 8.425 | 1.0524 | 0.50263 | 0.962 | 2.2445 | 11.15 | 5.025 | 12.025 | 921.25 | 558.875 | 786.25 | 0.45025 | 0.3235 | 0.434
22 | 30.02 | 11.396 | 13.366 | 24.762 | 0.014 | 11.382 | 4.516 | 8.85 | 1.7415 | 0.72711 | 1.231 | 1.9536 | 12 | 5.1 | 13 | 1018.75 | 523.75 | 801.25 | 0.48275 | 0.5565 | 0.54725
23 | 28.489 | 11.126 | 12.716 | 23.842 | 0.008 | 11.118 | 4.622 | 8.094 | 1.6112 | 0.77763 | 1.178 | 2.4048 | 11.0833 | 6.55 | 12.0833 | 837.5 | 394.1667 | 748.3333 | 0.4135 | 0.37375 | 0.422
24 | 27.727 | 10.786 | 13.749 | 24.535 | 0.001 | 10.785 | 4.799 | 8.95 | 1.6893 | 0.48441 | 1.028 | 2.0902 | 8.9 | 8.4 | 9.9 | 617.5 | 445 | 597.5 | 0.3305 | 0.3375 | 0.3715
25 | 26.321 | 10.062 | 12.989 | 23.051 | 0.009 | 10.053 | 4.458 | 8.531 | 1.2185 | 0 | 0.597 | 1.7519 | 6.92 | 9.02 | 10.02 | 460 | 542 | 582 | 0.333 | 0.348 | 0.36225
26 | 26.537 | 10.481 | 12.448 | 22.929 | 0.012 | 10.469 | 4.712 | 7.736 | 1.2694 | 0.68127 | 0.936 | 1.3791 | 5.6667 | 9.9333 | 10.9333 | 746.6667 | 583.3333 | 606.6667 | 0.36675 | 0.3185 | 0.38825
27 | 27.214 | 10.995 | 12.85 | 23.845 | 0.012 | 10.983 | 4.716 | 8.134 | 1.179 | 0.6594 | 1.03 | 2.2702 | 5 | 10.8 | 11.8 | 740 | 593.3333 | 656.6667 | 0.386 | 0.41725 | 0.4475
28 | 27.708 | 11.145 | 12.948 | 24.093 | 0.011 | 11.134 | 4.206 | 8.742 | 0.82915 | 0.34377 | 0.742 | 1.6134 | 5 | 10.4667 | 11.4667 | 733.3333 | 633.3333 | 650 | 0.327 | 0.35825 | 0.3865
29 | 26.75 | 10.4 | 12.267 | 22.667 | 0.01 | 10.39 | 4.264 | 8.003 | 1.7428 | 0.51305 | 1.038 | 1.5993 | 5.48 | 10.26 | 11.3 | 492.5 | 614 | 644 | 0.33875 | 0.365 | 0.4235
30 | 29.625 | 7.668 | 13.812 | 21.48 | 0.01 | 7.658 | 4.834 | 8.978 | 1.3423 | 0.78318 | 0.925 | 2.2736 | 5.875 | 11.25 | 12.45 | 540 | 692.5 | 697.5 | 0.36875 | 0.43 | 0.54425
31 | 28.127 | 13.382 | 13.299 | 26.681 | 0.015 | 13.367 | 4.846 | 8.453 | 1.5822 | 0.48284 | 1.125 | 2.7288 | 5.65 | 11.05 | 12.15 | 562.5 | 695 | 670 | 0.36825 | 0.371 | 0.64525
Total | 840.923 | 339.792 | 378.47 | 718.262 | 0.212 | 339.58 | 143.929 | 234.541 | 47.5979 | 15.224 | 29.474 |  | 266.6283 | 238.9833 | 331.8133 | 21418.475 | 18215.625 | 21148.125 | 11.5508 | 10.4495 | 12.2237
Average | 27.1265 | 10.961 | 12.2087 | 23.1697 | 0.0068387 | 10.9542 | 4.6429 | 7.5658 | 1.5354 | 0.4911 | 0.95077 |  | 8.6009 | 7.7091 | 10.7037 | 690.9185 | 587.6008 | 682.1976 | 0.37261 | 0.33708 | 0.39431
Maximum | 30.02 | 13.904 | 13.861 | 27.765 | 0.015 | 13.903 | 5.796 | 8.978 | 2.175 | 1.0521 | 1.298 |  | 12 | 11.25 | 13 | 1018.75 | 966.6667 | 816 | 0.501 | 0.5565 | 0.64525
Minimum | 25.273 | 7.668 | 10.654 | 21.23 | 0 | 7.658 | 4.206 | 6.082 | 0.82915 | 0 | 0.597 |  | 5 | 5 | 8.72 | 460 | 394.1667 | 582 | 0.27325 | 0.237 | 0.2285
Finished Water Pumped (from South + Conway+ Perry Meters) | [7 empty] | 718.262
Finished Water Pumped (Raw Flow - Blowdown + Backwash) | [7 empty] | 778.1011
Finished Water Pumped (Raw Flow -Decant + Sludge) | [7 empty] | 807.449
Total Decant Flow |  |  | 29.474 |  |  | MG
Total Sudge Pumped (est) |  |  | 4
Total Blowdown Flow |  |  | 47.5979
Total Backwash Flow |  |  | 15.224
Total Waste Flow from Decant and Sludge | [7 empty] | 33.474
Total Waste Flow from Blowdown and Backwash | [7 empty] | 62.8219

## Flows
Surface Water System Monthly Operation Report
Water Production Log
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  | 2019-01-01
Plant Name: Bull Creek SWTP |  |  | Plant Id #: | A26001 |  | Capacity (MGD): 45
| Number and Grade of Operator in Charge |  | Hours in Operation | Water Pumped (MG) |  |  |  | Peak Hourly Flow Rate (MGD)
Day | 1st Shift | 2nd Shift |  | Raw | Finished1 | Finished2 | Combined
1 | 4 | 20 | 24 | 26.6 | 12.487 | 11.194 | 23.681 | 26.4
2 | 17 | 14 | 24 | 25.555 | 11.864 | 10.654 | 22.518 | 28
3 | 17 | 14 | 24 | 25.359 | 10.666 | 11.353 | 22.019 | 25.9
4 | 17 | 14 | 24 | 27.356 | 11.175 | 12.091 | 23.266 | 28
5 | 17 | 14 | 24 | 25.813 | 11.059 | 11.159 | 22.218 | 28
6 | 17 | 14 | 24 | 26.647 | 12.146 | 11.353 | 23.499 | 26.9
7 | 17 | 14 | 24 | 25.963 | 10.396 | 11.462 | 21.858 | 26.9
8 | 17 | 14 | 24 | 26.242 | 9.413 | 11.817 | 21.23 | 26.8
9 | 20 | 4 | 24 | 29.769 | 13.904 | 13.861 | 27.765 | 29.9
10 | 20 | 4 | 24 | 25.72 | 11.073 | 10.9 | 21.973 | 28
11 | 20 | 4 | 24 | 25.395 | 10.614 | 11.591 | 22.205 | 26.5
12 | 20 | 4 | 24 | 25.569 | 11.083 | 11.115 | 22.198 | 27
13 | 20 | 4 | 24 | 27.833 | 10.821 | 12.1 | 22.921 | 27.9
14 | 20 | 4 | 24 | 26.612 | 11.155 | 11.758 | 22.913 | 27
15 | 20 | 4 | 24 | 26.769 | 10.652 | 11.421 | 22.073 | 28
16 | 18 | 17 | 24 | 27.294 | 11.009 | 11.89 | 22.899 | 28
17 | 18 | 17 | 24 | 25.273 | 9.813 | 11.417 | 21.23 | 26
18 | 18 | 17 | 24 | 27.372 | 10.084 | 12.273 | 22.357 | 30
19 | 14 | 17 | 24 | 29.545 | 11.115 | 13.438 | 24.553 | 30
20 | 14 | 17 | 24 | 27.113 | 10.628 | 12.282 | 22.91 | 28
21 | 14 | 17 | 24 | 28.606 | 11.194 | 12.897 | 24.091 | 30.1
22 | 14 | 17 | 24 | 30.02 | 11.396 | 13.366 | 24.762 | 30.1
23 | 4 | 20 | 24 | 28.489 | 11.126 | 12.716 | 23.842 | 30.1
24 | 4 | 20 | 24 | 27.727 | 10.786 | 13.749 | 24.535 | 29
25 | 4 | 20 | 24 | 26.321 | 10.062 | 12.989 | 23.051 | 26.5
26 | 4 | 20 | 24 | 26.537 | 10.481 | 12.448 | 22.929 | 27.6
27 | 4 | 20 | 24 | 27.214 | 10.995 | 12.85 | 23.845 | 27.6
28 | 4 | 20 | 24 | 27.708 | 11.145 | 12.948 | 24.093 | 28.1
29 | 4 | 20 | 24 | 26.75 | 10.4 | 12.267 | 22.667 | 29
30 | 17 | 14 | 24 | 29.625 | 7.668 | 13.812 | 21.48 | 29.9
31 | 17 | 18 | 24 | 28.127 | 13.382 | 13.299 | 26.681 | 29.7
Total |  |  | 744 | 840.923 | 339.792 | 378.47 | 718.262 | 870.9
Average |  |  | 24 | 27.1265 | 10.961 | 12.2087 | 23.1697 | 28.0935
Maximum |  |  | 24 | 30.02 | 13.904 | 13.861 | 27.765 | 30.1
Minimum |  |  | 24 | 25.273 | 7.668 | 10.654 | 21.23 | 25.9
| #3-Lederman A #21- Nobles D | #4-Hughes B #5-Nicolosi B | #12-Eaddy A #20 Brookover A | #14-Wall A #16-Eaton A | #17-Holden B #18-Mercer A
Prepared by: ___________________________________________ |  |  |  |  | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## Raw & Coagulated
Surface Water System Monthly Operation Report
Chemical & Physical Analyses of
Raw, Coagulated, & Settled Water
Bureau of Water
System Name: Grand Strand Regional | [6 empty] | System Number: 2620004
Certified Lab ID#: 26102 | [6 empty] | 2019-01-01
| Raw Water | [6 empty] | Coagulated Water |  | Settled Water
Day | pH | Alkalinity (mg/L) | Temp (oC) | Hardness (mg/L) | Turbidity (NTU) | True Color (CU) | Apparent Color (CU) | pH | Alkalinity (mg/L) | Turbidity (NTU) | Disinfectant Residual (mg/L)
1 | 6.2933 | 14.5 | 15.7167 | 15.3333 | 9 | 115 | 157.6667 | 5.9783 | 9.6667 | 0.286 | 0.55
2 | 6.2883 | 11.8333 | 16.0667 | 13.6667 | 9.52 | 117 | 160.5 | 5.97 | 7.4444 | 0.364 | 0.53
3 | 6.2917 | 11.8333 | 16.2167 | 12.5 | 8.96 | 115 | 158.3333 | 6.0628 | 7.6111 | 0.352 | 0.51
4 | 6.265 | 12.5 | 16.3667 | 13 | 9.71 | 118.6667 | 164 | 6.0861 | 7.8889 | 0.36 | 0.42
5 | 6.2967 | 12.6667 | 16.6333 | 12.8333 | 10.7 | 121.1667 | 164.6667 | 6.0939 | 9.2778 | 0.447 | 0.42
6 | 6.3267 | 13.6667 | 16.15 | 13.1667 | 10.4 | 123 | 171.8333 | 6.0272 | 9.4444 | 0.49 | 0.4
7 | 6.365 | 12.3333 | 16.1833 | 12.8333 | 11.7 | 122.5 | 177.3333 | 6.0261 | 8 | 0.464 | 0.4
8 | 6.3667 | 13 | 16.05 | 13.5 | 11.4 | 121.8333 | 174.1667 | 6.1083 | 8.2778 | 0.438 | 0.38
9 | 6.3883 | 14.5 | 41.15 | 14 | 12.8 | 125.1667 | 176.8333 | 6.0539 | 9.8333 | 0.466 | 0.41
10 | 6.41 | 15 | 15.55 | 13.8333 | 11.1 | 124 | 171.8333 | 6.0389 | 9.7778 | 0.488 | 0.47
11 | 6.4233 | 15.3333 | 14.6667 | 15 | 10.3 | 125.8333 | 173 | 6.0144 | 9.2778 | 0.393 | 0.54
12 | 6.4383 | 15.3333 | 13.8167 | 16 | 11.8 | 128.6667 | 181.8333 | 6.0158 | 10.0556 | 0.44 | 0.45
13 | 6.505 | 16.8333 | 13.2667 | 17 | 12.2 | 125.6667 | 186.3333 | 5.9706 | 9.8889 | 0.437 | 0.54
14 | 6.48 | 16 | 12.75 | 15.5 | 12.2 | 127.3333 | 188.6667 | 6.0267 | 9.9444 | 0.44 | 0.55
15 | 6.495 | 16.8333 | 12.35 | 15.8333 | 12.2 | 127 | 189.6667 | 6.035 | 9.3889 | 0.494 | 0.67
16 | 6.5167 | 16.1667 | 12.1 | 16.6667 | 12.3 | 129.5 | 190 | 6.0606 | 8.9444 | 0.525 | 0.6
17 | 6.5183 | 15 | 11.9167 | 15.1667 | 13.1 | 125.8333 | 190.1667 | 6.1472 | 8.5 | 0.487 | 0.43
18 | 6.475 | 15.8333 | 11.8167 | 15.8333 | 15.5 | 123.8333 | 197.8333 | 6.1133 | 8.2222 | 0.54 | 0.43
19 | 6.6067 | 16.5 | 12.2667 | 16.5 | 16.1 | 118.1667 | 202.6667 | 6.0461 | 9.2222 | 0.58 | 0.64
20 | 6.5783 | 17.5 | 12.7167 | 17 | 15.9 | 114.3333 | 196.6667 | 6.0828 | 9.2222 | 0.53 | 0.4
21 | 6.55 | 16.3333 | 12 | 17 | 15.2 | 114.3333 | 189.3333 | 6.0806 | 8.8333 | 0.518 | 0.33
22 | 6.5333 | 16.3333 | 11.0333 | 16.8333 | 15 | 105.6667 | 187.5 | 6.1759 | 9 | 0.63 | 0.39
23 | 6.52 | 17.5 | 11.55 | 16.8333 | 15 | 94.3333 | 173.5 | 6.1278 | 10.8333 | 0.531 | 0.61
24 | 6.56 | 16.6667 | 12.85 | 17.6667 | 14.8 | 95.8333 | 171.8333 | 6.1194 | 9.7222 | 0.401 | 0.64
25 | 6.4867 | 18.6667 | 12.7667 | 16.5 | 14.9 | 93.8333 | 170 | 6.1228 | 9.3889 | 0.408 | 0.59
26 | 6.5233 | 15.6667 | 12.4667 | 16.1667 | 14.9 | 91.5 | 168.5 | 6.0644 | 9.1111 | 0.427 | 0.52
27 | 6.545 | 18.1667 | 12.1167 | 17.1667 | 14.8 | 89 | 163.6667 | 6.0372 | 9.9444 | 0.474 | 0.6
28 | 6.5683 | 17.6667 | 12 | 17.3333 | 14.9 | 88.6667 | 164.1667 | 6.0194 | 9 | 0.444 | 0.5
29 | 6.6267 | 18.5 | 12.0667 | 17.8333 | 15.7 | 86.3333 | 164.8333 | 6.115 | 9.8333 | 0.481 | 0.61
30 | 6.6483 | 17 | 11.5333 | 18 | 16.4 | 91.6667 | 171.3333 | 6.0272 | 7.6667 | 0.692 | 0.46
31 | 6.65 | 16.8333 | 11.4 | 17 | 16.4 | 93.6667 | 173.5 | 6.0756 | 8.3333 | 0.716 | 0.67
Avg. | 6.469 | 15.5645 | 14.372 | 15.5968 | 13.061 | 112.7204 | 176.5215 | 6.062 | 9.0824 | 0.47558 | 0.50516
Max. | 6.65 | 18.6667 | 41.15 | 18 | 16.4 | 129.5 | 202.6667 | 6.1759 | 10.8333 | 0.716 | 0.67
Min. | 6.265 | 11.8333 | 11.0333 | 12.5 | 8.96 | 86.3333 | 157.6667 | 5.97 | 7.4444 | 0.286 | 0.33
Prepared by: ____________________________________________ | [7 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## Finished
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2019-01-01
Finished Water 1
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.29 | 21 | 13.2667 | 3.8 |  |  | 50.5 | 0.084 | 1 | 0.5124
2 | 7.2917 | 20 | 13.6667 | 3.9 |  |  | 51 | 0.067 | 1 | 0.5696
3 | 7.4333 | 20 | 13.95 | 3.9 |  |  | 50.5 | 0.065 | 1 | 0.5103
4 | 7.3733 | 20 | 14.2333 | 4 |  |  | 48 | 0.065 | 1 | 0.498
5 | 7.615 | 20.5 | 14.45 | 3.9 |  |  | 52.5 | 0.069 | 1.5 | 0.6372
6 | 7.2883 | 20.5 | 14.2167 | 4 |  |  | 51.5 | 0.069 | 1 | 0.4479
7 | 7.3433 | 21 | 14.0833 | 4.1 |  |  | 53 | 0.07 | 1 | 0.579
8 | 7.4667 | 19.5 | 14.3333 | 4 |  |  | 52 | 0.069 | 1 | 0.5691
9 | 7.5033 | 23.5 | 14.4167 | 3.8 | 0.45 | 0.012 | 47.5 | 0.069 | 1 | 0.5372
10 | 7.5633 | 20.5 | 13.75 | 3.7 |  |  | 49.5 | 0.064 | 1 | 0.597
11 | 7.3183 | 22.5 | 12.7 | 4.2 |  |  | 50.5 | 0.059 | 1 | 0.5974
12 | 7.29 | 21.5 | 12.1 | 3.9 |  |  | 46.5 | 0.056 | 1 | 0.5541
13 | 7.26 | 21.5 | 11.6 | 4.2 |  |  | 54.5 | 0.055 | 1 | 0.6533
14 | 7.525 | 23.5 | 11.0167 | 4.2 |  |  | 53 | 0.056 | 1 | 0.6022
15 | 7.4617 | 21.5 | 10.65 | 4.2 |  |  | 50.5 | 0.053 | 1 | 0.7202
16 | 7.4717 | 22 | 10.4833 | 4.4 |  |  | 53.5 | 0.063 | 1 | 0.6116
17 | 7.4667 | 21.5 | 10.2833 | 4.1 |  |  | 58.5 | 0.068 | 1 | 0.5976
18 | 7.2833 | 20.5 | 10.3333 | 4 |  |  | 57 | 0.06 | 1 | 0.5885
19 | 7.4833 | 20.5 | 10.7167 | 4.2 |  |  | 56 | 0.065 | 1 | 0.6057
20 | 7.4433 | 20.5 | 11.2333 | 3.8 |  |  | 55 | 0.067 | 1 | 0.5461
21 | 7.385 | 22 | 10.9667 | 4 |  |  | 63 | 0.062 | 1 | 0.5439
22 | 7.455 | 22 | 10.1833 | 4.1 |  |  | 63.5 | 0.063 | 1 | 0.6549
23 | 7.4033 | 23.5 | 9.7 | 4.2 |  |  | 52.5 | 0.064 | 1 | 0.7141
24 | 7.2967 | 22 | 10.3833 | 3.6 |  |  | 45 | 0.059 | 1 | 0.5561
25 | 7.2983 | 23 | 10.7 | 3.7 |  |  | 39 | 0.064 | 1 | 0.4899
26 | 7.2167 | 21.5 | 10.5333 | 3.6 |  |  | 31.5 | 0.056 | 1 | 0.5448
27 | 7.4017 | 21.5 | 10.2 | 3.7 |  |  | 35.5 | 0.067 | 1 | 0.7682
28 | 7.4083 | 22.5 | 10.15 | 4.2 |  |  | 44 | 0.052 | 1 | 0.551
29 | 7.2867 | 24.5 | 10.1667 | 4.2 |  |  | 49 | 0.052 | 1.1667 | 0.6611
30 | 7.2783 | 20 | 10.0167 | 4 | 0.34 | 0.012 | 42 | 0.065 | 1 | 0.6564
31 | 7.465 | 20.5 | 9.9333 | 4.1 |  |  | 40.5 | 0.064 | 1 | 0.7066
Avg. | 7.3892 | 21.4516 | 11.7554 | 3.9903 | 0.395 | 0.012 | 49.8871 | 0.063258 | 1.0215 | 0.59295
Max. | 7.615 | 24.5 | 14.45 | 4.4 | 0.45 | 0.012 | 63.5 | 0.084 | 1.5 | 0.7682
Min. | 7.2167 | 19.5 | 9.7 | 3.6 | 0.34 | 0.012 | 31.5 | 0.052 | 1 | 0.4479
Notes: | Phosphate reported as P
Prepared by: ____________________________________________ | [6 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## Finished2
Surface Water System Monthly Operation Report
Chemical & Physical Analyses-Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  |  | System Number: 2620004
Certified Lab ID#: 26102 |  |  |  |  | 2019-01-01
Finished Water 2
Day | pH | Alkalinity (mg/L) | Temp (°C) | Disinfect Residual (mg/L) | Total Phos- phate (mg/L) | Ortho Phos- phate (mg/L) | Hardness (mg/L) | Turbidity (NTU) | Color (CU) | Fluoride (mg/L)
1 | 7.285 | 21 | 15.4667 | 3.7 |  |  | 47 | 0.066 | 1 | 0.5103
2 | 7.34 | 20 | 15.3333 | 4 |  |  | 49 | 0.065 | 1 | 0.5166
3 | 7.3617 | 20 | 15.4 | 3.9 |  |  | 51 | 0.068 | 1 | 0.5082
4 | 7.3317 | 20.5 | 15.4333 | 3.9 |  |  | 50.5 | 0.07 | 1 | 0.4884
5 | 7.6367 | 20.5 | 15.5333 | 3.8 |  |  | 52 | 0.072 | 1 | 0.6732
6 | 7.2633 | 20.5 | 15.3833 | 4.1 |  |  | 53.5 | 0.071 | 1 | 0.4318
7 | 7.2983 | 20.5 | 15.2167 | 3.7 |  |  | 56.5 | 0.06 | 1 | 0.5559
8 | 7.4317 | 19.5 | 15.4333 | 4 |  |  | 51.5 | 0.062 | 1 | 0.5532
9 | 7.4467 | 23 | 15.55 | 3.8 | 0.42 | 0.012 | 50 | 0.064 | 1.1667 | 0.5243
10 | 7.565 | 20 | 15.4667 | 3.8 |  |  | 47 | 0.073 | 1 | 0.5494
11 | 7.27 | 23.5 | 14.5333 | 3.6 |  |  | 50 | 0.063 | 1 | 0.5621
12 | 7.2017 | 22 | 13.5833 | 3.7 |  |  | 50.5 | 0.058 | 1 | 0.4494
13 | 7.17 | 22 | 13.4667 | 3.4 |  |  | 51 | 0.054 | 1 | 0.4624
14 | 7.3 | 25.5 | 12.8333 | 3.6 |  |  | 52 | 0.061 | 1 | 0.9081
15 | 7.4283 | 20.5 | 12.6167 | 4.1 |  |  | 52.5 | 0.055 | 1 | 0.5507
16 | 7.2733 | 24 | 12.25 | 4 |  |  | 54 | 0.059 | 1 | 0.4568
17 | 7.415 | 22 | 11.8 | 3.9 |  |  | 60.5 | 0.071 | 1 | 0.4611
18 | 7.2467 | 21.5 | 11.95 | 3.8 |  |  | 59 | 0.059 | 1 | 0.3821
19 | 7.2633 | 21 | 12.2833 | 3.6 |  |  | 57.5 | 0.066 | 1 | 0.4854
20 | 7.4583 | 21.5 | 12.75 | 3.5 |  |  | 56.5 | 0.063 | 1 | 0.4522
21 | 7.3483 | 21 | 11.8667 | 3 |  |  | 62 | 0.066 | 1 | 0.3244
22 | 7.3683 | 23.5 | 10.95 | 3.8 |  |  | 60 | 0.065 | 1 | 0.4096
23 | 7.3683 | 22.5 | 11.9167 | 3.8 |  |  | 53 | 0.065 | 1 | 0.5103
24 | 7.25 | 20.5 | 12.8333 | 3.7 |  |  | 45.5 | 0.057 | 1 | 0.5145
25 | 7.3283 | 22.5 | 12.5833 | 3.8 |  |  | 38.5 | 0.059 | 1 | 0.5187
26 | 7.1467 | 22.5 | 12.45 | 3.3 |  |  | 32.5 | 0.057 | 1 | 0.5103
27 | 7.2633 | 22 | 11.85 | 3.6 |  |  | 37.5 | 0.056 | 1 | 0.4741
28 | 7.185 | 22 | 12.1 | 3.6 |  |  | 42.5 | 0.062 | 1.3333 | 0.4626
29 | 7.195 | 23 | 11.8 | 3.9 |  |  | 45.5 | 0.051 | 1.1667 | 0.5185
30 | 7.2617 | 20.5 | 11.1333 | 3.9 | 0.4 | 0.013 | 42.5 | 0.067 | 1 | 0.502
31 | 7.3833 | 20 | 10.9667 | 3.7 |  |  | 41.5 | 0.067 | 1 | 0.5229
Avg. | 7.3253 | 21.5806 | 13.314 | 3.7419 | 0.41 | 0.0125 | 50.0806 | 0.062968 | 1.0215 | 0.50805
Max. | 7.6367 | 25.5 | 15.55 | 4.1 | 0.42 | 0.013 | 62 | 0.073 | 1.3333 | 0.9081
Min. | 7.1467 | 19.5 | 10.95 | 3 | 0.4 | 0.012 | 32.5 | 0.051 | 1 | 0.3244
Notes: | Phosphate reported as P
Prepared by: ____________________________________________ | [6 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## Chems lbs
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2019-01-01
Pounds or Gallons of Chemicals Used
Day | Pre Disinf (gal) | Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | Post Disenfectant (gal) (gal) |  | Post-pH (gal) | Fluoride (gal) | Phosphate (gal) | Zinc (gal) | Filter Aid (gal) | Polymer (gal) | Pre-pH (gal) | PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 305.341 | 3733.2237 |  | 3187.5067 | 612.3792 | 90.8 | 141.1658 | 58.8216 | 45.3936 | 6.0146 | 3.0758 | 7.7011 |  | 650.2203
2 | 279.3703 | 3591.806 |  | 3329.1736 | 588.7384 | 85.69 | 143.9309 | 54.6746 | 42.1724 | 6.0696 | 2.8051 | 6.5552 |  | 650.2203
3 | 277.2127 | 3572.8554 |  | 3187.5067 | 572.9814 | 82.2021 | 142.6722 | 53.4542 | 41.3934 | 5.9691 | 2.436 | 6.5067 |  | 608.9868
4 | 292.4838 | 3848.6187 |  | 3093.062 | 608.2955 | 88.4291 | 145.0682 | 56.8272 | 43.3486 | 6.1552 | 2.724 | 6.4161 |  | 642.2907
5 | 271.589 | 3646.8135 |  | 3157.9927 | 577.8274 | 86.4556 | 136.2248 | 54.0336 | 41.919 | 5.9361 | 2.6688 | 5.7545 |  | 650.2203
6 | 275.4903 | 3767.8532 |  | 3175.7011 | 613.8282 | 93.2428 | 135.8401 | 57.5098 | 44.3614 | 6.4715 | 2.7303 | 5.9399 |  | 638.326
7 | 263.5498 | 3652.5779 |  | 3239.4512 | 576.6346 | 85.7481 | 128.9483 | 53.4202 | 41.9203 | 5.9631 | 2.6802 | 5.3768 |  | 650.2203
8 | 255.7235 | 3699.2237 |  | 3333.8797 | 552.3306 | 82.5144 | 126.9748 | 51.8515 | 40.8162 | 5.6163 | 2.6225 | 5.0969 |  | 650.2203
9 | 300.9704 | 4174.5492 |  | 3435.4239 | 730.3449 | 111.4737 | 178.297 | 67.7032 | 52.0669 | 7.5531 | 2.7753 | 6.5623 |  | 662.1145
10 | 277.7435 | 3597.6667 |  | 3344.9144 | 575.5848 | 88.8808 | 123.2084 | 53.659 | 40.9173 | 6.0499 | 2.795 | 5.1602 |  | 687.2247
11 | 274.6495 | 3561.0367 |  | 3014.3581 | 575.8698 | 86.6484 | 120.0836 | 53.758 | 42.5174 | 6.0667 | 2.6609 | 5.2584 |  | 644.9339
12 | 308.809 | 3565.653 |  | 2896.3023 | 567.4782 | 85.7676 | 114.7126 | 69.4076 | 41.9748 | 4.1922 | 2.9527 | 4.9648 |  | 623.7885
13 | 348.1933 | 3901.2974 |  | 3195.4093 | 589.6686 | 86.668 | 124.984 | 73.0347 | 43.1317 | 4.2423 | 3.2083 | 5.0284 |  | 666.0793
14 | 339.4266 | 3720.1585 |  | 3266.2105 | 589.6556 | 85.9844 | 133.872 | 73.0092 | 42.4246 | 4.2408 | 3.202 | 4.9132 |  | 666.0793
15 | 322.4474 | 3737.6338 |  | 3240.6318 | 564.4886 | 81.876 | 126.5608 | 69.5987 | 41.1517 | 4.2499 | 3.2532 | 6.0266 |  | 666.0793
16 | 320.173 | 3797.566 |  | 3267.7846 | 587.2859 | 83.0843 | 137.4974 | 71.7798 | 42.9947 | 4.3303 | 3.1874 | 6.1938 |  | 669.2511
17 | 272.6505 | 3563.4667 |  | 3116.6732 | 512.367 | 69.0112 | 125.7818 | 65.4891 | 39.6225 | 4.0083 | 2.9575 | 5.3698 |  | 586.7841
18 | 305.1646 | 3834.4805 |  | 3296.118 | 545.1485 | 71.9215 | 141.8583 | 69.6123 | 41.5073 | 4.128 | 3.337 | 5.0645 |  | 618.5022
19 | 339.7167 | 4164.525 |  | 3447.2294 | 610.0462 | 72.0264 | 171.1951 | 78.3657 | 46.5637 | 4.3677 | 3.4567 | 6.3886 |  | 733.4802
20 | 297.8947 | 3801.8142 |  | 3258.3401 | 596.5628 | 68.9546 | 155.5363 | 73.5695 | 43.3433 | 4.0754 | 3.0568 | 6.6717 |  | 655.5066
21 | 294.4378 | 3988.7215 |  | 3358.6876 | 617.8032 | 80.0246 | 161.0207 | 65.5997 | 44.7507 | 4.4571 | 3.0675 | 6.0939 |  | 658.1498
22 | 338.9231 | 4109.2015 |  | 3636.1187 | 633.8552 | 80.0347 | 169.5496 | 76.9343 | 45.2589 | 4.5031 | 2.9042 | 7.1997 |  | 729.5154
23 | 359.0107 | 3575.3775 |  | 3183.5715 | 597.8944 | 81.2354 | 148.948 | 75.0494 | 43.4737 | 4.4656 | 2.8849 | 5.8825 |  | 755.9471
24 | 350.5843 | 3235.3419 |  | 2609.0332 | 616.3301 | 83.564 | 165.171 | 79.0719 | 45.2248 | 4.5071 | 2.6428 | 5.5722 |  | 693.8326
25 | 313.8373 | 2820.4891 |  | 2210.0046 | 589.3724 | 85.3894 | 160.9418 | 75.2194 | 42.5368 | 4.407 | 2.4871 | 4.7212 |  | 650.2203
26 | 326.6876 | 2679.7858 |  | 1896.7632 | 588.0698 | 87.8755 | 161.109 | 74.1458 | 42.7216 | 4.3328 | 2.5269 | 5.0462 |  | 650.2203
27 | 321.3351 | 2744.3445 |  | 1841.6705 | 612.1397 | 91.732 | 172.3546 | 75.8967 | 45.087 | 4.4634 | 2.6184 | 5.2467 |  | 681.9383
28 | 358.673 | 2798.336 |  | 1912.5039 | 615.7059 | 91.6721 | 171.6989 | 76.2389 | 45.7174 | 4.4891 | 2.5616 | 5.5346 |  | 697.7974
29 | 359.6655 | 2707.389 |  | 2030.5597 | 575.629 | 86.6987 | 154.4801 | 71.8849 | 42.2552 | 4.0491 | 2.5837 | 5.0977 |  | 685.1101
30 | 335.9129 | 2902.8373 |  | 1983.3374 | 545.4598 | 71.505 | 164.8655 | 67.0731 | 40.3018 | 3.759 | 2.7871 | 4.3647 |  | 697.7974
31 | 308.2685 | 2751.1069 |  | 2172.2267 | 663.0794 | 85.5036 | 203.4039 | 82.8201 | 49.9096 | 4.7574 | 2.7138 | 5.569 |  | 697.7974
Tot | 9595.9355 | 109245.7509 |  | 91318.1464 | 18402.8551 | 2612.6142 | 4587.9558 | 2079.5137 | 1346.7782 | 153.891 | 88.3635 | 177.2779 |  | 20618.8546
Avg | 309.5463 | 3524.0565 |  | 2945.7467 | 593.6405 | 84.2779 | 147.9986 | 67.0811 | 43.4445 | 4.9642 | 2.8504 | 5.7186 |  | 665.1243
Max | 359.6655 | 4174.5492 |  | 3636.1187 | 730.3449 | 111.4737 | 203.4039 | 82.8201 | 52.0669 | 7.5531 | 3.4567 | 7.7011 |  | 755.9471
Min | 255.7235 | 2679.7858 |  | 1841.6705 | 512.367 | 68.9546 | 114.7126 | 51.8515 | 39.6225 | 3.759 | 2.436 | 4.3647 |  | 586.7841
* Please specify the chemical compound(s) and units used. Include product name if applicable
Pre-ph=Liquid Lime |  |  |  | Pre & Post Disinfectant= Sodium Hypochlorite | [5 empty] | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC | [5 empty] | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Polytec 1114 PWG | [5 empty] | Coagulant= Aluminum Sulfate
PAC= WaterCarb CW |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## Chem Dose
Surface Water System Monthly Operation Report
Treatment Chemicals
Bureau of Water
System Name: Grand Strand Regional | [8 empty] | System Number: 2620004
2019-01-01
Chemical dosage mg/l
Day | Pre Disinf (gal) | * Coagulant (gal) | Lime Pre pH Adjustment (lbs) (gal) |  | * Post Disenfectant (gal) (gal) |  | * Post-pH (gal) | * Fluoride (gal) | * Phosphate (gal) | * Zinc (gal) | Filter Aid | * Polymer (gal) | Pre-pH | * PAC (lb)
| HOCl |  | Hydrated | Liquid | HOCl | NH3 | NaOH | [5 empty] | NaOH
1 | 1.514 | 90.2474 |  | 35.9206 | 3.7828 | 0.6939 | 4.5697 | 0.56032 | 1.1216 | 0.095567 | 0.070277 | 0.33183 |  | 2.931
2 | 1.4419 | 90.3794 |  | 39.0512 | 3.8246 | 0.68867 | 4.9025 | 0.54772 | 1.0959 | 0.10142 | 0.069048 | 0.29704 |  | 3.0508
3 | 1.4418 | 90.5974 |  | 37.6784 | 3.8066 | 0.67561 | 4.8992 | 0.54763 | 1.1 | 0.102 | 0.060671 | 0.30153 |  | 2.8795
4 | 1.4102 | 90.4659 |  | 33.893 | 3.8246 | 0.68783 | 4.7143 | 0.55098 | 1.0902 | 0.099544 | 0.060566 | 0.28139 |  | 2.8152
5 | 1.3877 | 90.8464 |  | 36.673 | 3.8044 | 0.7042 | 4.656 | 0.5486 | 1.104 | 0.10053 | 0.060946 | 0.26428 |  | 3.0203
6 | 1.3636 | 90.9239 |  | 35.7244 | 3.8211 | 0.71808 | 4.4117 | 0.55207 | 1.1046 | 0.10362 | 0.060323 | 0.25793 |  | 2.8723
7 | 1.3389 | 90.4643 |  | 37.4016 | 3.8591 | 0.70994 | 4.4572 | 0.55131 | 1.1222 | 0.10265 | 0.060214 | 0.251 |  | 3.0029
8 | 1.2853 | 90.6455 |  | 38.0826 | 3.8058 | 0.70338 | 4.4791 | 0.55095 | 1.125 | 0.09954 | 0.060208 | 0.24498 |  | 2.971
9 | 1.3335 | 90.1733 |  | 34.5931 | 3.8479 | 0.72658 | 4.8809 | 0.55006 | 1.0973 | 0.10236 | 0.05995 | 0.24117 |  | 2.6669
10 | 1.4243 | 89.9461 |  | 38.9841 | 3.8319 | 0.73203 | 4.2652 | 0.55088 | 1.0896 | 0.1036 | 0.06044 | 0.23963 |  | 3.2038
11 | 1.4265 | 90.1697 |  | 35.5812 | 3.7937 | 0.70619 | 4.0898 | 0.54613 | 1.1204 | 0.1028 | 0.069569 | 0.24164 |  | 3.0451
12 | 1.593 | 89.6722 |  | 33.955 | 3.7396 | 0.69923 | 3.9258 | 0.54362 | 1.1064 | 0.10201 | 0.070216 | 0.22822 |  | 2.9252
13 | 1.65 | 90.1325 |  | 34.4144 | 3.7633 | 0.68428 | 4.0952 | 0.55398 | 1.1011 | 0.099976 | 0.070027 | 0.22385 |  | 2.8695
14 | 1.6823 | 89.891 |  | 36.7909 | 3.7645 | 0.67912 | 4.4146 | 0.55398 | 1.0834 | 0.099976 | 0.069836 | 0.2188 |  | 3.0011
15 | 1.5887 | 89.7836 |  | 36.2887 | 3.741 | 0.67128 | 4.3256 | 0.5482 | 1.0909 | 0.104 | 0.070078 | 0.2786 |  | 2.9835
16 | 1.5472 | 89.4686 |  | 35.8889 | 3.7517 | 0.65662 | 4.5287 | 0.54499 | 1.0986 | 0.10215 | 0.070607 | 0.276 |  | 2.9401
17 | 1.4229 | 90.6668 |  | 36.9665 | 3.5304 | 0.58827 | 4.4319 | 0.53632 | 1.0921 | 0.10199 | 0.070772 | 0.25809 |  | 2.7839
18 | 1.4705 | 90.0808 |  | 36.0969 | 3.5669 | 0.58218 | 4.7262 | 0.54135 | 1.0863 | 0.099736 | 0.07032 | 0.23114 |  | 2.7094
19 | 1.5166 | 90.6388 |  | 34.9752 | 3.6346 | 0.53088 | 5.2085 | 0.55491 | 1.1097 | 0.09609 | 0.069438 | 0.2655 |  | 2.9767
20 | 1.4491 | 90.1666 |  | 36.0241 | 3.8091 | 0.54469 | 5.1022 | 0.55831 | 1.107 | 0.09609 | 0.070444 | 0.29715 |  | 2.8989
21 | 1.3576 | 89.6621 |  | 35.1954 | 3.7514 | 0.60114 | 5.0103 | 0.47342 | 1.0869 | 0.099937 | 0.070386 | 0.25811 |  | 2.7587
22 | 1.4891 | 88.0196 |  | 36.3079 | 3.7445 | 0.58493 | 5.1157 | 0.54018 | 1.0695 | 0.098232 | 0.058339 | 0.29668 |  | 2.9138
23 | 1.6621 | 80.7007 |  | 33.4974 | 3.6684 | 0.61661 | 4.6786 | 0.54728 | 1.0669 | 0.10117 | 0.058055 | 0.25176 |  | 3.1816
24 | 1.6677 | 75.0326 |  | 28.2066 | 3.6747 | 0.61637 | 4.9835 | 0.56032 | 1.0786 | 0.09923 | 0.058229 | 0.23174 |  | 3.0004
25 | 1.5726 | 68.9056 |  | 25.1689 | 3.7402 | 0.67038 | 5.1606 | 0.56734 | 1.0798 | 0.10327 | 0.057267 | 0.20899 |  | 2.962
26 | 1.6237 | 64.9353 |  | 21.4257 | 3.7518 | 0.69357 | 5.2447 | 0.56222 | 1.0902 | 0.10207 | 0.057419 | 0.22457 |  | 2.9379
27 | 1.5574 | 64.8453 |  | 20.2859 | 3.7553 | 0.6962 | 5.413 | 0.55339 | 1.1064 | 0.10111 | 0.056897 | 0.22452 |  | 3.0046
28 | 1.7073 | 64.9422 |  | 20.6905 | 3.7383 | 0.68858 | 5.3322 | 0.55016 | 1.1103 | 0.10065 | 0.056983 | 0.2344 |  | 3.0197
29 | 1.7734 | 65.0818 |  | 22.7544 | 3.7149 | 0.69219 | 5.0804 | 0.55137 | 1.0908 | 0.096493 | 0.057446 | 0.22948 |  | 3.0709
30 | 1.4955 | 63.0082 |  | 20.0684 | 3.7147 | 0.60244 | 5.4487 | 0.5429 | 1.0979 | 0.094528 | 0.057143 | 0.20734 |  | 2.8243
31 | 1.4455 | 62.8951 |  | 23.1503 | 3.6354 | 0.57995 | 5.797 | 0.53968 | 1.0946 | 0.096316 | 0.056941 | 0.21298 |  | 2.9747
Tot | 46.6398 | 2593.3884 |  | 1011.7355 | 116.1933 | 20.4253 | 148.3487 | 16.9805 | 34.018 | 3.1087 | 1.9691 | 7.8103 |  | 91.1956
Avg | 1.5045 | 83.6577 |  | 32.6366 | 3.7482 | 0.65888 | 4.7854 | 0.54776 | 1.0974 | 0.10028 | 0.063518 | 0.25195 |  | 2.9418
Max | 1.7734 | 90.9239 |  | 39.0512 | 3.8591 | 0.73203 | 5.797 | 0.56734 | 1.125 | 0.104 | 0.070772 | 0.33183 |  | 3.2038
Min | 1.2853 | 62.8951 |  | 20.0684 | 3.5304 | 0.53088 | 3.9258 | 0.47342 | 1.0669 | 0.094528 | 0.056897 | 0.20734 |  | 2.6669
* Please specify the chemical compound(s) and units used. Include product name if applicable | 31 | 31 | 0 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 0 | 31
Pre-ph = Liquid Lime |  |  |  | Pre and Post Disinfectant= Sodium Hypochlorite |  |  |  |  | Phosphate= TKPP
Pre/Post-pH = Sodium Hydroxide |  |  |  | Zinc Chloride= Caliquest ZC |  |  |  |  | Filter Aid= Brennfloc CP 9884
Fluoride= Fluorosilicic Acid |  |  |  | Polymer= Polytec 1114 PWG |  |  |  |  | Coagulant= Aluminum Sulfate
PAC= WaterCarb CW |  |  |  | NH3= Aqueous Ammonia
Prepared by: _________________________________________________ | [7 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Supervisor

## Turbidity
Surface Water System Monthly Operation Report
Compliance with Turbidity Requirements for Filtered Systems &
Bacteriological Analysis for Raw and Finished Water
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  | 2019-01-01
Lab Cert ID #: 26102 |  |  |  | Total Population: | >10,000
| Combined Filtered Water Turbidity Compliance |  |  |  | Bacteriological Analysis
Day | Maximum Filtered Water Turbidity | (A) Number of Turbidity Measurements | (B) Number of Turbidity Measurements <= 95% Limit | Number of Turbidity Measurements > Max Allowed | Raw Water |  | Finished1 Finished2
[5 empty] | Total Coliform per 100 mls | E.coli per 100 mls | Total Coliform P/A | Total Coliform P/A
1 | 0.032 | 18 | 18 | 0 | 52 | <10 | A | A
2 | 0.027 | 18 | 18 | 0 | 85 | <10 | A | A
3 | 0.026 | 18 | 18 | 0 | 62 | <10 | A | A
4 | 0.081 | 18 | 18 | 0 | 122 | <10 | A | A
5 | 0.038 | 18 | 18 | 0 | 20 | <10 | A | A
6 | 0.028 | 18 | 18 | 0 | 75 | <10 | A | A
7 | 0.024 | 18 | 18 | 0 | 31 | 10 | A | A
8 | 0.057 | 18 | 18 | 0 | 31 | <10 | A | A
9 | 0.034 | 18 | 18 | 0 | 31 | <10 | A | A
10 | 0.033 | 18 | 18 | 0 | 63 | <10 | A | A
11 | 0.028 | 18 | 18 | 0 | 63 | <10 | A | A
12 | 0.052 | 18 | 18 | 0 | 109 | 10 | A | A
13 | 0.029 | 18 | 18 | 0 | 85 | 10 | A | A
14 | 0.029 | 18 | 18 | 0 | 95 | 41 | A | A
15 | 0.06 | 18 | 18 | 0 | 85 | 10 | A | A
16 | 0.027 | 18 | 18 | 0 | 187 | 30 | A | A
17 | 0.046 | 18 | 18 | 0 | 148 | 31 | A | A
18 | 0.053 | 18 | 18 | 0 | 345 | 41 | A | A
19 | 0.033 | 18 | 18 | 0 | 697 | 63 | A | A
20 | 0.043 | 18 | 18 | 0 | 602 | 63 | A | A
21 | 0.04 | 18 | 18 | 0 | 359 | 20 | A | A
22 | 0.031 | 18 | 18 | 0 | 480 | 30 | A | A
23 | 0.04 | 18 | 18 | 0 | 384 | 10 | A | A
24 | 0.04 | 18 | 18 | 0 | 573 | 10 | A | A
25 | 0.031 | 18 | 18 | 0 | 480 | 41 | A | A
26 | 0.024 | 18 | 18 | 0 | 548 | 10 | A | A
27 | 0.039 | 18 | 18 | 0 | 488 | 31 | A | A
28 | 0.023 | 18 | 18 | 0 | 341 | 31 | A | A
29 | 0.019 | 18 | 18 | 0 | 364 | <10 | A | A
30 | 0.066 | 18 | 18 | 0 | 292 | 10 | A | A
31 | 0.027 | 18 | 18 | 0 | 323 | <10 | A | A
| Total | 558 | 558 | 0
Max. Allow. Turbidity: |  | 1 NTU |  | Type of Plant: |  | Super Pulsator/Greenleaf Filters
95% Turbidity Limit: |  | 0.3 NTU |  | Max. Approved Filtration Rate: |  | 6 |  | (gpm/ft2)
The percentage of turbidity measurements |  |  |  | 100
meeting the specific limit is equal to: B/A x 100
Prepared by: ____________________________________________ |  |  |  |  | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## Indiv Filter
Surface Water System Monthly Operation Report
Turbidity Requirements for Individual Filters For Complaince With
Long Term 2 Enhanced Surface Water Treatment Rule
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  |  |  |  | 2019-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lab Cert ID #: 26102 |  |  | Population: >10,000
Turbidity Requirements |  |  |  | Individual Filters
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Was the turbidity recorded every 15 minutes for each
individual filter (while in operation) for the entire
month? | bar: Individual Filters 1 to Individual Filters 12
2 | Were 95% of the Turbidity Measurements less than
the 0.15 NTU Limit (excluding the 15 minute period
after a backwash cycle)? | bar: Individual Filters 1 to Individual Filters 12
3 | Were there any consecutive measurements greater
than 0.30 NTU? | bar: Individual Filters 1 to Individual Filters 12
Prepared by: |  |  |  | Individual Filters 5: Date:; Individual Filters 7: 2019-02-06
(signature) William Lederman Plant Superintendent

## Individual Filters
0 | Surface Water System Monthly Operation Report
Individual Filter Performance Worksheet
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  | 2019-01-01
Lab Cert ID #: 26102 |  | Total Population Served: >10,000
1. Was the turbidity recorded every 15 minutes for each individual filter |  |  |  |  | yes
(while in operation) for the entire month?
2a. Was there a failure of any of the continuous turbidity monitoring equipment during the month? |  |  |  |  | no
2b. If there was a failure, were grab samples taken from the filter effluent every 4 hours? |  |  |  |  | N.A.
2c. If there was failure of any continuous monitoring equipment, was it repaired within
5 working days? |  |  |  |  | N.A.
3a. Did any individual filter(s) have a measured effluent turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart? |  |  |  |  | no
3b. If the answer to 3a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
3c. If the answer to 3a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | N.A.
4a. Did any individual filter(s) have a measured effluent turbidity level of > 0.5 NTU in two consecutive
measurements taken 15 minutes apart, excluding the first four hours of operation after the filter
has been backwashed or otherwise taken out of service? |  |  |  |  | no
4b. If the answer to 4a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
4c. If the answer to 4a was "yes", was a filter run profile and/or obvious reason for the exceedance
sent to the Department within 7 days? |  |  |  |  | N.A.
5a. Did any individual filter(s) have a measured turbidity level of > 1.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 3 months? |  |  |  |  | no
5b. If the answer to 5a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
5c. If the answer to 5a was "yes", have arrangements been made for a filter self-assessment to be
conducted within 14 days of the exceedance? |  |  |  |  | N.A.
6a. Did any individual filter(s) have a measured turbidity level of > 2.0 NTU in two consecutive
measurements taken 15 minutes apart at any time in each of the last 2 months? |  |  |  |  | no
6b. If the answer to 6a was "yes", was the filter number(s), turbidity measurement(s), and date(s)
for the exceedance reported to the Department within 7 days? |  |  |  |  | N.A.
6c. If the answer to 6a was "yes", have arrangements been made to have a CPE conducted by the
Department or by a third party approved by the Department within 30 days of the exceedance? |  |  |  |  | N.A.
Prepared by: ___________________________________________ |  |  | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## MOR CT
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-01-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.02 | 14.8 | 15 | 1.076
2 | 0.58 | 9 | 28.2667 | 16.3947 | 6.07 | 14.6 | 15 | 1.093
3 | 0.51 | 7.7 | 33.039 | 16.8499 | 6.17 | 15.5 | 10 | 1.685
4 | 0.42 | 8.8 | 28.9091 | 12.1418 | 6.16 | 16 | 10 | 1.2142
5 | 0.42 | 8.3 | 30.6506 | 12.8733 | 6.22 | 15.9 | 10 | 1.2873
6 | 0.4 | 8.5 | 29.9294 | 11.9718 | 6.1 | 15.6 | 10 | 1.1972
7 | 0.45 | 9.6 | 28.125 | 12.6562 | 6.12 | 16.5 | 10 | 1.2656
8 | 0.38 | 8.2 | 31.0244 | 11.7893 | 6.27 | 15.5 | 10 | 1.1789
9 | 0.41 | 10.1 | 26.7327 | 10.9604 | 6.12 | 16.6 | 10 | 1.096
10 | 0.54 | 9 | 28.2667 | 15.264 | 6.11 | 14.9 | 15 | 1.0176
11 | 0.59 | 9.6 | 26.5 | 15.635 | 6.24 | 14.5 | 15 | 1.0423
12 | 0.61 | 10.4 | 25.9615 | 15.8365 | 6.15 | 14.9 | 15 | 1.0558
13 | 0.64 | 10 | 25.44 | 16.2816 | 6.1 | 12.6 | 15 | 1.0854
14 | 0.63 | 10.3 | 24.699 | 15.5604 | 6.04 | 12.5 | 15 | 1.0374
15 | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.15 | 11.5 | 15 | 1.0984
16 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.05 | 11.2 | 15 | 1.0661
17 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.16 | 10.9 | 15 | 1.0533
18 | 0.75 | 13.1 | 20.6107 | 15.458 | 6.13 | 13.3 | 15 | 1.0305
19 | 0.78 | 13.4 | 20.1493 | 15.7164 | 6.2 | 13.1 | 15 | 1.0478
20 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.25 | 12.7 | 15 | 1.0661
21 | 0.76 | 12 | 21.2 | 16.112 | 6.18 | 11.6 | 15 | 1.0741
22 | 0.75 | 13 | 20.7692 | 15.5769 | 6.24 | 13 | 15 | 1.0385
23 | 0.73 | 12 | 21.2 | 15.476 | 6.37 | 11.9 | 15 | 1.0317
24 | 0.64 | 8.6 | 29.5814 | 18.9321 | 6.13 | 12.2 | 15 | 1.2621
25 | 0.65 | 9.6 | 26.5 | 17.225 | 6.03 | 11.6 | 15 | 1.1483
26 | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.09 | 11.3 | 15 | 1.0338
27 | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.02 | 11.1 | 15 | 1.0338
28 | 0.66 | 11.5 | 23.4783 | 15.4957 | 6.03 | 12.7 | 15 | 1.033
29 | 0.73 | 11.1 | 22.9189 | 16.7308 | 6.23 | 10.9 | 15 | 1.1154
30 | 0.69 | 11.4 | 22.3158 | 15.3979 | 6.2 | 10.3 | 15 | 1.0265
31 | 0.72 | 12.5 | 21.6 | 15.552 | 6.12 | 12.7 | 15 | 1.0368
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## CT AVG (hidden)
|  |  |  | Plant 1 avg min CT per day | [11 empty] | Plant 2 avg min CT per day | [11 empty] | Plant 3 avg min CT per day
DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT | DAY | C X T | AVG Temp | use Temp | ph | use PH | min ct table | flow | t10 | MIN CL2 | min CT | DAILY CT
1 | #DIV/0! | 14.625 | 10 | 6.0725 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 14.85 | 10 | 6.11 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | 16.45 | 15 | 6.105 | 6.5 | 10 | 0 | #DIV/0! | 0.67 | #DIV/0! | #DIV/0!
2 | #DIV/0! | 14.775 | 10 | 6.09 | 6.5 | 15 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 14.825 | 10 | 6.0775 | 6.5 | 15 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | 16.325 | 15 | 6.075 | 6.5 | 10 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0!
3 | #DIV/0! | 15.15 | 15 | 6.1225 | 6.5 | 10 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 15.45 | 15 | 6.1575 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | 16.825 | 15 | 6.12 | 6.5 | 10 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0!
4 | #DIV/0! | 15.225 | 15 | 6.08 | 6.5 | 10 | 0 | #DIV/0! | 0.51 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 15.8 | 15 | 6.155 | 6.5 | 10 | 0 | #DIV/0! | 0.42 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | 17 | 15 | 6.1675 | 6.5 | 10 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
5 | #DIV/0! | 15.375 | 15 | 6.2 | 6.5 | 10 | 0 | #DIV/0! | 0.52 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 15.975 | 15 | 6.225 | 6.5 | 10 | 0 | #DIV/0! | 0.42 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | 17.25 | 15 | 6.22 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0!
6 | #DIV/0! | 15.35 | 15 | 6.1375 | 6.5 | 10 | 0 | #DIV/0! | 0.56 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 15.75 | 15 | 6.1175 | 6.5 | 10 | 0 | #DIV/0! | 0.4 | #DIV/0! | #DIV/0! | 6 | #DIV/0! | 16.5 | 15 | 6.15 | 6.5 | 10 | 0 | #DIV/0! | 0.44 | #DIV/0! | #DIV/0!
7 | #DIV/0! | 15.275 | 15 | 6.1425 | 6.5 | 10 | 0 | #DIV/0! | 0.57 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 15.775 | 15 | 6.1275 | 6.5 | 10 | 0 | #DIV/0! | 0.4 | #DIV/0! | #DIV/0! | 7 | #DIV/0! | 16.55 | 15 | 6.15 | 6.5 | 10 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0!
8 | #DIV/0! | 15.475 | 15 | 6.225 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 15.675 | 15 | 6.2075 | 6.5 | 10 | 0 | #DIV/0! | 0.38 | #DIV/0! | #DIV/0! | 8 | #DIV/0! | 16.7 | 15 | 6.2 | 6.5 | 10 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0!
9 | #DIV/0! | 15.425 | 15 | 6.1775 | 6.5 | 10 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 15.9 | 15 | 6.18 | 6.5 | 10 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 9 | #DIV/0! | 16.7 | 15 | 6.175 | 6.5 | 10 | 0 | #DIV/0! | 0.41 | #DIV/0! | #DIV/0!
10 | #DIV/0! | 14.975 | 15 | 6.1075 | 6.5 | 10 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 15.175 | 15 | 6.12 | 6.5 | 10 | 0 | #DIV/0! | 0.48 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | 16.1 | 15 | 6.1325 | 6.5 | 10 | 0 | #DIV/0! | 0.47 | #DIV/0! | #DIV/0!
11 | #DIV/0! | 14.45 | 10 | 6.1475 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 14.5 | 10 | 6.1525 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 11 | #DIV/0! | 15.5 | 15 | 6.14 | 6.5 | 10 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
12 | #DIV/0! | 13.625 | 10 | 6.1175 | 6.5 | 15 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 13.675 | 10 | 6.1225 | 6.5 | 15 | 0 | #DIV/0! | 0.45 | #DIV/0! | #DIV/0! | 12 | #DIV/0! | 14.725 | 10 | 6.115 | 6.5 | 15 | 0 | #DIV/0! | 0.53 | #DIV/0! | #DIV/0!
13 | #DIV/0! | 13.375 | 10 | 6.06 | 6.5 | 15 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 13.375 | 10 | 6.0575 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 13 | #DIV/0! | 14.475 | 10 | 6.06 | 6.5 | 15 | 0 | #DIV/0! | 0.54 | #DIV/0! | #DIV/0!
14 | #DIV/0! | 12.55 | 10 | 6.075 | 6.5 | 15 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 12.725 | 10 | 6.1125 | 6.5 | 15 | 0 | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | 14 | #DIV/0! | 13.475 | 10 | 6.0925 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0!
15 | #DIV/0! | 12 | 10 | 6.105 | 6.5 | 15 | 0 | #DIV/0! | 0.67 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 12.15 | 10 | 6.15 | 6.5 | 15 | 0 | #DIV/0! | 0.81 | #DIV/0! | #DIV/0! | 15 | #DIV/0! | 12.75 | 10 | 6.185 | 6.5 | 15 | 0 | #DIV/0! | 0.78 | #DIV/0! | #DIV/0!
16 | #DIV/0! | 11.75 | 10 | 6.1275 | 6.5 | 15 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 12.425 | 10 | 6.165 | 6.5 | 15 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0! | 16 | #DIV/0! | 12.9 | 10 | 6.1125 | 6.5 | 15 | 0 | #DIV/0! | 0.72 | #DIV/0! | #DIV/0!
17 | #DIV/0! | 11.35 | 10 | 6.25 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 12.175 | 10 | 6.2675 | 6.5 | 15 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 17 | #DIV/0! | 12.775 | 10 | 6.24 | 6.5 | 15 | 0 | #DIV/0! | 0.63 | #DIV/0! | #DIV/0!
18 | #DIV/0! | 11.55 | 10 | 6.1925 | 6.5 | 15 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 12.375 | 10 | 6.2 | 6.5 | 15 | 0 | #DIV/0! | 0.43 | #DIV/0! | #DIV/0! | 18 | #DIV/0! | 12.9 | 10 | 6.205 | 6.5 | 15 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0!
19 | #DIV/0! | 12.5 | 10 | 6.1375 | 6.5 | 15 | 0 | #DIV/0! | 0.76 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 13.2 | 10 | 6.125 | 6.5 | 15 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 19 | #DIV/0! | 13.575 | 10 | 6.14 | 6.5 | 15 | 0 | #DIV/0! | 0.78 | #DIV/0! | #DIV/0!
20 | #DIV/0! | 12.8 | 10 | 6.2325 | 6.5 | 15 | 0 | #DIV/0! | 0.66 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 13.425 | 10 | 6.1975 | 6.5 | 15 | 0 | #DIV/0! | 0.4 | #DIV/0! | #DIV/0! | 20 | #DIV/0! | 13.975 | 10 | 6.2175 | 6.5 | 15 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0!
21 | #DIV/0! | 11.925 | 10 | 6.18 | 6.5 | 15 | 0 | #DIV/0! | 0.69 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 12.875 | 10 | 6.2275 | 6.5 | 15 | 0 | #DIV/0! | 0.33 | #DIV/0! | #DIV/0! | 21 | #DIV/0! | 13.4 | 10 | 6.225 | 6.5 | 15 | 0 | #DIV/0! | 0.73 | #DIV/0! | #DIV/0!
22 | #DIV/0! | 11.175 | 10 | 6.18 | 6.5 | 15 | 0 | #DIV/0! | 0.74 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 12.175 | 10 | 6.22 | 6.5 | 15 | 0 | #DIV/0! | 0.39 | #DIV/0! | #DIV/0! | 22 | #DIV/0! | 12.625 | 10 | 6.2725 | 6.5 | 15 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0!
23 | #DIV/0! | 11.475 | 10 | 6.265 | 6.5 | 15 | 0 | #DIV/0! | 0.73 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 11.075 | 10 | 6.2825 | 6.5 | 15 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 23 | #DIV/0! | 12.975 | 10 | 6.2625 | 6.5 | 15 | 0 | #DIV/0! | 0.81 | #DIV/0! | #DIV/0!
24 | #DIV/0! | 12.05 | 10 | 6.105 | 6.5 | 15 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 11.3 | 10 | 6.175 | 6.5 | 15 | 0 | #DIV/0! | 0.67 | #DIV/0! | #DIV/0! | 24 | #DIV/0! | 13.9 | 10 | 6.19 | 6.5 | 15 | 0 | #DIV/0! | 0.82 | #DIV/0! | #DIV/0!
25 | #DIV/0! | 12.025 | 10 | 6.135 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 11.45 | 10 | 6.1725 | 6.5 | 15 | 0 | #DIV/0! | 0.59 | #DIV/0! | #DIV/0! | 25 | #DIV/0! | 14.2 | 10 | 6.1775 | 6.5 | 15 | 0 | #DIV/0! | 0.73 | #DIV/0! | #DIV/0!
26 | #DIV/0! | 11.975 | 10 | 6.0575 | 6.5 | 15 | 0 | #DIV/0! | 0.52 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 11.2 | 10 | 6.0625 | 6.5 | 15 | 0 | #DIV/0! | 0.64 | #DIV/0! | #DIV/0! | 26 | #DIV/0! | 13.275 | 10 | 6.0275 | 6.5 | 15 | 0 | #DIV/0! | 0.75 | #DIV/0! | #DIV/0!
27 | #DIV/0! | 11.7 | 10 | 5.965 | 6 | 13 | 0 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 10.85 | 10 | 5.9725 | 6 | 13 | 0 | #DIV/0! | 0.62 | #DIV/0! | #DIV/0! | 27 | #DIV/0! | 13.175 | 10 | 6.0025 | 6.5 | 15 | 0 | #DIV/0! | 0.65 | #DIV/0! | #DIV/0!
28 | #DIV/0! | 12.025 | 10 | 6.03 | 6.5 | 15 | 0 | #DIV/0! | 0.5 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 10.75 | 10 | 6.0675 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 28 | #DIV/0! | 12.725 | 10 | 6.0675 | 6.5 | 15 | 0 | #DIV/0! | 0.66 | #DIV/0! | #DIV/0!
29 | #DIV/0! | 11.25 | 10 | 6.1 | 6.5 | 15 | 0 | #DIV/0! | 0.61 | #DIV/0! | #DIV/0! | 29 | #DIV/0! | 10.75 | 10 | 6.1425 | 6.5 | 15 | 0 | #DIV/0! | 0.73 | #DIV/0! | #DIV/0! | 29 | #DIV/0! | 12.5 | 10 | 6.1325 | 6.5 | 15 | 0 | #DIV/0! | 0.79 | #DIV/0! | #DIV/0!
30 | #DIV/0! | 11.2 | 10 | 6.0875 | 6.5 | 15 | 0 | #DIV/0! | 0.46 | #DIV/0! | #DIV/0! | 30 | #DIV/0! | 10.475 | 10 | 6.1425 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0! | 30 | #DIV/0! | 12.475 | 10 | 6.125 | 6.5 | 15 | 0 | #DIV/0! | 0.73 | #DIV/0! | #DIV/0!
31 | #DIV/0! | 10.9 | 10 | 6.1525 | 6.5 | 15 | 0 | #DIV/0! | 0.67 | #DIV/0! | #DIV/0! | 31 | #DIV/0! | 10.3 | 10 | 6.13 | 6.5 | 15 | 0 | #DIV/0! | 0.71 | #DIV/0! | #DIV/0! | 31 | #DIV/0! | 12.425 | 10 | 6.1175 | 6.5 | 15 | 0 | #DIV/0! | 0.68 | #DIV/0! | #DIV/0!
ONLY FILL GREEN
|  |  |  | TEST | [8 empty] | DALY CAL SHEET FLOW, DALY AVG TEMP & PH Min CT Calculater
| Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# |  |  |  | Settle temp |  | use temp | Settle PH |  | use ph |  | FLOW CAL SHEET | t10#
| Plt 1 | 18.8 | 15 | Plt 1 PH | 6.09 | 6.5 | plt 1 flow | 12 | 21.2 |  |  |  | Plt 1 | 13.625 | 10 | Plt 1 PH | 6.1175 | 6.5 | plt 1 flow | 5.3 | 48
| Plt 2 | 18.9 | 15 | Plt 2 PH | 6.13 | 6.5 | plt 2 flow | 12 | 21.2 |  |  |  | Plt 2 | 13.675 | 10 | Plt 2 PH | 6.1225 | 6.5 | plt 2 flow | 10.3 | 24.699
| Plt 3 | 19.5 | 15 | Plt 3 PH | 6.24 | 6.5 | plt 3 flow | 12 | 22.5 |  |  |  | Plt 3 | 14.725 | 10 | Plt 3 PH | 6.115 | 6.5 | plt 3 flow | 11.4 | 23.6842
2019-08-12 08:45
|  | min CT | TARGET CT |  | temp | ph | min ct table | [7 empty] | min CT | TARGET CT |  | temp | ph | min ct table
| ct plt 1 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 1 | 0.3125 | 0.4125 |  | 10 | 6.5 | 15
| ct plt 2 | 0.4717 | 0.5717 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 2 | 0.60731 | 0.70731 |  | 10 | 6.5 | 15
| ct plt 3 | 0.44444 | 0.54444 |  | 15 | 6.5 | 10 | [6 empty] | ct plt 3 | 0.63333 | 0.73333 |  | 10 | 6.5 | 15
Bill's Cal | flow | temp | ph | t10# | cal ct table | MIN CT | target ct
plt1 | 12 | 18.8 | 6.09 | 21.2 | 7.1064 | 0.33521 | 0.43521
plt2 | 12 | 18.9 | 6.13 | 21.2 | 7.1599 | 0.33773 | 0.43773
plt3 | 12 | 19.5 | 6.24 | 22.5 | 7.1424 | 0.31744 | 0.41744

## CT Calc
Surface Water System Monthly Operation Report
Disinfection Information
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | 2019-01-01
| Min. Disinfect. Resid. | Sample Type for | CT calc/CT table Disinfectant Sequence | [5 empty] | SUM (CT calc/CT table)
Day | at Point-of-Entry to Distribution System (mg/L) | Point-of-Entry (POE) | 1st | 2nd | 3rd | 4th | 5th | 6th
1 | 3 | A | 1.076 | 0 | 0 | 0 | 0 | 0 | 1.076
2 | 2.9 | A | 1.093 | 0 | 0 | 0 | 0 | 0 | 1.093
3 | 2.1 | A | 1.685 | 0 | 0 | 0 | 0 | 0 | 1.685
4 | 2.7 | A | 1.2142 | 0 | 0 | 0 | 0 | 0 | 1.2142
5 | 2.6 | A | 1.2873 | 0 | 0 | 0 | 0 | 0 | 1.2873
6 | 2.7 | A | 1.1972 | 0 | 0 | 0 | 0 | 0 | 1.1972
7 | 2.6 | A | 1.2656 | 0 | 0 | 0 | 0 | 0 | 1.2656
8 | 2.5 | A | 1.1789 | 0 | 0 | 0 | 0 | 0 | 1.1789
9 | 2.6 | A | 1.096 | 0 | 0 | 0 | 0 | 0 | 1.096
10 | 2.7 | A | 1.0176 | 0 | 0 | 0 | 0 | 0 | 1.0176
11 | 2.8 | A | 1.0423 | 0 | 0 | 0 | 0 | 0 | 1.0423
12 | 2.4 | A | 1.0558 | 0 | 0 | 0 | 0 | 0 | 1.0558
13 | 2.6 | A | 1.0854 | 0 | 0 | 0 | 0 | 0 | 1.0854
14 | 2.6 | A | 1.0374 | 0 | 0 | 0 | 0 | 0 | 1.0374
15 | 2.5 | A | 1.0984 | 0 | 0 | 0 | 0 | 0 | 1.0984
16 | 2.2 | A | 1.0661 | 0 | 0 | 0 | 0 | 0 | 1.0661
17 | 2.5 | A | 1.0533 | 0 | 0 | 0 | 0 | 0 | 1.0533
18 | 2.09 | A | 1.0305 | 0 | 0 | 0 | 0 | 0 | 1.0305
19 | 2.4 | A | 1.0478 | 0 | 0 | 0 | 0 | 0 | 1.0478
20 | 2.5 | A | 1.0661 | 0 | 0 | 0 | 0 | 0 | 1.0661
21 | 2.2 | A | 1.0741 | 0 | 0 | 0 | 0 | 0 | 1.0741
22 | 2.4 | A | 1.0385 | 0 | 0 | 0 | 0 | 0 | 1.0385
23 | 2.5 | A | 1.0317 | 0 | 0 | 0 | 0 | 0 | 1.0317
24 | 2.6 | A | 1.2621 | 0 | 0 | 0 | 0 | 0 | 1.2621
25 | 2.9 | A | 1.1483 | 0 | 0 | 0 | 0 | 0 | 1.1483
26 | 2.3 | A | 1.0338 | 0 | 0 | 0 | 0 | 0 | 1.0338
27 | 2.5 | A | 1.0338 | 0 | 0 | 0 | 0 | 0 | 1.0338
28 | 2.5 | A | 1.033 | 0 | 0 | 0 | 0 | 0 | 1.033
29 | 2.5 | A | 1.1154 | 0 | 0 | 0 | 0 | 0 | 1.1154
30 | 3.3 | A | 1.0265 | 0 | 0 | 0 | 0 | 0 | 1.0265
31 | 2.5 | A | 1.0368 | 0 | 0 | 0 | 0 | 0 | 1.0368
A. Number of days SUM (CT calc/CT table) <1: |  |  | 0 |  | Days the Distribution Residual was <0.2 mg/L
[5 empty] | Day | Duration (hrs) |  | Date Reported
B. Compliance with disinfection residual criteria |  |  |  |  | None | None |  | None
at Point-of-Entry to distribution system: |  |  | Yes |  | None | None |  | None
Prepared by: _________________________________________________ | [6 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Superintendent

## CT (1)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-01-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.59 | 9.3 | 27.3548 | 16.1394 | 6.02 | 14.8 | 15 | 1.076
2 | 0.62 | 9 | 28.2667 | 17.5253 | 6.11 | 14.7 | 15 | 1.1684
3 | 0.55 | 8.1 | 31.4074 | 17.2741 | 6.05 | 15.1 | 10 | 1.7274
4 | 0.51 | 8.6 | 29.5814 | 15.0865 | 6.11 | 15 | 10 | 1.5087
5 | 0.52 | 9 | 28.2667 | 14.6987 | 6.27 | 15.2 | 10 | 1.4699
6 | 0.57 | 9 | 28.2667 | 16.112 | 6.21 | 15.3 | 10 | 1.6112
7 | 0.65 | 8.2 | 31.0244 | 20.1659 | 6.16 | 14.8 | 15 | 1.3444
8 | 0.47 | 8.3 | 30.6506 | 14.4058 | 6.18 | 16.3 | 10 | 1.4406
9 | 0.46 | 8.9 | 28.5843 | 13.1488 | 6.12 | 15.2 | 10 | 1.3149
10 | 0.55 | 8.9 | 28.5843 | 15.7213 | 6.06 | 14.9 | 15 | 1.0481
11 | 0.59 | 9.6 | 26.5 | 15.635 | 6.24 | 14.5 | 15 | 1.0423
12 | 0.65 | 10 | 25.44 | 16.536 | 6.12 | 12.9 | 15 | 1.1024
13 | 0.64 | 10 | 25.44 | 16.2816 | 6.1 | 12.6 | 15 | 1.0854
14 | 0.63 | 10.3 | 24.699 | 15.5604 | 6.04 | 12.5 | 15 | 1.0374
15 | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.15 | 11.5 | 15 | 1.0984
16 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.05 | 11.2 | 15 | 1.0661
17 | 0.59 | 9.5 | 26.7789 | 15.7996 | 6.16 | 10.9 | 15 | 1.0533
18 | 0.75 | 12.2 | 20.8525 | 15.6393 | 6.16 | 11.9 | 15 | 1.0426
19 | 0.76 | 12.3 | 20.6829 | 15.719 | 6.17 | 12 | 15 | 1.0479
20 | 0.66 | 10.5 | 24.2286 | 15.9909 | 6.25 | 12.7 | 15 | 1.0661
21 | 0.76 | 12 | 21.2 | 16.112 | 6.18 | 11.6 | 15 | 1.0741
22 | 0.74 | 12 | 21.2 | 15.688 | 6.1 | 11.5 | 15 | 1.0459
23 | 0.73 | 12 | 21.2 | 15.476 | 6.37 | 11.9 | 15 | 1.0317
24 | 0.64 | 8.6 | 29.5814 | 18.9321 | 6.13 | 12.2 | 15 | 1.2621
25 | 0.67 | 8.6 | 29.5814 | 19.8195 | 6.17 | 12 | 15 | 1.3213
26 | 0.55 | 6 | 42.4 | 23.32 | 6.04 | 12.2 | 15 | 1.5547
27 | 0.64 | 5 | 50.88 | 32.5632 | 6.03 | 11.4 | 15 | 2.1709
28 | 0.52 | 5 | 50.88 | 26.4576 | 6.11 | 13 | 15 | 1.7638
29 | 0.66 | 5.6 | 45.4286 | 29.9829 | 6.2 | 11.3 | 15 | 1.9989
30 | 0.46 | 5.9 | 43.1186 | 19.8346 | 6.09 | 11 | 15 | 1.3223
31 | 0.67 | 5.9 | 43.1186 | 28.8895 | 6.19 | 11 | 15 | 1.926
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) Randall Johnson Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (2)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-01-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.55 | 8.4 | 30.2857 | 16.6571 | 6.08 | 14.9 | 15 | 1.1105
2 | 0.58 | 9 | 28.2667 | 16.3947 | 6.07 | 14.6 | 15 | 1.093
3 | 0.51 | 7.7 | 33.039 | 16.8499 | 6.17 | 15.5 | 10 | 1.685
4 | 0.42 | 8.8 | 28.9091 | 12.1418 | 6.16 | 16 | 10 | 1.2142
5 | 0.42 | 8.3 | 30.6506 | 12.8733 | 6.22 | 15.9 | 10 | 1.2873
6 | 0.4 | 8.5 | 29.9294 | 11.9718 | 6.1 | 15.6 | 10 | 1.1972
7 | 0.49 | 8.7 | 29.2414 | 14.3283 | 6.14 | 15.7 | 10 | 1.4328
8 | 0.38 | 8.2 | 31.0244 | 11.7893 | 6.27 | 15.5 | 10 | 1.1789
9 | 0.43 | 9 | 28.2667 | 12.1547 | 6.11 | 16.3 | 10 | 1.2155
10 | 0.54 | 9 | 28.2667 | 15.264 | 6.11 | 14.9 | 15 | 1.0176
11 | 0.73 | 8.5 | 29.9294 | 21.8485 | 6.17 | 14.5 | 15 | 1.4566
12 | 0.45 | 5.1 | 49.8824 | 22.4471 | 6.15 | 13.9 | 15 | 1.4965
13 | 0.55 | 6 | 42.4 | 23.32 | 6.12 | 14 | 15 | 1.5547
14 | 0.55 | 6 | 42.4 | 23.32 | 6.15 | 13.5 | 15 | 1.5547
15 | 0.81 | 6 | 42.4 | 34.344 | 6.19 | 11.4 | 15 | 2.2896
16 | 0.75 | 6 | 42.4 | 31.8 | 6.1 | 12 | 15 | 2.12
17 | 0.43 | 6 | 42.4 | 18.232 | 6.33 | 12.2 | 15 | 1.2155
18 | 0.43 | 5.7 | 44.6316 | 19.1916 | 6.22 | 12.1 | 15 | 1.2794
19 | 0.64 | 5 | 50.88 | 32.5632 | 6.21 | 12.9 | 15 | 2.1709
20 | 0.4 | 5 | 50.88 | 20.352 | 6.24 | 13.6 | 15 | 1.3568
21 | 0.33 | 5 | 50.88 | 16.7904 | 6.25 | 13 | 15 | 1.1194
22 | 0.39 | 5.3 | 48 | 18.72 | 6.2 | 12.5 | 15 | 1.248
23 | 0.74 | 5.1 | 49.8824 | 36.9129 | 6.33 | 9.9 | 20 | 1.8456
24 | 0.67 | 8.6 | 29.5814 | 19.8195 | 6.22 | 11.6 | 15 | 1.3213
25 | 0.65 | 9.6 | 26.5 | 17.225 | 6.03 | 11.6 | 15 | 1.1483
26 | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.09 | 11.3 | 15 | 1.0338
27 | 0.64 | 10.5 | 24.2286 | 15.5063 | 6.02 | 11.1 | 15 | 1.0338
28 | 0.68 | 10.5 | 24.2286 | 16.4754 | 6.02 | 10.9 | 15 | 1.0984
29 | 0.73 | 11.1 | 22.9189 | 16.7308 | 6.23 | 10.9 | 15 | 1.1154
30 | 0.69 | 11.4 | 22.3158 | 15.3979 | 6.2 | 10.3 | 15 | 1.0265
31 | 0.71 | 11.3 | 22.5133 | 15.9844 | 6.1 | 10.8 | 15 | 1.0656
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## CT (3)
Surface Water System Monthly Operation Report
CT Determination per Disinfectant Sequence
Bureau of Water
System Name: Grand Strand Regional |  |  |  | System Number: 2620004 |  |  |  |  | 16 | 18
Lab Cert ID #: 26102 |  |  |  | 2019-01-01 |  |  |  |  | 19.6 | 15
Day | Disinfectant Concentration C (mg/L) | Peak Hourly Flow Through Treatment Segment (MGD) | Disinfectant Contact Time T (min) | CT Calc (= C x T) | pH | Water Temperature (°C) | CT Table | CT Calc/CT (table)
1 | 0.68 | 10.2 | 26.4706 | 18 | 6.1 | 16.6 | 10 | 1.8
2 | 0.71 | 10 | 27 | 19.17 | 6.1 | 16.1 | 10 | 1.917
3 | 0.65 | 9.1 | 29.6703 | 19.2857 | 6.1 | 16.8 | 10 | 1.9286
4 | 0.53 | 10 | 27 | 14.31 | 6.16 | 17 | 10 | 1.431
5 | 0.49 | 10 | 27 | 13.23 | 6.22 | 17 | 10 | 1.323
6 | 0.44 | 9.9 | 27.2727 | 12 | 6.16 | 15.5 | 10 | 1.2
7 | 0.45 | 9.6 | 28.125 | 12.6562 | 6.12 | 16.5 | 10 | 1.2656
8 | 0.43 | 9.2 | 29.3478 | 12.6196 | 6.25 | 16.4 | 10 | 1.262
9 | 0.41 | 10.1 | 26.7327 | 10.9604 | 6.12 | 16.6 | 10 | 1.096
10 | 0.47 | 10 | 27 | 12.69 | 6.11 | 16.5 | 10 | 1.269
11 | 0.54 | 10 | 27 | 14.58 | 6.09 | 15.1 | 10 | 1.458
12 | 0.61 | 10.4 | 25.9615 | 15.8365 | 6.15 | 14.9 | 15 | 1.0558
13 | 0.54 | 11.2 | 24.1071 | 13.0179 | 6.01 | 15 | 10 | 1.3018
14 | 0.69 | 11.2 | 24.1071 | 16.6339 | 6.07 | 13.2 | 15 | 1.1089
15 | 0.78 | 11 | 24.5455 | 19.1455 | 6.13 | 13 | 15 | 1.2764
16 | 0.72 | 11.5 | 23.4783 | 16.9043 | 6.09 | 12.4 | 15 | 1.127
17 | 0.63 | 9.5 | 28.4211 | 17.9053 | 6.26 | 13 | 15 | 1.1937
18 | 0.75 | 13.1 | 20.6107 | 15.458 | 6.13 | 13.3 | 15 | 1.0305
19 | 0.78 | 13.4 | 20.1493 | 15.7164 | 6.2 | 13.1 | 15 | 1.0478
20 | 0.76 | 12 | 22.5 | 17.1 | 6.23 | 14 | 15 | 1.14
21 | 0.8 | 13 | 20.7692 | 16.6154 | 6.2 | 13 | 15 | 1.1077
22 | 0.75 | 13 | 20.7692 | 15.5769 | 6.24 | 13 | 15 | 1.0385
23 | 0.81 | 13 | 20.7692 | 16.8231 | 6.31 | 13 | 15 | 1.1215
24 | 0.9 | 10.9 | 24.7706 | 22.2936 | 6.16 | 13.7 | 15 | 1.4862
25 | 0.73 | 10.5 | 25.7143 | 18.7714 | 6.09 | 14.2 | 15 | 1.2514
26 | 0.75 | 11.8 | 22.8814 | 17.161 | 6 | 13.3 | 13 | 1.3201
27 | 0.66 | 10.6 | 25.4717 | 16.8113 | 6.03 | 13.1 | 15 | 1.1208
28 | 0.66 | 11.5 | 23.4783 | 15.4957 | 6.03 | 12.7 | 15 | 1.033
29 | 0.79 | 12.2 | 22.1311 | 17.4836 | 6.21 | 12.4 | 15 | 1.1656
30 | 0.73 | 12.6 | 21.4286 | 15.6429 | 6.11 | 12.5 | 15 | 1.0429
31 | 0.72 | 12.5 | 21.6 | 15.552 | 6.12 | 12.7 | 15 | 1.0368
Disinfectant: |  | Chlorine |  | Level of Inactivation Required: |  |  | Giardia | 0.5
Treatment Segment: |  | 1 |  |  |  |  | Viruses | 2
Prepared by: _________________________________________________ | [5 empty] | Date: | 2019-02-06
(signature) William Lederman Plant Supervisor
Note on B7: PLANT 3 SETT CL2
Note on C7: FILTERED PLANT 3 MAX FLOW
Note on D7: BASED ON PLANT 3 AS PEAK FLOW
Note on F7: PLANT 3 SETT AVG
Note on G7: RAW TEMP

## ct CAL
ONLY FILL GREEN
TEST
Settle temp |  | use temp | Settle PH |  | use ph |  |  | t10# | Flows from Plant Check Sheet
Plt 1 | 11.4 | 10 | Plt 1 PH | 6.08 | 6.5 | plt 1 flow | 5.4 | 47.1111 | Raw PLT 1 | 5.3
Plt 2 | 10.3 | 10 | Plt 2 PH | 6.09 | 6.5 | plt 2 flow | 10.8 | 47.1111 | Raw PLT 2 | 10.3
Plt 3 | 12.3 | 10 | Plt 3 PH | 6.09 | 6.5 | plt 3 flow | 11.8 | 22.8814 | Raw PLT 3 | 11.4
| min CT | TARGET CT |  | temp | ph | min ct table
ct plt 1 | 0.3184 | 0.4184 |  | 10 | 6.5 | 15
ct plt 2 | 0.3184 | 0.4184 |  | 10 | 6.5 | 15
ct plt 3 | 0.65556 | 0.75556 |  | 10 | 6.5 | 15

## Turbidity Analysis
South Carolina Department of Health and Environmental Control
Bureau of Drinking Water Protection
Turbidity Analysis Input Form
System Number .............................................................…………… |  |  | 2620004
Name of Water System ................................................……………. |  |  | GSWSA
Analytical Method ..........................................................…………… |  |  | 001
Contaminant ID ..............................................................…………… |  |  | 0100
Compliance Period Begin (mo/day/yr) ........................………………. |  |  | 2019-01-01
Compliance Period End (mo/day/yr) ..........................……………….. |  |  | 2019-01-31
Number of Samples Required ....................................……………….. |  |  | 186
Number of Samples Taken .........................................………………. |  |  | 558
Highest Turbidity for Compliance Period ..................………………… |  |  | 0.081
Lowest Turbidity for Compliance Period ...................………………… |  |  | 0.019
Average Turbidity for Compliance Period ..................………………… |  |  | 0.037419
Laboratory ID ..................................................................…………… |  |  | 26102
Laboratory Name ...........................................................……………. |  |  | GSWSA /BCSWTP
Comments:
Signature ________________________________ Date |  | 2019-02-06
William Lederman Plant Supervisor
This signature certifies that all samples were collected, analyzed and reported according to the State Primary Drinking
Water Regulations.
DHEC 1975 (Rev. 5/00)

## Distribution
Surface Water System Monthly Operation Report
Distribution System Disinfectant Residual Data
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: |  | 2016-08-01
Lab Cert ID #: 26102 |  |  | Lab # for lab conducting HPC analyses: 26102
Day | No. of Sites Disinfect. Residual was Measured | No. of Sites Disinfect. Residual NOT Measured, but HPC Measured | No. of Sites where Disinfect. Residual NOT Detected & HPC NOT Measured | No. of Sites where Disinfectant Residual was NOT Detected and HPC > 500/ml | No. of Sites Disinfect. Residual NOT Measured and HPC > 500/ml | Average Disinfectant Residual (mg/L)
1 |  | 0 | 0 | 0 | 0
2 |  | 0 | 0 | 0 | 0
3 |  | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 0 | 0
5 |  | 0 | 0 | 0 | 0
6 |  | 0 | 0 | 0 | 0
7 |  | 0 | 0 | 0 | 0
8 |  | 0 | 0 | 0 | 0
9 |  | 0 | 0 | 0 | 0
10 |  | 0 | 0 | 0 | 0
11 |  | 0 | 0 | 0 | 0
12 |  | 0 | 0 | 0 | 0
13 |  | 0 | 0 | 0 | 0
14 |  | 0 | 0 | 0 | 0
15 |  | 0 | 0 | 0 | 0
16 |  | 0 | 0 | 0 | 0
17 |  | 0 | 0 | 0 | 0
18 |  | 0 | 0 | 0 | 0
19 |  | 0 | 0 | 0 | 0
20 |  | 0 | 0 | 0 | 0
21 |  | 0 | 0 | 0 | 0
22 |  | 0 | 0 | 0 | 0
23 |  | 0 | 0 | 0 | 0
24 |  | 0 | 0 | 0 | 0
25 |  | 0 | 0 | 0 | 0
26 |  | 0 | 0 | 0 | 0
27 |  | 0 | 0 | 0 | 0
28 |  | 0 | 0 | 0 | 0
29 |  | 0 | 0 | 0 | 0
30 |  | 0 | 0 | 0 | 0
31 |  | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | Avg. Resid.
| a | b | c | d | e | #DIV/0!
Compliance with Distribution System Disinfectant Residual Criteria |  |  |  |  | #DIV/0!
V = ( c + d + e ) / ( a + b ) x 100 = ( + + ) / ( + ) x 100 =
For Previous Month: V =
Prepared by: __________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## Chloramine
Surface Water System Monthly Operation Report
For Systems Using Chlorine and/or Chloramines
To Maintain A Residual In The Distribution System
Bureau of Water
System Name: Grand Strand Regional |  |  | System Number: 2620004
Lab Cert ID #: 26102 |  |  | For (Month/yr): | 2016-08-01
Month/Year | *Average Residual |  | Quarterly Average (mg/L)
| Chlorine (mg/L) | Chloramines (mg/L)
2016-01-02 |  | 3.42 | 3.17
2016-02-03 |  | 2.79 |  | *Average residual values may be obtained from page 10 of 15 of this form
2016-03-03 |  | 3.3
2016-04-02 |  | 3.42 | 3.14
2016-05-03 |  | 3.46
2016-06-02 |  | 2.75
2016-07-02 |  | 3.42
2016-08-02 |  | 2.86
2016-09-02
2015-10-02 |  | 3.11 | 2.99
2015-11-02 |  | 2.78
2015-12-02 |  | 3.08
RAA at the end of the most recent quarter: |  |  | 3.1
Prepared by: _________________________________________________ |  |  |  | Date:
(signature) Clint Elliott Lab Supervisor

## TOC
Surface Water System Monthly Operation Report
Compliance With DBP Precursor Removal Requirements
Bureau of Water
System Name: Grand Strand Regional |  | System Number: 2620004 |  |  | For (Month/yr): |  | 2016-08-01
Lab Cert ID #: 26102
Month | Source Water |  | Treated Water TOC (mg/L) | (A) Actual % TOC Removal | (B) Required % TOC Removal | Basis for Required % Removal | Removal Ratio (A) / (B) | Quarterly Average Ratio | RAA1 Ratio (Last 4 Quarters)
| Alkalinity (mg/L) | TOC (mg/L)
2016-01-01 | 14 | 21.88 | 4.05 | 81.4899 | 50 | Step 1 | 1.6298 | 1.51
2016-02-01 | 20 | 9.738 | 2.72 | 72.0682 | 50 | Step 1 | 1.4414
2016-03-01 | 14 | 10.23 | 2.81 | 72.5318 | 50 | Step 1 | 1.4506
2016-04-01 | 21 | 9.776 | 2.82 | 71.1538 | 50 | Step 1 | 1.4231 | 1.3387 | 1.37
2016-05-01 | 23 | 10.09 | 2.97 | 70.5649 | 50 | Step 1 | 1.4113
2016-06-01 | 23 | 8.579 | 3.51 | 59.0861 | 50 | Step 1 | 1.1817
2016-07-01 | 24 | 8.27 | 3.538 | 57.2189 | 50 | Step 1 | 1.1444
2016-08-01 | 22 | 11.4 | 3.69 | 67.6316 | 50 | Step 1 | 1.3526
2016-09-01
2015-10-01 | 21 | 12.04 | 3.49 | 71.0133 | 50 | Step 1 | 1.4203 | 1.5
2015-11-01 | 28 | 17.264 | 4.18 | 75.7878 | 50 | Step 1 | 1.5158
2015-12-01 | 18 | 18.612 | 4.11 | 77.9175 | 50 | Step 1 | 1.5583
1 RAA = Running Annual Average, Computed Quarterly
Alternate Criteria
**Should only be filled out if Alternate Criteria 3 or 4 are being used
Month | Source water |  |  |  | Finished water
| DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m) |  | DOC (mg/L) | UV254 (m-1) | SUVA (L/mg-m)
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
Alternate Criteria
Alt. 1 | Source Water TOC < 2.0 mg/L
Alt. 2 | Treated Water TOC < 2.0 mg/L
Alt. 3 | Source Water SUVA < 2.0 L/mg-m
Alt. 4 | Treated Water SUVA < 2.0 L/mg-m
Prepared by: ____________________________________________ | [5 empty] | Date:
(signature) Clint Elliott Lab Supervisor

## Bacteria(new)
Bacteriological Analysis Sample Summary
1. Please fill out page 2 of this form if you have a total coliform posative sample and repeat samples.
2. Submit this form to SCDHEC along with a copy of your labrotories chain of custody no later than ten (10) days after the end of the compliance period.
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
COMPLIANCE PERIOD |  |  | 2016-09-01
CYCLE |  |  | M
(Q)-QUARTERLY (M)-MONTHLY
CHLORINE RESIDUAL |  |  | #DIV/0!
Lab ID measuring chlorine residual |  |  | 26102
# OF INITIAL SAMPLES |  |  | 0
# OF INITIAL TC POSITIVE SAMPLES |  |  | 0
# OF E. COLI POSITIVE SAMPLES |  |  | 0
TOTAL COLIFORM ANALYSIS METHOD CODE |  |  | SM9223B-2004
E. COLI ANALYSIS METHOD |  |  | SM9223B-2004
Lab ID |  |  | 26102
SIGNATURE
Date
Bacteriological Analysis Individual Samples (Part 2)
PART 2 CAN BE USED FOR ALL TOTAL COLIFORM SAMPLES AND ASSOCIATED
REPEATS AND SOURCE WATER SAMPLES
PWS ID |  |  | S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4
PWS NAME |  |  | GSWSA BC SWTP
LAB ID |  |  | #VALUE!
TYPE | REPEAT | LAB SAMPLE NUMBER | COLLECTION DATE (MM/DD/YYYY) | [7 empty] | SAMPLING LOCATION |  | SOURCE ID | TOTAL A/P | E.COLI A/P | TOTAL/FREE CHLORINE RESIDUAL
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
Explanation: | [11 empty] | Comments
Type (RT, RP or GW ) |  |  |  | RT = Routine; RP=Repeat; GW=Groundwater
Repeat (only if sample type =RP) |  |  |  | DN = Downstream; UP=Upstream;
Lab Sample # |  |  |  | # assigned by lab for that particular sample
Collection Date (mmddyyyy) |  |  |  | Date sample was collected
Sampling Location |  |  |  | Physical address where sample was collected
Source ID(only used for source samples) |  |  |  | 5 digit DHEC Source ID (ie. G_ _ _ _ _)
Total Coliform (A or P) |  |  |  | Indicate with an "A" if absent or a "P" if present
E. Coli = (A or P) |  |  |  | E = Ecoli Positive
Total/Free Chlorine Residual |  |  |  | Chlorine Residual Reading
Within 24 hours of learning of a total coliform-positive (TC+) sample result, REPEAT samples must be collected and analyzed for total coliforms:
One REPEAT sample must be collected from the same tap as the TC+ sample.
One REPEAT sample must be collected within five service connections upstream of the TC+ sample.
One REPEAT sample must be collected within five service connections downstream of the TC+ sample.
If the system is served by Ground water then a Triggered Source sample must be collected prior to treatment from each source in use at the time the total coliform-positive sample was collected. The number of samples taken PER WELL must equal the number of positive TCR samples. If you collected three TC+ samples, then three well samples must be taken at EACH WELL that was in service at the time.
The triggered source water sample must be analyzed for the presence of E.coli.
If any triggered source water sample is E.coli-positive, the Ground Water system (GWS) must either take corrective action, as directed by the state, or the GWS must take 5 additional source water sampleswithin 24 hours.
If the GW system Purchases some or all af there water they must notify the wholesale system (s) within 24 hours.
If any REPEAT sample is TC+:
The system must analyze that total coliform-positive culture for E.coli.
The system must collect another set of REPEAT samples, as before, unless the E.coli MCL has been violated or an assessment has been triggered.
For a system on quarterly monitoring, a TC+ result requires a minimum of three ROUTINE samples be collected the following month.
CALL SCDHEC on the same day you learned of the E. coli-positive (EC+) result, or by the end of the next business day if the result came in after business hours
Please submit a copy of your labrotories chain of custody along with this form.

## Bacteria
Bacteriological Analysis Sample Summary (Part 1)
PART 1 CAN BE USED IN ONE (1) OF TWO (2) WAYS
1. If the system has had no Total Coliform (TC) Positives samples for a compliance cycle or,
2. If the system wants to report those samples that were initial TC Absent and use Part 2 for
the TC Present and all repeats.
DESCRIPTION
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
0 | 4 | 0 | 1 | 2 | 0 | 1 | 6 | 2 |  |  |  |  | First day of month / quarter
1 | 2 | 0 | [10 empty] | # of Initial Total Coliform Negative
0 | 4 | 0 | 2 | 2 | 0 | 1 | 6 | [5 empty] | M=Month; Q=Quarter; Y=Year
| 2 | 6 | 1 | 0 | 2 |  |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
Note: This can be used for any system that does
not have a total coliform positive
DOES SYSTEM ADD DISINFECTION | [8 empty] | YES
AVERAGE DISINFECTION RESIDUAL | [8 empty] | 3 | . | 4 | 2
AND/OR
Bacteriological Analysis Individual Samples (Part 2)
NOTE: This form would only be used for the initial routine (RT) TC or TC/FC Positive and
and the Repeats that are required by regulation.
PART 2 CAN MUST BE USED FOR ALL TOTAL COLIFORM POSITIVES AND ALL ASSOCIATED
REPEATS
S | C | 2 | 6 | 2 | 0 | 0 | 0 | 4 | System Number |  |  |  | SC followed by 7 digit system number
|  | 2 | 6 | 1 | 0 | 2 |  |  | Lab State ID # |  |  |  | Number assigned by Lab Certification
[15 empty] | Total | Fecal (F) or | Free/Total
[13 empty] | TYPE | Lab Sample ID | Coliform | E Coli (E) + | Chlorine
SAMPLE ID # AND LOCATION | [8 empty] | COLLECTION DATE (MMDDYYYY) |  |  |  | (RT or RP) | Number | A/P | If Present | Residual*
.
.
.
.
.
.
Explanation:
Collection Date (mmddyyyy)………………..Date sample was collected
Lab Sample #…………………………………# assigned by lab for that particular sample
Type (RT or RP)………………………………RT = Routine; RP=Repeat
Sampling Point ID……………………………..If lab has something that identifies site other than physical location
Sampling Location……………………………Physical address where sample was collected from
Total Coliform (A or P)…………………….Indicate with an "A" if absent or a "P" if present
FC (F = FC+ or E = Ecoli+)…………………..F= Fecal Coliform Positive; E = Ecoli Positive
Total/Free Chlorine Residual…………………………Chlorine Residiual Reading

## TOC Sample ID
TOC SAMPLE ID LOG
System Name: Grand Strand Regional |  |  | System Number: 2620004 |  | 2019-01-01
Lab Cert ID #: 26102
Treated | TOC | Raw | TOC | Alkalinity
D-02011608 |  | D-02011611 |  | 20
D-02011609
D-02011610

## Calculation for TOC
| TOC | [6 empty] | Sample Number | [5 empty] | Raw
| Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled |  | Finished | Finished2 | Raw | 1 Settled | 2 Settled | 3 Settled | Alkalinity
Week 1
| 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 |  | D-07061506 | D-07061507 | D-07061511 | D-07061508 | D-07061509 | D-07061510 | 36
2.47
5.88
Week 2
#DIV/0!
#DIV/0!
Week 3
#DIV/0!
#DIV/0!
Week 4 | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786
2.931
7.579
Average | 2.7005 | 2.555 | 6.7295 | 4.2765 | 2.8045 | 2.619 | [5 empty] | Average Alkalinity Raw |  | 36
Max | 2.931 | 2.734 | 7.579 | 5.226 | 3.166 | 2.786 | 3.726
Min | 2.47 | 2.376 | 5.88 | 3.327 | 2.443 | 2.452 | 2.7407
Average Treated TOC |  |  | 3.2333
Average % TOC Removal |  |  | 51.9528
Max % TOC Removal |  |  | 59.2738
Min % TOC Removal |  |  | 44.6318
TOC Sample ID Number Submittal
Treated | TOC |  |  | Raw | TOC | Alkalinity

## Chem Cost
2019-01-01
Chemical Usage / Dosage / Cost
Chemical | Usage |  | Dosage (mg/l) |  |  | Cost ($) |  |  | Alternate Units |  |  | density as is |  | Purity
| Unit | Total | Average | Maximum | Minimum | $/Unit | Total $ | $/1000 gal water | Unit | Total | $/unit | g/ml | lb/gal | wt. % | lb/gal
Pre Chlorine | gals | 9595.9355 | 1.5045 | 1.7734 | 1.2853 | 0.81 | 7772.7077 | 0.010822 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Aluminum Sulfate | gals | 109245.7509 | 83.6577 | 90.9239 | 62.8951 | 1.69 | 184625.319 | 0.25704 | lbs | 1209787.4452 | 0.15225 | 1.325 | 11.05 | 48.5 | 5.36
Pre Caustic | gals | 0 | 0 | 0 | 0 | 1.86 | 0 | 0 | lbs | 0 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Post Chlorine | gals | 18402.8551 | 3.7482 | 3.8591 | 3.5304 | 0.81 | 14906.3126 | 0.020753 |  |  |  | 1.204 | 10.04 | 14 | 1.41
Ammonia | gals | 2612.6142 | 0.65888 | 0.73203 | 0.53088 | 0.68 | 1776.5777 | 0.0024734 |  |  |  | 0.928 | 7.74 | 19.5 | 1.51
Post Caustic | gals | 4587.9558 | 4.7854 | 5.797 | 3.9258 | 1.86 | 8533.5978 | 0.011881 | lbs | 58542.3163 | 0.1585 | 1.53 | 12.76 | 50 | 6.38
Lime | gals | 91318.1464 | 32.6366 | 39.0512 | 20.0684 | 0.055 | 5022.4981 | 0.0069926
Fluoride | gals | 2079.5137 | 0.54776 | 0.56734 | 0.47342 | 3.2 | 6654.4439 | 0.0092646 | lbs | 21003.0884
Activated Carbon | lbs | 20618.8546 | 2.9418 | 3.2038 | 2.6669 | 0.89 | 18350.7806 | 0.025549
Polymer | gals | 177.2779 | 0.25195 | 0.33183 | 0.20734 | 11.95 | 2118.471 | 0.0029494 | lbs | 1524.59 | 1.39
Filter Aid | gals | 0 | 0 | 0 | 0 | 5.59 | 0 | 0 | lbs | 0 | 0.65
Zinc Chloride Dosed as Zinc | gals | 153.891 | 0.10028 | 0.104 | 0.094528 | 6.89 | 1060.3089 | 0.0014762 | lbs | 2015.9718 | 0.526
Corrosion Inhibitor Dosed as Phosphorus | gals | 1346.7782 | 1.0974 | 1.125 | 1.0669 | 11.72 | 15784.2408 | 0.021976 | lbs | 19528.2842 | 0.808
|  |  | Total Chemical Cost |  |  |  | 266605.2579
|  |  | Cost per 1000 gallons |  |  |  | 0.37118

## Extras
| TOC | [25 empty] | pH |  |  |  | Alkalinity |  |  |  | Hardness |  |  |  | Turbidity |  |  |  | Color |  |  |  | Temp |  |  |  | TRC |  |  | Fluoride |  |  | Flow (MG) |  |  |  | COLIFORM
| Finish1 | Finish2 | Raw |  | Conductivity |  |  | TDS |  |  | Chloride |  |  |  | Sodium |  |  | Sulfate |  |  | Iron |  |  | Manganese |  |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 |  | Finish1 | Finish2 |  | Raw | Finish1 | Finish2 |  | Raw | Finish1 | Finish2
Week 1 |  |  |  |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw |  | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | Finish1 | Finish2 | Raw | 7.29 | 7.285 | 6.2933 |  | 21 | 21 | 14.5 |  | 50.5 | 47 | 15.3333 |  | 0.084 | 0.066 | 9 |  | 1 | 1 | 115 |  | 13.2667 | 15.4667 | 15.7167 |  | 3.8 | 3.7 |  | 0.5124 | 0.5103 |  | 26.6 | 12.487 | 11.194 |  | 52 | A | A
|  |  |  | Week 1 | [6 empty] | 11.1 | 11.3 | 7.27 |  |  |  |  | 21.8 | 21.9 | 7.46 | [6 empty] | 7.2917 | 7.34 | 6.2883 |  | 20 | 20 | 11.8333 |  | 51 | 49 | 13.6667 |  | 0.067 | 0.065 | 9.52 |  | 1 | 1 | 117 |  | 13.6667 | 15.3333 | 16.0667 |  | 3.9 | 4 |  | 0.5696 | 0.5166 |  | 11.864 | 11.864 | 10.654 |  | 85 | A | A
|  |  |  | Week 2 | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  |  |  |  | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.4333 | 7.3617 | 6.2917 |  | 20 | 20 | 11.8333 |  | 50.5 | 51 | 12.5 |  | 0.065 | 0.068 | 8.96 |  | 1 | 1 | 115 |  | 13.95 | 15.4 | 16.2167 |  | 3.9 | 3.9 |  | 0.5103 | 0.5082 |  | 10.666 | 10.666 | 11.353 |  | 62 | A | A
|  |  |  | Week 3 | [22 empty] | 7.3733 | 7.3317 | 6.265 |  | 20 | 20.5 | 12.5 |  | 48 | 50.5 | 13 |  | 0.065 | 0.07 | 9.71 |  | 1 | 1 | 118.6667 |  | 14.2333 | 15.4333 | 16.3667 |  | 4 | 3.9 |  | 0.498 | 0.4884 |  | 11.175 | 11.175 | 12.091 |  | 122 | A | A
|  |  |  | Week 4 | [10 empty] | 13.3 | 13.5 | 9.1 | [9 empty] | 7.615 | 7.6367 | 6.2967 |  | 20.5 | 20.5 | 12.6667 |  | 52.5 | 52 | 12.8333 |  | 0.069 | 0.072 | 10.7 |  | 1.5 | 1 | 121.1667 |  | 14.45 | 15.5333 | 16.6333 |  | 3.9 | 3.8 |  | 0.6372 | 0.6732 |  | 11.059 | 11.059 | 11.159 |  | 20 | A | A
[27 empty] | 7.2883 | 7.2633 | 6.3267 |  | 20.5 | 20.5 | 13.6667 |  | 51.5 | 53.5 | 13.1667 |  | 0.069 | 0.071 | 10.4 |  | 1 | 1 | 123 |  | 14.2167 | 15.3833 | 16.15 |  | 4 | 4.1 |  | 0.4479 | 0.4318 |  | 12.146 | 12.146 | 11.353 |  | 75 | A | A
#DIV/0! | [26 empty] | 7.3433 | 7.2983 | 6.365 |  | 21 | 20.5 | 12.3333 |  | 53 | 56.5 | 12.8333 |  | 0.07 | 0.06 | 11.7 |  | 1 | 1 | 122.5 |  | 14.0833 | 15.2167 | 16.1833 |  | 4.1 | 3.7 |  | 0.579 | 0.5559 |  | 10.396 | 10.396 | 11.462 |  | 31 | A | A
#DIV/0! |  |  |  | Average | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.8 | 11.95 | 8.535 |  | 13.3 | 13.5 | 9.1 | 23.65 | 23.8 | 8.705 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.4667 | 7.4317 | 6.3667 |  | 19.5 | 19.5 | 13 |  | 52 | 51.5 | 13.5 |  | 0.069 | 0.062 | 11.4 |  | 1 | 1 | 121.8333 |  | 14.3333 | 15.4333 | 16.05 |  | 4 | 4 |  | 0.5691 | 0.5532 |  | 9.413 | 9.413 | 11.817 |  | 31 | A | A
Week 2 | 2.74 | 2.51 | 7.02 | Max | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 12.5 | 12.6 | 9.8 |  | 13.3 | 13.5 | 9.1 | 25.5 | 25.7 | 9.95 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.5033 | 7.4467 | 6.3883 |  | 23.5 | 23 | 14.5 |  | 47.5 | 50 | 14 |  | 0.069 | 0.064 | 12.8 |  | 1 | 1.1667 | 125.1667 |  | 14.4167 | 15.55 | 41.15 |  | 3.8 | 3.8 |  | 0.5372 | 0.5243 |  | 13.904 | 13.904 | 13.861 |  | 31 | A | A
|  |  |  | Min | 188 | 182 | 297 | 122.2 | 118.3 | 193.05 | 11.1 | 11.3 | 7.27 |  | 13.3 | 13.5 | 9.1 | 21.8 | 21.9 | 7.46 | 0.003 | 0.006 | 0.133 | 0.029 | 0.033 | 0.052 | 7.5633 | 7.565 | 6.41 |  | 20.5 | 20 | 15 |  | 49.5 | 47 | 13.8333 |  | 0.064 | 0.073 | 11.1 |  | 1 | 1 | 124 |  | 13.75 | 15.4667 | 15.55 |  | 3.7 | 3.8 |  | 0.597 | 0.5494 |  | 11.073 | 11.073 | 10.9 |  | 63 | A | A
[27 empty] | 7.3183 | 7.27 | 6.4233 |  | 22.5 | 23.5 | 15.3333 |  | 50.5 | 50 | 15 |  | 0.059 | 0.063 | 10.3 |  | 1 | 1 | 125.8333 |  | 12.7 | 14.5333 | 14.6667 |  | 4.2 | 3.6 |  | 0.5974 | 0.5621 |  | 10.614 | 10.614 | 11.591 |  | 63 | A | A
[15 empty] | Flow (MG) | [11 empty] | 7.29 | 7.2017 | 6.4383 |  | 21.5 | 22 | 15.3333 |  | 46.5 | 50.5 | 16 |  | 0.056 | 0.058 | 11.8 |  | 1 | 1 | 128.6667 |  | 12.1 | 13.5833 | 13.8167 |  | 3.9 | 3.7 |  | 0.5541 | 0.4494 |  | 11.083 | 11.083 | 11.115 |  | 109 | A | A
[15 empty] | Raw | Comb Fin |  |  | Aluminum |  |  | Phosph Fin1 |  | Phosph Fin2 |  |  | 7.26 | 7.17 | 6.505 |  | 21.5 | 22 | 16.8333 |  | 54.5 | 51 | 17 |  | 0.055 | 0.054 | 12.2 |  | 1 | 1 | 125.6667 |  | 11.6 | 13.4667 | 13.2667 |  | 4.2 | 3.4 |  | 0.6533 | 0.4624 |  | 10.821 | 10.821 | 12.1 |  | 85 | A | A
[14 empty] | 1 | 26.6 | 23.681 |  |  | 1 Filter | 2 Filter | 3 Filter | Total | Ortho | Total | Ortho |  | 7.525 | 7.3 | 6.48 |  | 23.5 | 25.5 | 16 |  | 53 | 52 | 15.5 |  | 0.056 | 0.061 | 12.2 |  | 1 | 1 | 127.3333 |  | 11.0167 | 12.8333 | 12.75 |  | 4.2 | 3.6 |  | 0.6022 | 0.9081 |  | 11.155 | 11.155 | 11.758 |  | 95 | A | A
2.74 | [13 empty] | 2 | 25.555 | 22.518 |  | Week 1 |  |  |  | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.4617 | 7.4283 | 6.495 |  | 21.5 | 20.5 | 16.8333 |  | 50.5 | 52.5 | 15.8333 |  | 0.053 | 0.055 | 12.2 |  | 1 | 1 | 127 |  | 10.65 | 12.6167 | 12.35 |  | 4.2 | 4.1 |  | 0.7202 | 0.5507 |  | 10.652 | 10.652 | 11.421 |  | 85 | A | A
7.02 | [13 empty] | 3 | 25.359 | 22.019 |  | Week 2 | 0.036 | 0.036 | 0.029 | [5 empty] | 7.4717 | 7.2733 | 6.5167 |  | 22 | 24 | 16.1667 |  | 53.5 | 54 | 16.6667 |  | 0.063 | 0.059 | 12.3 |  | 1 | 1 | 129.5 |  | 10.4833 | 12.25 | 12.1 |  | 4.4 | 4 |  | 0.6116 | 0.4568 |  | 11.009 | 11.009 | 11.89 |  | 187 | A | A
Week 3 | [13 empty] | 4 | 27.356 | 23.266 |  | Week 3 |  |  |  | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.4667 | 7.415 | 6.5183 |  | 21.5 | 22 | 15 |  | 58.5 | 60.5 | 15.1667 |  | 0.068 | 0.071 | 13.1 |  | 1 | 1 | 125.8333 |  | 10.2833 | 11.8 | 11.9167 |  | 4.1 | 3.9 |  | 0.5976 | 0.4611 |  | 9.813 | 9.813 | 11.417 |  | 148 | A | A
[14 empty] | 5 | 25.813 | 22.218 |  | Week 4 | [8 empty] | 7.2833 | 7.2467 | 6.475 |  | 20.5 | 21.5 | 15.8333 |  | 57 | 59 | 15.8333 |  | 0.06 | 0.059 | 15.5 |  | 1 | 1 | 123.8333 |  | 10.3333 | 11.95 | 11.8167 |  | 4 | 3.8 |  | 0.5885 | 0.3821 |  | 10.084 | 10.084 | 12.273 |  | 345 | A | A
[14 empty] | 6 | 26.647 | 23.499 | [10 empty] | 7.4833 | 7.2633 | 6.6067 |  | 20.5 | 21 | 16.5 |  | 56 | 57.5 | 16.5 |  | 0.065 | 0.066 | 16.1 |  | 1 | 1 | 118.1667 |  | 10.7167 | 12.2833 | 12.2667 |  | 4.2 | 3.6 |  | 0.6057 | 0.4854 |  | 11.115 | 11.115 | 13.438 |  | 697 | A | A
[14 empty] | 7 | 25.963 | 21.858 | [10 empty] | 7.4433 | 7.4583 | 6.5783 |  | 20.5 | 21.5 | 17.5 |  | 55 | 56.5 | 17 |  | 0.067 | 0.063 | 15.9 |  | 1 | 1 | 114.3333 |  | 11.2333 | 12.75 | 12.7167 |  | 3.8 | 3.5 |  | 0.5461 | 0.4522 |  | 10.628 | 10.628 | 12.282 |  | 602 | A | A
[14 empty] | 8 | 26.242 | 21.23 |  | Average | 0.036 | 0.036 | 0.029 | 0.681 | 0.048 | 0.6905 | 0.0445 |  | 7.385 | 7.3483 | 6.55 |  | 22 | 21 | 16.3333 |  | 63 | 62 | 17 |  | 0.062 | 0.066 | 15.2 |  | 1 | 1 | 114.3333 |  | 10.9667 | 11.8667 | 12 |  | 4 | 3 |  | 0.5439 | 0.3244 |  | 11.194 | 11.194 | 12.897 |  | 359 | A | A
[14 empty] | 9 | 29.769 | 27.765 |  | Max | 0.036 | 0.036 | 0.029 | 0.696 | 0.051 | 0.711 | 0.052 |  | 7.455 | 7.3683 | 6.5333 |  | 22 | 23.5 | 16.3333 |  | 63.5 | 60 | 16.8333 |  | 0.063 | 0.065 | 15 |  | 1 | 1 | 105.6667 |  | 10.1833 | 10.95 | 11.0333 |  | 4.1 | 3.8 |  | 0.6549 | 0.4096 |  | 11.396 | 11.396 | 13.366 |  | 480 | A | A
#DIV/0! | [13 empty] | 10 | 25.72 | 21.973 |  | Min | 0.036 | 0.036 | 0.029 | 0.666 | 0.045 | 0.67 | 0.037 |  | 7.4033 | 7.3683 | 6.52 |  | 23.5 | 22.5 | 17.5 |  | 52.5 | 53 | 16.8333 |  | 0.064 | 0.065 | 15 |  | 1 | 1 | 94.3333 |  | 9.7 | 11.9167 | 11.55 |  | 4.2 | 3.8 |  | 0.7141 | 0.5103 |  | 11.126 | 11.126 | 12.716 |  | 384 | A | A
#DIV/0! | [13 empty] | 11 | 25.395 | 22.205 | [10 empty] | 7.2967 | 7.25 | 6.56 |  | 22 | 20.5 | 16.6667 |  | 45 | 45.5 | 17.6667 |  | 0.059 | 0.057 | 14.8 |  | 1 | 1 | 95.8333 |  | 10.3833 | 12.8333 | 12.85 |  | 3.6 | 3.7 |  | 0.5561 | 0.5145 |  | 10.786 | 10.786 | 13.749 |  | 573 | A | A
Week 4 | [13 empty] | 12 | 25.569 | 22.198 |  | Average 1,2,3 |  | 0.033667 | [6 empty] | 7.2983 | 7.3283 | 6.4867 |  | 23 | 22.5 | 18.6667 |  | 39 | 38.5 | 16.5 |  | 0.064 | 0.059 | 14.9 |  | 1 | 1 | 93.8333 |  | 10.7 | 12.5833 | 12.7667 |  | 3.7 | 3.8 |  | 0.4899 | 0.5187 |  | 10.062 | 10.062 | 12.989 |  | 480 | A | A
[14 empty] | 13 | 27.833 | 22.921 | [10 empty] | 7.2167 | 7.1467 | 6.5233 |  | 21.5 | 22.5 | 15.6667 |  | 31.5 | 32.5 | 16.1667 |  | 0.056 | 0.057 | 14.9 |  | 1 | 1 | 91.5 |  | 10.5333 | 12.45 | 12.4667 |  | 3.6 | 3.3 |  | 0.5448 | 0.5103 |  | 10.481 | 10.481 | 12.448 |  | 548 | A | A
[14 empty] | 14 | 26.612 | 22.913 | [8 empty] | Day |  | 7.4017 | 7.2633 | 6.545 |  | 21.5 | 22 | 18.1667 |  | 35.5 | 37.5 | 17.1667 |  | 0.067 | 0.056 | 14.8 |  | 1 | 1 | 89 |  | 10.2 | 11.85 | 12.1167 |  | 3.7 | 3.6 |  | 0.7682 | 0.4741 |  | 10.995 | 10.995 | 12.85 |  | 488 | A | A
[14 empty] | 15 | 26.769 | 22.073 | [8 empty] | 28 |  | 7.4083 | 7.185 | 6.5683 |  | 22.5 | 22 | 17.6667 |  | 44 | 42.5 | 17.3333 |  | 0.052 | 0.062 | 14.9 |  | 1 | 1.3333 | 88.6667 |  | 10.15 | 12.1 | 12 |  | 4.2 | 3.6 |  | 0.551 | 0.4626 |  | 11.145 | 11.145 | 12.948 |  | 341 | A | A
[14 empty] | 16 | 27.294 | 22.899 | [8 empty] | 29 |  | 7.2867 | 7.195 | 6.6267 |  | 24.5 | 23 | 18.5 |  | 49 | 45.5 | 17.8333 |  | 0.052 | 0.051 | 15.7 |  | 1.1667 | 1.1667 | 86.3333 |  | 10.1667 | 11.8 | 12.0667 |  | 4.2 | 3.9 |  | 0.6611 | 0.5185 |  | 10.4 | 10.4 | 12.267 |  | 364 | A | A
#DIV/0! | [13 empty] | 17 | 25.273 | 21.23 | [8 empty] | 30 |  | 7.2783 | 7.2617 | 6.6483 |  | 20 | 20.5 | 17 |  | 42 | 42.5 | 18 |  | 0.065 | 0.067 | 16.4 |  | 1 | 1 | 91.6667 |  | 10.0167 | 11.1333 | 11.5333 |  | 4 | 3.9 |  | 0.6564 | 0.502 |  | 7.668 | 7.668 | 13.812 |  | 292 | A | A
#DIV/0! | [13 empty] | 18 | 27.372 | 22.357 | [8 empty] | 31 |  | 7.465 | 7.3833 | 6.65 |  | 20.5 | 20 | 16.8333 |  | 40.5 | 41.5 | 17 |  | 0.064 | 0.067 | 16.4 |  | 1 | 1 | 93.6667 |  | 9.9333 | 10.9667 | 11.4 |  | 4.1 | 3.7 |  | 0.7066 | 0.5229 |  | 13.382 | 13.382 | 13.299 |  | 323 | A | A
Average | 2.74 | 2.51 | 7.02 | [10 empty] | 19 | 29.545 | 24.553 | [8 empty] | Avg 1 |  | 7.3877 | 7.3685 | 6.3117 | Avg 1 | 20.3125 | 20.3125 | 12.7917 | Avg 1 | 51.125 | 51.375 | 13.3542 | Avg 1 | 0.06975 | 0.06675 | 10.1738 | Avg 1 | 1.0625 | 1 | 119.2708 | Avg 1 | 14.025 | 15.4 | 16.1729 | Avg 1 | 3.95 | 3.8875 | Avg 1 | 0.54044 | 0.5297 | Avg 1 | 12.9149 | 11.1507 | 11.3854 | Avg 1 | 59.75
Max | 2.74 | 2.51 | 7.02 | [10 empty] | 20 | 27.113 | 22.91 | [8 empty] | Avg 2 |  | 7.4174 | 7.3402 | 6.4486 | Avg 2 | 22.0714 | 22.3571 | 15.6905 | Avg 2 | 50.2857 | 50.4286 | 15.3095 | Avg 2 | 0.058857 | 0.061143 | 11.8 | Avg 2 | 1 | 1.0238 | 126.2381 | Avg 2 | 12.319 | 14.0071 | 17.65 | Avg 2 | 4.0286 | 3.7143 | Avg 2 | 0.60877 | 0.57234 | Avg 2 | 11.3289 | 11.3289 | 11.8209 | Avg 2 | 75.8571
Min | 2.74 | 2.51 | 7.02 | [10 empty] | 21 | 28.606 | 24.091 | [8 empty] | Avg 3 |  | 7.424 | 7.3427 | 6.5373 | Avg 3 | 21.5625 | 22.125 | 16.3958 | Avg 3 | 57.375 | 57.8125 | 16.4792 | Avg 3 | 0.064 | 0.06425 | 14.7625 | Avg 3 | 1 | 1 | 115.75 | Avg 3 | 10.4875 | 11.9708 | 11.925 | Avg 3 | 4.1 | 3.675 | Avg 3 | 0.6078 | 0.43524 | Avg 3 | 10.7956 | 10.7956 | 12.5349 | Avg 3 | 400.25
[14 empty] | 22 | 30.02 | 24.762 | [8 empty] | Avg 4 |  | 7.3315 | 7.2517 | 6.576 | Avg 4 | 21.9375 | 21.625 | 17.3958 | Avg 4 | 40.8125 | 40.75 | 17.2083 | Avg 4 | 0.059875 | 0.0595 | 15.35 | Avg 4 | 1.0208 | 1.0625 | 91.3125 | Avg 4 | 10.2604 | 11.9646 | 12.15 | Avg 4 | 3.8875 | 3.6875 | Avg 4 | 0.61676 | 0.50295 | Avg 4 | 10.6149 | 10.6149 | 13.0452 | Avg 4 | 426.125
Fin1 | [13 empty] | 23 | 28.489 | 23.842 | [12 empty] | pH | Alk | Hard |  | Turb | Color | Temp |  | Coliform | TRC | Fluoride
CCR Data | High |  | Low | Avg | [9 empty] | 24 | 27.727 | 24.535 | [8 empty] | Avg 1 |  | Raw |  | 6.3117 | 12.7917 | 13.3542 |  | 10.1738 | 119.2708 | 16.1729 |  | 59.75
Turbidity | 0.081 |  | 0.019 | 0.037419 | [9 empty] | 25 | 26.321 | 23.051 | [8 empty] | Avg 2 |  |  |  | 6.4486 | 15.6905 | 15.3095 |  | 11.8 | 126.2381 | 17.65 |  | 75.8571
Fluoride | 0.7682 |  | 0.4479 | 0.58916 | [9 empty] | 26 | 26.537 | 22.929 | [8 empty] | Avg 3 |  |  |  | 6.5373 | 16.3958 | 16.4792 |  | 14.7625 | 115.75 | 11.925 |  | 400.25
Sulfate | 25.5 |  | 21.8 | 23.65 | [9 empty] | 27 | 27.214 | 23.845 | [8 empty] | Avg 4 |  |  |  | 6.576 | 17.3958 | 17.2083 |  | 15.35 | 91.3125 | 12.15 |  | 426.125
Iron | 0.003 |  | 0.003 | 0.003 | [9 empty] | 28 | 27.708 | 24.093 | [8 empty] | Avg 1 |  | Finished |  | 7.3877 | 20.3125 | 51.125 |  | 0.06975 | 1.0625 | 14.025 |  |  | 3.95 | 0.54044
Manganes | 0.029 |  | 0.029 | 0.029 | [9 empty] | 29 | 26.75 | 22.667 | [8 empty] | Avg 2 |  |  |  | 7.4174 | 22.0714 | 50.2857 |  | 0.058857 | 1 | 12.319 |  |  | 4.0286 | 0.60877
pH | 7.615 |  | 7.2167 | 7.3867 | [9 empty] | 30 | 29.625 | 21.48 | [8 empty] | Avg 3 |  |  |  | 7.424 | 21.5625 | 57.375 |  | 0.064 | 1 | 10.4875 |  |  | 4.1 | 0.6078
Color | 1.5 |  | 1 | 1.0222 | [9 empty] | 31 | [10 empty] | Avg 4 |  |  |  | 7.3315 | 21.9375 | 40.8125 |  | 0.059875 | 1.0208 | 10.2604 |  |  | 3.8875 | 0.61676
Chloride | 12.5 |  | 11.1 | 11.8
TOC | 2.74 |  | 2.74 | 2.74
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.681
o-phosph |  |  |  | 0.048
Aluminum |  |  |  | 0.033667
Fin2
CCR Data | High |  | Low | Avg
Turbidity | 0.081 |  | 0.019 | 0.037765
Fluoride | 0.9081 |  | 0.3244 | 0.50805
Sulfate | 25.7 |  | 21.9 | 23.8
Iron | 0.006 |  | 0.006 | 0.006
Manganes | 0.033 |  | 0.033 | 0.033
pH | 7.6367 |  | 7.1467 | 7.3234
Color | 1.3333 |  | 1 | 1.0222
Chloride | 12.6 |  | 11.3 | 11.95
TOC | 2.51 |  | 2.51 | 2.51
Chloramine | Avg |  |  | #REF!
Choramine RAA |  |  |  | #REF!
T-phosph |  |  |  | 0.6905
o-phosph |  |  |  | 0.0445
Aluminum |  |  |  | 0.033667
TOC Ratio |  |  |  | #REF!
TOC % Removal |  |  |  | #REF!

## LAB
DAILY LAB SHEET
2019-01-01
| RAW | [13 empty] | Filtered #1 |  |  |  | Filtered #2 |  |  |  | Filtered #3 |  |  |  | Treated #1 | Treated #2 | Treated #3 | Settled #1 | [11 empty] | Settled #2 | [11 empty] | Settled #3 | [12 empty] | Finished Plant #1 | [16 empty] | Finished Plant #2
| pH | Temp | Alk | DO | TOC | DOC | UV-254 | SUVA | Factor | Low | High | Total Coliform | E. coli | Temp. °C | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | Mn | Color | Turbidity | Free Cl-2 | pH | pH | pH | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Mn | Fe | Al | pH | Temp | Color | NTU | TOC | DOC | UV-254 | TOC Percent Removal | SUVA | Settled Water Average TOC | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T | pH | Temp | Color | NTU | Alkalinity | Calcium Hardness | Chloramine | Mn | Fe | Fluoride | T-Phos | O-Phos | TOC | DOC | UV-254 | SUVA | Bac-T |  | Decant Flow | Back Wash Water | Backwash Waste Sludge flow | Alum sludge | Raw
1 | [11 empty] | 52 | <10 | [62 empty] | 0.5124 | [6 empty] | A | [9 empty] | 0.5103 | [6 empty] | A |  | 0.877 | 0 | 0 | 0
2 | [11 empty] | 85 | <10 | [62 empty] | 0.5696 | [6 empty] | A | [9 empty] | 0.5166 | [6 empty] | A |  | 0.705 | 0 | 0 | 0
3 | [11 empty] | 62 | <10 | [62 empty] | 0.5103 | [6 empty] | A | [9 empty] | 0.5082 | [6 empty] | A |  | 0.825 | 0 | 0 | 0
4 | [11 empty] | 122 | <10 | [62 empty] | 0.498 | [6 empty] | A | [9 empty] | 0.4884 | [6 empty] | A |  | 0.867 | 0 | 0 | 0
5 | [11 empty] | 20 | <10 | [62 empty] | 0.6372 | [6 empty] | A | [9 empty] | 0.6732 | [6 empty] | A |  | 1.093 | 0 | 0 | 0
6 | [11 empty] | 75 | <10 | [62 empty] | 0.4479 | [6 empty] | A | [9 empty] | 0.4318 | [6 empty] | A |  | 0.651 | 0 | 0 | 0
7 | [11 empty] | 31 | 10 | [62 empty] | 0.579 | [6 empty] | A | [9 empty] | 0.5559 | [6 empty] | A |  | 0.869 | 0 | 0 | 0
8 | 6.57 | 15.9 | [9 empty] | 31 | <10 |  |  | 2 | 0.083 | 0.41 |  | 1 | 0.056 | 0.25 |  | 1 | 0.058 | 0.31 | 5.84 | 5.92 | 5.97 |  |  |  | 6.14 | 14.7 | 5 | 0.401 | [8 empty] | 6.16 | 15.2 | 5 | 0.384 | [8 empty] | 6.18 | 16.1 | 5 | 0.376 | [6 empty] | 7.42 | 15 | 2 | 0.059 | 24 | 72 | 4.1 |  |  | 0.5691 | [6 empty] | A | 7.34 | 15.9 | 2 | 0.06 | 25 | 62 | 4 |  |  | 0.5532 | [6 empty] | A |  | 0.9 | 0 | 0 | 0
9 | 6.52 | 16.2 | [9 empty] | 31 | <10 |  |  | 3 | 0.064 | 0.39 |  | 3 | 0.06 | 0.29 |  | 3 | 0.066 | 0.44 | 6.01 | 5.99 | 6.01 |  |  |  | 6.12 | 15.1 | 9 | 0.531 | [8 empty] | 6.16 | 15.7 | 8 | 0.449 | [8 empty] | 6.15 | 16.8 | 6 | 0.332 | [6 empty] | 7.36 | 14.7 | 3 | 0.061 | 25 | 70 | 4.1 |  |  | 0.5372 | [6 empty] | A | 7.36 | 15.3 | 3 | 0.064 | 23 | 65 | 4.1 |  |  | 0.5243 | [6 empty] | A |  | 0.96 | 0 | 0 | 0
10 | 6.63 | 15.2 | 22 |  | 11.14 | 11.4 | 0.529 | 4.64 | 21.5501 | 107.7505 | 215.5009 | 63 | <10 |  |  | 3 | 0.064 | 0.24 |  | 2 | 0.057 | 0.28 |  | 3 | 0.064 | 0.34 | 5.98 | 5.99 | 5.94 |  |  |  | 6.11 | 14.6 | 7 | 0.456 | 2.97 | 2.846 | 0.05 | 73.3393 | 1.7569 |  |  |  | 6.13 | 14.7 | 7 | 0.488 | 2.938 | 2.8 | 0.049 | 73.6266 | 1.75 |  |  |  | 6.14 | 15.9 | 7 | 0.447 | 2.936 | 2.833 | 0.049 | 73.6445 | 1.7296 | 2.948 | 7.38 | 13.6 | 2 | 0.055 | 24 | 70 | 4.1 |  |  | 0.597 |  |  | 2.844 | 2.828 | 0.071 | 2.5106 | A | 7.4 | 14.3 | 3 | 0.073 | 25 | 63 | 4.3 |  |  | 0.5494 |  |  | 2.819 | 2.798 | 0.07 | 2.5018 | A |  | 0.884 | 0 | 0 | 0
11 | 6.61 | 14.3 | [9 empty] | 63 | <10 |  |  | 2 | 0.056 | 0.5 |  | 2 | 0.064 | 0.64 |  | 2 | 0.055 | 0.45 | 6.03 | 6.01 | 5.97 |  |  |  | 6.14 | 13.6 | 6 | 0.415 | [8 empty] | 6.17 | 13.7 | 7 | 0.492 | [8 empty] | 6.15 | 14.9 | 6 | 0.399 | [6 empty] | 7.47 | 12.5 | 2 | 0.058 | 24 | 66 | 4.5 |  |  | 0.5974 | [6 empty] | A | 7.46 | 13.9 | 3 | 0.068 | 25 | 60 | 4.4 |  |  | 0.5621 | [6 empty] | A |  | 0.821 | 0 | 0 | 0
12 | [11 empty] | 109 | 10 | [62 empty] | 0.5541 | [6 empty] | A | [9 empty] | 0.4494 | [6 empty] | A |  | 0.914 | 0 | 0 | 0
13 | [11 empty] | 85 | 10 | [62 empty] | 0.6533 | [6 empty] | A | [9 empty] | 0.4624 | [6 empty] | A |  | 1.065 | 0 | 0 | 0
14 | 6.74 | 12.5 | 23 |  | 11.21 | 11.03 | 0.528 | 4.787 | 20.8902 | 104.4508 | 208.9015 | 95 | 41 |  |  | 3 | 0.061 | 0.4 |  | 3 | 0.059 | 0.42 |  | 4 | 0.072 | 0.59 | 5.99 | 6.01 | 5.98 |  |  |  | 6.04 | 12.5 | 8 | 0.509 | 2.869 | 2.746 | 0.047 | 74.4068 | 1.7116 |  |  |  | 6.06 | 12.3 | 8 | 0.475 | 2.819 | 2.719 | 0.047 | 74.8528 | 1.7286 |  |  |  | 6.07 | 13.6 | 10 | 0.601 | 2.881 | 2.761 | 0.047 | 74.2997 | 1.7023 | 2.8563 | 7.37 | 11.4 | 3 | 0.055 | 24 | 57 | 4.6 |  |  | 0.6022 |  |  | 2.76 | 2.715 | 0.07 | 2.5783 | A | 8.24 | 12.4 | 4 | 0.061 | 29 | 53 | 7.1 |  |  | 0.9081 |  |  | 2.77 | 2.712 | 0.075 | 2.7655 | A |  | 0.895 | 0 | 0 | 0
15 | 6.75 | 12 | [9 empty] | 85 | 10 |  |  | 2 | 0.059 | 0.43 |  | 2 | 0.056 | 0.34 |  | 2 | 0.052 | 0.6 | 5.85 | 5.98 | 5.97 |  |  |  | 6.07 | 11.6 | 6 | 0.408 | [8 empty] | 6.06 | 11.7 | 4 | 0.375 | [8 empty] | 6.09 | 12.7 | 6 | 0.472 | [6 empty] | 7.61 | 11.1 | 2 | 0.053 | 24 | 66 | 5.1 |  |  | 0.7202 | [6 empty] | A | 7.32 | 12 | 2 | 0.055 | 23 | 63 | 4.3 |  |  | 0.5507 | [6 empty] | A |  | 1.079 | 0 | 0 | 0
16 | 6.77 | 11.7 | [9 empty] | 187 | 30 |  |  | 2 | 0.054 | 0.4 |  | 2 | 0.05 | 0.83 |  | 2 | 0.06 | 0.58 | 5.91 | 5.95 | 5.93 |  |  |  | 6.05 | 11.2 | 6 | 0.45 | [8 empty] | 6.14 | 12.1 | 5 | 0.346 | [8 empty] | 6.09 | 12.4 | 7 | 0.539 | [6 empty] | 7.44 | 10.8 | 2 | 0.055 | 24 | 60 | 4.7 |  |  | 0.6116 | [6 empty] | A | 7.19 | 11.9 | 2 | 0.056 | 26 | 58 | 4 |  |  | 0.4568 | [6 empty] | A |  | 0.836 | 0 | 0 | 0
17 | 6.74 | 11.7 | 22 |  | 11.09 | 10.72 | 0.526 | 4.907 | 20.3802 | 101.9011 | 203.8023 | 148 | 31 |  |  | 2 | 0.053 | 0.34 |  | 2 | 0.056 | 0.36 |  | 2 | 0.058 | 0.58 | 6.11 | 6.12 | 6.09 |  |  |  | 6.16 | 10.9 | 7 | 0.42 | 2.862 | 2.735 | 0.046 | 74.193 | 1.6819 |  |  |  | 6.22 | 11.7 | 7 | 0.415 | 2.897 | 2.73 | 0.046 | 73.8774 | 1.685 |  |  |  | 6.2 | 12.5 | 7 | 0.478 | 2.853 | 2.791 | 0.046 | 74.2741 | 1.6482 | 2.8707 | 7.38 | 10.4 | 2 | 0.054 | 23 | 60 | 4.1 |  |  | 0.5976 |  |  | 2.711 | 2.713 | 0.067 | 2.4696 | A | 7.27 | 11.6 | 3 | 0.063 | 22 | 62 | 3.9 |  |  | 0.4611 |  |  | 2.71 | 2.711 | 0.062 | 2.287 | A |  | 0.922 | 0 | 0 | 0
18 | 6.75 | 11.7 | [9 empty] | 345 | 41 |  |  | 3 | 0.072 | 0.57 |  | 3 | 0.069 | 0.55 |  | 3 | 0.06 | 0.6 | 5.87 | 5.93 | 5.95 |  |  |  | 6.15 | 11.1 | 8 | 0.519 | [8 empty] | 6.19 | 11.9 | 4 | 0.292 | [8 empty] | 6.2 | 12.7 | 6 | 0.506 | [6 empty] | 7.57 | 10.5 | 2 | 0.055 | 21 | 56 | 4.6 |  |  | 0.5885 | [6 empty] | A | 7.33 | 12 | 2 | 0.056 | 23 | 58 | 3.9 |  |  | 0.3821 | [6 empty] | A |  | 1.115 | 0 | 0 | 0
19 | [11 empty] | 697 | 63 | [62 empty] | 0.6057 | [6 empty] | A | [9 empty] | 0.4854 | [6 empty] | A |  | 1.298 | 0 | 0 | 0
20 | [11 empty] | 602 | 63 | [62 empty] | 0.5461 | [6 empty] | A | [9 empty] | 0.4522 | [6 empty] | A |  | 1.106 | 0 | 0 | 0
21 | 6.83 | 12.1 | 23 |  | 9.737 | 9.271 | 0.431 | 4.649 | 21.5104 | 107.5522 | 215.1044 | 359 | 20 |  |  | 3 | 0.071 | 0.56 |  | 2 | 0.053 | 0.28 |  | 3.086 | 0.64 |  | 6.02 |  | 6 |  |  |  | 6.19 | 11.8 | 6 | 0.467 | 2.615 | 2.497 | 0.043 | 73.1437 | 1.7221 |  |  |  | 6.23 | 12.7 | 4 | 0.308 | 2.555 | 2.465 | 0.043 | 73.7599 | 1.7444 |  |  |  | 6.24 | 13.5 | 6 | 0.482 | 2.624 | 2.497 | 0.041 | 73.0512 | 1.642 | 2.598 | 7.49 | 12.1 | 2 | 0.054 | 24 | 65 | 4 |  |  | 0.5439 |  |  | 2.497 | 2.508 | 0.06 | 2.3923 | A | 7.45 | 11.6 | 2 | 0.06 | 22 | 64 | 3.6 |  |  | 0.3244 |  |  | 2.435 | 2.467 | 0.056 | 2.27 | A |  | 0.962 | 0 | 0 | 0
22 | 6.86 | 10.9 | [9 empty] | 480 | 30 |  |  | 2 | 0.05 | 0.56 |  | 2 | 0.055 | 0.52 |  | 2 | 0.067 | 0.6 | 6.07 |  | 6.03 |  |  |  | 6.18 | 10.9 | 7 | 0.543 | [8 empty] | 6.23 | 12 | 7 | 0.626 | [8 empty] | 6.24 | 12.6 | 10 | 0.68 | [6 empty] | 7.5 | 11 | 2 | 0.056 | 23 | 65 | 4.2 |  |  | 0.6549 | [6 empty] | A | 7.32 | 10.8 | 2 | 0.055 | 25 | 60 | 3.8 |  |  | 0.4096 | [6 empty] | A |  | 1.231 | 0 | 0 | 0
23 | 6.9 | 11 | [9 empty] | 384 | 10 |  |  | 2 | 0.072 | 0.65 |  | 2 | 0.069 | 0.56 |  | 2 | 0.07 | 0.52 | 5.99 | 6.04 | 6.03 |  |  |  | 6.16 | 10.9 | 7 | 0.508 | [8 empty] | 6.28 | 12.1 | 6 | 0.433 | [8 empty] | 6.27 | 12.4 | 8 | 0.576 | [6 empty] | 7.44 | 9.8 | 2 | 0.059 | 27 | 58 | 4.4 |  |  | 0.7141 | [6 empty] | A | 7.37 | 11 | 2 | 0.069 | 24 | 60 | 4 |  |  | 0.5103 | [6 empty] | A |  | 1.178 | 0 | 0 | 0
24 | [11 empty] | 573 | 10 | [62 empty] | 0.5561 | [6 empty] | A | [9 empty] | 0.5145 | [6 empty] | A |  | 1.028 | 0 | 0 | 0
25 | [11 empty] | 480 | 41 | [62 empty] | 0.4899 | [6 empty] | A | [9 empty] | 0.5187 | [6 empty] | A |  | 0.597 | 0 | 0 | 0
26 | [11 empty] | 548 | 10 | [62 empty] | 0.5448 | [6 empty] | A | [9 empty] | 0.5103 | [6 empty] | A |  | 0.936 | 0 | 0 | 0
27 | [11 empty] | 488 | 31 | [62 empty] | 0.7682 | [6 empty] | A | [9 empty] | 0.4741 | [6 empty] | A |  | 1.03 | 0 | 0 | 0
28 | 6.82 | 11.6 | 25 |  | 8.071 | 7.836 | 0.36 | 4.594 | 21.7667 | 108.8333 | 217.6667 | 341 | 31 |  |  | 2 | 0.069 | 0.31 |  | 2 | 0.052 | 0.37 |  | 2 | 0.059 | 0.65 |  | 5.66 | 5.67 |  |  |  | 5.83 | 11.4 | 6 | 0.485 | 2.303 | 2.197 | 0.035 | 71.4657 | 1.5931 |  |  |  | 5.97 | 10.2 | 9 | 0.707 | 2.351 | 2.174 | 0.035 | 70.871 | 1.6099 |  |  |  | 5.98 | 12.3 | 8 | 0.588 | 2.316 | 2.222 | 0.035 | 71.3047 | 1.5752 | 2.3233 | 7.3 | 10.6 | 1 | 0.052 | 24 | 50 | 4.7 |  |  | 0.551 |  |  | 2.177 | 2.178 | 0.059 | 2.7089 | A | 7.1 | 11.7 | 2 | 0.062 | 22 | 45 | 4 |  |  | 0.4626 |  |  | 2.162 | 2.184 | 0.053 | 2.4267 | A |  | 0.742 | 0 | 0 | 0
29 | 6.91 | 11.7 | [9 empty] | 364 | <10 |  |  | 2 | 0.051 | 0.42 |  | 2 | 0.05 | 0.46 |  | 2 | 0.054 | 0.62 |  | 5.89 | 5.88 |  |  |  | 6.02 | 10.8 | 5 | 0.369 | [8 empty] | 6.11 | 10.2 | 7 | 0.554 | [8 empty] | 6.1 | 12.3 | 7 | 0.505 | [6 empty] | 7.46 | 10.6 | 2 | 0.049 | 28 | 57 | 4.6 |  |  | 0.6611 | [6 empty] | A | 7.29 | 11.3 | 2 | 0.048 | 24 | 47 | 4 |  |  | 0.5185 | [6 empty] | A |  | 1.038 | 0 | 0 | 0
30 | 6.29 | 11.4 | [9 empty] | 292 | 10 |  |  | 2 | 0.065 | 0.51 |  | 2 | 0.059 | 0.44 |  | 2 | 0.066 | 0.72 | 6.11 | 6.09 | 6.04 |  |  |  | 6.19 | 10.7 | 5 | 0.331 | [8 empty] | 6.2 | 10.3 | 7 | 0.507 | [8 empty] | 6.19 | 12.3 | 7 | 0.47 | [6 empty] | 7.21 | 10 | 2 | 0.054 | 52 | 45 | 4.5 |  |  | 0.6564 | [6 empty] | A | 7.28 | 10.9 | 2 | 0.055 | 23 | 42 | 4 |  |  | 0.502 | [6 empty] | A |  | 0.925 | 0 | 0 | 0
31 | [11 empty] | 323 | <10 | [62 empty] | 0.7066 | [6 empty] | A | [9 empty] | 0.5229 | [6 empty] | A |  | 1.125 | 0 | 0 | 0
[5 empty] | 10.2496 |  |  | 4.7154 | 21.2195 | 106.0976 | 212.1952 |  |  |  | #DIV/0! | 2.3333 |  |  | #DIV/0! | 2.1333 |  |  | #DIV/0! | 2.3391 | [5 empty] | #DIV/0! | #DIV/0! | [5 empty] | 2.7238 |  |  | 73.3097 |  | #DIV/0! | #DIV/0! | [5 empty] | 2.712 |  |  | 73.3975 |  | #DIV/0! | #DIV/0! | [5 empty] | 2.722 |  |  | 73.3149 |  | 2.7193 | [12 empty] | 2.5978 | [16 empty] | 2.5792 |  |  |  |  | Sum | 29.474 | 0 | 0 | 0
[101 empty] | Max | 1.298 | 0 | 0 | 0
[101 empty] | Avg. | 0.95077 | 0 | 0 | 0
Note on DK37: Sum
Note on DK38: Max
Note on DK39: Avg.

## LAB pH
[5 empty] | pH |  |  |  | Meter: | VSTAS40B2
[9 empty] | Probe: | 8102BNUWP
Date | Time | Analyst | Slope | Std. | Lot Number | Sample ID | QC | Temp | PH | Comments
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
SETTLED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | Dup.
# 2
|  |  |  | 10 | 156700
|  |  |  | 7 | 156652
|  |  |  | 4 | 155559
|  |  |  | 10 | 156700
BLANK
|  |  |  | 7 | 156652
TREATED # 1
# 2
# 3
FINISHED # 1
[6 empty] | # 1 | D
# 2
SETTLED # 1
# 2
# 3
|  |  |  | 10 | 156700